LV Distribution Network — Cable Sizing & Voltage Drop

BS 7671:2018+A2:2022

Worst 3.55% at db-l10-ac — COMPLIANT

| Project Information |  |
| --- | --- |
| Project Name | Marina Commercial Tower |
| Project No. | MCT-2026-MEP-001 |
| Revision | P2 |
| Client | — |
| Prepared by | Hussein Ragab |
| Checked by | — |
| Date | 2026-10-20 |

Values in this report are displayed in SI (metric) units.  Conductor sizes are the BS 7671 metric series (mm2) and never unit-converted.

# 1.  Methodology

The network is a radial forest: one or more sources, with every panel fed by exactly one feeder and tracing to exactly one source, so two main boards are independent trees in one network (no tie or bus-coupler is modelled). Cumulative drop is referenced to each panel's OWN source. Loads aggregate leaf to root in apparent power with an engineer-entered diversity factor per panel; the protective device and cable on each feeder are sized from the diversified maximum-demand current Ib by default - an AHJ profile may switch the device and/or cable basis onto the total-connected current, and a panel rule may raise it (the next rating at or above the basis on the ruled ladder: BS EN 60898-1 # 5.3.2 preferred ratings 6 A to 125 A (8 A and 13 A omitted by ruling); 160 A to 1600 A per BS EN 60059 clause 3 standard current ratings (R10 series); BS 7671 applies no continuous-load factor) and the voltage drop is computed at the diversified maximum-demand current. Each cable feeder is sized by the single-circuit BS chain of this tool (Tables 4E4A/4D2A tabulated capacity with the 4B1 and 4C1 rating factors, mV/A/m voltage drop from Tables 4E4B/4D2B, circuit protective conductor by Table 54.7 with the Regulation 543.1.1 minimum for a separate conductor). Busway segments use the manufacturer's nameplate rating and R/X in ohm/km (equal to mohm/m) as entered, with the bar's protection kept within the manufacturer nameplate, each tap given its own tap-off device on its own basis (ruling D117), and the drop walked segment by segment as the current diminishes past each tap. The cumulative drop is carried down the tree as a PERCENTAGE referenced to each board's own nominal voltage and checked against the total limit; per-stage allocations are advisory design targets only.

# 2.  Inputs

| Parameter | Value |
| --- | --- |
| Source panel | MDB-01 |
| Panels / feeders | 10 / 9 |
| Power factor | 0.90 |
| Continuous loads | not applicable (BS 7671 — no 1.25 continuous factor) |
| Total VD limit | 4 % (advisory basis) |
| Stage targets | none — total only |

# 3.  Assumptions

mV/A/m voltage-drop values are the BS 7671 Appendix 4 printed values (Tables 4E4B/4D2B) at the conductor maximum operating temperature.

Voltage-drop limits (3% lighting / 5% other) are the deemed-to-satisfy values of Regulation 525.202 via Appendix 4 section 6.4, Table 4Ab (installations supplied directly from a public LV distribution system; the private-supply row 6% / 8% is not offered) — a project specification may govern.

Table 4Ab (printed p.430) permits its limits to be increased by 0.005% per metre of wiring beyond 100 m, at most by 0.5%; the tool keeps the target as set and warns, naming the permitted figure, when a run or path longer than 100 m is judged against a printed Table 4Ab value (ruling D121).

Parallel runs are assumed to share the current equally; the tabulated capacity and voltage drop are taken per run, and the runs are counted into the Table 4C1 group as touching cables (Table 4C1 NOTE 2 spacing is not modelled; ruling D118).

Neutral conductors, where reported, are sized equal to the phase conductors; the circuit protective conductor follows the Table 54.7 selection rule in the same material and, as a separate G/Y single ASSUMED mechanically protected (in conduit or trunking), is never below 2.5 mm2 (Regulation 543.1.1, printed p.199; 4 mm2 applies where it is not protected; ruling D115).

Rating factors applied: Ca (Table 4B1, air), Cg (Table 4C1) and — where a run is DECLARED totally surrounded by thermal insulation — Ci per Regulation 523.9 and Appendix 4 item 2.6 (0.5 x the Method C rating at 0.5 m or more). A route in insulation that is not declared is not derated: declaring it is the designer's input.

Automatic disconnection (fault protection) is NOT verified: the earth fault loop impedance Zs x Ia <= U0 x Cmin of Regulation 411.4.4 (printed p.66) and the disconnection time of Regulation 411.3.2.2 need the external loop impedance Ze and the device's maximum Zs, which this tool does not hold - verify them separately (ruling C057).

Fault levels are computed ONLY where a source declares its prospective fault level (simple-method reactive source; 3-phase symmetrical estimate with U = V_LN on 3-phase boards; a single-phase source or board takes U = its own nominal). Two currents are reported per board (ruling 37-3): Ipf,max with the conductor resistance at 20 degC (IET On-Site Guide Appendix I Table I1; Table I3 multipliers above its printed range) - the basis for device breaking capacity, bus withstand and the adiabatic check - and Ipf,min at maximum operating temperature (the Appendix 4 mV/A/m tables) - the disconnection-time basis, printed for reference; earth-fault loop impedance is not verified. Busway R/X are catalogue values at Ith in both.

The adiabatic CPC check (Reg 543.1.3) uses Ipf,max at the fed board, the entered duration and k by the CPC's OWN insulation as entered in Network settings (ruling 37-4): a separate conductor bunched with the cable takes Table 54.3 - 70 degC thermoplastic k 115 / 103 above 300 mm2 (the default), 90 degC thermosetting k 143; a separate conductor NOT bunched takes Table 54.2 - 70 degC thermoplastic k 143 / 133 above 300 mm2, 90 degC thermosetting k 176 (printed p.200); an integral core of the cable takes the cable's own insulation (Table 54.3). Where the check upsizes the CPC, k is re-read at the new size (the thermoplastic k drops above 300 mm2), and a CPC no standard size can cover FAILS. A separate CPC is a G/Y single ASSUMED mechanically protected (in conduit or trunking) and is never below 2.5 mm2 (Reg 543.1.1, printed p.199; 4 mm2 if not protected; ruling D115). Steel-wire armour as CPC (ruling 37-6) takes k = 46 from Table 54.4 (90 C thermosetting steel, printed p.200) and the armour CSA from BS 5467:1997+A3:2008 Table N.2 (printed p.29). Armour cannot be upsized; if N.2 is short of S_min the feeder FAILS. PVC (Table 4D2A) is non-armoured and refuses that option.

Busway nameplate ratings and impedances are manufacturer data as entered — cite the datasheet in the submission.

Voltage-drop limits are the deemed-to-satisfy values (3% lighting / 5% other, Regulation 525.202 via Appendix 4 section 6.4 Table 4Ab, public LV supply row) unless a project specification or authority imposes its own.

# 4.  Step-by-Step Calculation

Step 1: Load aggregation — DB-POD-RT1

Formula: TCL = own + sum(children); demand = (own + sum children demand) x div

Substitution: TCL = 33.33 kVA; demand = 33.33 kVA (div 1.0) [NETWORK_MODE_PLAN.md #3.2 (per-panel diversity, ruling 2)]

Result: 33.333 kVA

Step 2: Load aggregation — DB-POD-KIT

Formula: TCL = own + sum(children); demand = (own + sum children demand) x div

Substitution: TCL = 50.00 kVA; demand = 50.00 kVA (div 1.0) [NETWORK_MODE_PLAN.md #3.2 (per-panel diversity, ruling 2)]

Result: 50.0 kVA

Step 3: Load aggregation — SMDB-POD

Formula: TCL = own + sum(children); demand = (own + sum children demand) x div

Substitution: TCL = 83.33 kVA; demand = 66.67 kVA (div 0.8) [NETWORK_MODE_PLAN.md #3.2 (per-panel diversity, ruling 2)]

Result: 66.667 kVA

Step 4: Load aggregation — DB-L10-LP

Formula: TCL = own + sum(children); demand = (own + sum children demand) x div

Substitution: TCL = 31.11 kVA; demand = 31.11 kVA (div 1.0) [NETWORK_MODE_PLAN.md #3.2 (per-panel diversity, ruling 2)]

Result: 31.111 kVA

Step 5: Load aggregation — DB-L10-AC

Formula: TCL = own + sum(children); demand = (own + sum children demand) x div

Substitution: TCL = 17.78 kVA; demand = 17.78 kVA (div 1.0) [NETWORK_MODE_PLAN.md #3.2 (per-panel diversity, ruling 2)]

Result: 17.778 kVA

Step 6: Load aggregation — SMDB-L10

Formula: TCL = own + sum(children); demand = (own + sum children demand) x div

Substitution: TCL = 48.89 kVA; demand = 39.11 kVA (div 0.8) [NETWORK_MODE_PLAN.md #3.2 (per-panel diversity, ruling 2)]

Result: 39.111 kVA

Step 7: Load aggregation — DB-RF-AHU

Formula: TCL = own + sum(children); demand = (own + sum children demand) x div

Substitution: TCL = 61.11 kVA; demand = 61.11 kVA (div 1.0) [NETWORK_MODE_PLAN.md #3.2 (per-panel diversity, ruling 2)]

Result: 61.111 kVA

Step 8: Load aggregation — DB-RF-PMP

Formula: TCL = own + sum(children); demand = (own + sum children demand) x div

Substitution: TCL = 24.44 kVA; demand = 24.44 kVA (div 1.0) [NETWORK_MODE_PLAN.md #3.2 (per-panel diversity, ruling 2)]

Result: 24.444 kVA

Step 9: Load aggregation — SMDB-RF

Formula: TCL = own + sum(children); demand = (own + sum children demand) x div

Substitution: TCL = 85.56 kVA; demand = 72.72 kVA (div 0.85) [NETWORK_MODE_PLAN.md #3.2 (per-panel diversity, ruling 2)]

Result: 72.722 kVA

Step 10: Load aggregation — MDB-01

Formula: TCL = own + sum(children); demand = (own + sum children demand) x div

Substitution: TCL = 217.78 kVA; demand = 160.65 kVA (div 0.9) [NETWORK_MODE_PLAN.md #3.2 (per-panel diversity, ruling 2)]

Result: 160.65 kVA

Step 11: Feeder sizing — MDB-01 -> SMDB-POD

Formula: base engine on the demand basis (breaker basis demand, cable basis demand); VD at the demand current

Substitution: demand 66.7 kVA -> 1 x 35, OCPD 100 A; TCL 83.3 kVA; VD current 96.2 A (demand 66.7 kVA) -> VD 1.053 % [size_circuit (BS 7671 Appendix 4) + Tables 4E4B/4D2B mV/A/m; TCL/demand split per plan #2]

Result: 1.053 %

Step 12: Feeder sizing — SMDB-POD -> DB-POD-RT1

Formula: base engine on the demand basis (breaker basis demand, cable basis demand); VD at the demand current

Substitution: demand 33.3 kVA -> 1 x 10, OCPD 50 A; TCL 33.3 kVA; VD current 48.1 A (demand 33.3 kVA) -> VD 1.684 % [size_circuit (BS 7671 Appendix 4) + Tables 4E4B/4D2B mV/A/m; TCL/demand split per plan #2]

Result: 1.684 %

Step 13: Feeder sizing — SMDB-POD -> DB-POD-KIT

Formula: base engine on the demand basis (breaker basis demand, cable basis demand); VD at the demand current

Substitution: demand 50.0 kVA -> 1 x 25, OCPD 80 A; TCL 50.0 kVA; VD current 72.2 A (demand 50.0 kVA) -> VD 0.677 % [size_circuit (BS 7671 Appendix 4) + Tables 4E4B/4D2B mV/A/m; TCL/demand split per plan #2]

Result: 0.677 %

Step 14: Feeder sizing — MDB-01 -> SMDB-L10

Formula: base engine on the demand basis (breaker basis demand, cable basis demand); VD at the demand current

Substitution: demand 39.1 kVA -> 1 x 16, OCPD 63 A; TCL 48.9 kVA; VD current 56.5 A (demand 39.1 kVA) -> VD 1.941 % [size_circuit (BS 7671 Appendix 4) + Tables 4E4B/4D2B mV/A/m; TCL/demand split per plan #2]

Result: 1.941 %

Step 15: Feeder sizing — SMDB-L10 -> DB-L10-LP

Formula: base engine on the demand basis (breaker basis demand, cable basis demand); VD at the demand current

Substitution: demand 31.1 kVA -> 1 x 10, OCPD 50 A; TCL 31.1 kVA; VD current 44.9 A (demand 31.1 kVA) -> VD 0.898 % [size_circuit (BS 7671 Appendix 4) + Tables 4E4B/4D2B mV/A/m; TCL/demand split per plan #2]

Result: 0.898 %

Step 16: Feeder sizing — SMDB-L10 -> DB-L10-AC

Formula: base engine on the demand basis (breaker basis demand, cable basis demand); VD at the demand current

Substitution: demand 17.8 kVA -> 1 x 4, OCPD 32 A; TCL 17.8 kVA; VD current 25.7 A (demand 17.8 kVA) -> VD 1.604 % [size_circuit (BS 7671 Appendix 4) + Tables 4E4B/4D2B mV/A/m; TCL/demand split per plan #2]

Result: 1.604 %

Step 17: Feeder sizing — MDB-01 -> SMDB-RF

Formula: base engine on the demand basis (breaker basis demand, cable basis demand); VD at the demand current

Substitution: demand 72.7 kVA -> 1 x 50, OCPD 125 A; TCL 85.6 kVA; VD current 105.0 A (demand 72.7 kVA) -> VD 2.076 % [size_circuit (BS 7671 Appendix 4) + Tables 4E4B/4D2B mV/A/m; TCL/demand split per plan #2]

Result: 2.076 %

Step 18: Feeder sizing — SMDB-RF -> DB-RF-AHU

Formula: base engine on the demand basis (breaker basis demand, cable basis demand); VD at the demand current

Substitution: demand 61.1 kVA -> 1 x 35, OCPD 100 A; TCL 61.1 kVA; VD current 88.2 A (demand 61.1 kVA) -> VD 0.482 % [size_circuit (BS 7671 Appendix 4) + Tables 4E4B/4D2B mV/A/m; TCL/demand split per plan #2]

Result: 0.482 %

Step 19: Feeder sizing — SMDB-RF -> DB-RF-PMP

Formula: base engine on the demand basis (breaker basis demand, cable basis demand); VD at the demand current

Substitution: demand 24.4 kVA -> 1 x 6, OCPD 40 A; TCL 24.4 kVA; VD current 35.3 A (demand 24.4 kVA) -> VD 0.900 % [size_circuit (BS 7671 Appendix 4) + Tables 4E4B/4D2B mV/A/m; TCL/demand split per plan #2]

Result: 0.9 %

# 5.  Results

Feeder schedule — one row per feeder (runs x cores x size designation; ECC one per run; the VD figure column shows the value the calculation used; * = engineer override, see the per-feeder blocks).

| Fed From | Fed To | TCL (kW) | Load Current (A) | Breaker (A) | Length (m) | Cable / Bus | Runs | ECC | Type | mV/A/m | Seg VD (V) | Seg VD (%) | Cum VD (V) | Cum VD (%) | Ipf max/min (kA) | Check |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| MDB-01 | SMDB-POD | 75.0 | 96.2 | 100 | 40.0 | 1x4C 35 | 1 | 1x1C 16 | XLPE/SWA/LSZH | 1.09 | 4.21 | 1.05 | 4.21 | 1.05 | - | ok |
| SMDB-POD | DB-POD-RT1 | 30.0 | 48.1 | 50 | 35.0 | 1x4C 10 | 1 | 1x1C 10 | XLPE/SWA/LSZH | 4.00 | 6.74 | 1.68 | 10.95 | 2.74 | - | ok |
| SMDB-POD | DB-POD-KIT | 45.0 | 72.2 | 80 | 25.0 | 1x4C 25 | 1 | 1x1C 16 | XLPE/SWA/LSZH | 1.50 | 2.71 | 0.68 | 6.92 | 1.73 | - | ok |
| MDB-01 | SMDB-L10 | 44.0 | 56.5 | 63 | 55.0 | 1x4C 16 | 1 | 1x1C 16 | XLPE/SWA/LSZH | 2.50 | 7.76 | 1.94 | 7.76 | 1.94 | - | ok |
| SMDB-L10 | DB-L10-LP | 28.0 | 44.9 | 50 | 20.0 | 1x4C 10 | 1 | 1x1C 10 | XLPE/SWA/LSZH | 4.00 | 3.59 | 0.90 | 11.36 | 2.84 | - | ok |
| SMDB-L10 | DB-L10-AC | 16.0 | 25.7 | 32 | 25.0 | 1x4C 4 | 1 | 1x1C 4 | XLPE/SWA/LSZH | 10.0 | 6.42 | 1.60 | 14.18 | 3.55 | - | ok |
| MDB-01 | SMDB-RF | 77.0 | 105.0 | 125 | 95.0 | 1x4C 50 | 1 | 1x1C 25 | XLPE/SWA/LSZH | 0.83 | 8.30 | 2.08 | 8.30 | 2.08 | - | ok |
| SMDB-RF | DB-RF-AHU | 55.0 | 88.2 | 100 | 20.0 | 1x4C 35 | 1 | 1x1C 16 | XLPE/SWA/LSZH | 1.09 | 1.93 | 0.48 | 10.23 | 2.56 | - | ok |
| SMDB-RF | DB-RF-PMP | 22.0 | 35.3 | 40 | 15.0 | 1x4C 6 | 1 | 1x1C 6 | XLPE/SWA/LSZH | 6.80 | 3.60 | 0.90 | 11.90 | 2.98 | - | ok |

Per-feeder detail

MDB-01 → SMDB-POD

| Parameter | Value |
| --- | --- |
| Feeder | 1x4C 35 |
| Type | XLPE/SWA/LSZH |
| Breaker / CPC (Table 54.7) | 100 A / 1x1C 16 mm2 |
| TCL / demand current | 120.3 A (75.0 kW) / 96.2 A |
| Segment / cumulative VD | 1.05 % (4.21 V) / 1.05 % (4.21 V) [ok] |
| VD figure (mV/A/m) | 1.09 |

SMDB-POD → DB-POD-RT1

| Parameter | Value |
| --- | --- |
| Feeder | 1x4C 10 |
| Type | XLPE/SWA/LSZH |
| Breaker / CPC (Table 54.7) | 50 A / 1x1C 10 mm2 |
| TCL / demand current | 48.1 A (30.0 kW) / 48.1 A |
| Segment / cumulative VD | 1.68 % (6.74 V) / 2.74 % (10.95 V) [ok] |
| VD figure (mV/A/m) | 4.00 |

SMDB-POD → DB-POD-KIT

| Parameter | Value |
| --- | --- |
| Feeder | 1x4C 25 |
| Type | XLPE/SWA/LSZH |
| Breaker / CPC (Table 54.7) | 80 A / 1x1C 16 mm2 |
| TCL / demand current | 72.2 A (45.0 kW) / 72.2 A |
| Segment / cumulative VD | 0.68 % (2.71 V) / 1.73 % (6.92 V) [ok] |
| VD figure (mV/A/m) | 1.50 |

MDB-01 → SMDB-L10

| Parameter | Value |
| --- | --- |
| Feeder | 1x4C 16 |
| Type | XLPE/SWA/LSZH |
| Breaker / CPC (Table 54.7) | 63 A / 1x1C 16 mm2 |
| TCL / demand current | 70.6 A (44.0 kW) / 56.5 A |
| Segment / cumulative VD | 1.94 % (7.76 V) / 1.94 % (7.76 V) [ok] |
| VD figure (mV/A/m) | 2.50 |

SMDB-L10 → DB-L10-LP

| Parameter | Value |
| --- | --- |
| Feeder | 1x4C 10 |
| Type | XLPE/SWA/LSZH |
| Breaker / CPC (Table 54.7) | 50 A / 1x1C 10 mm2 |
| TCL / demand current | 44.9 A (28.0 kW) / 44.9 A |
| Segment / cumulative VD | 0.90 % (3.59 V) / 2.84 % (11.36 V) [ok] |
| VD figure (mV/A/m) | 4.00 |

SMDB-L10 → DB-L10-AC

| Parameter | Value |
| --- | --- |
| Feeder | 1x4C 4 |
| Type | XLPE/SWA/LSZH |
| Breaker / CPC (Table 54.7) | 32 A / 1x1C 4 mm2 |
| TCL / demand current | 25.7 A (16.0 kW) / 25.7 A |
| Segment / cumulative VD | 1.60 % (6.42 V) / 3.55 % (14.18 V) [ok] |
| VD figure (mV/A/m) | 10.0 |

MDB-01 → SMDB-RF

| Parameter | Value |
| --- | --- |
| Feeder | 1x4C 50 |
| Type | XLPE/SWA/LSZH |
| Breaker / CPC (Table 54.7) | 125 A / 1x1C 25 mm2 |
| TCL / demand current | 123.5 A (77.0 kW) / 105.0 A |
| Segment / cumulative VD | 2.08 % (8.30 V) / 2.08 % (8.30 V) [ok] |
| VD figure (mV/A/m) | 0.83 |

SMDB-RF → DB-RF-AHU

| Parameter | Value |
| --- | --- |
| Feeder | 1x4C 35 |
| Type | XLPE/SWA/LSZH |
| Breaker / CPC (Table 54.7) | 100 A / 1x1C 16 mm2 |
| TCL / demand current | 88.2 A (55.0 kW) / 88.2 A |
| Segment / cumulative VD | 0.48 % (1.93 V) / 2.56 % (10.23 V) [ok] |
| VD figure (mV/A/m) | 1.09 |

SMDB-RF → DB-RF-PMP

| Parameter | Value |
| --- | --- |
| Feeder | 1x4C 6 |
| Type | XLPE/SWA/LSZH |
| Breaker / CPC (Table 54.7) | 40 A / 1x1C 6 mm2 |
| TCL / demand current | 35.3 A (22.0 kW) / 35.3 A |
| Segment / cumulative VD | 0.90 % (3.60 V) / 2.98 % (11.90 V) [ok] |
| VD figure (mV/A/m) | 6.80 |

# 6.  Notes

⚠ Advisory

• Voltage-drop limits (3% lighting / 5% other) are the deemed-to-satisfy values of Regulation 525.202 (printed p.148) via Appendix 4 section 6.4, Table 4Ab p.430 (public LV supply row; the private-supply 6% / 8% row is not offered) — the project may impose stricter limits.

• mV/A/m values are the Appendix 4 printed values at the conductor maximum operating temperature.

• Rating factors Ca (Table 4B1), Cg (Table 4C1) and — where a run is declared totally surrounded by thermal insulation — Ci (Regulation 523.9 printed p.146 / Appendix 4 item 2.6 printed p.423). An undeclared insulated route is not derated; declaring it is the designer's input.

# R.  Reference Standards

BS 7671:2018+A2:2022 — Appendix 4 Tables 4E4A/4E4B, 4D2A/4D2B, 4B1, 4C1; Table 54.7

Cable Sizer & Voltage Drop — Hussein Ragab