## Network Schedule
LV DISTRIBUTION NETWORK · BS 7671:2018+A2:2022
Total VD limit 4% · worst 3.55% at DB-L10-AC · COMPLIANT
Project: Marina Commercial Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: - ¦ By: Hussein Ragab ¦ Chkd: - ¦ Rev: P2 ¦ Date: 2026-10-20
Units: SI ¦ conductor sizes are the BS 7671 metric series (mm2) and never unit-converted
Fed From | Fed To | TCL (kW) | Load Current (A) | Breaker (A) | Length (m) | Cable / Bus | Runs | ECC | Type | mV/A/m | Seg VD (V) | Seg VD (%) | Cum VD (V) | Cum VD (%) | Ipf max/min (kA) | Check
MDB-01 | SMDB-POD | 75.0 | 96.2 | 100 | 40.0 | 1x4C 35 | 1 | 1x1C 16 | XLPE/SWA/LSZH | 1.09 | 4.21 | 1.05 | 4.21 | 1.05 | - | ok
SMDB-POD | DB-POD-RT1 | 30.0 | 48.1 | 50 | 35.0 | 1x4C 10 | 1 | 1x1C 10 | XLPE/SWA/LSZH | 4.00 | 6.74 | 1.68 | 10.95 | 2.74 | - | ok
SMDB-POD | DB-POD-KIT | 45.0 | 72.2 | 80 | 25.0 | 1x4C 25 | 1 | 1x1C 16 | XLPE/SWA/LSZH | 1.50 | 2.71 | 0.68 | 6.92 | 1.73 | - | ok
MDB-01 | SMDB-L10 | 44.0 | 56.5 | 63 | 55.0 | 1x4C 16 | 1 | 1x1C 16 | XLPE/SWA/LSZH | 2.50 | 7.76 | 1.94 | 7.76 | 1.94 | - | ok
SMDB-L10 | DB-L10-LP | 28.0 | 44.9 | 50 | 20.0 | 1x4C 10 | 1 | 1x1C 10 | XLPE/SWA/LSZH | 4.00 | 3.59 | 0.90 | 11.36 | 2.84 | - | ok
SMDB-L10 | DB-L10-AC | 16.0 | 25.7 | 32 | 25.0 | 1x4C 4 | 1 | 1x1C 4 | XLPE/SWA/LSZH | 10.0 | 6.42 | 1.60 | 14.18 | 3.55 | - | ok
MDB-01 | SMDB-RF | 77.0 | 105.0 | 125 | 95.0 | 1x4C 50 | 1 | 1x1C 25 | XLPE/SWA/LSZH | 0.83 | 8.30 | 2.08 | 8.30 | 2.08 | - | ok
SMDB-RF | DB-RF-AHU | 55.0 | 88.2 | 100 | 20.0 | 1x4C 35 | 1 | 1x1C 16 | XLPE/SWA/LSZH | 1.09 | 1.93 | 0.48 | 10.23 | 2.56 | - | ok
SMDB-RF | DB-RF-PMP | 22.0 | 35.3 | 40 | 15.0 | 1x4C 6 | 1 | 1x1C 6 | XLPE/SWA/LSZH | 6.80 | 3.60 | 0.90 | 11.90 | 2.98 | - | ok
Reference standards
Reference | Application
BS 7671:2018+A2:2022 | Appendix 4 Tables 4E4A/4E4B, 4D2A/4D2B, 4B1, 4C1; Table 54.7
Notes
Voltage-drop limits (3% lighting / 5% other) are the deemed-to-satisfy values of Regulation 525.202 (printed p.148) via Appendix 4 section 6.4, Table 4Ab p.430 (public LV supply row; the private-supply 6% / 8% row is not offered) — the project may impose stricter limits.
mV/A/m values are the Appendix 4 printed values at the conductor maximum operating temperature.
Rating factors Ca (Table 4B1), Cg (Table 4C1) and — where a run is declared totally surrounded by thermal insulation — Ci (Regulation 523.9 printed p.146 / Appendix 4 item 2.6 printed p.423). An undeclared insulated route is not derated; declaring it is the designer's input.