Clean Agent System — NFPA 2001 Sizing

Total Flooding Quantity Calculation

Mass, cylinder count, design concentration

| Project Information |  |
| --- | --- |
| Project Name | Test Tower |
| Project No. | MCT-2026-MEP-001 |
| Revision | P2 |
| Client | Test Dev |
| Prepared by | Hussein Ragab |
| Checked by | Principal MEP Review |
| Date | 2026-09-02 |

Values in this report are displayed in SI (metric) units.

# 1.  Methodology & Standards

| Reference | Application |
| --- | --- |
| NFPA 2001 (2022 ed.) | Standard on Clean Agent Fire Extinguishing Systems — total flooding design, quantity, distribution, hold time. |

# 2.  Design Inputs

| Parameter | Value |
| --- | --- |
| Agent | FK-5-1-12 |
| Hazard class | Class C |
| Gross volume V | 187.49 m³ |
| Net volume V_net | 179.09 m³ |
| Design temperature | 20.0 °C |
| Max expected temperature | 40.0 °C |
| Altitude | 5 m |
| Piping tees (design factor count) | tees 4 → factor 0.00 (Table 7.3.3.1) |
| Additional ΣDF | 0.00 (# 7.3.3.2) |

# 3.  Design Assumptions

Enclosure is sealed to the integrity required by NFPA # 7.1.

Listed nozzles and hydraulic flow software per UL 2127 / UL 2166 shall be used for pipe routing — not calculated here.

Sized to NFPA 2001 (2022 ed.). ISO 14520-1 / EN 15004-1 use the same flooding equations; EN applies a flat Class A safety factor of 1.3 and a different altitude-correction table.

# 4.  Step-by-Step Calculation

Step 1: Atmospheric correction factor (system-wide)

Formula: ACF = f(altitude) per Table 7.3.3.3

Substitution: altitude = 5 m

Result: 0.999

Note: Interpolated within NFPA tabulated range.

Step 2: [LV-B1-01] Net protected volume

Formula: V_net = V_gross − V_displaced

Substitution: 187.49 − 8.40

Result: 179.09 m³

Note: NFPA 2001 # 7.3.1 — gross enclosure minus impervious structures.

Step 3: [LV-B1-01] Design concentration

Formula: C_design = max(MEC × SF, NFPA published min-design floor)

Substitution: hazard=Class C, actuation=auto, SF=1.35, MEC=3.3

Result: 4.50 vol-%

Note: NFPA-published Class C design conc 4.50 % > MEC×SF 4.46 %; using NFPA floor (Table A.7.2.2.3(b) Class C column).

Step 4: [LV-B1-01] Specific volume of agent vapour

Formula: s = K1 + K2·t (0.0664 + 0.0002741·t)

Substitution: 0.0664 + 0.0002741 × 20.0

Result: 0.0719 m³/kg

Note: NFPA 2001 Table A.7.3.1(b) footer (SI form).

Step 5: [LV-B1-01] Halocarbon flooding mass (# 7.3.1)

Formula: W = (V / s) × ( C / (100 − C) )

Substitution: (179.09 / 0.0719) × (4.50 / 95.50)

Result: 117.40 kg

Step 6: [LV-B1-01] Altitude-corrected mass

Formula: W_corr = W × ACF

Substitution: 117.397 × 0.999

Result: 117.32 kg

Note: NFPA 2001 # 7.3.3.3.

Step 7: [LV-B1-01] Achieved concentration at max temp

Formula: C_max = 100·r/(1+r), r = W·s(t_max)/V

Substitution: W=117.40 kg, s(40.0 °C)=0.0774 m³/kg, V=179.09 m³

Result: 4.83 vol-%

Note: Developed concentration per NFPA # 7.3.1.1 (calculated at both the minimum and maximum design temperature). Exposure limits per NFPA # 4.3.2.3 apply to the maximum achieved concentration of the installed quantity (W includes the # 7.3.3 ΣDF agent; the # 7.3.3.3 altitude correction is excluded — the developed vol-% is altitude-invariant), not the design value at the minimum (design) temperature.

Step 8: Cylinder count (system-wide)

Formula: n = ⌈ W_corr / m_cyl ⌉

Substitution: ⌈ 117.32 kg / 259.5 kg ⌉

Result: 1

Note: Cylinder: NFPA-Generic 180 L — 259.5 kg max.

Step 9: Cylinder fill density (this design)

Formula: ρ_fill = (W_corr / n) / (V_water)

Substitution: (117.32 / 1) / 180.0 L

Result: 651.8 kg/m³ (45 % of NFPA max 1441.6)

Note: NFPA 2001 Table A.5.1.4.1 max fill density must not be exceeded; well below it means the cylinders are oversized.

Standing NFPA reminders

Discharge time ≤ 10 s per NFPA # 7.5.1 (halocarbon, # 7.5.1.1) — verify via listed OEM hydraulic-flow software (UL 2127 / UL 2166).

Hold time ≥ 10 min per NFPA # 7.4.1 — at least 85 % of the design concentration must persist at the highest protected-content height for the hold period (or the trained-personnel response time); verify by an enclosure door-fan integrity test.

Class C (energised electrical) hazard: NFPA # A.7.2.2.3 and EN 15004-1 # 7.5.1.3 note that higher concentrations may be needed for cable bundles > 100 mm dia, cable-tray fill > 20 %, tray stacks < 250 mm apart, or equipment energised > 5 kW during discharge — confirm the listed design concentration covers the configuration.

# 5.  Results

| Parameter | Value |
| --- | --- |
| Agent | FK-5-1-12 |
| Design concentration | 4.50 vol-% |
| Atm. correction factor | 0.999 |
| Agent mass W (system) | 117.32 kg |
| Achieved conc. @ max temp | 4.83 vol-% @ 40.0 °C (# 4.3.2.3 exposure basis) |
| Cylinder count | 1 |
| Discharge time limit | ≤ 10 s (NFPA # 7.5.1.1) |
| Hold time | ≥ 10 min (NFPA # 7.4.1) |
| GWP (100-yr, IPCC 2013) | <1 (Table A.4.6) |
| ODP (rel. CFC-11) | 0 — Table A.4.6 |

Selected cylinder

| Cylinder | Value |
| --- | --- |
| Model / selection | NFPA-Generic 180 L — 259.5 kg max |
| Quantity | 1 × 259.5 kg |
| Water volume | 180 L |
| Working pressure | 25 bar @ 21 °C |
| Envelope (Ø × H) | 386 × 1542 mm (estimated from water volume — confirm with OEM) |
| Fill density (this design) | 651.8 kg/m³ (45 % of NFPA max 1441.6 kg/m³) |

# 6.  Schematic

Single-zone clean-agent total-flooding arrangement.

Schematic is indicative for quantity/zoning intent only. Pipe routing, nozzle placement and hydraulic balance must use listed flow-calculation software per UL 2127 / UL 2166.

# R.  Reference Standards

NFPA 2001 (2022 ed.) — Standard on Clean Agent Fire Extinguishing Systems — total flooding design, quantity, distribution, hold time.

ISO 14520-1 — Gaseous fire-extinguishing systems — physical properties + system design (parallel international standard).

EN 15004-1 — Fixed firefighting systems — gas extinguishing systems — design, installation, maintenance (parallel European standard).

UL 2127 / UL 2166 — Listing standards for inert-gas and halocarbon clean-agent system units — hydraulic flow calc must use software listed under these.

Engineer of record: Hussein Ragab

Generated by Clean Agent Calculator — NFPA 2001 sizing.