## Cylinder Schedule
Clean Agent System - Cylinder / Equipment Schedule
LV-B1-01 ¦ NFPA 2001 (2022 ed.) total flooding ¦ working units: SI
Project: Test Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: Test Dev ¦ By: Hussein Ragab ¦ Chkd: Principal MEP Review ¦ Rev: P2 ¦ Date: 2026-09-02
Agent: FK-5-1-12 (halocarbon) ¦ System mode: flame-extinguishing ¦ Rooms: 1 ¦ Sizing basis: largest ¦ ACF: 0.999 ¦ Design factor ΣDF: +0.0 %
Hazard schedule
Ref | Hazard / room | Hazard class | Agent | Design conc. (vol-%) | Net volume (m³) | Design temp (°C) | Agent quantity (kg) | Cylinder (selected) | Cylinder qty | Capacity each (kg) | Water volume (L) | Discharge time basis | Hold time basis
1 | LV-B1-01 | Class C | FK-5-1-12 | 4.5 | 179.09 | 20 | 117.32 | NFPA-Generic 180 L — 259.5 kg max | 1 | 259.49 | 180 | ≤ 10 s (NFPA # 7.5.1.1) | ≥ 10 min (NFPA # 7.4.1)
Quantities are per NFPA 2001 (2022 ed.); pipe routing, nozzle placement and hydraulic balance must use listed flow-calculation software per UL 2127 / UL 2166. Cylinder water volume (L), pressure (bar) and envelope (mm) are OEM catalogue values and are shown unconverted in both unit systems.

## Basis & Notes
Design Basis & Notes
LV-B1-01 ¦ units: SI
Project: Test Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: Test Dev ¦ By: Hussein Ragab ¦ Chkd: Principal MEP Review ¦ Rev: P2 ¦ Date: 2026-09-02
Agent & system
Item | Value | Unit / basis
Agent | FK-5-1-12 | halocarbon
System mode (NFPA branch) | flame-extinguishing
Rooms | 1 | -
Sizing basis | largest
Design concentration | 4.5 | vol-%
Minimum extinguishing conc. | 3.3 | vol-%
Safety factor | 1.35 | -
Atm. correction factor (Table 7.3.3.3) | 0.999 | -
Design factor ΣDF (# 7.3.3) | 0% | of agent mass W
Tee count (# 7.3.3.1) | 4 | -
Tee design factor | 0 | -
Additional design factor | 0 | -
Agent mass W (system) | 117.32 | kg
GWP (100-yr, IPCC 2013) | <1 | Table A.4.6
ODP (rel. CFC-11) | 0 | Table A.4.6
Selected cylinder
Cylinder | Value | Unit / basis
Model / selection | NFPA-Generic 180 L — 259.5 kg max
Quantity | 1 | cylinders
Capacity each | 259.49 | kg
Water volume | 180 | L
Working pressure | 25 | bar @ 21 °C
Envelope (Ø × H) | 386 × 1542 | mm (est. from water volume - confirm with OEM)
Fill density (this design) | 651.8 | kg/m³
Fill vs NFPA max fill | 45 | % of 1441.6 kg/m³
Discharge & hold time basis
Requirement | Value | Basis
Discharge time (max) | 10 | s
Discharge time clause | NFPA # 7.5.1.1
Hold time (min.) | 10 | min
Hold time basis | NFPA # 7.4.1
Hold time clause | # 7.4.1
Standing NFPA reminders
Discharge time ≤ 10 s per NFPA # 7.5.1 (halocarbon, # 7.5.1.1) — verify via listed OEM hydraulic-flow software (UL 2127 / UL 2166).
Hold time ≥ 10 min per NFPA # 7.4.1 — at least 85 % of the design concentration must persist at the highest protected-content height for the hold period (or the trained-personnel response time); verify by an enclosure door-fan integrity test.
Class C (energised electrical) hazard: NFPA # A.7.2.2.3 and EN 15004-1 # 7.5.1.3 note that higher concentrations may be needed for cable bundles > 100 mm dia, cable-tray fill > 20 %, tray stacks < 250 mm apart, or equipment energised > 5 kW during discharge — confirm the listed design concentration covers the configuration.
Reference standards
Reference | Application
NFPA 2001 (2022 ed.) | Standard on Clean Agent Fire Extinguishing Systems — total flooding design, quantity, distribution, hold time.
ISO 14520-1 | Gaseous fire-extinguishing systems — physical properties + system design (parallel international standard).
EN 15004-1 | Fixed firefighting systems — gas extinguishing systems — design, installation, maintenance (parallel European standard).
UL 2127 / UL 2166 | Listing standards for inert-gas and halocarbon clean-agent system units — hydraulic flow calc must use software listed under these.