## Summary
Condensate Simulation - Schedule
FAHU with enthalpy wheel only ¦ working units: SI
Project: Marina Commercial Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: - ¦ By: Hussein Ragab ¦ Chkd: - ¦ Rev: P2 ¦ Date: 2026-10-20
Location: Dubai ¦ Period: 2025-01-01 to 2025-12-31
Weather data: Open-Meteo archive — live fetch, site timezone Asia/Dubai, data written 2026-10-20 10:07
Annual Results
Quantity | Value | Unit
Total condensate / yr | 850041.4685 | L
Peak daily condensate | 6280.0877 | L/day
Date of peak | 24 Jul 2025
Average daily condensate | 2328.8807 | L/day
Dec-Feb average daily | 901.3366 | L/day
Mar-May average daily | 1602.8117 | L/day
Jun-Aug average daily | 3730.6566 | L/day
Sep-Nov average daily | 3057.6055 | L/day
Monthly Schedule
Month | Total (L) | Avg daily (L/day) | Peak daily (L/day)
Jan 2025 | 15451.0315 | 498.4204 | 1712.204
Feb 2025 | 29301.4638 | 1046.4808 | 2561.631
Mar 2025 | 30247.7571 | 975.7341 | 2214.9226
Apr 2025 | 38613.3919 | 1287.1131 | 2856.4421
May 2025 | 78597.5253 | 2535.404 | 4294.9805
Jun 2025 | 113205.3273 | 3773.5109 | 5173.5689
Jul 2025 | 120003.2068 | 3871.0712 | 6280.0877
Aug 2025 | 110011.8697 | 3548.77 | 4991.9913
Sep 2025 | 130756.5789 | 4358.5526 | 6186.615
Oct 2025 | 104776.69 | 3379.8932 | 5838.4715
Nov 2025 | 42708.8285 | 1423.6276 | 3129.5593
Dec 2025 | 36367.7978 | 1173.1548 | 2366.454
Seasonal Average Daily
Season | Avg daily (L/day)
Dec-Feb | 901.3366
Mar-May | 1602.8117
Jun-Aug | 3730.6566
Sep-Nov | 3057.6055
Generated by the Condensate Simulator (Tool 09). Internal calc is SI; displayed magnitudes follow the unit system.

## Hourly Data
Hourly Condensate Data
Per-hour simulation frame ¦ working units: SI
Time | Outdoor DB (°C) | Outdoor RH (%) | Schedule (%) | On-coil DB (°C) | On-coil WB (°C) | On-coil RH (%) | Condensate (L/h) | FA condensate (L/h) | Return condensate (L/h) | Wheel condensate (L/h)
2025-01-01 | 18.15 | 82 | 70 | 21.8383 | 16.753 | 60.1365 | 51.6354 | 51.6354 | 0 | 0
2025-01-01 01:00 | 17.7 | 81.5 | 70 | 21.6636 | 16.5632 | 59.8655 | 46.317 | 46.317 | 0 | 0
2025-01-01 02:00 | 17.2 | 79 | 70 | 21.4665 | 16.2668 | 58.9669 | 36.9136 | 36.9136 | 0 | 0
2025-01-01 03:00 | 16.95 | 72 | 70 | 21.3625 | 15.8629 | 56.7246 | 21.7205 | 21.7205 | 0 | 0
2025-01-01 04:00 | 17.35 | 68 | 70 | 21.516 | 15.8177 | 55.4876 | 17.5496 | 17.5496 | 0 | 0
2025-01-01 05:00 | 17.7 | 67 | 70 | 21.6519 | 15.89 | 55.1896 | 18.4828 | 18.4828 | 0 | 0
2025-01-01 06:00 | 17.55 | 64 | 100 | 21.591 | 15.6989 | 54.2075 | 16.415 | 16.415 | 0 | 0
2025-01-01 07:00 | 17.8 | 61 | 100 | 21.6861 | 15.6393 | 53.2329 | 10.8139 | 10.8139 | 0 | 0
2025-01-01 08:00 | 19.1 | 55.5 | 100 | 22.1845 | 15.7881 | 51.4037 | 8.728 | 8.728 | 0 | 0
2025-01-01 09:00 | 21.15 | 49.5 | 100 | 22.9569 | 16.1077 | 49.306 | 10.9998 | 10.9998 | 0 | 0
2025-01-01 10:00 | 23.3 | 44 | 100 | 23.7471 | 16.432 | 47.2713 | 13.3889 | 13.3889 | 0 | 0
2025-01-01 11:00 | 24.85 | 40.5 | 100 | 24.3042 | 16.66 | 45.9136 | 15.2322 | 15.2322 | 0 | 0
2025-01-01 12:00 | 25.25 | 48 | 100 | 24.444 | 17.2894 | 49.1115 | 50.0748 | 50.0748 | 0 | 0
2025-01-01 13:00 | 24.8 | 57.5 | 100 | 24.2836 | 17.7707 | 52.987 | 82.8941 | 82.8941 | 0 | 0
2025-01-01 14:00 | 24.05 | 62 | 100 | 24.0178 | 17.7987 | 54.6077 | 90.3926 | 90.3926 | 0 | 0
2025-01-01 15:00 | 23.3 | 66 | 100 | 23.75 | 17.7789 | 55.9586 | 94.9638 | 94.9638 | 0 | 0
2025-01-01 16:00 | 22.8 | 68 | 100 | 23.57 | 17.719 | 56.5686 | 95.1278 | 95.1278 | 0 | 0
2025-01-01 17:00 | 22.2 | 68.5 | 100 | 23.3521 | 17.5338 | 56.5647 | 88.4276 | 88.4276 | 0 | 0
2025-01-01 18:00 | 21.55 | 65.5 | 100 | 23.1123 | 17.1372 | 55.2621 | 69.3408 | 69.3408 | 0 | 0
2025-01-01 19:00 | 21 | 64 | 100 | 22.9077 | 16.8653 | 54.5856 | 57.2122 | 57.2122 | 0 | 0
2025-01-01 20:00 | 20.5 | 66 | 100 | 22.7219 | 16.8011 | 55.2027 | 57.2975 | 57.2975 | 0 | 0
2025-01-01 21:00 | 20.1 | 66.5 | 100 | 22.5718 | 16.6892 | 55.3016 | 53.7873 | 53.7873 | 0 | 0
2025-01-01 22:00 | 19.6 | 67 | 70 | 22.3829 | 16.5428 | 55.387 | 34.3281 | 34.3281 | 0 | 0
2025-01-01 23:00 | 19.2 | 67 | 70 | 22.2306 | 16.4049 | 55.3252 | 30.8646 | 30.8646 | 0 | 0
2025-01-02 | 19.05 | 63.5 | 70 | 22.1709 | 16.1778 | 54.118 | 22.3366 | 22.3366 | 0 | 0
2025-01-02 01:00 | 18.95 | 61.5 | 70 | 22.1312 | 16.0439 | 53.4332 | 17.4029 | 17.4029 | 0 | 0
2025-01-02 02:00 | 18.95 | 61 | 70 | 22.1308 | 16.019 | 53.2653 | 16.3783 | 16.3783 | 0 | 0
2025-01-02 03:00 | 19.05 | 58.5 | 70 | 22.1674 | 15.9249 | 52.4216 | 11.9705 | 11.9705 | 0 | 0
2025-01-02 04:00 | 18.9 | 56 | 70 | 22.1081 | 15.75 | 51.5654 | 5.6399 | 5.6399 | 0 | 0
2025-01-02 05:00 | 18.65 | 55.5 | 70 | 22.0115 | 15.646 | 51.3911 | 2.7563 | 2.7563 | 0 | 0
2025-01-02 06:00 | 18.6 | 56 | 100 | 21.9926 | 15.6553 | 51.555 | 4.8383 | 4.8383 | 0 | 0
2025-01-02 07:00 | 19 | 54 | 100 | 22.1452 | 15.6811 | 50.8705 | 3.0345 | 3.0345 | 0 | 0
2025-01-02 08:00 | 20.15 | 49 | 100 | 22.5806 | 15.7752 | 49.1055 | 0 | 0 | 0 | 0
2025-01-02 09:00 | 21.25 | 44.5 | 100 | 22.9921 | 15.8542 | 47.4392 | 0 | 0 | 0 | 0
2025-01-02 10:00 | 21.9 | 42 | 100 | 23.233 | 15.8989 | 46.4789 | 0 | 0 | 0 | 0
2025-01-02 11:00 | 22.1 | 42.5 | 100 | 23.3072 | 15.9866 | 46.6656 | 0 | 0 | 0 | 0
2025-01-02 12:00 | 22.15 | 43.5 | 100 | 23.326 | 16.0611 | 47.0523 | 0.2143 | 0.2143 | 0 | 0
2025-01-02 13:00 | 22.35 | 42 | 100 | 23.3993 | 16.0278 | 46.4812 | 0 | 0 | 0 | 0
2025-01-02 14:00 | 22.35 | 40 | 100 | 23.3987 | 15.9047 | 45.7174 | 0 | 0 | 0 | 0
2025-01-02 15:00 | 22.05 | 38.5 | 100 | 23.2874 | 15.7279 | 45.1656 | 0 | 0 | 0 | 0
2025-01-02 16:00 | 21.6 | 39 | 100 | 23.1204 | 15.6309 | 45.3925 | 0 | 0 | 0 | 0
2025-01-02 17:00 | 20.85 | 42.5 | 100 | 22.8412 | 15.6202 | 46.746 | 0 | 0 | 0 | 0
2025-01-02 18:00 | 20.1 | 46.5 | 100 | 22.5602 | 15.6228 | 48.23 | 0 | 0 | 0 | 0
2025-01-02 19:00 | 19.75 | 48.5 | 100 | 22.4284 | 15.6255 | 48.9487 | 0 | 0 | 0 | 0
2025-01-02 20:00 | 19.5 | 49 | 100 | 22.3334 | 15.5763 | 49.1328 | 0 | 0 | 0 | 0
2025-01-02 21:00 | 19.2 | 49.5 | 100 | 22.2189 | 15.5111 | 49.3207 | 0 | 0 | 0 | 0
2025-01-02 22:00 | 18.9 | 50 | 70 | 22.104 | 15.4454 | 49.5092 | 0 | 0 | 0 | 0
2025-01-02 23:00 | 18.6 | 50.5 | 70 | 21.9886 | 15.3795 | 49.7005 | 0 | 0 | 0 | 0
2025-01-03 | 18.25 | 51 | 70 | 21.8535 | 15.2966 | 49.8965 | 0 | 0 | 0 | 0
2025-01-03 01:00 | 17.95 | 51.5 | 70 | 21.7372 | 15.2292 | 50.0877 | 0 | 0 | 0 | 0
2025-01-03 02:00 | 17.65 | 52.5 | 70 | 21.6209 | 15.1854 | 50.4422 | 0 | 0 | 0 | 0
2025-01-03 03:00 | 17.3 | 53.5 | 70 | 21.4846 | 15.1247 | 50.7971 | 0 | 0 | 0 | 0
2025-01-03 04:00 | 17.25 | 51.5 | 70 | 21.4633 | 15.0148 | 50.1576 | 0 | 0 | 0 | 0
2025-01-03 05:00 | 17.2 | 49 | 70 | 21.4416 | 14.8807 | 49.3583 | 0 | 0 | 0 | 0
2025-01-03 06:00 | 17.05 | 49 | 100 | 21.3826 | 14.8364 | 49.3754 | 0 | 0 | 0 | 0
2025-01-03 07:00 | 17.75 | 47 | 100 | 21.6557 | 14.9497 | 48.618 | 0 | 0 | 0 | 0
2025-01-03 08:00 | 19.05 | 43 | 100 | 22.1569 | 15.1283 | 47.0873 | 0 | 0 | 0 | 0
2025-01-03 09:00 | 19.7 | 42.5 | 100 | 22.4057 | 15.2905 | 46.8229 | 0 | 0 | 0 | 0
2025-01-03 10:00 | 20.05 | 42.5 | 100 | 22.539 | 15.3921 | 46.7819 | 0 | 0 | 0 | 0
2025-01-03 11:00 | 20.65 | 40.5 | 100 | 22.765 | 15.4528 | 46.006 | 0 | 0 | 0 | 0
2025-01-03 12:00 | 21 | 40 | 100 | 22.8964 | 15.5229 | 45.7942 | 0 | 0 | 0 | 0
2025-01-03 13:00 | 21.15 | 40 | 100 | 22.9527 | 15.5647 | 45.7862 | 0 | 0 | 0 | 0
2025-01-03 14:00 | 21.05 | 39.5 | 100 | 22.915 | 15.5068 | 45.616 | 0 | 0 | 0 | 0
2025-01-03 15:00 | 20.7 | 40 | 100 | 22.7836 | 15.4358 | 45.8371 | 0 | 0 | 0 | 0
2025-01-03 16:00 | 20.5 | 40.5 | 100 | 22.7083 | 15.4077 | 46.0378 | 0 | 0 | 0 | 0
2025-01-03 17:00 | 19.9 | 42 | 100 | 22.4816 | 15.3192 | 46.6395 | 0 | 0 | 0 | 0
2025-01-03 18:00 | 18.95 | 45 | 100 | 22.1198 | 15.2033 | 47.7896 | 0 | 0 | 0 | 0
2025-01-03 19:00 | 18.1 | 48 | 100 | 21.793 | 15.104 | 48.8948 | 0 | 0 | 0 | 0
2025-01-03 20:00 | 17.2 | 51.5 | 100 | 21.4438 | 15.0019 | 50.1377 | 0 | 0 | 0 | 0
2025-01-03 21:00 | 16.25 | 54 | 100 | 21.0702 | 14.8252 | 51.0416 | 0 | 0 | 0 | 0
2025-01-03 22:00 | 15.2 | 55.5 | 70 | 20.6513 | 14.565 | 51.6528 | 0 | 0 | 0 | 0
2025-01-03 23:00 | 14.15 | 55 | 70 | 20.2252 | 14.2192 | 51.708 | 0 | 0 | 0 | 0
2025-01-04 | 13.2 | 53 | 70 | 19.8336 | 13.8489 | 51.3798 | 0 | 0 | 0 | 0
2025-01-04 01:00 | 12.55 | 51.5 | 70 | 19.5631 | 13.5953 | 51.1638 | 0 | 0 | 0 | 0
2025-01-04 02:00 | 11.95 | 52 | 70 | 19.3134 | 13.4346 | 51.5029 | 0 | 0 | 0 | 0
2025-01-04 03:00 | 11.4 | 53.5 | 70 | 19.0842 | 13.3239 | 52.0958 | 0 | 0 | 0 | 0
2025-01-04 04:00 | 11.65 | 49.5 | 70 | 19.1852 | 13.2537 | 50.9489 | 0 | 0 | 0 | 0
2025-01-04 05:00 | 12.25 | 44 | 70 | 19.4306 | 13.224 | 49.2355 | 0 | 0 | 0 | 0
2025-01-04 06:00 | 12 | 44 | 100 | 19.3263 | 13.153 | 49.3324 | 0 | 0 | 0 | 0
2025-01-04 07:00 | 12.15 | 43 | 100 | 19.388 | 13.1586 | 48.9925 | 0 | 0 | 0 | 0
2025-01-04 08:00 | 14.2 | 37 | 100 | 20.2283 | 13.4892 | 46.4697 | 0 | 0 | 0 | 0
2025-01-04 09:00 | 17.15 | 30.5 | 100 | 21.4068 | 13.9753 | 43.3741 | 0 | 0 | 0 | 0
2025-01-04 10:00 | 19.6 | 28.5 | 100 | 22.3588 | 14.4975 | 41.9145 | 0 | 0 | 0 | 0
2025-01-04 11:00 | 21.05 | 30 | 100 | 22.9106 | 14.9538 | 42.0904 | 0 | 0 | 0 | 0
2025-01-04 12:00 | 21.9 | 30.5 | 100 | 23.229 | 15.203 | 42.111 | 0 | 0 | 0 | 0
2025-01-04 13:00 | 22.55 | 30 | 100 | 23.4698 | 15.3391 | 41.808 | 0 | 0 | 0 | 0
2025-01-04 14:00 | 22.65 | 31 | 100 | 23.507 | 15.4279 | 42.1861 | 0 | 0 | 0 | 0
2025-01-04 15:00 | 22.2 | 33 | 100 | 23.3412 | 15.4336 | 43.0312 | 0 | 0 | 0 | 0
2025-01-04 16:00 | 21.55 | 34.5 | 100 | 23.1 | 15.3508 | 43.6956 | 0 | 0 | 0 | 0
2025-01-04 17:00 | 20.6 | 38 | 100 | 22.7448 | 15.2944 | 45.1202 | 0 | 0 | 0 | 0
2025-01-04 18:00 | 19.55 | 41 | 100 | 22.3474 | 15.1653 | 46.3317 | 0 | 0 | 0 | 0
2025-01-04 19:00 | 18.55 | 43 | 100 | 21.9639 | 14.9842 | 47.1632 | 0 | 0 | 0 | 0
2025-01-04 20:00 | 17.7 | 46.5 | 100 | 21.6358 | 14.9111 | 48.4541 | 0 | 0 | 0 | 0
2025-01-04 21:00 | 17.25 | 49.5 | 100 | 21.4618 | 14.9219 | 49.4918 | 0 | 0 | 0 | 0
2025-01-04 22:00 | 16.85 | 52.5 | 70 | 21.3067 | 14.9409 | 50.503 | 0 | 0 | 0 | 0
2025-01-04 23:00 | 16.45 | 55 | 70 | 21.1505 | 14.9313 | 51.3394 | 0 | 0 | 0 | 0
2025-01-05 | 16.25 | 57.5 | 70 | 21.0732 | 14.981 | 52.1413 | 0 | 0 | 0 | 0
2025-01-05 01:00 | 16.2 | 59.5 | 70 | 21.0551 | 15.0544 | 52.7666 | 0 | 0 | 0 | 0
2025-01-05 02:00 | 16.35 | 60.5 | 70 | 21.1156 | 15.1477 | 53.0666 | 0 | 0 | 0 | 0
2025-01-05 03:00 | 16.05 | 63 | 70 | 20.9985 | 15.1605 | 53.8544 | 0 | 0 | 0 | 0
2025-01-05 04:00 | 15.7 | 64.5 | 70 | 20.8602 | 15.1111 | 54.3272 | 0 | 0 | 0 | 0
2025-01-05 05:00 | 15.8 | 64.5 | 70 | 20.9002 | 15.1445 | 54.319 | 0 | 0 | 0 | 0
2025-01-05 06:00 | 15.55 | 66.5 | 100 | 20.802 | 15.1476 | 54.93 | 0.6276 | 0.6276 | 0 | 0
2025-01-05 07:00 | 15.5 | 68 | 100 | 20.7834 | 15.1953 | 55.3781 | 3.7383 | 3.7383 | 0 | 0
2025-01-05 08:00 | 17.2 | 62 | 100 | 21.4525 | 15.4939 | 53.4953 | 6.6161 | 6.6161 | 0 | 0
2025-01-05 09:00 | 19.7 | 52 | 100 | 22.4116 | 15.7991 | 50.1439 | 3.833 | 3.833 | 0 | 0
2025-01-05 10:00 | 21.4 | 44.5 | 100 | 23.0481 | 15.9011 | 47.4145 | 0 | 0 | 0 | 0
2025-01-05 11:00 | 22.35 | 40 | 100 | 23.3987 | 15.9092 | 45.683 | 0 | 0 | 0 | 0
2025-01-05 12:00 | 22.65 | 39.5 | 100 | 23.509 | 15.9635 | 45.4834 | 0 | 0 | 0 | 0
2025-01-05 13:00 | 22.65 | 40 | 100 | 23.5091 | 15.994 | 45.684 | 0 | 0 | 0 | 0
2025-01-05 14:00 | 22.5 | 40.5 | 100 | 23.4541 | 15.9811 | 45.887 | 0 | 0 | 0 | 0
2025-01-05 15:00 | 22.25 | 42 | 100 | 23.3624 | 16.0002 | 46.4732 | 0 | 0 | 0 | 0
2025-01-05 16:00 | 21.6 | 45 | 100 | 23.1227 | 15.9872 | 47.621 | 0.0993 | 0.0993 | 0 | 0
2025-01-05 17:00 | 20.5 | 49.5 | 100 | 22.7131 | 15.9098 | 49.2772 | 4.2092 | 4.2092 | 0 | 0
2025-01-05 18:00 | 19.4 | 54 | 100 | 22.2984 | 15.8083 | 50.8572 | 7.0457 | 7.0457 | 0 | 0
2025-01-05 19:00 | 18.6 | 58 | 100 | 21.9941 | 15.7569 | 52.2047 | 10.4705 | 10.4705 | 0 | 0
2025-01-05 20:00 | 18.05 | 62 | 100 | 21.7843 | 15.7734 | 53.5152 | 15.9133 | 15.9133 | 0 | 0
2025-01-05 21:00 | 17.65 | 65.5 | 100 | 21.6314 | 15.8067 | 54.6374 | 21.1635 | 21.1635 | 0 | 0
2025-01-05 22:00 | 17.2 | 68.5 | 70 | 21.4578 | 15.7932 | 55.5727 | 16.8959 | 16.8959 | 0 | 0
2025-01-05 23:00 | 16.3 | 72 | 70 | 21.1059 | 15.6402 | 56.6142 | 15.9662 | 15.9662 | 0 | 0
2025-01-06 | 15 | 76 | 70 | 20.59 | 15.3571 | 57.7594 | 12.2292 | 12.2292 | 0 | 0
2025-01-06 01:00 | 13.75 | 79.5 | 70 | 20.0858 | 15.057 | 58.7425 | 7.6856 | 7.6856 | 0 | 0
2025-01-06 02:00 | 12.95 | 81.5 | 70 | 19.759 | 14.85 | 59.3034 | 4.2744 | 4.2744 | 0 | 0
2025-01-06 03:00 | 12.4 | 82.5 | 70 | 19.5321 | 14.6923 | 59.5911 | 1.352 | 1.352 | 0 | 0
2025-01-06 04:00 | 11.8 | 82 | 70 | 19.2813 | 14.4625 | 59.4935 | 0 | 0 | 0 | 0
2025-01-06 05:00 | 11.2 | 82 | 70 | 19.0293 | 14.2522 | 59.5465 | 0 | 0 | 0 | 0
2025-01-06 06:00 | 10.75 | 83 | 100 | 18.8402 | 14.1291 | 59.8506 | 0 | 0 | 0 | 0
2025-01-06 07:00 | 11.25 | 79 | 100 | 19.0473 | 14.1679 | 58.757 | 0 | 0 | 0 | 0
2025-01-06 08:00 | 13.65 | 67.5 | 100 | 20.0331 | 14.5586 | 55.3505 | 0 | 0 | 0 | 0
2025-01-06 09:00 | 17.1 | 55 | 100 | 21.4073 | 15.1362 | 51.2609 | 0 | 0 | 0 | 0
2025-01-06 10:00 | 20.1 | 45 | 100 | 22.5594 | 15.544 | 47.6649 | 0 | 0 | 0 | 0
2025-01-06 11:00 | 22.2 | 36 | 100 | 23.3422 | 15.6213 | 44.1631 | 0 | 0 | 0 | 0
2025-01-06 12:00 | 23.6 | 31 | 100 | 23.8549 | 15.6783 | 42.0442 | 0 | 0 | 0 | 0
2025-01-06 13:00 | 24.7 | 29.5 | 100 | 24.2523 | 15.8619 | 41.3047 | 0 | 0 | 0 | 0
2025-01-06 14:00 | 25.55 | 28 | 100 | 24.5558 | 15.9726 | 40.5801 | 0 | 0 | 0 | 0
2025-01-06 15:00 | 25.65 | 27.5 | 100 | 24.5914 | 15.96 | 40.3576 | 0 | 0 | 0 | 0
2025-01-06 16:00 | 24.35 | 34.5 | 100 | 24.1261 | 16.1106 | 43.4247 | 0 | 0 | 0 | 0
2025-01-06 17:00 | 22.45 | 45 | 100 | 23.4369 | 16.2392 | 47.6418 | 8.5921 | 8.5921 | 0 | 0
2025-01-06 18:00 | 21.05 | 51 | 100 | 22.9203 | 16.1615 | 49.8513 | 14.9359 | 14.9359 | 0 | 0
2025-01-06 19:00 | 20.1 | 49 | 100 | 22.5616 | 15.7579 | 49.1206 | 0 | 0 | 0 | 0
2025-01-06 20:00 | 19.3 | 47 | 100 | 22.2556 | 15.4102 | 48.4591 | 0 | 0 | 0 | 0
2025-01-06 21:00 | 18.45 | 53.5 | 100 | 21.9328 | 15.4834 | 50.7179 | 0 | 0 | 0 | 0
2025-01-06 22:00 | 17.7 | 59 | 70 | 21.6456 | 15.5135 | 52.5522 | 2.7635 | 2.7635 | 0 | 0
2025-01-06 23:00 | 17.05 | 60 | 70 | 21.3917 | 15.3501 | 52.8903 | 0 | 0 | 0 | 0
2025-01-07 | 16.2 | 61 | 70 | 21.0564 | 15.1202 | 53.2441 | 0 | 0 | 0 | 0
2025-01-07 01:00 | 15.2 | 63 | 70 | 20.6582 | 14.8822 | 53.9247 | 0 | 0 | 0 | 0
2025-01-07 02:00 | 14.35 | 64.5 | 70 | 20.3157 | 14.6675 | 54.4479 | 0 | 0 | 0 | 0
2025-01-07 03:00 | 13.75 | 65 | 70 | 20.0714 | 14.4918 | 54.6626 | 0 | 0 | 0 | 0
2025-01-07 04:00 | 13.35 | 65 | 70 | 19.9073 | 14.3615 | 54.716 | 0 | 0 | 0 | 0
2025-01-07 05:00 | 12.95 | 63.5 | 70 | 19.7408 | 14.1752 | 54.3619 | 0 | 0 | 0 | 0
2025-01-07 06:00 | 12.55 | 61 | 100 | 19.5726 | 13.9532 | 53.7558 | 0 | 0 | 0 | 0
2025-01-07 07:00 | 13 | 58.5 | 100 | 19.7566 | 14.0008 | 52.9587 | 0 | 0 | 0 | 0
2025-01-07 08:00 | 15.15 | 51.5 | 100 | 20.6274 | 14.378 | 50.4673 | 0 | 0 | 0 | 0
2025-01-07 09:00 | 18.45 | 41.5 | 100 | 21.9241 | 14.8798 | 46.664 | 0 | 0 | 0 | 0
2025-01-07 10:00 | 21.75 | 33 | 100 | 23.1741 | 15.3175 | 43.0782 | 0 | 0 | 0 | 0
2025-01-07 11:00 | 24.1 | 27 | 100 | 24.0362 | 15.5385 | 40.3372 | 0 | 0 | 0 | 0
2025-01-07 12:00 | 25.35 | 23.5 | 100 | 24.486 | 15.5962 | 38.6625 | 0 | 0 | 0 | 0
2025-01-07 13:00 | 26 | 22 | 100 | 24.7175 | 15.6375 | 37.9034 | 0 | 0 | 0 | 0
2025-01-07 14:00 | 25.85 | 25.5 | 100 | 24.663 | 15.8633 | 39.4635 | 0 | 0 | 0 | 0
2025-01-07 15:00 | 24.65 | 33.5 | 100 | 24.2338 | 16.1237 | 42.9918 | 0 | 0 | 0 | 0
2025-01-07 16:00 | 23.2 | 40.5 | 100 | 23.7103 | 16.1805 | 45.8852 | 0 | 0 | 0 | 0
2025-01-07 17:00 | 22 | 48.5 | 100 | 23.2722 | 16.3127 | 48.9578 | 16.3256 | 16.3256 | 0 | 0
2025-01-07 18:00 | 20.9 | 57 | 100 | 22.867 | 16.449 | 52.0226 | 33.0193 | 33.0193 | 0 | 0
2025-01-07 19:00 | 19.8 | 64 | 100 | 22.4569 | 16.4571 | 54.3738 | 42.2884 | 42.2884 | 0 | 0
2025-01-07 20:00 | 18.95 | 68 | 100 | 22.1357 | 16.3688 | 55.622 | 43.9226 | 43.9226 | 0 | 0
2025-01-07 21:00 | 18.4 | 68 | 100 | 21.9242 | 16.1793 | 55.5473 | 37.193 | 37.193 | 0 | 0
2025-01-07 22:00 | 17.55 | 67 | 70 | 21.5935 | 15.8416 | 55.1423 | 17.0486 | 17.0486 | 0 | 0
2025-01-07 23:00 | 16.75 | 66.5 | 70 | 21.2791 | 15.5481 | 54.951 | 9.7679 | 9.7679 | 0 | 0
2025-01-08 | 16.15 | 69 | 70 | 21.0436 | 15.456 | 55.7167 | 9.5919 | 9.5919 | 0 | 0
2025-01-08 01:00 | 15.25 | 72.5 | 70 | 20.6871 | 15.2977 | 56.7602 | 8.5415 | 8.5415 | 0 | 0
2025-01-08 02:00 | 14.25 | 75 | 70 | 20.2852 | 15.0545 | 57.492 | 4.7522 | 4.7522 | 0 | 0
2025-01-08 03:00 | 13.55 | 75 | 70 | 19.9993 | 14.8132 | 57.5164 | 0 | 0 | 0 | 0
2025-01-08 04:00 | 12.8 | 72.5 | 70 | 19.6877 | 14.4629 | 56.8856 | 0 | 0 | 0 | 0
2025-01-08 05:00 | 11.9 | 71.5 | 70 | 19.3122 | 14.1245 | 56.7404 | 0 | 0 | 0 | 0
2025-01-08 06:00 | 11.25 | 71 | 100 | 19.0388 | 13.8907 | 56.7259 | 0 | 0 | 0 | 0
2025-01-08 07:00 | 11.55 | 66 | 100 | 19.1599 | 13.8144 | 55.3478 | 0 | 0 | 0 | 0
2025-01-08 08:00 | 13.6 | 57 | 100 | 20.002 | 14.1282 | 52.4211 | 0 | 0 | 0 | 0
2025-01-08 09:00 | 16.3 | 48.5 | 100 | 21.0852 | 14.5893 | 49.342 | 0 | 0 | 0 | 0
2025-01-08 10:00 | 18.7 | 42.5 | 100 | 22.0216 | 15.0001 | 46.9806 | 0 | 0 | 0 | 0
2025-01-08 11:00 | 20.4 | 39.5 | 100 | 22.67 | 15.3219 | 45.7001 | 0 | 0 | 0 | 0
2025-01-08 12:00 | 21.65 | 37 | 100 | 23.1382 | 15.5259 | 44.6382 | 0 | 0 | 0 | 0
2025-01-08 13:00 | 23 | 33.5 | 100 | 23.6361 | 15.6764 | 43.1446 | 0 | 0 | 0 | 0
2025-01-08 14:00 | 23.85 | 33 | 100 | 23.9457 | 15.8718 | 42.8615 | 0 | 0 | 0 | 0
2025-01-08 15:00 | 24 | 36.5 | 100 | 24 | 16.146 | 44.2741 | 0 | 0 | 0 | 0
2025-01-08 16:00 | 23.35 | 42.5 | 100 | 23.7651 | 16.3498 | 46.6928 | 8.4156 | 8.4156 | 0 | 0
2025-01-08 17:00 | 21.75 | 53 | 100 | 23.1814 | 16.4953 | 50.6508 | 29.3509 | 29.3509 | 0 | 0
2025-01-08 18:00 | 20.65 | 66 | 100 | 22.7781 | 16.8524 | 55.2452 | 59.3246 | 59.3246 | 0 | 0
2025-01-08 19:00 | 20.05 | 76.5 | 100 | 22.5588 | 17.1861 | 58.8061 | 84.3067 | 84.3067 | 0 | 0
2025-01-08 20:00 | 19.35 | 81 | 100 | 22.2971 | 17.1525 | 60.1412 | 87.9124 | 87.9124 | 0 | 0
2025-01-08 21:00 | 18.95 | 82.5 | 100 | 22.1458 | 17.075 | 60.5233 | 86.5316 | 86.5316 | 0 | 0
2025-01-08 22:00 | 18.4 | 85.5 | 70 | 21.9373 | 17.01 | 61.3499 | 60.9981 | 60.9981 | 0 | 0
2025-01-08 23:00 | 17.95 | 87 | 70 | 21.7649 | 16.9085 | 61.7028 | 59.3397 | 59.3397 | 0 | 0
2025-01-09 | 17.55 | 87.5 | 70 | 21.6101 | 16.7788 | 61.7486 | 56.2485 | 56.2485 | 0 | 0
2025-01-09 01:00 | 16.95 | 88.5 | 70 | 21.3766 | 16.5951 | 61.8999 | 52.0854 | 52.0854 | 0 | 0
2025-01-09 02:00 | 16.3 | 89.5 | 70 | 21.1214 | 16.3919 | 62.0438 | 47.4346 | 47.4346 | 0 | 0
2025-01-09 03:00 | 15.85 | 90 | 70 | 20.9433 | 16.2422 | 62.0914 | 43.9039 | 43.9039 | 0 | 0
2025-01-09 04:00 | 15.75 | 91.5 | 70 | 20.9049 | 16.2666 | 62.5206 | 45.5182 | 45.5182 | 0 | 0
2025-01-09 05:00 | 15.7 | 92.5 | 70 | 20.8859 | 16.2893 | 62.8058 | 46.7258 | 46.7258 | 0 | 0
2025-01-09 06:00 | 15.6 | 90.5 | 100 | 20.8442 | 16.1693 | 62.1794 | 60.4176 | 60.4176 | 0 | 0
2025-01-09 07:00 | 16.05 | 87 | 100 | 21.0201 | 16.1925 | 61.2154 | 57.9221 | 57.9221 | 0 | 0
2025-01-09 08:00 | 17.75 | 79.5 | 100 | 21.6814 | 16.4903 | 59.2195 | 61.2593 | 61.2593 | 0 | 0
2025-01-09 09:00 | 20.05 | 66.5 | 100 | 22.5529 | 16.672 | 55.2965 | 53.1924 | 53.1924 | 0 | 0
2025-01-09 10:00 | 21.65 | 55 | 100 | 23.1452 | 16.5792 | 51.3744 | 34.943 | 34.943 | 0 | 0
2025-01-09 11:00 | 22.4 | 50.5 | 100 | 23.42 | 16.5542 | 49.7572 | 27.7243 | 27.7243 | 0 | 0
2025-01-09 12:00 | 22.65 | 49.5 | 100 | 23.5113 | 16.571 | 49.4043 | 26.9611 | 26.9611 | 0 | 0
2025-01-09 13:00 | 22.7 | 49 | 100 | 23.5294 | 16.5556 | 49.2229 | 25.7729 | 25.7729 | 0 | 0
2025-01-09 14:00 | 22.55 | 50 | 100 | 23.4748 | 16.5691 | 49.6011 | 27.7869 | 27.7869 | 0 | 0
2025-01-09 15:00 | 22.2 | 51.5 | 100 | 23.3468 | 16.5483 | 50.1441 | 29.2792 | 29.2792 | 0 | 0
2025-01-09 16:00 | 21.8 | 53.5 | 100 | 23.2001 | 16.5385 | 50.858 | 31.7632 | 31.7632 | 0 | 0
2025-01-09 17:00 | 21.1 | 58 | 100 | 22.9421 | 16.5668 | 52.441 | 38.9016 | 38.9016 | 0 | 0
2025-01-09 18:00 | 20.05 | 65 | 100 | 22.552 | 16.5921 | 54.7917 | 48.7118 | 48.7118 | 0 | 0
2025-01-09 19:00 | 19.1 | 71 | 100 | 22.1951 | 16.5684 | 56.6901 | 54.9005 | 54.9005 | 0 | 0
2025-01-09 20:00 | 18.35 | 75 | 100 | 21.9102 | 16.4963 | 57.8799 | 56.7158 | 56.7158 | 0 | 0
2025-01-09 21:00 | 17.6 | 78.5 | 100 | 21.6223 | 16.3897 | 58.8712 | 56.5606 | 56.5606 | 0 | 0
2025-01-09 22:00 | 16.75 | 82 | 70 | 21.2924 | 16.2359 | 59.8159 | 38.223 | 38.223 | 0 | 0
2025-01-09 23:00 | 15.85 | 86 | 70 | 20.9397 | 16.0763 | 60.876 | 36.9231 | 36.9231 | 0 | 0
2025-01-10 | 15.1 | 89 | 70 | 20.6424 | 15.9202 | 61.638 | 34.9938 | 34.9938 | 0 | 0
2025-01-10 01:00 | 14.5 | 91 | 70 | 20.4023 | 15.7744 | 62.1217 | 32.6567 | 32.6567 | 0 | 0
2025-01-10 02:00 | 14 | 92 | 70 | 20.2002 | 15.6265 | 62.3308 | 29.5886 | 29.5886 | 0 | 0
2025-01-10 03:00 | 13.8 | 92 | 70 | 20.1186 | 15.5514 | 62.3011 | 27.7298 | 27.7298 | 0 | 0
2025-01-10 04:00 | 13.75 | 92.5 | 70 | 20.0986 | 15.5517 | 62.4314 | 28.025 | 28.025 | 0 | 0
2025-01-10 05:00 | 13.45 | 94 | 70 | 19.9773 | 15.4953 | 62.807 | 27.5394 | 27.5394 | 0 | 0
2025-01-10 06:00 | 12.9 | 95.5 | 100 | 19.7525 | 15.3426 | 63.1471 | 35.2845 | 35.2845 | 0 | 0
2025-01-10 07:00 | 12.95 | 94.5 | 100 | 19.7721 | 15.3254 | 62.8723 | 33.767 | 33.767 | 0 | 0
2025-01-10 08:00 | 15.15 | 85.5 | 100 | 20.6593 | 15.7974 | 60.5856 | 42.0729 | 42.0729 | 0 | 0
2025-01-10 09:00 | 18.65 | 71 | 100 | 22.0227 | 16.4118 | 56.574 | 48.8439 | 48.8439 | 0 | 0
2025-01-10 10:00 | 21.35 | 59 | 100 | 23.0356 | 16.7091 | 52.7947 | 44.7473 | 44.7473 | 0 | 0
2025-01-10 11:00 | 23.15 | 48.5 | 100 | 23.6933 | 16.6691 | 49.0232 | 28.3926 | 28.3926 | 0 | 0
2025-01-10 12:00 | 24.4 | 39 | 100 | 24.1437 | 16.4293 | 45.2717 | 4.8217 | 4.8217 | 0 | 0
2025-01-10 13:00 | 25.15 | 33.5 | 100 | 24.4122 | 16.2594 | 42.9682 | 0 | 0 | 0 | 0
2025-01-10 14:00 | 25.2 | 34.5 | 100 | 24.4298 | 16.3435 | 43.3934 | 0 | 0 | 0 | 0
2025-01-10 15:00 | 24.45 | 41.5 | 100 | 24.1614 | 16.6095 | 46.3137 | 15.3052 | 15.3052 | 0 | 0
2025-01-10 16:00 | 23.1 | 51.5 | 100 | 23.6756 | 16.8364 | 50.2151 | 39.0696 | 39.0696 | 0 | 0
2025-01-10 17:00 | 21.55 | 63 | 100 | 23.1113 | 16.998 | 54.3305 | 60.8582 | 60.8582 | 0 | 0
2025-01-10 18:00 | 20.4 | 72 | 100 | 22.6877 | 17.0817 | 57.3118 | 75.0191 | 75.0191 | 0 | 0
2025-01-10 19:00 | 19.5 | 76.5 | 100 | 22.3511 | 16.9859 | 58.6328 | 76.443 | 76.443 | 0 | 0
2025-01-10 20:00 | 18.75 | 77 | 100 | 22.0654 | 16.7373 | 58.6055 | 67.5672 | 67.5672 | 0 | 0
2025-01-10 21:00 | 17.95 | 77 | 100 | 21.7571 | 16.4478 | 58.4272 | 56.8216 | 56.8216 | 0 | 0
2025-01-10 22:00 | 16.9 | 79 | 70 | 21.3489 | 16.1601 | 58.8732 | 33.9297 | 33.9297 | 0 | 0
2025-01-10 23:00 | 15.85 | 81 | 70 | 20.9352 | 15.8668 | 59.3334 | 28.0616 | 28.0616 | 0 | 0
2025-01-11 | 14.9 | 81 | 70 | 20.5544 | 15.5245 | 59.2344 | 19.7544 | 19.7544 | 0 | 0
2025-01-11 01:00 | 14.1 | 78.5 | 70 | 20.2277 | 15.1406 | 58.477 | 9.0358 | 9.0358 | 0 | 0
2025-01-11 02:00 | 13.4 | 76.5 | 70 | 19.9393 | 14.8192 | 57.9249 | 0.3789 | 0.3789 | 0 | 0
2025-01-11 03:00 | 12.7 | 77 | 70 | 19.651 | 14.5961 | 58.1026 | 0 | 0 | 0 | 0
2025-01-11 04:00 | 12.2 | 78.5 | 70 | 19.4447 | 14.4779 | 58.5463 | 0 | 0 | 0 | 0
2025-01-11 05:00 | 11.9 | 78 | 70 | 19.319 | 14.3565 | 58.4405 | 0 | 0 | 0 | 0
2025-01-11 06:00 | 11.6 | 75 | 100 | 19.1902 | 14.1484 | 57.6863 | 0 | 0 | 0 | 0
2025-01-11 07:00 | 12.15 | 67.5 | 100 | 19.4127 | 14.0641 | 55.6021 | 0 | 0 | 0 | 0
2025-01-11 08:00 | 14.7 | 53.5 | 100 | 20.4473 | 14.3256 | 51.166 | 0 | 0 | 0 | 0
2025-01-11 09:00 | 18.45 | 39.5 | 100 | 21.9226 | 14.7761 | 46.0017 | 0 | 0 | 0 | 0
2025-01-11 10:00 | 21.8 | 30.5 | 100 | 23.1918 | 15.177 | 42.1303 | 0 | 0 | 0 | 0
2025-01-11 11:00 | 24.3 | 24.5 | 100 | 24.1087 | 15.4138 | 39.2765 | 0 | 0 | 0 | 0
2025-01-11 12:00 | 25.8 | 21.5 | 100 | 24.6468 | 15.5537 | 37.7183 | 0 | 0 | 0 | 0
2025-01-11 13:00 | 26.6 | 20.5 | 100 | 24.9298 | 15.6608 | 37.1312 | 0 | 0 | 0 | 0
2025-01-11 14:00 | 26.85 | 20.5 | 100 | 25.0175 | 15.7178 | 37.0915 | 0 | 0 | 0 | 0
2025-01-11 15:00 | 26 | 28.5 | 100 | 24.7147 | 16.1221 | 40.7629 | 0 | 0 | 0 | 0
2025-01-11 16:00 | 24.2 | 43.5 | 100 | 24.0718 | 16.6681 | 47.1194 | 20.6366 | 20.6366 | 0 | 0
2025-01-11 17:00 | 22.5 | 55 | 100 | 23.4578 | 16.8547 | 51.4865 | 44.7745 | 44.7745 | 0 | 0
2025-01-11 18:00 | 21.5 | 61.5 | 100 | 23.0922 | 16.8981 | 53.761 | 55.1337 | 55.1337 | 0 | 0
2025-01-11 19:00 | 20.85 | 65 | 100 | 22.8523 | 16.8685 | 54.9082 | 58.4851 | 58.4851 | 0 | 0
2025-01-11 20:00 | 19.9 | 68.5 | 100 | 22.4975 | 16.7242 | 55.9572 | 57.3897 | 57.3897 | 0 | 0
2025-01-11 21:00 | 18.55 | 70 | 100 | 21.9835 | 16.3279 | 56.2328 | 44.775 | 44.775 | 0 | 0
2025-01-11 22:00 | 17.15 | 64.5 | 70 | 21.4348 | 15.5906 | 54.3239 | 9.1412 | 9.1412 | 0 | 0
2025-01-11 23:00 | 15.95 | 58.5 | 70 | 20.9546 | 14.9287 | 52.4997 | 0 | 0 | 0 | 0
2025-01-12 | 15.1 | 57 | 70 | 20.6122 | 14.595 | 52.156 | 0 | 0 | 0 | 0
2025-01-12 01:00 | 14.75 | 56 | 70 | 20.4698 | 14.4436 | 51.9195 | 0 | 0 | 0 | 0
2025-01-12 02:00 | 14.65 | 53.5 | 70 | 20.4269 | 14.308 | 51.207 | 0 | 0 | 0 | 0
2025-01-12 03:00 | 14.4 | 53.5 | 70 | 20.3253 | 14.231 | 51.2636 | 0 | 0 | 0 | 0
2025-01-12 04:00 | 13.9 | 57.5 | 70 | 20.1253 | 14.2403 | 52.5218 | 0 | 0 | 0 | 0
2025-01-12 05:00 | 13.3 | 63 | 70 | 19.8846 | 14.2672 | 54.1842 | 0 | 0 | 0 | 0
2025-01-12 06:00 | 12.4 | 68.5 | 100 | 19.5177 | 14.182 | 55.8428 | 0 | 0 | 0 | 0
2025-01-12 07:00 | 11.9 | 67 | 100 | 19.3077 | 13.9635 | 55.5288 | 0 | 0 | 0 | 0
2025-01-12 08:00 | 13.35 | 54.5 | 100 | 19.8968 | 13.9524 | 51.7753 | 0 | 0 | 0 | 0
2025-01-12 09:00 | 16.35 | 40.5 | 100 | 21.098 | 14.2348 | 46.8341 | 0 | 0 | 0 | 0
2025-01-12 10:00 | 19.65 | 31.5 | 100 | 22.3798 | 14.6727 | 42.9852 | 0 | 0 | 0 | 0
2025-01-12 11:00 | 22.45 | 28 | 100 | 23.4324 | 15.1851 | 41.0586 | 0 | 0 | 0 | 0
2025-01-12 12:00 | 24.25 | 28 | 100 | 24.0905 | 15.641 | 40.7476 | 0 | 0 | 0 | 0
2025-01-12 13:00 | 25.2 | 27 | 100 | 24.4316 | 15.8103 | 40.1999 | 0 | 0 | 0 | 0
2025-01-12 14:00 | 25.4 | 26.5 | 100 | 24.503 | 15.8227 | 39.9639 | 0 | 0 | 0 | 0
2025-01-12 15:00 | 24.75 | 29.5 | 100 | 24.2702 | 15.8714 | 41.3178 | 0 | 0 | 0 | 0
2025-01-12 16:00 | 23.2 | 40 | 100 | 23.7102 | 16.1484 | 45.6922 | 0 | 0 | 0 | 0
2025-01-12 17:00 | 21.25 | 56.5 | 100 | 22.9973 | 16.5347 | 51.8848 | 35.4331 | 35.4331 | 0 | 0
2025-01-12 18:00 | 19.85 | 68 | 100 | 22.4783 | 16.6803 | 55.7822 | 55.288 | 55.288 | 0 | 0
2025-01-12 19:00 | 19.15 | 71 | 100 | 22.2142 | 16.5869 | 56.6778 | 55.354 | 55.354 | 0 | 0
2025-01-12 20:00 | 18.8 | 70.5 | 100 | 22.08 | 16.4396 | 56.4428 | 49.3866 | 49.3866 | 0 | 0
2025-01-12 21:00 | 18.75 | 70 | 100 | 22.0604 | 16.3977 | 56.2632 | 47.2705 | 47.2705 | 0 | 0
2025-01-12 22:00 | 18.5 | 70.5 | 70 | 21.9646 | 16.3346 | 56.3901 | 31.9022 | 31.9022 | 0 | 0
2025-01-12 23:00 | 17.9 | 71.5 | 70 | 21.7334 | 16.1727 | 56.6343 | 28.6621 | 28.6621 | 0 | 0
2025-01-13 | 17.2 | 73 | 70 | 21.4615 | 15.997 | 57.0313 | 25.5006 | 25.5006 | 0 | 0
2025-01-13 01:00 | 16.3 | 75.5 | 70 | 21.109 | 15.7915 | 57.7191 | 22.3729 | 22.3729 | 0 | 0
2025-01-13 02:00 | 15.85 | 77.5 | 70 | 20.9319 | 15.718 | 58.2883 | 22.0533 | 22.0533 | 0 | 0
2025-01-13 03:00 | 16 | 78 | 70 | 20.9921 | 15.7925 | 58.4571 | 24.2327 | 24.2327 | 0 | 0
2025-01-13 04:00 | 16.35 | 77.5 | 70 | 21.1306 | 15.8959 | 58.3437 | 26.397 | 26.397 | 0 | 0
2025-01-13 05:00 | 16 | 82 | 70 | 20.9957 | 15.9634 | 59.6718 | 31.2348 | 31.2348 | 0 | 0
2025-01-13 06:00 | 15.75 | 86 | 100 | 20.8999 | 16.0397 | 60.8384 | 51.2511 | 51.2511 | 0 | 0
2025-01-13 07:00 | 16.4 | 83.5 | 100 | 21.1557 | 16.1739 | 60.1917 | 53.6162 | 53.6162 | 0 | 0
2025-01-13 08:00 | 17.7 | 77.5 | 100 | 21.6604 | 16.3808 | 58.541 | 54.9124 | 54.9124 | 0 | 0
2025-01-13 09:00 | 20.15 | 67 | 100 | 22.5909 | 16.734 | 55.4681 | 55.8158 | 55.8158 | 0 | 0
2025-01-13 10:00 | 22.1 | 59 | 100 | 23.3125 | 16.9594 | 52.9152 | 53.7811 | 53.7811 | 0 | 0
2025-01-13 11:00 | 22.95 | 54.5 | 100 | 23.6217 | 16.9736 | 51.3403 | 48.0607 | 48.0607 | 0 | 0
2025-01-13 12:00 | 23.15 | 53.5 | 100 | 23.6941 | 16.9766 | 50.9887 | 46.8273 | 46.8273 | 0 | 0
2025-01-13 13:00 | 23.1 | 54.5 | 100 | 23.6761 | 17.0209 | 51.3792 | 49.9723 | 49.9723 | 0 | 0
2025-01-13 14:00 | 23.1 | 54.5 | 100 | 23.6761 | 17.0203 | 51.383 | 50.0076 | 50.0076 | 0 | 0
2025-01-13 15:00 | 22.7 | 57 | 100 | 23.5313 | 17.0399 | 52.2839 | 54.2565 | 54.2565 | 0 | 0
2025-01-13 16:00 | 22.25 | 60.5 | 100 | 23.3679 | 17.0945 | 53.5325 | 61.061 | 61.061 | 0 | 0
2025-01-13 17:00 | 21.6 | 63 | 100 | 23.1298 | 17.0164 | 54.3312 | 61.4047 | 61.4047 | 0 | 0
2025-01-13 18:00 | 20.9 | 65 | 100 | 22.8709 | 16.8862 | 54.9143 | 59.0858 | 59.0858 | 0 | 0
2025-01-13 19:00 | 20.55 | 67 | 100 | 22.7412 | 16.8722 | 55.5557 | 61.0047 | 61.0047 | 0 | 0
2025-01-13 20:00 | 20.15 | 69.5 | 100 | 22.5924 | 16.8638 | 56.3527 | 63.6773 | 63.6773 | 0 | 0
2025-01-13 21:00 | 19.6 | 72 | 100 | 22.3861 | 16.7971 | 57.1 | 64.1162 | 64.1162 | 0 | 0
2025-01-13 22:00 | 19.05 | 73.5 | 70 | 22.1778 | 16.6753 | 57.493 | 42.9339 | 42.9339 | 0 | 0
2025-01-13 23:00 | 18.7 | 74.5 | 70 | 22.0445 | 16.5991 | 57.7583 | 41.7613 | 41.7613 | 0 | 0
2025-01-14 | 18.35 | 76 | 70 | 21.9109 | 16.5451 | 58.1868 | 41.5491 | 41.5491 | 0 | 0
2025-01-14 01:00 | 17.85 | 78 | 70 | 21.7191 | 16.4582 | 58.7396 | 40.8334 | 40.8334 | 0 | 0
2025-01-14 02:00 | 17.45 | 79.5 | 70 | 21.5646 | 16.3814 | 59.1432 | 39.9871 | 39.9871 | 0 | 0
2025-01-14 03:00 | 17.1 | 80.5 | 70 | 21.4286 | 16.2986 | 59.3937 | 38.6135 | 38.6135 | 0 | 0
2025-01-14 04:00 | 17.2 | 78 | 70 | 21.4657 | 16.2231 | 58.6194 | 34.8657 | 34.8657 | 0 | 0
2025-01-14 05:00 | 17.25 | 76 | 70 | 21.4836 | 16.1508 | 57.9888 | 31.5485 | 31.5485 | 0 | 0
2025-01-14 06:00 | 16.55 | 79.5 | 100 | 21.2114 | 16.0553 | 58.9764 | 45.2754 | 45.2754 | 0 | 0
2025-01-14 07:00 | 16.4 | 79 | 100 | 21.1517 | 15.9799 | 58.7944 | 42.0262 | 42.0262 | 0 | 0
2025-01-14 08:00 | 17.9 | 69 | 100 | 21.7314 | 16.0558 | 55.8048 | 33.8638 | 33.8638 | 0 | 0
2025-01-14 09:00 | 20.2 | 58 | 100 | 22.6047 | 16.2766 | 52.2883 | 28.0535 | 28.0535 | 0 | 0
2025-01-14 10:00 | 22 | 51 | 100 | 23.2731 | 16.4621 | 49.8763 | 24.783 | 24.783 | 0 | 0
2025-01-14 11:00 | 23.1 | 45.5 | 100 | 23.6747 | 16.4681 | 47.8338 | 16.7339 | 16.7339 | 0 | 0
2025-01-14 12:00 | 23.65 | 42.5 | 100 | 23.8738 | 16.442 | 46.6737 | 11.1096 | 11.1096 | 0 | 0
2025-01-14 13:00 | 23.8 | 42 | 100 | 23.9279 | 16.4527 | 46.4823 | 10.7272 | 10.7272 | 0 | 0
2025-01-14 14:00 | 23.45 | 44 | 100 | 23.8015 | 16.4772 | 47.2728 | 14.8548 | 14.8548 | 0 | 0
2025-01-14 15:00 | 22.65 | 49 | 100 | 23.5112 | 16.5436 | 49.1862 | 24.9303 | 24.9303 | 0 | 0
2025-01-14 16:00 | 22.1 | 50.5 | 100 | 23.3097 | 16.4618 | 49.7184 | 24.3384 | 24.3384 | 0 | 0
2025-01-14 17:00 | 21.55 | 48.5 | 100 | 23.1055 | 16.1745 | 48.9389 | 11.6623 | 11.6623 | 0 | 0
2025-01-14 18:00 | 20.6 | 50 | 100 | 22.751 | 15.9674 | 49.4694 | 6.9419 | 6.9419 | 0 | 0
2025-01-14 19:00 | 19.65 | 54 | 100 | 22.3937 | 15.8863 | 50.8701 | 9.7369 | 9.7369 | 0 | 0
2025-01-14 20:00 | 18.8 | 59.5 | 100 | 22.0722 | 15.8959 | 52.7259 | 17.1071 | 17.1071 | 0 | 0
2025-01-14 21:00 | 18.15 | 65 | 100 | 21.8253 | 15.9503 | 54.5185 | 25.6008 | 25.6008 | 0 | 0
2025-01-14 22:00 | 17.65 | 69 | 70 | 21.6341 | 15.9701 | 55.7789 | 21.608 | 21.608 | 0 | 0
2025-01-14 23:00 | 17.05 | 73 | 70 | 21.4027 | 15.9452 | 56.9964 | 24.1102 | 24.1102 | 0 | 0
2025-01-15 | 16.3 | 76 | 70 | 21.1095 | 15.8139 | 57.8542 | 23.1576 | 23.1576 | 0 | 0
2025-01-15 01:00 | 15.5 | 77.5 | 70 | 20.7922 | 15.5951 | 58.2366 | 18.945 | 18.945 | 0 | 0
2025-01-15 02:00 | 14.65 | 79.5 | 70 | 20.452 | 15.3754 | 58.7706 | 15.1158 | 15.1158 | 0 | 0
2025-01-15 03:00 | 13.65 | 84 | 70 | 20.0494 | 15.193 | 60.0053 | 13.8291 | 13.8291 | 0 | 0
2025-01-15 04:00 | 13.25 | 84 | 70 | 19.8852 | 15.0501 | 59.9896 | 10.4598 | 10.4598 | 0 | 0
2025-01-15 05:00 | 13.3 | 81.5 | 70 | 19.9033 | 14.9745 | 59.2942 | 7.0694 | 7.0694 | 0 | 0
2025-01-15 06:00 | 13 | 83 | 100 | 19.7812 | 14.9233 | 59.7003 | 9.7697 | 9.7697 | 0 | 0
2025-01-15 07:00 | 13.4 | 81 | 100 | 19.9439 | 14.9912 | 59.1401 | 10.0583 | 10.0583 | 0 | 0
2025-01-15 08:00 | 15.55 | 71 | 100 | 20.8063 | 15.3401 | 56.2607 | 11.5045 | 11.5045 | 0 | 0
2025-01-15 09:00 | 18.7 | 58 | 100 | 22.0327 | 15.7914 | 52.1811 | 11.3208 | 11.3208 | 0 | 0
2025-01-15 10:00 | 21.3 | 47.5 | 100 | 23.0121 | 16.0455 | 48.5137 | 5.2984 | 5.2984 | 0 | 0
2025-01-15 11:00 | 23 | 41.5 | 100 | 23.6375 | 16.1918 | 46.2327 | 0.7409 | 0.7409 | 0 | 0
2025-01-15 12:00 | 24.15 | 39 | 100 | 24.054 | 16.3622 | 45.2372 | 2.1561 | 2.1561 | 0 | 0
2025-01-15 13:00 | 24.85 | 37.5 | 100 | 24.3047 | 16.4591 | 44.6277 | 2.7869 | 2.7869 | 0 | 0
2025-01-15 14:00 | 24.95 | 39.5 | 100 | 24.3399 | 16.6243 | 45.4741 | 11.9153 | 11.9153 | 0 | 0
2025-01-15 15:00 | 24.2 | 47 | 100 | 24.0717 | 16.9 | 48.5239 | 34.0565 | 34.0565 | 0 | 0
2025-01-15 16:00 | 23 | 55.5 | 100 | 23.64 | 17.0502 | 51.7386 | 52.298 | 52.298 | 0 | 0
2025-01-15 17:00 | 22 | 62 | 100 | 23.2768 | 17.0975 | 54.0263 | 62.9244 | 62.9244 | 0 | 0
2025-01-15 18:00 | 21.3 | 67 | 100 | 23.0205 | 17.1349 | 55.7141 | 70.6963 | 70.6963 | 0 | 0
2025-01-15 19:00 | 20.65 | 69.5 | 100 | 22.7799 | 17.041 | 56.4534 | 70.1502 | 70.1502 | 0 | 0
2025-01-15 20:00 | 19.8 | 70.5 | 100 | 22.4609 | 16.7927 | 56.6059 | 62.0079 | 62.0079 | 0 | 0
2025-01-15 21:00 | 19.1 | 71 | 100 | 22.1952 | 16.5715 | 56.6329 | 54.4015 | 54.4015 | 0 | 0
2025-01-15 22:00 | 18.6 | 71.5 | 70 | 22.0039 | 16.4201 | 56.708 | 34.6093 | 34.6093 | 0 | 0
2025-01-15 23:00 | 17.8 | 73 | 70 | 21.6957 | 16.2093 | 57.0749 | 30.5051 | 30.5051 | 0 | 0
2025-01-16 | 16.85 | 75 | 70 | 21.3258 | 15.9651 | 57.591 | 26.0143 | 26.0143 | 0 | 0
2025-01-16 01:00 | 16.1 | 77 | 70 | 21.031 | 15.7867 | 58.1298 | 23.1511 | 23.1511 | 0 | 0
2025-01-16 02:00 | 15.75 | 77.5 | 70 | 20.8921 | 15.6838 | 58.2491 | 21.0263 | 21.0263 | 0 | 0
2025-01-16 03:00 | 15.6 | 77 | 70 | 20.8317 | 15.6097 | 58.0897 | 18.9081 | 18.9081 | 0 | 0
2025-01-16 04:00 | 15.5 | 76 | 70 | 20.7908 | 15.5325 | 57.7849 | 16.3656 | 16.3656 | 0 | 0
2025-01-16 05:00 | 15.1 | 76 | 70 | 20.6302 | 15.3922 | 57.7634 | 13.0497 | 13.0497 | 0 | 0
2025-01-16 06:00 | 14.3 | 78 | 100 | 20.3086 | 15.1924 | 58.3178 | 13.9436 | 13.9436 | 0 | 0
2025-01-16 07:00 | 14.3 | 77.5 | 100 | 20.3082 | 15.1727 | 58.1692 | 12.7604 | 12.7604 | 0 | 0
2025-01-16 08:00 | 16.35 | 69.5 | 100 | 21.1236 | 15.548 | 55.8369 | 16.9235 | 16.9235 | 0 | 0
2025-01-16 09:00 | 19.65 | 56.5 | 100 | 22.3954 | 16.0198 | 51.7113 | 17.1685 | 17.1685 | 0 | 0
2025-01-16 10:00 | 22.2 | 48.5 | 100 | 23.346 | 16.3785 | 48.9251 | 18.0177 | 18.0177 | 0 | 0
2025-01-16 11:00 | 23.7 | 45 | 100 | 23.892 | 16.6201 | 47.6517 | 20.8647 | 20.8647 | 0 | 0
2025-01-16 12:00 | 24.65 | 42 | 100 | 24.2327 | 16.707 | 46.4966 | 18.9647 | 18.9647 | 0 | 0
2025-01-16 13:00 | 24.9 | 44 | 100 | 24.3213 | 16.9147 | 47.3563 | 29.6565 | 29.6565 | 0 | 0
2025-01-16 14:00 | 24.35 | 49 | 100 | 24.1251 | 17.0765 | 49.3602 | 43.5351 | 43.5351 | 0 | 0
2025-01-16 15:00 | 23.65 | 52 | 100 | 23.8744 | 17.0455 | 50.467 | 47.0186 | 47.0186 | 0 | 0
2025-01-16 16:00 | 23.25 | 54 | 100 | 23.7303 | 17.0406 | 51.1949 | 49.7878 | 49.7878 | 0 | 0
2025-01-16 17:00 | 22.45 | 57.5 | 100 | 23.4402 | 16.9878 | 52.414 | 52.843 | 52.843 | 0 | 0
2025-01-16 18:00 | 21.45 | 63 | 100 | 23.0744 | 16.9663 | 54.2835 | 59.3484 | 59.3484 | 0 | 0
2025-01-16 19:00 | 20.5 | 69.5 | 100 | 22.7238 | 16.9875 | 56.4256 | 68.2288 | 68.2288 | 0 | 0
2025-01-16 20:00 | 19.5 | 76 | 100 | 22.3507 | 16.9618 | 58.4453 | 74.7965 | 74.7965 | 0 | 0
2025-01-16 21:00 | 18.75 | 82 | 100 | 22.069 | 16.9776 | 60.2629 | 81.9142 | 81.9142 | 0 | 0
2025-01-16 22:00 | 18.15 | 86 | 70 | 21.8414 | 16.9393 | 61.4025 | 59.2208 | 59.2208 | 0 | 0
2025-01-16 23:00 | 17.65 | 86.5 | 70 | 21.6482 | 16.773 | 61.4198 | 55.1371 | 55.1371 | 0 | 0
2025-01-17 | 17.1 | 86 | 70 | 21.4333 | 16.5431 | 61.1188 | 48.7586 | 48.7586 | 0 | 0
2025-01-17 01:00 | 16.35 | 87 | 70 | 21.139 | 16.3051 | 61.2572 | 43.2974 | 43.2974 | 0 | 0
2025-01-17 02:00 | 15.55 | 88 | 70 | 20.8219 | 16.048 | 61.4 | 37.4188 | 37.4188 | 0 | 0
2025-01-17 03:00 | 14.95 | 89 | 70 | 20.5821 | 15.8642 | 61.5918 | 33.4729 | 33.4729 | 0 | 0
2025-01-17 04:00 | 14.75 | 89.5 | 70 | 20.502 | 15.8098 | 61.7051 | 32.4301 | 32.4301 | 0 | 0
2025-01-17 05:00 | 14.75 | 89 | 70 | 20.5015 | 15.79 | 61.56 | 31.6139 | 31.6139 | 0 | 0
2025-01-17 06:00 | 14.6 | 89.5 | 100 | 20.4414 | 15.7537 | 61.6781 | 44.3099 | 44.3099 | 0 | 0
2025-01-17 07:00 | 14.9 | 89 | 100 | 20.562 | 15.8458 | 61.5742 | 47.0776 | 47.0776 | 0 | 0
2025-01-17 08:00 | 16.5 | 82.5 | 100 | 21.1943 | 16.168 | 59.8948 | 52.3284 | 52.3284 | 0 | 0
2025-01-17 09:00 | 18.9 | 73 | 100 | 22.1201 | 16.5975 | 57.2911 | 57.878 | 57.878 | 0 | 0
2025-01-17 10:00 | 20.8 | 65 | 100 | 22.8336 | 16.8524 | 54.888 | 57.7574 | 57.7574 | 0 | 0
2025-01-17 11:00 | 21.9 | 57.5 | 100 | 23.2384 | 16.8053 | 52.3325 | 46.3225 | 46.3225 | 0 | 0
2025-01-17 12:00 | 22.55 | 53 | 100 | 23.4756 | 16.7522 | 50.7238 | 38.2131 | 38.2131 | 0 | 0
2025-01-17 13:00 | 22.6 | 54 | 100 | 23.4941 | 16.8273 | 51.1224 | 42.4281 | 42.4281 | 0 | 0
2025-01-17 14:00 | 22.25 | 56 | 100 | 23.3666 | 16.8313 | 51.8434 | 45.4819 | 45.4819 | 0 | 0
2025-01-17 15:00 | 21.85 | 57 | 100 | 23.2198 | 16.7573 | 52.1668 | 44.28 | 44.28 | 0 | 0
2025-01-17 16:00 | 21.45 | 59 | 100 | 23.0727 | 16.7393 | 52.8518 | 46.3259 | 46.3259 | 0 | 0
2025-01-17 17:00 | 20.7 | 62 | 100 | 22.7947 | 16.6537 | 53.8304 | 47.1709 | 47.1709 | 0 | 0
2025-01-17 18:00 | 19.6 | 67 | 100 | 22.3829 | 16.5412 | 55.4145 | 49.2827 | 49.2827 | 0 | 0
2025-01-17 19:00 | 18.7 | 72.5 | 100 | 22.043 | 16.5005 | 57.1235 | 54.1625 | 54.1625 | 0 | 0
2025-01-17 20:00 | 17.9 | 76 | 100 | 21.7369 | 16.3816 | 58.1292 | 53.7039 | 53.7039 | 0 | 0
2025-01-17 21:00 | 17.1 | 77.5 | 100 | 21.4261 | 16.1632 | 58.4752 | 47.44 | 47.44 | 0 | 0
2025-01-17 22:00 | 16.45 | 78 | 70 | 21.1705 | 15.9523 | 58.539 | 28.3363 | 28.3363 | 0 | 0
2025-01-17 23:00 | 16.05 | 75.5 | 70 | 21.0097 | 15.702 | 57.7291 | 20.4327 | 20.4327 | 0 | 0
2025-01-18 | 15.75 | 71 | 70 | 20.886 | 15.4046 | 56.3494 | 10.1168 | 10.1168 | 0 | 0
2025-01-18 01:00 | 15.5 | 68.5 | 70 | 20.7836 | 15.2126 | 55.5982 | 3.8661 | 3.8661 | 0 | 0
2025-01-18 02:00 | 15.4 | 68.5 | 70 | 20.7435 | 15.1789 | 55.6033 | 3.1203 | 3.1203 | 0 | 0
2025-01-18 03:00 | 15.4 | 70.5 | 70 | 20.7454 | 15.2632 | 56.2049 | 6.5514 | 6.5514 | 0 | 0
2025-01-18 04:00 | 15.5 | 70.5 | 70 | 20.7855 | 15.2972 | 56.2046 | 7.3309 | 7.3309 | 0 | 0
2025-01-18 05:00 | 15.5 | 73 | 70 | 20.7878 | 15.4031 | 56.9511 | 11.5968 | 11.5968 | 0 | 0
2025-01-18 06:00 | 15.45 | 78.5 | 100 | 20.7729 | 15.6165 | 58.59 | 29.363 | 29.363 | 0 | 0
2025-01-18 07:00 | 15.65 | 80 | 100 | 20.8543 | 15.7508 | 59.0544 | 35.4706 | 35.4706 | 0 | 0
2025-01-18 08:00 | 16.9 | 76.5 | 100 | 21.3467 | 16.0472 | 58.1314 | 42.2555 | 42.2555 | 0 | 0
2025-01-18 09:00 | 19.45 | 68.5 | 100 | 22.3268 | 16.5652 | 55.903 | 51.9187 | 51.9187 | 0 | 0
2025-01-18 10:00 | 21.65 | 58.5 | 100 | 23.1465 | 16.7774 | 52.6943 | 47.0043 | 47.0043 | 0 | 0
2025-01-18 11:00 | 22.45 | 53 | 100 | 23.439 | 16.718 | 50.7339 | 37.2844 | 37.2844 | 0 | 0
2025-01-18 12:00 | 22.7 | 50 | 100 | 23.5297 | 16.6159 | 49.6132 | 29.4085 | 29.4085 | 0 | 0
2025-01-18 13:00 | 22.35 | 50 | 100 | 23.4015 | 16.506 | 49.5922 | 25.692 | 25.692 | 0 | 0
2025-01-18 14:00 | 21.6 | 53.5 | 100 | 23.126 | 16.473 | 50.8561 | 29.6902 | 29.6902 | 0 | 0
2025-01-18 15:00 | 21.45 | 54 | 100 | 23.0706 | 16.4538 | 51.0297 | 29.7305 | 29.7305 | 0 | 0
2025-01-18 16:00 | 21.45 | 52.5 | 100 | 23.0699 | 16.3681 | 50.4723 | 24.6493 | 24.6493 | 0 | 0
2025-01-18 17:00 | 20.9 | 50.5 | 100 | 22.8638 | 16.0827 | 49.7091 | 12.1286 | 12.1286 | 0 | 0
2025-01-18 18:00 | 20.15 | 53.5 | 100 | 22.5831 | 16.0128 | 50.7619 | 13.925 | 13.925 | 0 | 0
2025-01-18 19:00 | 19.75 | 56.5 | 100 | 22.4332 | 16.0457 | 51.7958 | 18.9555 | 18.9555 | 0 | 0
2025-01-18 20:00 | 19.4 | 57 | 100 | 22.3003 | 15.9593 | 51.9497 | 16.6475 | 16.6475 | 0 | 0
2025-01-18 21:00 | 19.1 | 58 | 100 | 22.1862 | 15.9139 | 52.2799 | 16.3882 | 16.3882 | 0 | 0
2025-01-18 22:00 | 18.85 | 57.5 | 70 | 22.0899 | 15.8076 | 52.1029 | 8.5481 | 8.5481 | 0 | 0
2025-01-18 23:00 | 18.65 | 57 | 70 | 22.0125 | 15.7181 | 51.9327 | 6.0423 | 6.0423 | 0 | 0
2025-01-19 | 18.4 | 57.5 | 70 | 21.9163 | 15.6627 | 52.1019 | 5.2285 | 5.2285 | 0 | 0
2025-01-19 01:00 | 18.15 | 57.5 | 70 | 21.8195 | 15.5825 | 52.1033 | 3.3954 | 3.3954 | 0 | 0
2025-01-19 02:00 | 18.05 | 57 | 70 | 21.7802 | 15.5257 | 51.9399 | 1.678 | 1.678 | 0 | 0
2025-01-19 03:00 | 17.9 | 57.5 | 70 | 21.7223 | 15.5019 | 52.1079 | 1.5818 | 1.5818 | 0 | 0
2025-01-19 04:00 | 17.9 | 56.5 | 70 | 21.7215 | 15.4536 | 51.7776 | 0 | 0 | 0 | 0
2025-01-19 05:00 | 17.8 | 55.5 | 70 | 21.6817 | 15.3739 | 51.4514 | 0 | 0 | 0 | 0
2025-01-19 06:00 | 17.45 | 56.5 | 100 | 21.5458 | 15.3116 | 51.7897 | 0 | 0 | 0 | 0
2025-01-19 07:00 | 17.7 | 56 | 100 | 21.6431 | 15.3674 | 51.6083 | 0 | 0 | 0 | 0
2025-01-19 08:00 | 19.1 | 51.5 | 100 | 22.1818 | 15.5817 | 50.0401 | 0 | 0 | 0 | 0
2025-01-19 09:00 | 20.9 | 44.5 | 100 | 22.861 | 15.7478 | 47.4828 | 0 | 0 | 0 | 0
2025-01-19 10:00 | 21.95 | 40 | 100 | 23.2508 | 15.7897 | 45.7466 | 0 | 0 | 0 | 0
2025-01-19 11:00 | 22.4 | 37.5 | 100 | 23.4164 | 15.7637 | 44.7615 | 0 | 0 | 0 | 0
2025-01-19 12:00 | 22.7 | 36 | 100 | 23.5265 | 15.7528 | 44.1604 | 0 | 0 | 0 | 0
2025-01-19 13:00 | 22.75 | 35.5 | 100 | 23.5447 | 15.7343 | 43.9672 | 0 | 0 | 0 | 0
2025-01-19 14:00 | 22.45 | 36 | 100 | 23.4344 | 15.6827 | 44.1955 | 0 | 0 | 0 | 0
2025-01-19 15:00 | 22.05 | 38 | 100 | 23.2872 | 15.6942 | 45.0022 | 0 | 0 | 0 | 0
2025-01-19 16:00 | 21.8 | 40 | 100 | 23.1951 | 15.7444 | 45.7795 | 0 | 0 | 0 | 0
2025-01-19 17:00 | 21.25 | 43.5 | 100 | 22.9916 | 15.7909 | 47.1179 | 0 | 0 | 0 | 0
2025-01-19 18:00 | 20.4 | 47.5 | 100 | 22.6742 | 15.7641 | 48.6056 | 0 | 0 | 0 | 0
2025-01-19 19:00 | 19.7 | 50.5 | 100 | 22.4105 | 15.7138 | 49.6817 | 0 | 0 | 0 | 0
2025-01-19 20:00 | 19.1 | 53.5 | 100 | 22.1832 | 15.6847 | 50.7267 | 2.8059 | 2.8059 | 0 | 0
2025-01-19 21:00 | 18.5 | 56.5 | 100 | 21.9543 | 15.6464 | 51.7457 | 5.4425 | 5.4425 | 0 | 0
2025-01-19 22:00 | 17.95 | 59.5 | 70 | 21.7433 | 15.6167 | 52.7401 | 5.7409 | 5.7409 | 0 | 0
2025-01-19 23:00 | 17.55 | 63.5 | 70 | 21.5906 | 15.6758 | 54.0367 | 10.4758 | 10.4758 | 0 | 0
2025-01-20 | 17.25 | 67 | 70 | 21.4761 | 15.7383 | 55.1487 | 14.7746 | 14.7746 | 0 | 0
2025-01-20 01:00 | 16.8 | 70 | 70 | 21.3017 | 15.7211 | 56.0738 | 16.728 | 16.728 | 0 | 0
2025-01-20 02:00 | 16.3 | 72.5 | 70 | 21.1063 | 15.6596 | 56.8204 | 17.1581 | 17.1581 | 0 | 0
2025-01-20 03:00 | 15.9 | 73 | 70 | 20.9477 | 15.5422 | 56.95 | 14.7509 | 14.7509 | 0 | 0
2025-01-20 04:00 | 15.3 | 76 | 70 | 20.7105 | 15.4603 | 57.8189 | 14.9577 | 14.9577 | 0 | 0
2025-01-20 05:00 | 14.9 | 79.5 | 70 | 20.5528 | 15.4631 | 58.8245 | 17.4385 | 17.4385 | 0 | 0
2025-01-20 06:00 | 14.75 | 80.5 | 100 | 20.4933 | 15.4502 | 59.1004 | 25.3958 | 25.3958 | 0 | 0
2025-01-20 07:00 | 15.25 | 78 | 100 | 20.6923 | 15.526 | 58.3918 | 25.4509 | 25.4509 | 0 | 0
2025-01-20 08:00 | 17.25 | 69 | 100 | 21.4778 | 15.8313 | 55.7635 | 26.2977 | 26.2977 | 0 | 0
2025-01-20 09:00 | 19.55 | 57.5 | 100 | 22.3579 | 16.0372 | 52.0852 | 19.4173 | 19.4173 | 0 | 0
2025-01-20 10:00 | 20.85 | 50.5 | 100 | 22.8452 | 16.0727 | 49.649 | 11.0835 | 11.0835 | 0 | 0
2025-01-20 11:00 | 21.45 | 48 | 100 | 23.0681 | 16.1151 | 48.7471 | 8.9137 | 8.9137 | 0 | 0
2025-01-20 12:00 | 21.8 | 46.5 | 100 | 23.1975 | 16.1332 | 48.1994 | 7.3658 | 7.3658 | 0 | 0
2025-01-20 13:00 | 21.85 | 46 | 100 | 23.2159 | 16.1181 | 48.0197 | 6.207 | 6.207 | 0 | 0
2025-01-20 14:00 | 21.65 | 46 | 100 | 23.1417 | 16.0573 | 48.0246 | 4.285 | 4.285 | 0 | 0
2025-01-20 15:00 | 21.25 | 47 | 100 | 22.9931 | 15.9946 | 48.3992 | 3.756 | 3.756 | 0 | 0
2025-01-20 16:00 | 20.85 | 49 | 100 | 22.8444 | 15.9859 | 49.1316 | 6.4094 | 6.4094 | 0 | 0
2025-01-20 17:00 | 20.2 | 52.5 | 100 | 22.6015 | 15.9773 | 50.3803 | 11.0359 | 11.0359 | 0 | 0
2025-01-20 18:00 | 19.3 | 57.5 | 100 | 22.2624 | 15.955 | 52.0953 | 16.8777 | 16.8777 | 0 | 0
2025-01-20 19:00 | 18.6 | 61.5 | 100 | 21.9966 | 15.9281 | 53.4121 | 20.9246 | 20.9246 | 0 | 0
2025-01-20 20:00 | 18.05 | 64.5 | 100 | 21.7861 | 15.8914 | 54.3694 | 23.2313 | 23.2313 | 0 | 0
2025-01-20 21:00 | 17.6 | 67.5 | 100 | 21.6134 | 15.8814 | 55.3125 | 26.35 | 26.35 | 0 | 0
2025-01-20 22:00 | 17.1 | 69.5 | 70 | 21.4194 | 15.8025 | 55.916 | 18.1413 | 18.1413 | 0 | 0
2025-01-20 23:00 | 16.6 | 71 | 70 | 21.2237 | 15.6981 | 56.3565 | 16.8185 | 16.8185 | 0 | 0
2025-01-21 | 16.25 | 73.5 | 70 | 21.0873 | 15.6867 | 57.1102 | 18.4448 | 18.4448 | 0 | 0
2025-01-21 01:00 | 16 | 76 | 70 | 20.9903 | 15.7068 | 57.8573 | 20.774 | 20.774 | 0 | 0
2025-01-21 02:00 | 15.95 | 76.5 | 70 | 20.9708 | 15.7105 | 58.0061 | 21.2312 | 21.2312 | 0 | 0
2025-01-21 03:00 | 16.2 | 74 | 70 | 21.0679 | 15.6906 | 57.2649 | 18.9442 | 18.9442 | 0 | 0
2025-01-21 04:00 | 16.2 | 71 | 70 | 21.0653 | 15.5597 | 56.3446 | 13.6153 | 13.6153 | 0 | 0
2025-01-21 05:00 | 16.4 | 65.5 | 70 | 21.1397 | 15.3848 | 54.6492 | 5.3239 | 5.3239 | 0 | 0
2025-01-21 06:00 | 16.9 | 61 | 100 | 21.3335 | 15.3464 | 53.2276 | 1.1412 | 1.1412 | 0 | 0
2025-01-21 07:00 | 17.45 | 60.5 | 100 | 21.5491 | 15.5027 | 53.0523 | 5.5398 | 5.5398 | 0 | 0
2025-01-21 08:00 | 19.2 | 54.5 | 100 | 22.2222 | 15.7694 | 51.0473 | 6.6469 | 6.6469 | 0 | 0
2025-01-21 09:00 | 20.95 | 47.5 | 100 | 22.8812 | 15.9348 | 48.5589 | 2.2318 | 2.2318 | 0 | 0
2025-01-21 10:00 | 21.8 | 43 | 100 | 23.1963 | 15.9283 | 46.8696 | 0 | 0 | 0 | 0
2025-01-21 11:00 | 22.3 | 39.5 | 100 | 23.3801 | 15.8613 | 45.5198 | 0 | 0 | 0 | 0
2025-01-21 12:00 | 22.45 | 39.5 | 100 | 23.4354 | 15.903 | 45.5205 | 0 | 0 | 0 | 0
2025-01-21 13:00 | 22.45 | 40.5 | 100 | 23.4357 | 15.963 | 45.914 | 0 | 0 | 0 | 0
2025-01-21 14:00 | 22.3 | 40.5 | 100 | 23.3804 | 15.9199 | 45.9255 | 0 | 0 | 0 | 0
2025-01-21 15:00 | 21.85 | 40.5 | 100 | 23.2139 | 15.7897 | 45.9529 | 0 | 0 | 0 | 0
2025-01-21 16:00 | 21.3 | 42.5 | 100 | 23.0099 | 15.7488 | 46.7337 | 0 | 0 | 0 | 0
2025-01-21 17:00 | 20.7 | 46 | 100 | 22.7865 | 15.7724 | 48.043 | 0 | 0 | 0 | 0
2025-01-21 18:00 | 20.15 | 49 | 100 | 22.5806 | 15.7722 | 49.1336 | 0 | 0 | 0 | 0
2025-01-21 19:00 | 19.9 | 50 | 100 | 22.4863 | 15.7496 | 49.4896 | 0.0592 | 0.0592 | 0 | 0
2025-01-21 20:00 | 19.75 | 49.5 | 100 | 22.429 | 15.6777 | 49.3149 | 0 | 0 | 0 | 0
2025-01-21 21:00 | 19.7 | 49 | 100 | 22.4096 | 15.6361 | 49.1384 | 0 | 0 | 0 | 0
2025-01-21 22:00 | 19.65 | 50 | 70 | 22.3912 | 15.6739 | 49.4881 | 0 | 0 | 0 | 0
2025-01-21 23:00 | 19.5 | 50.5 | 70 | 22.3343 | 15.6544 | 49.6681 | 0 | 0 | 0 | 0
2025-01-22 | 19.3 | 51 | 70 | 22.2582 | 15.6188 | 49.8499 | 0 | 0 | 0 | 0
2025-01-22 01:00 | 19.05 | 53 | 70 | 22.1637 | 15.6442 | 50.5442 | 0.488 | 0.488 | 0 | 0
2025-01-22 02:00 | 18.6 | 54.5 | 70 | 21.9915 | 15.5791 | 51.0629 | 0.4005 | 0.4005 | 0 | 0
2025-01-22 03:00 | 17.8 | 55.5 | 70 | 21.6818 | 15.3761 | 51.4238 | 0 | 0 | 0 | 0
2025-01-22 04:00 | 17.2 | 54.5 | 70 | 21.4461 | 15.1402 | 51.1394 | 0 | 0 | 0 | 0
2025-01-22 05:00 | 16.55 | 54 | 70 | 21.1891 | 14.9148 | 51.0419 | 0 | 0 | 0 | 0
2025-01-22 06:00 | 15.4 | 57.5 | 100 | 20.7335 | 14.7117 | 52.2526 | 0 | 0 | 0 | 0
2025-01-22 07:00 | 14.85 | 61 | 100 | 20.5151 | 14.6858 | 53.3546 | 0 | 0 | 0 | 0
2025-01-22 08:00 | 16.25 | 58 | 100 | 21.0737 | 15.0041 | 52.2913 | 0 | 0 | 0 | 0
2025-01-22 09:00 | 19 | 47 | 100 | 22.1404 | 15.3226 | 48.4594 | 0 | 0 | 0 | 0
2025-01-22 10:00 | 21.45 | 35.5 | 100 | 23.0631 | 15.386 | 44.0639 | 0 | 0 | 0 | 0
2025-01-22 11:00 | 23.2 | 26.5 | 100 | 23.7083 | 15.2796 | 40.3 | 0 | 0 | 0 | 0
2025-01-22 12:00 | 24.15 | 21.5 | 100 | 24.0545 | 15.1681 | 38.0738 | 0 | 0 | 0 | 0
2025-01-22 13:00 | 24.45 | 20.5 | 100 | 24.1632 | 15.1654 | 37.5942 | 0 | 0 | 0 | 0
2025-01-22 14:00 | 24.65 | 20.5 | 100 | 24.2355 | 15.211 | 37.5481 | 0 | 0 | 0 | 0
2025-01-22 15:00 | 24.4 | 23 | 100 | 24.145 | 15.33 | 38.6486 | 0 | 0 | 0 | 0
2025-01-22 16:00 | 23.45 | 29 | 100 | 23.8 | 15.505 | 41.2739 | 0 | 0 | 0 | 0
2025-01-22 17:00 | 22.1 | 34.5 | 100 | 23.3046 | 15.4994 | 43.6194 | 0 | 0 | 0 | 0
2025-01-22 18:00 | 20.9 | 37 | 100 | 22.8574 | 15.3207 | 44.7128 | 0 | 0 | 0 | 0
2025-01-22 19:00 | 20.05 | 40 | 100 | 22.5375 | 15.2532 | 45.9054 | 0 | 0 | 0 | 0
2025-01-22 20:00 | 18.95 | 42.5 | 100 | 22.1181 | 15.0739 | 46.9255 | 0 | 0 | 0 | 0
2025-01-22 21:00 | 17.6 | 43 | 100 | 21.5939 | 14.7113 | 47.3202 | 0 | 0 | 0 | 0
2025-01-22 22:00 | 16.25 | 44 | 70 | 21.0614 | 14.3704 | 47.9319 | 0 | 0 | 0 | 0
2025-01-22 23:00 | 15.1 | 47 | 70 | 20.603 | 14.1695 | 49.1332 | 0 | 0 | 0 | 0
2025-01-23 | 14.25 | 49.5 | 70 | 20.2607 | 14.0236 | 50.0929 | 0 | 0 | 0 | 0
2025-01-23 01:00 | 13.45 | 51 | 70 | 19.9346 | 13.8458 | 50.7456 | 0 | 0 | 0 | 0
2025-01-23 02:00 | 12.6 | 53 | 70 | 19.5853 | 13.6676 | 51.5561 | 0 | 0 | 0 | 0
2025-01-23 03:00 | 12.2 | 51.5 | 70 | 19.4174 | 13.4907 | 51.2803 | 0 | 0 | 0 | 0
2025-01-23 04:00 | 12.6 | 47 | 70 | 19.5793 | 13.4384 | 49.9187 | 0 | 0 | 0 | 0
2025-01-23 05:00 | 13.1 | 48.5 | 70 | 19.7879 | 13.6427 | 50.1578 | 0 | 0 | 0 | 0
2025-01-23 06:00 | 13.2 | 55 | 100 | 19.8356 | 13.9272 | 51.9332 | 0 | 0 | 0 | 0
2025-01-23 07:00 | 13.7 | 56 | 100 | 20.0423 | 14.1216 | 52.085 | 0 | 0 | 0 | 0
2025-01-23 08:00 | 15.8 | 50 | 100 | 20.8872 | 14.5096 | 49.8686 | 0 | 0 | 0 | 0
2025-01-23 09:00 | 19 | 42 | 100 | 22.1371 | 15.0647 | 46.7247 | 0 | 0 | 0 | 0
2025-01-23 10:00 | 21.7 | 33 | 100 | 23.1554 | 15.3064 | 43.0665 | 0 | 0 | 0 | 0
2025-01-23 11:00 | 23.4 | 24.5 | 100 | 23.7813 | 15.1991 | 39.4401 | 0 | 0 | 0 | 0
2025-01-23 12:00 | 24.3 | 20 | 100 | 24.109 | 15.101 | 37.4001 | 0 | 0 | 0 | 0
2025-01-23 13:00 | 24.75 | 18.5 | 100 | 24.2718 | 15.0933 | 36.6647 | 0 | 0 | 0 | 0
2025-01-23 14:00 | 24.95 | 17.5 | 100 | 24.3441 | 15.0639 | 36.1931 | 0 | 0 | 0 | 0
2025-01-23 15:00 | 24.8 | 17 | 100 | 24.2901 | 14.9937 | 36.0271 | 0 | 0 | 0 | 0
2025-01-23 16:00 | 24.2 | 19 | 100 | 24.0727 | 15.0027 | 37.0354 | 0 | 0 | 0 | 0
2025-01-23 17:00 | 22.65 | 22 | 100 | 23.5049 | 14.8477 | 38.6736 | 0 | 0 | 0 | 0
2025-01-23 18:00 | 20.7 | 25.5 | 100 | 22.7762 | 14.5958 | 40.5528 | 0 | 0 | 0 | 0
2025-01-23 19:00 | 19.3 | 30.5 | 100 | 22.2448 | 14.527 | 42.7301 | 0 | 0 | 0 | 0
2025-01-23 20:00 | 18.1 | 33 | 100 | 21.7816 | 14.3458 | 43.9176 | 0 | 0 | 0 | 0
2025-01-23 21:00 | 16.9 | 34.5 | 100 | 21.3112 | 14.1015 | 44.771 | 0 | 0 | 0 | 0
2025-01-23 22:00 | 15.7 | 39 | 70 | 20.837 | 13.9851 | 46.5601 | 0 | 0 | 0 | 0
2025-01-23 23:00 | 14.5 | 44.5 | 70 | 20.3575 | 13.8864 | 48.5841 | 0 | 0 | 0 | 0
2025-01-24 | 13.4 | 49 | 70 | 19.9119 | 13.7496 | 50.2207 | 0 | 0 | 0 | 0
2025-01-24 01:00 | 12.5 | 52.5 | 70 | 19.5431 | 13.6169 | 51.4751 | 0 | 0 | 0 | 0
2025-01-24 02:00 | 11.85 | 53.5 | 70 | 19.2729 | 13.4577 | 51.9611 | 0 | 0 | 0 | 0
2025-01-24 03:00 | 11.6 | 50.5 | 70 | 19.165 | 13.2735 | 51.2613 | 0 | 0 | 0 | 0
2025-01-24 04:00 | 11.8 | 49.5 | 70 | 19.2479 | 13.2959 | 50.9224 | 0 | 0 | 0 | 0
2025-01-24 05:00 | 11.7 | 53.5 | 70 | 19.21 | 13.4123 | 52.0173 | 0 | 0 | 0 | 0
2025-01-24 06:00 | 11.2 | 59 | 100 | 19.0054 | 13.4561 | 53.6198 | 0 | 0 | 0 | 0
2025-01-24 07:00 | 11.5 | 62 | 100 | 19.1349 | 13.6565 | 54.306 | 0 | 0 | 0 | 0
2025-01-24 08:00 | 13.6 | 57 | 100 | 20.0021 | 14.1282 | 52.4171 | 0 | 0 | 0 | 0
2025-01-24 09:00 | 17.1 | 46 | 100 | 21.3998 | 14.7089 | 48.4039 | 0 | 0 | 0 | 0
2025-01-24 10:00 | 20.5 | 36.5 | 100 | 22.7062 | 15.1814 | 44.5906 | 0 | 0 | 0 | 0
2025-01-24 11:00 | 23.1 | 28 | 100 | 23.6718 | 15.3501 | 40.9314 | 0 | 0 | 0 | 0
2025-01-24 12:00 | 24.7 | 20.5 | 100 | 24.2535 | 15.2215 | 37.5412 | 0 | 0 | 0 | 0
2025-01-24 13:00 | 25.5 | 17.5 | 100 | 24.5414 | 15.1795 | 36.0707 | 0 | 0 | 0 | 0
2025-01-24 14:00 | 25.75 | 16.5 | 100 | 24.6309 | 15.1568 | 35.5764 | 0 | 0 | 0 | 0
2025-01-24 15:00 | 25.05 | 21.5 | 100 | 24.3792 | 15.3719 | 37.9029 | 0 | 0 | 0 | 0
2025-01-24 16:00 | 23.35 | 32.5 | 100 | 23.7639 | 15.7047 | 42.7133 | 0 | 0 | 0 | 0
2025-01-24 17:00 | 21.65 | 41 | 100 | 23.1398 | 15.7626 | 46.1512 | 0 | 0 | 0 | 0
2025-01-24 18:00 | 20.5 | 46.5 | 100 | 22.7115 | 15.7404 | 48.2272 | 0 | 0 | 0 | 0
2025-01-24 19:00 | 19.6 | 50.5 | 100 | 22.3725 | 15.6845 | 49.668 | 0 | 0 | 0 | 0
2025-01-24 20:00 | 18.6 | 55.5 | 100 | 21.9922 | 15.6296 | 51.3947 | 3.4487 | 3.4487 | 0 | 0
2025-01-24 21:00 | 17.35 | 57.5 | 100 | 21.5075 | 15.3291 | 52.0869 | 0 | 0 | 0 | 0
2025-01-24 22:00 | 16.2 | 55 | 70 | 21.051 | 14.8516 | 51.3969 | 0 | 0 | 0 | 0
2025-01-24 23:00 | 15.1 | 55.5 | 70 | 20.6108 | 14.531 | 51.7128 | 0 | 0 | 0 | 0
2025-01-25 | 14 | 59.5 | 70 | 20.1682 | 14.3521 | 53.074 | 0 | 0 | 0 | 0
2025-01-25 01:00 | 13 | 63.5 | 70 | 19.7613 | 14.1895 | 54.3825 | 0 | 0 | 0 | 0
2025-01-25 02:00 | 12.1 | 66.5 | 70 | 19.3906 | 14.01 | 55.3761 | 0 | 0 | 0 | 0
2025-01-25 03:00 | 11.4 | 70 | 70 | 19.1009 | 13.9052 | 56.4454 | 0 | 0 | 0 | 0
2025-01-25 04:00 | 11.3 | 69.5 | 70 | 19.0583 | 13.8545 | 56.3369 | 0 | 0 | 0 | 0
2025-01-25 05:00 | 11.25 | 69 | 70 | 19.0367 | 13.8209 | 56.2161 | 0 | 0 | 0 | 0
2025-01-25 06:00 | 10.75 | 70 | 100 | 18.8265 | 13.6912 | 56.5846 | 0 | 0 | 0 | 0
2025-01-25 07:00 | 10.95 | 65.5 | 100 | 18.9066 | 13.6029 | 55.3757 | 0 | 0 | 0 | 0
2025-01-25 08:00 | 13.05 | 56 | 100 | 19.7746 | 13.9182 | 52.2776 | 0 | 0 | 0 | 0
2025-01-25 09:00 | 16.5 | 45 | 100 | 21.1616 | 14.4864 | 48.2117 | 0 | 0 | 0 | 0
2025-01-25 10:00 | 19.4 | 40 | 100 | 22.2893 | 15.0681 | 46.0122 | 0 | 0 | 0 | 0
2025-01-25 11:00 | 21.4 | 36.5 | 100 | 23.0447 | 15.4283 | 44.4682 | 0 | 0 | 0 | 0
2025-01-25 12:00 | 22.95 | 30.5 | 100 | 23.6172 | 15.4718 | 41.9584 | 0 | 0 | 0 | 0
2025-01-25 13:00 | 23.85 | 28 | 100 | 23.9456 | 15.5366 | 40.8246 | 0 | 0 | 0 | 0
2025-01-25 14:00 | 24.05 | 29 | 100 | 24.0181 | 15.6546 | 41.2083 | 0 | 0 | 0 | 0
2025-01-25 15:00 | 23.6 | 30.5 | 100 | 23.8548 | 15.6386 | 41.8818 | 0 | 0 | 0 | 0
2025-01-25 16:00 | 22.6 | 36 | 100 | 23.4897 | 15.7253 | 44.1722 | 0 | 0 | 0 | 0
2025-01-25 17:00 | 21.3 | 49 | 100 | 23.0127 | 16.1244 | 49.1391 | 10.9877 | 10.9877 | 0 | 0
2025-01-25 18:00 | 20.1 | 61.5 | 100 | 22.5689 | 16.4262 | 53.555 | 38.2658 | 38.2658 | 0 | 0
2025-01-25 19:00 | 19.2 | 67 | 100 | 22.2306 | 16.4045 | 55.3332 | 44.1628 | 44.1628 | 0 | 0
2025-01-25 20:00 | 18.5 | 68 | 100 | 21.9628 | 16.2133 | 55.5703 | 38.4967 | 38.4967 | 0 | 0
2025-01-25 21:00 | 17.8 | 66.5 | 100 | 21.6905 | 15.9022 | 55.0066 | 25.9468 | 25.9468 | 0 | 0
2025-01-25 22:00 | 16.95 | 65 | 70 | 21.3566 | 15.5468 | 54.4865 | 8.5739 | 8.5739 | 0 | 0
2025-01-25 23:00 | 16.15 | 66 | 70 | 21.0409 | 15.3241 | 54.7955 | 4.2609 | 4.2609 | 0 | 0
2025-01-26 | 15.65 | 68.5 | 70 | 20.8438 | 15.2647 | 55.5647 | 4.8403 | 4.8403 | 0 | 0
2025-01-26 01:00 | 15.3 | 72 | 70 | 20.7067 | 15.2938 | 56.6164 | 8.1164 | 8.1164 | 0 | 0
2025-01-26 02:00 | 14.65 | 76.5 | 70 | 20.449 | 15.2534 | 57.9329 | 10.4068 | 10.4068 | 0 | 0
2025-01-26 03:00 | 13.75 | 81 | 70 | 20.0872 | 15.1134 | 59.2044 | 10.2287 | 10.2287 | 0 | 0
2025-01-26 04:00 | 13 | 84.5 | 70 | 19.7825 | 14.9776 | 60.1632 | 9.346 | 9.346 | 0 | 0
2025-01-26 05:00 | 12.5 | 86 | 70 | 19.5771 | 14.8527 | 60.5627 | 7.3862 | 7.3862 | 0 | 0
2025-01-26 06:00 | 12.15 | 85.5 | 100 | 19.431 | 14.7095 | 60.4267 | 5.3886 | 5.3886 | 0 | 0
2025-01-26 07:00 | 12.55 | 80.5 | 100 | 19.5923 | 14.6716 | 59.0644 | 0 | 0 | 0 | 0
2025-01-26 08:00 | 14.9 | 68 | 100 | 20.542 | 14.993 | 55.4208 | 0 | 0 | 0 | 0
2025-01-26 09:00 | 18.45 | 54.5 | 100 | 21.9336 | 15.5332 | 51.0497 | 0 | 0 | 0 | 0
2025-01-26 10:00 | 21.25 | 47 | 100 | 22.9932 | 15.9977 | 48.3712 | 3.503 | 3.503 | 0 | 0
2025-01-26 11:00 | 23.1 | 40.5 | 100 | 23.6738 | 16.1526 | 45.88 | 0 | 0 | 0 | 0
2025-01-26 12:00 | 24.45 | 34 | 100 | 24.1621 | 16.1034 | 43.2147 | 0 | 0 | 0 | 0
2025-01-26 13:00 | 24.95 | 34.5 | 100 | 24.3408 | 16.273 | 43.4092 | 0 | 0 | 0 | 0
2025-01-26 14:00 | 24.5 | 38.5 | 100 | 24.1796 | 16.4207 | 45.0912 | 4.0195 | 4.0195 | 0 | 0
2025-01-26 15:00 | 23.75 | 39.5 | 100 | 23.9098 | 16.2715 | 45.5047 | 0.9602 | 0.9602 | 0 | 0
2025-01-26 16:00 | 22.95 | 45.5 | 100 | 23.62 | 16.4178 | 47.8743 | 15.647 | 15.647 | 0 | 0
2025-01-26 17:00 | 21.75 | 57 | 100 | 23.1829 | 16.7243 | 52.1573 | 43.1465 | 43.1465 | 0 | 0
2025-01-26 18:00 | 20.45 | 65 | 100 | 22.7026 | 16.7294 | 54.8611 | 53.6978 | 53.6978 | 0 | 0
2025-01-26 19:00 | 19.4 | 71.5 | 100 | 22.3098 | 16.6992 | 56.9212 | 60.2937 | 60.2937 | 0 | 0
2025-01-26 20:00 | 18.65 | 76 | 100 | 22.0263 | 16.652 | 58.2747 | 63.5551 | 63.5551 | 0 | 0
2025-01-26 21:00 | 17.95 | 77.5 | 100 | 21.7574 | 16.47 | 58.6178 | 58.4491 | 58.4491 | 0 | 0
2025-01-26 22:00 | 17 | 78.5 | 70 | 21.3877 | 16.1724 | 58.7628 | 34.0911 | 34.0911 | 0 | 0
2025-01-26 23:00 | 16.15 | 80 | 70 | 21.0535 | 15.9315 | 59.1011 | 29.1647 | 29.1647 | 0 | 0
2025-01-27 | 15.5 | 82 | 70 | 20.7963 | 15.7809 | 59.6246 | 26.8664 | 26.8664 | 0 | 0
2025-01-27 01:00 | 14.9 | 84 | 70 | 20.5571 | 15.6447 | 60.1486 | 24.9099 | 24.9099 | 0 | 0
2025-01-27 02:00 | 14.3 | 86 | 70 | 20.3163 | 15.5046 | 60.6676 | 22.8587 | 22.8587 | 0 | 0
2025-01-27 03:00 | 13.7 | 88 | 70 | 20.0737 | 15.3627 | 61.1818 | 20.7163 | 20.7163 | 0 | 0
2025-01-27 04:00 | 13.25 | 89 | 70 | 19.89 | 15.2348 | 61.4264 | 18.2972 | 18.2972 | 0 | 0
2025-01-27 05:00 | 13 | 89 | 70 | 19.787 | 15.1431 | 61.4087 | 16.11 | 16.11 | 0 | 0
2025-01-27 06:00 | 12.8 | 89.5 | 100 | 19.7049 | 15.0877 | 61.5305 | 21.5684 | 21.5684 | 0 | 0
2025-01-27 07:00 | 13.4 | 88 | 100 | 19.9507 | 15.2523 | 61.1487 | 25.7612 | 25.7612 | 0 | 0
2025-01-27 08:00 | 15.65 | 80 | 100 | 20.8544 | 15.7515 | 59.0359 | 35.321 | 35.321 | 0 | 0
2025-01-27 09:00 | 18.75 | 70.5 | 100 | 22.0608 | 16.4211 | 56.4487 | 48.8785 | 48.8785 | 0 | 0
2025-01-27 10:00 | 21.35 | 65.5 | 100 | 23.0384 | 17.0679 | 55.2102 | 66.6795 | 66.6795 | 0 | 0
2025-01-27 11:00 | 23.3 | 58 | 100 | 23.7489 | 17.2982 | 52.807 | 65.4369 | 65.4369 | 0 | 0
2025-01-27 12:00 | 24.8 | 46.5 | 100 | 24.2854 | 17.0475 | 48.4273 | 39.0274 | 39.0274 | 0 | 0
2025-01-27 13:00 | 24.75 | 47 | 100 | 24.2676 | 17.0642 | 48.6372 | 40.56 | 40.56 | 0 | 0
2025-01-27 14:00 | 23.45 | 57 | 100 | 23.8028 | 17.2852 | 52.469 | 63.8381 | 63.8381 | 0 | 0
2025-01-27 15:00 | 23.05 | 59.5 | 100 | 23.6588 | 17.3027 | 53.3641 | 68.0134 | 68.0134 | 0 | 0
2025-01-27 16:00 | 23.2 | 58 | 100 | 23.7128 | 17.2628 | 52.8119 | 64.4333 | 64.4333 | 0 | 0
2025-01-27 17:00 | 22.3 | 64 | 100 | 23.3872 | 17.3106 | 54.9123 | 74.3222 | 74.3222 | 0 | 0
2025-01-27 18:00 | 21.05 | 75 | 100 | 22.9315 | 17.4735 | 58.6165 | 94.1128 | 94.1128 | 0 | 0
2025-01-27 19:00 | 20.3 | 83.5 | 100 | 22.6566 | 17.6342 | 61.3694 | 109.9706 | 109.9706 | 0 | 0
2025-01-27 20:00 | 20.1 | 87 | 100 | 22.5838 | 17.7338 | 62.5075 | 117.6598 | 117.6598 | 0 | 0
2025-01-27 21:00 | 20.3 | 86 | 100 | 22.6581 | 17.7608 | 62.2416 | 117.7131 | 117.7131 | 0 | 0
2025-01-27 22:00 | 20.35 | 84 | 70 | 22.6756 | 17.6788 | 61.5609 | 78.587 | 78.587 | 0 | 0
2025-01-27 23:00 | 19.85 | 86 | 70 | 22.4893 | 17.5866 | 62.0598 | 77.4873 | 77.4873 | 0 | 0
2025-01-28 | 19.1 | 90.5 | 70 | 22.2086 | 17.5144 | 63.2944 | 78.6887 | 78.6887 | 0 | 0
2025-01-28 01:00 | 18.6 | 92.5 | 70 | 22.0193 | 17.4118 | 63.7596 | 77.2146 | 77.2146 | 0 | 0
2025-01-28 02:00 | 18.2 | 93 | 70 | 21.8661 | 17.278 | 63.7653 | 73.8022 | 73.8022 | 0 | 0
2025-01-28 03:00 | 18 | 93 | 70 | 21.789 | 17.1997 | 63.6903 | 71.6298 | 71.6298 | 0 | 0
2025-01-28 04:00 | 18.05 | 91.5 | 70 | 21.8071 | 17.1513 | 63.2217 | 69.2608 | 69.2608 | 0 | 0
2025-01-28 05:00 | 18.35 | 89.5 | 70 | 21.9211 | 17.176 | 62.6719 | 68.5262 | 68.5262 | 0 | 0
2025-01-28 06:00 | 18.75 | 88.5 | 100 | 22.0737 | 17.2838 | 62.4806 | 101.0979 | 101.0979 | 0 | 0
2025-01-28 07:00 | 19.2 | 87 | 100 | 22.2442 | 17.3857 | 62.1405 | 103.5818 | 103.5818 | 0 | 0
2025-01-28 08:00 | 20.4 | 81.5 | 100 | 22.6929 | 17.5712 | 60.6873 | 105.0898 | 105.0898 | 0 | 0
2025-01-28 09:00 | 22 | 72.5 | 100 | 23.2803 | 17.6862 | 57.9934 | 99.2828 | 99.2828 | 0 | 0
2025-01-28 10:00 | 23.1 | 64 | 100 | 23.6777 | 17.5905 | 55.1003 | 84.7558 | 84.7558 | 0 | 0
2025-01-28 11:00 | 23.75 | 58 | 100 | 23.9106 | 17.4494 | 52.9107 | 71.1456 | 71.1456 | 0 | 0
2025-01-28 12:00 | 24.1 | 54.5 | 100 | 24.0357 | 17.3458 | 51.5896 | 62.2688 | 62.2688 | 0 | 0
2025-01-28 13:00 | 24.05 | 54 | 100 | 24.0179 | 17.2966 | 51.3843 | 59.8032 | 59.8032 | 0 | 0
2025-01-28 14:00 | 23.8 | 55 | 100 | 23.9284 | 17.2774 | 51.7412 | 60.6109 | 60.6109 | 0 | 0
2025-01-28 15:00 | 23.4 | 55.5 | 100 | 23.7847 | 17.1766 | 51.8644 | 57.631 | 57.631 | 0 | 0
2025-01-28 16:00 | 22.75 | 59 | 100 | 23.5499 | 17.1721 | 53.0992 | 62.3648 | 62.3648 | 0 | 0
2025-01-28 17:00 | 21.85 | 64 | 100 | 23.2223 | 17.1555 | 54.7938 | 68.3411 | 68.3411 | 0 | 0
2025-01-28 18:00 | 21.05 | 66.5 | 100 | 22.9275 | 17.0172 | 55.5258 | 66.2447 | 66.2447 | 0 | 0
2025-01-28 19:00 | 20.6 | 67 | 100 | 22.7599 | 16.8876 | 55.6006 | 61.9597 | 61.9597 | 0 | 0
2025-01-28 20:00 | 20.2 | 68 | 100 | 22.6103 | 16.8013 | 55.8664 | 59.9112 | 59.9112 | 0 | 0
2025-01-28 21:00 | 19.75 | 70 | 100 | 22.4416 | 16.7473 | 56.4701 | 60.2521 | 60.2521 | 0 | 0
2025-01-28 22:00 | 19.25 | 72.5 | 70 | 22.2534 | 16.6959 | 57.2223 | 42.8667 | 42.8667 | 0 | 0
2025-01-28 23:00 | 18.8 | 76 | 70 | 22.0839 | 16.7064 | 58.3045 | 45.8738 | 45.8738 | 0 | 0
2025-01-29 | 18.45 | 79 | 70 | 21.9517 | 16.7224 | 59.2219 | 48.5932 | 48.5932 | 0 | 0
2025-01-29 01:00 | 18.25 | 81 | 70 | 21.8761 | 16.7431 | 59.8314 | 50.6269 | 50.6269 | 0 | 0
2025-01-29 02:00 | 18.15 | 82 | 70 | 21.8383 | 16.7526 | 60.1339 | 51.6199 | 51.6199 | 0 | 0
2025-01-29 03:00 | 18 | 82 | 70 | 21.7803 | 16.6967 | 60.096 | 50.1581 | 50.1581 | 0 | 0
2025-01-29 04:00 | 17.85 | 81 | 70 | 21.7214 | 16.5955 | 59.7332 | 46.7592 | 46.7592 | 0 | 0
2025-01-29 05:00 | 17.6 | 80.5 | 70 | 21.6239 | 16.4809 | 59.5131 | 43.4035 | 43.4035 | 0 | 0
2025-01-29 06:00 | 17.15 | 81 | 100 | 21.4486 | 16.3385 | 59.5736 | 57.258 | 57.258 | 0 | 0
2025-01-29 07:00 | 17.45 | 79.5 | 100 | 21.5646 | 16.3809 | 59.1495 | 57.1775 | 57.1775 | 0 | 0
2025-01-29 08:00 | 19.2 | 72 | 100 | 22.234 | 16.6547 | 57.0231 | 58.9317 | 58.9317 | 0 | 0
2025-01-29 09:00 | 21.15 | 61 | 100 | 22.9622 | 16.7529 | 53.5005 | 49.0213 | 49.0213 | 0 | 0
2025-01-29 10:00 | 22.25 | 54.5 | 100 | 23.3661 | 16.7463 | 51.2397 | 39.9064 | 39.9064 | 0 | 0
2025-01-29 11:00 | 22.75 | 52.5 | 100 | 23.5485 | 16.7876 | 50.5398 | 38.5443 | 38.5443 | 0 | 0
2025-01-29 12:00 | 23 | 51 | 100 | 23.6392 | 16.7752 | 49.9934 | 35.9808 | 35.9808 | 0 | 0
2025-01-29 13:00 | 23.05 | 50 | 100 | 23.6572 | 16.729 | 49.6145 | 32.9373 | 32.9373 | 0 | 0
2025-01-29 14:00 | 22.85 | 51 | 100 | 23.5846 | 16.7269 | 49.9868 | 34.4034 | 34.4034 | 0 | 0
2025-01-29 15:00 | 22.5 | 53 | 100 | 23.4573 | 16.7356 | 50.7205 | 37.6713 | 37.6713 | 0 | 0
2025-01-29 16:00 | 22 | 54.5 | 100 | 23.2742 | 16.6636 | 51.2298 | 37.2363 | 37.2363 | 0 | 0
2025-01-29 17:00 | 21.2 | 56.5 | 100 | 22.9787 | 16.518 | 51.8802 | 34.869 | 34.869 | 0 | 0
2025-01-29 18:00 | 20.25 | 60.5 | 100 | 22.6249 | 16.4236 | 53.2113 | 36.8099 | 36.8099 | 0 | 0
2025-01-29 19:00 | 19.3 | 65.5 | 100 | 22.2678 | 16.3634 | 54.8277 | 40.8352 | 40.8352 | 0 | 0
2025-01-29 20:00 | 18.4 | 70 | 100 | 21.9257 | 16.2759 | 56.2135 | 42.9339 | 42.9339 | 0 | 0
2025-01-29 21:00 | 17.7 | 75.5 | 100 | 21.6588 | 16.2887 | 57.9008 | 49.4702 | 49.4702 | 0 | 0
2025-01-29 22:00 | 17.15 | 81 | 70 | 21.4487 | 16.3394 | 59.5557 | 39.9755 | 39.9755 | 0 | 0
2025-01-29 23:00 | 16.8 | 82.5 | 70 | 21.3126 | 16.277 | 59.9582 | 39.4665 | 39.4665 | 0 | 0
2025-01-30 | 16.6 | 81.5 | 70 | 21.2329 | 16.1604 | 59.6138 | 35.814 | 35.814 | 0 | 0
2025-01-30 01:00 | 16 | 83 | 70 | 20.9966 | 16.0055 | 59.9767 | 32.9916 | 32.9916 | 0 | 0
2025-01-30 02:00 | 14.95 | 87 | 70 | 20.5802 | 15.7846 | 61.013 | 30.2048 | 30.2048 | 0 | 0
2025-01-30 03:00 | 13.75 | 91.5 | 70 | 20.0977 | 15.5141 | 62.1455 | 26.4494 | 26.4494 | 0 | 0
2025-01-30 04:00 | 13.1 | 92.5 | 70 | 19.8319 | 15.3091 | 62.3502 | 22.0729 | 22.0729 | 0 | 0
2025-01-30 05:00 | 13 | 91.5 | 70 | 19.7897 | 15.2354 | 62.0628 | 19.6663 | 19.6663 | 0 | 0
2025-01-30 06:00 | 12.7 | 92.5 | 100 | 19.6667 | 15.16 | 62.3049 | 26.3505 | 26.3505 | 0 | 0
2025-01-30 07:00 | 12.9 | 91 | 100 | 19.7479 | 15.1805 | 61.9035 | 25.6592 | 25.6592 | 0 | 0
2025-01-30 08:00 | 15.25 | 80 | 100 | 20.6943 | 15.6094 | 58.9606 | 30.0715 | 30.0715 | 0 | 0
2025-01-30 09:00 | 18.75 | 65.5 | 100 | 22.0572 | 16.1777 | 54.7357 | 34.0228 | 34.0228 | 0 | 0
2025-01-30 10:00 | 21.25 | 57.5 | 100 | 22.9978 | 16.5928 | 52.2229 | 38.5012 | 38.5012 | 0 | 0
2025-01-30 11:00 | 22.85 | 52 | 100 | 23.5848 | 16.7902 | 50.3528 | 37.818 | 37.818 | 0 | 0
2025-01-30 12:00 | 23.6 | 48 | 100 | 23.8561 | 16.7773 | 48.8705 | 31.4244 | 31.4244 | 0 | 0
2025-01-30 13:00 | 23.75 | 45.5 | 100 | 23.9101 | 16.663 | 47.8922 | 23.6339 | 23.6339 | 0 | 0
2025-01-30 14:00 | 23.65 | 45 | 100 | 23.874 | 16.6003 | 47.6924 | 20.765 | 20.765 | 0 | 0
2025-01-30 15:00 | 23.1 | 48.5 | 100 | 23.6751 | 16.6512 | 49.0412 | 28.0644 | 28.0644 | 0 | 0
2025-01-30 16:00 | 22.6 | 50.5 | 100 | 23.4933 | 16.6175 | 49.7745 | 29.9021 | 29.9021 | 0 | 0
2025-01-30 17:00 | 22 | 54 | 100 | 23.274 | 16.6341 | 51.047 | 35.5553 | 35.5553 | 0 | 0
2025-01-30 18:00 | 21.25 | 59.5 | 100 | 22.9987 | 16.7019 | 52.9911 | 45.4711 | 45.4711 | 0 | 0
2025-01-30 19:00 | 20.85 | 60.5 | 100 | 22.8501 | 16.6239 | 53.2915 | 43.93 | 43.93 | 0 | 0
2025-01-30 20:00 | 20.45 | 59.5 | 100 | 22.6996 | 16.437 | 52.8764 | 35.9472 | 35.9472 | 0 | 0
2025-01-30 21:00 | 20.05 | 60 | 100 | 22.5491 | 16.3312 | 53.0086 | 32.875 | 32.875 | 0 | 0
2025-01-30 22:00 | 19.8 | 60 | 70 | 22.4544 | 16.2484 | 52.9847 | 21.002 | 21.002 | 0 | 0
2025-01-30 23:00 | 19.5 | 58.5 | 70 | 22.3394 | 16.0716 | 52.4436 | 15.4326 | 15.4326 | 0 | 0
2025-01-31 | 19.1 | 59.5 | 70 | 22.1873 | 15.9917 | 52.7688 | 14.4644 | 14.4644 | 0 | 0
2025-01-31 01:00 | 18.7 | 61.5 | 70 | 22.0351 | 15.9602 | 53.427 | 15.488 | 15.488 | 0 | 0
2025-01-31 02:00 | 18.4 | 63 | 70 | 21.9205 | 15.9345 | 53.9121 | 16.1644 | 16.1644 | 0 | 0
2025-01-31 03:00 | 18.2 | 63 | 70 | 21.8431 | 15.8682 | 53.9014 | 14.5877 | 14.5877 | 0 | 0
2025-01-31 04:00 | 18.1 | 60.5 | 70 | 21.8024 | 15.7139 | 53.0726 | 8.8537 | 8.8537 | 0 | 0
2025-01-31 05:00 | 17.8 | 57 | 70 | 21.683 | 15.4478 | 51.9242 | 0 | 0 | 0 | 0
2025-01-31 06:00 | 17.15 | 56 | 100 | 21.4277 | 15.1943 | 51.6295 | 0 | 0 | 0 | 0
2025-01-31 07:00 | 17.3 | 56 | 100 | 21.4866 | 15.2423 | 51.6119 | 0 | 0 | 0 | 0
2025-01-31 08:00 | 18.95 | 51 | 100 | 22.1239 | 15.511 | 49.8599 | 0 | 0 | 0 | 0
2025-01-31 09:00 | 21 | 42 | 100 | 22.8973 | 15.6357 | 46.5487 | 0 | 0 | 0 | 0
2025-01-31 10:00 | 22.25 | 35.5 | 100 | 23.3605 | 15.6013 | 43.9917 | 0 | 0 | 0 | 0
2025-01-31 11:00 | 22.85 | 33.5 | 100 | 23.5811 | 15.6378 | 43.153 | 0 | 0 | 0 | 0
2025-01-31 12:00 | 22.95 | 35.5 | 100 | 23.6181 | 15.7908 | 43.9367 | 0 | 0 | 0 | 0
2025-01-31 13:00 | 22.9 | 37.5 | 100 | 23.6002 | 15.9036 | 44.7306 | 0 | 0 | 0 | 0
2025-01-31 14:00 | 22.65 | 39.5 | 100 | 23.5089 | 15.9573 | 45.5284 | 0 | 0 | 0 | 0
2025-01-31 15:00 | 22.15 | 42.5 | 100 | 23.3256 | 15.9969 | 46.7039 | 0 | 0 | 0 | 0
2025-01-31 16:00 | 21.8 | 44.5 | 100 | 23.1968 | 16.0128 | 47.4691 | 0.6553 | 0.6553 | 0 | 0
2025-01-31 17:00 | 21.1 | 47.5 | 100 | 22.9373 | 15.9766 | 48.5902 | 4.0036 | 4.0036 | 0 | 0
2025-01-31 18:00 | 20.1 | 51.5 | 100 | 22.563 | 15.8913 | 50.029 | 6.8832 | 6.8832 | 0 | 0
2025-01-31 19:00 | 19.25 | 56 | 100 | 22.2423 | 15.861 | 51.5816 | 11.8483 | 11.8483 | 0 | 0
2025-01-31 20:00 | 18.7 | 58.5 | 100 | 22.0329 | 15.811 | 52.4146 | 13.3412 | 13.3412 | 0 | 0
2025-01-31 21:00 | 18.25 | 60 | 100 | 21.8602 | 15.7388 | 52.9025 | 12.7858 | 12.7858 | 0 | 0
2025-01-31 22:00 | 17.6 | 62 | 70 | 21.6089 | 15.6219 | 53.5451 | 7.9301 | 7.9301 | 0 | 0
2025-01-31 23:00 | 16.75 | 64.5 | 70 | 21.2773 | 15.4568 | 54.337 | 6.1721 | 6.1721 | 0 | 0
2025-02-01 | 15.7 | 68.5 | 70 | 20.8637 | 15.281 | 55.5747 | 5.2836 | 5.2836 | 0 | 0
2025-02-01 01:00 | 14.55 | 74 | 70 | 20.406 | 15.1175 | 57.2128 | 5.5693 | 5.5693 | 0 | 0
2025-02-01 02:00 | 13.3 | 81 | 70 | 19.9026 | 14.9532 | 59.2056 | 6.5786 | 6.5786 | 0 | 0
2025-02-01 03:00 | 12.1 | 87.5 | 70 | 19.4121 | 14.7614 | 60.9761 | 6.2872 | 6.2872 | 0 | 0
2025-02-01 04:00 | 12.1 | 85.5 | 70 | 19.4101 | 14.691 | 60.444 | 3.4499 | 3.4499 | 0 | 0
2025-02-01 05:00 | 12.45 | 81 | 70 | 19.5512 | 14.6547 | 59.224 | 0 | 0 | 0 | 0
2025-02-01 06:00 | 11.95 | 82.5 | 100 | 19.3444 | 14.5325 | 59.6456 | 0 | 0 | 0 | 0
2025-02-01 07:00 | 12 | 81.5 | 100 | 19.3643 | 14.515 | 59.3712 | 0 | 0 | 0 | 0
2025-02-01 08:00 | 14.2 | 72 | 100 | 20.262 | 14.9186 | 56.6228 | 0 | 0 | 0 | 0
2025-02-01 09:00 | 17.75 | 57 | 100 | 21.6635 | 15.434 | 51.9009 | 0 | 0 | 0 | 0
2025-02-01 10:00 | 20.65 | 43 | 100 | 22.7662 | 15.5913 | 46.9334 | 0 | 0 | 0 | 0
2025-02-01 11:00 | 22.6 | 31.5 | 100 | 23.4886 | 15.445 | 42.3966 | 0 | 0 | 0 | 0
2025-02-01 12:00 | 23.9 | 23.5 | 100 | 23.9636 | 15.244 | 38.9717 | 0 | 0 | 0 | 0
2025-02-01 13:00 | 24.6 | 20.5 | 100 | 24.2175 | 15.1961 | 37.5767 | 0 | 0 | 0 | 0
2025-02-01 14:00 | 24.65 | 22.5 | 100 | 24.2353 | 15.3494 | 38.4112 | 0 | 0 | 0 | 0
2025-02-01 15:00 | 23.85 | 27.5 | 100 | 23.9456 | 15.5009 | 40.6331 | 0 | 0 | 0 | 0
2025-02-01 16:00 | 22.65 | 36 | 100 | 23.5081 | 15.7381 | 44.173 | 0 | 0 | 0 | 0
2025-02-01 17:00 | 21.6 | 43.5 | 100 | 23.1221 | 15.8945 | 47.101 | 0 | 0 | 0 | 0
2025-02-01 18:00 | 20.65 | 48 | 100 | 22.7687 | 15.8685 | 48.7758 | 1.2014 | 1.2014 | 0 | 0
2025-02-01 19:00 | 19.75 | 54.5 | 100 | 22.432 | 15.9423 | 51.0744 | 12.5742 | 12.5742 | 0 | 0
2025-02-01 20:00 | 18.9 | 61 | 100 | 22.1116 | 16.0019 | 53.2651 | 22.861 | 22.861 | 0 | 0
2025-02-01 21:00 | 18.1 | 64 | 100 | 21.8051 | 15.8835 | 54.2144 | 22.4453 | 22.4453 | 0 | 0
2025-02-01 22:00 | 17.25 | 65.5 | 70 | 21.4748 | 15.6692 | 54.6615 | 11.896 | 11.896 | 0 | 0
2025-02-01 23:00 | 16.3 | 69 | 70 | 21.1032 | 15.5063 | 55.7339 | 10.8552 | 10.8552 | 0 | 0
2025-02-02 | 15.25 | 73 | 70 | 20.6876 | 15.3179 | 56.9259 | 9.4814 | 9.4814 | 0 | 0
2025-02-02 01:00 | 14.3 | 75 | 70 | 20.3055 | 15.071 | 57.5099 | 5.2472 | 5.2472 | 0 | 0
2025-02-02 02:00 | 13.75 | 73.5 | 70 | 20.0797 | 14.8229 | 57.1033 | 0 | 0 | 0 | 0
2025-02-02 03:00 | 13.45 | 70 | 70 | 19.9531 | 14.5857 | 56.1456 | 0 | 0 | 0 | 0
2025-02-02 04:00 | 13.5 | 67 | 70 | 19.9707 | 14.4861 | 55.2998 | 0 | 0 | 0 | 0
2025-02-02 05:00 | 13.6 | 63.5 | 70 | 20.0082 | 14.3816 | 54.2983 | 0 | 0 | 0 | 0
2025-02-02 06:00 | 13.35 | 60.5 | 100 | 19.9026 | 14.185 | 53.4945 | 0 | 0 | 0 | 0
2025-02-02 07:00 | 13.35 | 58.5 | 100 | 19.9006 | 14.107 | 52.9283 | 0 | 0 | 0 | 0
2025-02-02 08:00 | 15.35 | 52 | 100 | 20.7082 | 14.4567 | 50.6225 | 0 | 0 | 0 | 0
2025-02-02 09:00 | 18.7 | 45.5 | 100 | 22.0236 | 15.1528 | 48.0149 | 0 | 0 | 0 | 0
2025-02-02 10:00 | 21.05 | 42.5 | 100 | 22.9163 | 15.6787 | 46.7305 | 0 | 0 | 0 | 0
2025-02-02 11:00 | 22.35 | 38.5 | 100 | 23.3983 | 15.8132 | 45.1414 | 0 | 0 | 0 | 0
2025-02-02 12:00 | 21.75 | 43.5 | 100 | 23.1779 | 15.9402 | 47.0798 | 0 | 0 | 0 | 0
2025-02-02 13:00 | 20.4 | 54 | 100 | 22.6778 | 16.122 | 50.9201 | 17.9149 | 17.9149 | 0 | 0
2025-02-02 14:00 | 20.25 | 54 | 100 | 22.6212 | 16.0741 | 50.9171 | 16.3412 | 16.3412 | 0 | 0
2025-02-02 15:00 | 20.45 | 49.5 | 100 | 22.6942 | 15.8908 | 49.3152 | 4.0447 | 4.0447 | 0 | 0
2025-02-02 16:00 | 20.55 | 44 | 100 | 22.729 | 15.6147 | 47.332 | 0 | 0 | 0 | 0
2025-02-02 17:00 | 20.05 | 41.5 | 100 | 22.5383 | 15.3307 | 46.4816 | 0 | 0 | 0 | 0
2025-02-02 18:00 | 19.15 | 44.5 | 100 | 22.1963 | 15.232 | 47.6318 | 0 | 0 | 0 | 0
2025-02-02 19:00 | 18.6 | 48 | 100 | 21.9868 | 15.2504 | 48.8765 | 0 | 0 | 0 | 0
2025-02-02 20:00 | 18.45 | 49.5 | 100 | 21.9299 | 15.2816 | 49.3894 | 0 | 0 | 0 | 0
2025-02-02 21:00 | 18.4 | 50 | 100 | 21.9109 | 15.292 | 49.56 | 0 | 0 | 0 | 0
2025-02-02 22:00 | 18.15 | 52 | 70 | 21.8154 | 15.3148 | 50.2457 | 0 | 0 | 0 | 0
2025-02-02 23:00 | 17.85 | 53.5 | 70 | 21.6998 | 15.2949 | 50.7624 | 0 | 0 | 0 | 0
2025-02-03 | 17.5 | 55 | 70 | 21.5642 | 15.2577 | 51.2796 | 0 | 0 | 0 | 0
2025-02-03 01:00 | 17.15 | 57 | 70 | 21.4285 | 15.241 | 51.9494 | 0 | 0 | 0 | 0
2025-02-03 02:00 | 16.85 | 58.5 | 70 | 21.3116 | 15.2153 | 52.4462 | 0 | 0 | 0 | 0
2025-02-03 03:00 | 16.7 | 59 | 70 | 21.2528 | 15.1895 | 52.6146 | 0 | 0 | 0 | 0
2025-02-03 04:00 | 16.65 | 57 | 70 | 21.2313 | 15.0823 | 51.989 | 0 | 0 | 0 | 0
2025-02-03 05:00 | 16.75 | 55 | 70 | 21.2691 | 15.0224 | 51.3448 | 0 | 0 | 0 | 0
2025-02-03 06:00 | 17 | 55.5 | 100 | 21.3682 | 15.1242 | 51.4738 | 0 | 0 | 0 | 0
2025-02-03 07:00 | 17.25 | 56.5 | 100 | 21.4674 | 15.2506 | 51.7707 | 0 | 0 | 0 | 0
2025-02-03 08:00 | 18.7 | 52 | 100 | 22.0283 | 15.4853 | 50.2072 | 0 | 0 | 0 | 0
2025-02-03 09:00 | 20.8 | 43.5 | 100 | 22.8229 | 15.6637 | 47.1056 | 0 | 0 | 0 | 0
2025-02-03 10:00 | 21.8 | 40 | 100 | 23.1952 | 15.7492 | 45.739 | 0 | 0 | 0 | 0
2025-02-03 11:00 | 22.15 | 40 | 100 | 23.3249 | 15.8486 | 45.7216 | 0 | 0 | 0 | 0
2025-02-03 12:00 | 22.7 | 38 | 100 | 23.527 | 15.8803 | 44.9256 | 0 | 0 | 0 | 0
2025-02-03 13:00 | 22.9 | 36.5 | 100 | 23.6 | 15.8405 | 44.3344 | 0 | 0 | 0 | 0
2025-02-03 14:00 | 22.65 | 37.5 | 100 | 23.5085 | 15.8328 | 44.7506 | 0 | 0 | 0 | 0
2025-02-03 15:00 | 22.45 | 38.5 | 100 | 23.4351 | 15.8382 | 45.1536 | 0 | 0 | 0 | 0
2025-02-03 16:00 | 22.15 | 39.5 | 100 | 23.3247 | 15.8148 | 45.5568 | 0 | 0 | 0 | 0
2025-02-03 17:00 | 21.45 | 42 | 100 | 23.0656 | 15.7634 | 46.5419 | 0 | 0 | 0 | 0
2025-02-03 18:00 | 20.2 | 47 | 100 | 22.5983 | 15.6775 | 48.4247 | 0 | 0 | 0 | 0
2025-02-03 19:00 | 19.05 | 52.5 | 100 | 22.1633 | 15.6184 | 50.378 | 0 | 0 | 0 | 0
2025-02-03 20:00 | 18.35 | 58 | 100 | 21.8974 | 15.6741 | 52.2329 | 8.0767 | 8.0767 | 0 | 0
2025-02-03 21:00 | 17.8 | 64.5 | 100 | 21.6889 | 15.8074 | 54.3528 | 20.3706 | 20.3706 | 0 | 0
2025-02-03 22:00 | 17.35 | 69.5 | 70 | 21.5173 | 15.8886 | 55.9334 | 20.1903 | 20.1903 | 0 | 0
2025-02-03 23:00 | 17.1 | 69 | 70 | 21.4189 | 15.7801 | 55.7538 | 17.1857 | 17.1857 | 0 | 0
2025-02-04 | 17 | 63.5 | 70 | 21.375 | 15.4948 | 54.007 | 6.1351 | 6.1351 | 0 | 0
2025-02-04 01:00 | 16.8 | 61.5 | 70 | 21.2945 | 15.3376 | 53.3792 | 0.9392 | 0.9392 | 0 | 0
2025-02-04 02:00 | 16.35 | 65 | 70 | 21.1195 | 15.3472 | 54.4817 | 3.97 | 3.97 | 0 | 0
2025-02-04 03:00 | 15.85 | 69.5 | 70 | 20.9246 | 15.3759 | 55.8615 | 8.0971 | 8.0971 | 0 | 0
2025-02-04 04:00 | 15.5 | 70 | 70 | 20.7851 | 15.2782 | 56.0092 | 6.2195 | 6.2195 | 0 | 0
2025-02-04 05:00 | 15.25 | 69 | 70 | 20.6839 | 15.1516 | 55.7097 | 2.5695 | 2.5695 | 0 | 0
2025-02-04 06:00 | 14.5 | 72.5 | 100 | 20.3844 | 15.0412 | 56.7493 | 3.6865 | 3.6865 | 0 | 0
2025-02-04 07:00 | 13.75 | 74 | 100 | 20.0804 | 14.844 | 57.1983 | 0 | 0 | 0 | 0
2025-02-04 08:00 | 15.15 | 66.5 | 100 | 20.6414 | 15.0145 | 54.9514 | 0 | 0 | 0 | 0
2025-02-04 09:00 | 18.25 | 55 | 100 | 21.8565 | 15.4965 | 51.2078 | 0 | 0 | 0 | 0
2025-02-04 10:00 | 20.7 | 47.5 | 100 | 22.7874 | 15.861 | 48.5433 | 0 | 0 | 0 | 0
2025-02-04 11:00 | 22 | 43.5 | 100 | 23.2705 | 16.0181 | 47.0407 | 0 | 0 | 0 | 0
2025-02-04 12:00 | 22.65 | 41 | 100 | 23.5093 | 16.0549 | 46.0749 | 0 | 0 | 0 | 0
2025-02-04 13:00 | 22.95 | 40 | 100 | 23.619 | 16.0782 | 45.6849 | 0 | 0 | 0 | 0
2025-02-04 14:00 | 22.7 | 41.5 | 100 | 23.5278 | 16.0989 | 46.2832 | 0 | 0 | 0 | 0
2025-02-04 15:00 | 22.05 | 44.5 | 100 | 23.2893 | 16.0895 | 47.4459 | 2.8789 | 2.8789 | 0 | 0
2025-02-04 16:00 | 21.5 | 47.5 | 100 | 23.0865 | 16.1009 | 48.5697 | 7.79 | 7.79 | 0 | 0
2025-02-04 17:00 | 20.75 | 51 | 100 | 22.8079 | 16.0684 | 49.8378 | 11.7735 | 11.7735 | 0 | 0
2025-02-04 18:00 | 19.75 | 55.5 | 100 | 22.4327 | 15.9968 | 51.4037 | 15.4899 | 15.4899 | 0 | 0
2025-02-04 19:00 | 18.9 | 60 | 100 | 22.1109 | 15.9532 | 52.9078 | 19.7512 | 19.7512 | 0 | 0
2025-02-04 20:00 | 18.1 | 64 | 100 | 21.8052 | 15.8852 | 54.1932 | 22.2655 | 22.2655 | 0 | 0
2025-02-04 21:00 | 17.2 | 68.5 | 100 | 21.4578 | 15.7922 | 55.5906 | 24.2862 | 24.2862 | 0 | 0
2025-02-04 22:00 | 16.45 | 74 | 70 | 21.1671 | 15.7789 | 57.2595 | 20.8977 | 20.8977 | 0 | 0
2025-02-04 23:00 | 15.95 | 78.5 | 70 | 20.9727 | 15.7965 | 58.5922 | 24.6088 | 24.6088 | 0 | 0
2025-02-05 | 15.4 | 81.5 | 70 | 20.7558 | 15.7244 | 59.4369 | 24.9797 | 24.9797 | 0 | 0
2025-02-05 01:00 | 14.8 | 83.5 | 70 | 20.5164 | 15.5886 | 59.9648 | 23.0531 | 23.0531 | 0 | 0
2025-02-05 02:00 | 14.15 | 85 | 70 | 20.2544 | 15.4122 | 60.3422 | 19.8082 | 19.8082 | 0 | 0
2025-02-05 03:00 | 13.35 | 87 | 70 | 19.9292 | 15.1972 | 60.8536 | 16.0036 | 16.0036 | 0 | 0
2025-02-05 04:00 | 12.55 | 85.5 | 70 | 19.5973 | 14.8525 | 60.4257 | 7.0618 | 7.0618 | 0 | 0
2025-02-05 05:00 | 11.4 | 87 | 70 | 19.1185 | 14.4929 | 60.854 | 0 | 0 | 0 | 0
2025-02-05 06:00 | 10.45 | 91.5 | 100 | 18.7215 | 14.301 | 62.0512 | 0 | 0 | 0 | 0
2025-02-05 07:00 | 11 | 88.5 | 100 | 18.9515 | 14.4007 | 61.2507 | 0 | 0 | 0 | 0
2025-02-05 08:00 | 13.45 | 79.5 | 100 | 19.9628 | 14.951 | 58.7568 | 7.6291 | 7.6291 | 0 | 0
2025-02-05 09:00 | 16.75 | 67.5 | 100 | 21.2799 | 15.5933 | 55.2535 | 16.4854 | 16.4854 | 0 | 0
2025-02-05 10:00 | 19.15 | 58.5 | 100 | 22.2058 | 15.9589 | 52.4103 | 18.0591 | 18.0591 | 0 | 0
2025-02-05 11:00 | 20.6 | 53 | 100 | 22.7526 | 16.1319 | 50.5547 | 16.6948 | 16.6948 | 0 | 0
2025-02-05 12:00 | 21.75 | 47.5 | 100 | 23.1794 | 16.176 | 48.5822 | 10.3858 | 10.3858 | 0 | 0
2025-02-05 13:00 | 22.75 | 42.5 | 100 | 23.5463 | 16.1727 | 46.6905 | 2.6345 | 2.6345 | 0 | 0
2025-02-05 14:00 | 23.35 | 40 | 100 | 23.7648 | 16.1893 | 45.7069 | 0 | 0 | 0 | 0
2025-02-05 15:00 | 22.85 | 46 | 100 | 23.5836 | 16.4182 | 48.0638 | 16.4402 | 16.4402 | 0 | 0
2025-02-05 16:00 | 21.75 | 53 | 100 | 23.1814 | 16.4938 | 50.6637 | 29.4696 | 29.4696 | 0 | 0
2025-02-05 17:00 | 20.55 | 60.5 | 100 | 22.7377 | 16.5218 | 53.2751 | 40.5824 | 40.5824 | 0 | 0
2025-02-05 18:00 | 19.1 | 72 | 100 | 22.1958 | 16.6171 | 57.0368 | 57.9246 | 57.9246 | 0 | 0
2025-02-05 19:00 | 18.1 | 78 | 100 | 21.8159 | 16.5477 | 58.8221 | 61.9286 | 61.9286 | 0 | 0
2025-02-05 20:00 | 17.55 | 79.5 | 100 | 21.6036 | 16.4166 | 59.1885 | 58.6701 | 58.6701 | 0 | 0
2025-02-05 21:00 | 17 | 80.5 | 100 | 21.3894 | 16.2614 | 59.3938 | 53.9957 | 53.9957 | 0 | 0
2025-02-05 22:00 | 16.3 | 82.5 | 70 | 21.1152 | 16.0929 | 59.8889 | 34.9507 | 34.9507 | 0 | 0
2025-02-05 23:00 | 15.45 | 85.5 | 70 | 20.7795 | 15.9076 | 60.6604 | 32.3632 | 32.3632 | 0 | 0
2025-02-06 | 14.55 | 88.5 | 70 | 20.4201 | 15.6956 | 61.4135 | 29.1124 | 29.1124 | 0 | 0
2025-02-06 01:00 | 13.75 | 91 | 70 | 20.0971 | 15.4947 | 62.0264 | 25.7907 | 25.7907 | 0 | 0
2025-02-06 02:00 | 13.25 | 93 | 70 | 19.8941 | 15.3822 | 62.5284 | 24.3133 | 24.3133 | 0 | 0
2025-02-06 03:00 | 13.25 | 93.5 | 70 | 19.8946 | 15.4012 | 62.6701 | 25.0862 | 25.0862 | 0 | 0
2025-02-06 04:00 | 13.4 | 91.5 | 70 | 19.9542 | 15.3829 | 62.1333 | 23.4229 | 23.4229 | 0 | 0
2025-02-06 05:00 | 13.25 | 90.5 | 70 | 19.8915 | 15.2904 | 61.841 | 20.5606 | 20.5606 | 0 | 0
2025-02-06 06:00 | 13.05 | 89.5 | 100 | 19.8082 | 15.1792 | 61.5507 | 24.7142 | 24.7142 | 0 | 0
2025-02-06 07:00 | 13.75 | 87.5 | 100 | 20.0936 | 15.3614 | 61.0469 | 29.1279 | 29.1279 | 0 | 0
2025-02-06 08:00 | 15.8 | 80 | 100 | 20.9142 | 15.805 | 59.071 | 37.3488 | 37.3488 | 0 | 0
2025-02-06 09:00 | 18.9 | 64.5 | 100 | 22.114 | 16.1759 | 54.4675 | 33.3259 | 33.3259 | 0 | 0
2025-02-06 10:00 | 22.35 | 47.5 | 100 | 23.4008 | 16.3575 | 48.6164 | 16.6514 | 16.6514 | 0 | 0
2025-02-06 11:00 | 24.85 | 32 | 100 | 24.3056 | 16.0705 | 42.3726 | 0 | 0 | 0 | 0
2025-02-06 12:00 | 26.05 | 24 | 100 | 24.7344 | 15.7935 | 38.8095 | 0 | 0 | 0 | 0
2025-02-06 13:00 | 26.65 | 23.5 | 100 | 24.9457 | 15.8989 | 38.5064 | 0 | 0 | 0 | 0
2025-02-06 14:00 | 27.05 | 24 | 100 | 25.0851 | 16.0335 | 38.6838 | 0 | 0 | 0 | 0
2025-02-06 15:00 | 27.1 | 24.5 | 100 | 25.1022 | 16.0841 | 38.9086 | 0 | 0 | 0 | 0
2025-02-06 16:00 | 26.85 | 28 | 100 | 25.0128 | 16.2953 | 40.5154 | 0 | 0 | 0 | 0
2025-02-06 17:00 | 25.5 | 37 | 100 | 24.5353 | 16.5973 | 44.4969 | 7.5009 | 7.5009 | 0 | 0
2025-02-06 18:00 | 23.65 | 44 | 100 | 23.8739 | 16.5315 | 47.3296 | 17.3291 | 17.3291 | 0 | 0
2025-02-06 19:00 | 21.9 | 49.5 | 100 | 23.2356 | 16.3358 | 49.3743 | 19.157 | 19.157 | 0 | 0
2025-02-06 20:00 | 20.25 | 65 | 100 | 22.6274 | 16.6596 | 54.8423 | 51.3461 | 51.3461 | 0 | 0
2025-02-06 21:00 | 19.25 | 80.5 | 100 | 22.2587 | 17.0892 | 59.973 | 85.2727 | 85.2727 | 0 | 0
2025-02-06 22:00 | 18.65 | 85 | 70 | 22.0329 | 17.08 | 61.2955 | 62.7608 | 62.7608 | 0 | 0
2025-02-06 23:00 | 18.3 | 82.5 | 70 | 21.8965 | 16.8305 | 60.3669 | 54.2566 | 54.2566 | 0 | 0
2025-02-07 | 17.85 | 80 | 70 | 21.7206 | 16.5483 | 59.4415 | 45.0204 | 45.0204 | 0 | 0
2025-02-07 01:00 | 17.3 | 82 | 70 | 21.5081 | 16.4371 | 59.9623 | 43.6025 | 43.6025 | 0 | 0
2025-02-07 02:00 | 16.9 | 83 | 70 | 21.3522 | 16.334 | 60.1942 | 41.6709 | 41.6709 | 0 | 0
2025-02-07 03:00 | 16.7 | 80 | 70 | 21.2709 | 16.1291 | 59.2222 | 34.3439 | 34.3439 | 0 | 0
2025-02-07 04:00 | 17.15 | 75 | 70 | 21.4435 | 16.0674 | 57.7177 | 29.1472 | 29.1472 | 0 | 0
2025-02-07 05:00 | 17.95 | 69 | 70 | 21.7507 | 16.0691 | 55.8812 | 24.5475 | 24.5475 | 0 | 0
2025-02-07 06:00 | 18.05 | 67.5 | 100 | 21.7884 | 16.0324 | 55.3939 | 32.0062 | 32.0062 | 0 | 0
2025-02-07 07:00 | 18.1 | 69 | 100 | 21.8089 | 16.1216 | 55.882 | 36.7426 | 36.7426 | 0 | 0
2025-02-07 08:00 | 19 | 67.5 | 100 | 22.1545 | 16.3597 | 55.49 | 43.3251 | 43.3251 | 0 | 0
2025-02-07 09:00 | 20.6 | 63.5 | 100 | 22.758 | 16.7015 | 54.3396 | 50.6601 | 50.6601 | 0 | 0
2025-02-07 10:00 | 22.15 | 58 | 100 | 23.3305 | 16.9158 | 52.5775 | 51.2031 | 51.2031 | 0 | 0
2025-02-07 11:00 | 23.3 | 53 | 100 | 23.7483 | 16.9922 | 50.84 | 46.9696 | 46.9696 | 0 | 0
2025-02-07 12:00 | 24.4 | 49.5 | 100 | 24.1429 | 17.1202 | 49.6118 | 46.4463 | 46.4463 | 0 | 0
2025-02-07 13:00 | 25.5 | 45.5 | 100 | 24.5326 | 17.1938 | 48.1112 | 42.8015 | 42.8015 | 0 | 0
2025-02-07 14:00 | 26.45 | 40.5 | 100 | 24.8663 | 17.1243 | 46.068 | 31.7974 | 31.7974 | 0 | 0
2025-02-07 15:00 | 27.1 | 36 | 100 | 25.0939 | 16.976 | 44.1175 | 18.346 | 18.346 | 0 | 0
2025-02-07 16:00 | 27.1 | 37 | 100 | 25.0932 | 17.052 | 44.5702 | 22.8856 | 22.8856 | 0 | 0
2025-02-07 17:00 | 26.35 | 43 | 100 | 24.8302 | 17.2746 | 47.1626 | 41.6865 | 41.6865 | 0 | 0
2025-02-07 18:00 | 24.3 | 53 | 100 | 24.1071 | 17.3122 | 51.0501 | 59.1848 | 59.1848 | 0 | 0
2025-02-07 19:00 | 22.3 | 66.5 | 100 | 23.388 | 17.4532 | 55.8673 | 83.1216 | 83.1216 | 0 | 0
2025-02-07 20:00 | 21.45 | 74.5 | 100 | 23.0791 | 17.5931 | 58.5786 | 98.3536 | 98.3536 | 0 | 0
2025-02-07 21:00 | 20.8 | 76.5 | 100 | 22.8394 | 17.4602 | 59.0845 | 95.4439 | 95.4439 | 0 | 0
2025-02-07 22:00 | 20.2 | 78.5 | 70 | 22.6163 | 17.342 | 59.5966 | 65.1402 | 65.1402 | 0 | 0
2025-02-07 23:00 | 19.8 | 78.5 | 70 | 22.4658 | 17.1934 | 59.4715 | 61.1073 | 61.1073 | 0 | 0
2025-02-08 | 19.45 | 77.5 | 70 | 22.3327 | 17.0142 | 59.0283 | 55.5374 | 55.5374 | 0 | 0
2025-02-08 01:00 | 19.1 | 76.5 | 70 | 22.1989 | 16.8373 | 58.5988 | 50.0807 | 50.0807 | 0 | 0
2025-02-08 02:00 | 18.95 | 71 | 70 | 22.1377 | 16.5126 | 56.7113 | 37.3807 | 37.3807 | 0 | 0
2025-02-08 03:00 | 18.95 | 66 | 70 | 22.1342 | 16.2648 | 55.0234 | 27.0968 | 27.0968 | 0 | 0
2025-02-08 04:00 | 19.15 | 65 | 70 | 22.2101 | 16.2826 | 54.706 | 26.691 | 26.691 | 0 | 0
2025-02-08 05:00 | 19.55 | 65 | 70 | 22.3626 | 16.419 | 54.753 | 30.0376 | 30.0376 | 0 | 0
2025-02-08 06:00 | 19.8 | 66.5 | 100 | 22.4584 | 16.5824 | 55.3043 | 50.5129 | 50.5129 | 0 | 0
2025-02-08 07:00 | 20 | 68.5 | 100 | 22.5352 | 16.7559 | 56.0297 | 59.1444 | 59.1444 | 0 | 0
2025-02-08 08:00 | 20.85 | 67.5 | 100 | 22.8535 | 17.0009 | 55.8488 | 66.949 | 66.949 | 0 | 0
2025-02-08 09:00 | 22.25 | 64 | 100 | 23.369 | 17.2942 | 54.8884 | 73.5566 | 73.5566 | 0 | 0
2025-02-08 10:00 | 23.8 | 59.5 | 100 | 23.9286 | 17.5575 | 53.5364 | 77.5862 | 77.5862 | 0 | 0
2025-02-08 11:00 | 25.2 | 54.5 | 100 | 24.4248 | 17.7071 | 51.8559 | 76.1531 | 76.1531 | 0 | 0
2025-02-08 12:00 | 26.25 | 50.5 | 100 | 24.7918 | 17.777 | 50.413 | 72.7536 | 72.7536 | 0 | 0
2025-02-08 13:00 | 27.4 | 46 | 100 | 25.189 | 17.8176 | 48.6836 | 66.9414 | 66.9414 | 0 | 0
2025-02-08 14:00 | 26.8 | 52.5 | 100 | 24.9796 | 18.096 | 51.4499 | 88.5366 | 88.5366 | 0 | 0
2025-02-08 15:00 | 24.55 | 66.5 | 100 | 24.1944 | 18.2527 | 56.6347 | 115.1022 | 115.1022 | 0 | 0
2025-02-08 16:00 | 23.2 | 73.5 | 100 | 23.7151 | 18.1825 | 58.8751 | 121.081 | 121.081 | 0 | 0
2025-02-08 17:00 | 22.1 | 80.5 | 100 | 23.3195 | 18.1634 | 61.0607 | 128.5042 | 128.5042 | 0 | 0
2025-02-08 18:00 | 21.1 | 87 | 100 | 22.9557 | 18.1228 | 62.9756 | 133.9251 | 133.9251 | 0 | 0
2025-02-08 19:00 | 20.55 | 90 | 100 | 22.7535 | 18.0604 | 63.7751 | 134.3819 | 134.3819 | 0 | 0
2025-02-08 20:00 | 20.05 | 91.5 | 100 | 22.5677 | 17.9369 | 64.0552 | 130.7278 | 130.7278 | 0 | 0
2025-02-08 21:00 | 19.45 | 92 | 100 | 22.3423 | 17.7234 | 63.9486 | 122.4073 | 122.4073 | 0 | 0
2025-02-08 22:00 | 18.8 | 92 | 70 | 22.0953 | 17.4671 | 63.6714 | 78.4032 | 78.4032 | 0 | 0
2025-02-08 23:00 | 18.25 | 92 | 70 | 21.8845 | 17.252 | 63.4563 | 72.38 | 72.38 | 0 | 0
2025-02-09 | 17.8 | 92 | 70 | 21.7108 | 17.0769 | 63.2944 | 67.5516 | 67.5516 | 0 | 0
2025-02-09 01:00 | 17.45 | 91.5 | 70 | 21.5745 | 16.9184 | 63.018 | 62.9149 | 62.9149 | 0 | 0
2025-02-09 02:00 | 17.3 | 90.5 | 70 | 21.5152 | 16.8164 | 62.6552 | 59.4926 | 59.4926 | 0 | 0
2025-02-09 03:00 | 17.3 | 89 | 70 | 21.5139 | 16.7496 | 62.1825 | 56.7048 | 56.7048 | 0 | 0
2025-02-09 04:00 | 18.15 | 85 | 70 | 21.8406 | 16.8913 | 61.1478 | 57.6972 | 57.6972 | 0 | 0
2025-02-09 05:00 | 18.8 | 81.5 | 70 | 22.0878 | 16.9696 | 60.1808 | 57.2572 | 57.2572 | 0 | 0
2025-02-09 06:00 | 18.15 | 81.5 | 100 | 21.8379 | 16.7284 | 59.9983 | 72.5822 | 72.5822 | 0 | 0
2025-02-09 07:00 | 18.4 | 79 | 100 | 21.9324 | 16.7033 | 59.2333 | 68.9364 | 68.9364 | 0 | 0
2025-02-09 08:00 | 19.55 | 72.5 | 100 | 22.3674 | 16.8021 | 57.3036 | 65.3431 | 65.3431 | 0 | 0
2025-02-09 09:00 | 20.4 | 67 | 100 | 22.6849 | 16.8185 | 55.5558 | 59.3536 | 59.3536 | 0 | 0
2025-02-09 10:00 | 21.15 | 63 | 100 | 22.9631 | 16.8608 | 54.2612 | 55.9063 | 55.9063 | 0 | 0
2025-02-09 11:00 | 21.6 | 59.5 | 100 | 23.1284 | 16.8177 | 53.0568 | 49.7841 | 49.7841 | 0 | 0
2025-02-09 12:00 | 21.9 | 56.5 | 100 | 23.238 | 16.7453 | 51.9888 | 43.1705 | 43.1705 | 0 | 0
2025-02-09 13:00 | 22.25 | 51.5 | 100 | 23.3652 | 16.5646 | 50.1448 | 29.7933 | 29.7933 | 0 | 0
2025-02-09 14:00 | 22.35 | 46 | 100 | 23.4004 | 16.2657 | 48.0552 | 11.4491 | 11.4491 | 0 | 0
2025-02-09 15:00 | 22 | 45 | 100 | 23.271 | 16.1002 | 47.6718 | 4.4731 | 4.4731 | 0 | 0
2025-02-09 16:00 | 21.45 | 45 | 100 | 23.0669 | 15.9366 | 47.6773 | 0 | 0 | 0 | 0
2025-02-09 17:00 | 20.55 | 48.5 | 100 | 22.7313 | 15.8639 | 48.9729 | 1.9741 | 1.9741 | 0 | 0
2025-02-09 18:00 | 19.5 | 54 | 100 | 22.3365 | 15.8348 | 50.9149 | 8.5808 | 8.5808 | 0 | 0
2025-02-09 19:00 | 18.9 | 56.5 | 100 | 22.1084 | 15.7732 | 51.7614 | 9.7619 | 9.7619 | 0 | 0
2025-02-09 20:00 | 18.45 | 60 | 100 | 21.9375 | 15.8032 | 52.9258 | 15.1144 | 15.1144 | 0 | 0
2025-02-09 21:00 | 18.05 | 63.5 | 100 | 21.7853 | 15.8415 | 54.0664 | 20.6323 | 20.6323 | 0 | 0
2025-02-09 22:00 | 17.7 | 67 | 70 | 21.6519 | 15.8901 | 55.1865 | 18.4643 | 18.4643 | 0 | 0
2025-02-09 23:00 | 17.3 | 70.5 | 70 | 21.4985 | 15.9156 | 56.2799 | 21.8478 | 21.8478 | 0 | 0
2025-02-10 | 16.85 | 73.5 | 70 | 21.3244 | 15.8949 | 57.1871 | 23.644 | 23.644 | 0 | 0
2025-02-10 01:00 | 16.4 | 76.5 | 70 | 21.1494 | 15.8692 | 58.0728 | 25.2238 | 25.2238 | 0 | 0
2025-02-10 02:00 | 16.05 | 79.5 | 70 | 21.0133 | 15.8736 | 58.9521 | 27.4904 | 27.4904 | 0 | 0
2025-02-10 03:00 | 15.8 | 81.5 | 70 | 20.9156 | 15.8683 | 59.5267 | 28.7602 | 28.7602 | 0 | 0
2025-02-10 04:00 | 15.9 | 81.5 | 70 | 20.9554 | 15.9044 | 59.5376 | 29.6413 | 29.6413 | 0 | 0
2025-02-10 05:00 | 16.1 | 81 | 70 | 21.0345 | 15.9558 | 59.4091 | 30.5361 | 30.5361 | 0 | 0
2025-02-10 06:00 | 16.05 | 81.5 | 100 | 21.0151 | 15.9594 | 59.5477 | 44.1822 | 44.1822 | 0 | 0
2025-02-10 07:00 | 16.6 | 79.5 | 100 | 21.2311 | 16.0726 | 59.0075 | 46.1137 | 46.1137 | 0 | 0
2025-02-10 08:00 | 18.25 | 71 | 100 | 21.8685 | 16.2709 | 56.529 | 43.9708 | 43.9708 | 0 | 0
2025-02-10 09:00 | 19.65 | 63.5 | 100 | 22.3997 | 16.3803 | 54.1791 | 38.9426 | 38.9426 | 0 | 0
2025-02-10 10:00 | 20.3 | 60.5 | 100 | 22.6437 | 16.4413 | 53.2063 | 37.2996 | 37.2996 | 0 | 0
2025-02-10 11:00 | 20.8 | 57.5 | 100 | 22.8299 | 16.4436 | 52.1917 | 33.4952 | 33.4952 | 0 | 0
2025-02-10 12:00 | 21.1 | 55 | 100 | 22.9408 | 16.4021 | 51.3172 | 28.7259 | 28.7259 | 0 | 0
2025-02-10 13:00 | 21.2 | 53 | 100 | 22.9772 | 16.3213 | 50.5989 | 23.2428 | 23.2428 | 0 | 0
2025-02-10 14:00 | 21.1 | 52.5 | 100 | 22.9396 | 16.2607 | 50.4146 | 20.5485 | 20.5485 | 0 | 0
2025-02-10 15:00 | 20.75 | 54.5 | 100 | 22.8096 | 16.2605 | 51.1229 | 23.3494 | 23.3494 | 0 | 0
2025-02-10 16:00 | 20.15 | 58 | 100 | 22.5857 | 16.257 | 52.3281 | 27.88 | 27.88 | 0 | 0
2025-02-10 17:00 | 19.3 | 63 | 100 | 22.2661 | 16.2358 | 53.9864 | 33.462 | 33.462 | 0 | 0
2025-02-10 18:00 | 18.35 | 69.5 | 100 | 21.906 | 16.2333 | 56.0595 | 41.0494 | 41.0494 | 0 | 0
2025-02-10 19:00 | 17.7 | 73.5 | 100 | 21.6572 | 16.1952 | 57.2715 | 44.1186 | 44.1186 | 0 | 0
2025-02-10 20:00 | 17.2 | 75 | 100 | 21.4632 | 16.0872 | 57.675 | 41.8522 | 41.8522 | 0 | 0
2025-02-10 21:00 | 16.55 | 77 | 100 | 21.2092 | 15.9454 | 58.2145 | 38.9348 | 38.9348 | 0 | 0
2025-02-10 22:00 | 15.9 | 79.5 | 70 | 20.9537 | 15.8209 | 58.9013 | 25.9823 | 25.9823 | 0 | 0
2025-02-10 23:00 | 15.15 | 83.5 | 70 | 20.6574 | 15.7164 | 60.0086 | 26.1789 | 26.1789 | 0 | 0
2025-02-11 | 14.1 | 88.5 | 70 | 20.2375 | 15.5291 | 61.3356 | 24.9117 | 24.9117 | 0 | 0
2025-02-11 01:00 | 13.2 | 91.5 | 70 | 19.8721 | 15.3088 | 62.0826 | 21.4607 | 21.4607 | 0 | 0
2025-02-11 02:00 | 12.8 | 91.5 | 70 | 19.7071 | 15.1614 | 62.0522 | 17.9226 | 17.9226 | 0 | 0
2025-02-11 03:00 | 12.75 | 91 | 70 | 19.6858 | 15.1241 | 61.9153 | 16.7611 | 16.7611 | 0 | 0
2025-02-11 04:00 | 13.15 | 87 | 70 | 19.8469 | 15.1242 | 60.8453 | 14.2975 | 14.2975 | 0 | 0
2025-02-11 05:00 | 13.35 | 84 | 70 | 19.9262 | 15.0848 | 60.0226 | 11.4567 | 11.4567 | 0 | 0
2025-02-11 06:00 | 12.75 | 87 | 100 | 19.6818 | 14.9797 | 60.8238 | 15.5193 | 15.5193 | 0 | 0
2025-02-11 07:00 | 12.9 | 86 | 100 | 19.7428 | 14.9978 | 60.5476 | 15.1588 | 15.1588 | 0 | 0
2025-02-11 08:00 | 15.15 | 76.5 | 100 | 20.6508 | 15.4298 | 57.9245 | 20.5163 | 20.5163 | 0 | 0
2025-02-11 09:00 | 18.25 | 65 | 100 | 21.864 | 15.9839 | 54.5293 | 26.7832 | 26.7832 | 0 | 0
2025-02-11 10:00 | 20.6 | 56 | 100 | 22.7541 | 16.2978 | 51.6168 | 26.2348 | 26.2348 | 0 | 0
2025-02-11 11:00 | 22.4 | 47.5 | 100 | 23.4192 | 16.3773 | 48.5818 | 16.8263 | 16.8263 | 0 | 0
2025-02-11 12:00 | 24.05 | 40 | 100 | 24.018 | 16.3953 | 45.675 | 5.4043 | 5.4043 | 0 | 0
2025-02-11 13:00 | 25 | 38 | 100 | 24.3579 | 16.5318 | 44.8678 | 6.5021 | 6.5021 | 0 | 0
2025-02-11 14:00 | 25 | 41 | 100 | 24.3573 | 16.7374 | 46.1359 | 18.8008 | 18.8008 | 0 | 0
2025-02-11 15:00 | 24.45 | 42.5 | 100 | 24.1613 | 16.6752 | 46.7324 | 19.3278 | 19.3278 | 0 | 0
2025-02-11 16:00 | 23.85 | 45.5 | 100 | 23.9461 | 16.6919 | 47.9166 | 24.8426 | 24.8426 | 0 | 0
2025-02-11 17:00 | 22.7 | 53.5 | 100 | 23.5305 | 16.829 | 50.95 | 41.8529 | 41.8529 | 0 | 0
2025-02-11 18:00 | 21.2 | 61.5 | 100 | 22.981 | 16.7951 | 53.7213 | 51.5568 | 51.5568 | 0 | 0
2025-02-11 19:00 | 20.2 | 66.5 | 100 | 22.6094 | 16.7231 | 55.3325 | 55.1614 | 55.1614 | 0 | 0
2025-02-11 20:00 | 19.45 | 70.5 | 100 | 22.3282 | 16.6671 | 56.5758 | 57.8253 | 57.8253 | 0 | 0
2025-02-11 21:00 | 18.75 | 73.5 | 100 | 22.0629 | 16.5676 | 57.4529 | 57.5822 | 57.5822 | 0 | 0
2025-02-11 22:00 | 18.15 | 70.5 | 70 | 21.8295 | 16.2119 | 56.3576 | 28.9655 | 28.9655 | 0 | 0
2025-02-11 23:00 | 17.45 | 64 | 70 | 21.5519 | 15.6664 | 54.1875 | 10.6135 | 10.6135 | 0 | 0
2025-02-12 | 16.55 | 62 | 70 | 21.1961 | 15.2777 | 53.5584 | 0.1073 | 0.1073 | 0 | 0
2025-02-12 01:00 | 16.1 | 64.5 | 70 | 21.0197 | 15.2411 | 54.3496 | 1.2975 | 1.2975 | 0 | 0
2025-02-12 02:00 | 16.3 | 64.5 | 70 | 21.0991 | 15.3068 | 54.347 | 2.8047 | 2.8047 | 0 | 0
2025-02-12 03:00 | 16.5 | 59.5 | 70 | 21.174 | 15.148 | 52.7886 | 0 | 0 | 0 | 0
2025-02-12 04:00 | 16.55 | 57.5 | 70 | 21.1921 | 15.0728 | 52.1603 | 0 | 0 | 0 | 0
2025-02-12 05:00 | 16.35 | 58.5 | 70 | 21.1137 | 15.0552 | 52.4844 | 0 | 0 | 0 | 0
2025-02-12 06:00 | 15.9 | 57.5 | 100 | 20.9336 | 14.8676 | 52.2135 | 0 | 0 | 0 | 0
2025-02-12 07:00 | 16.35 | 55 | 100 | 21.1106 | 14.898 | 51.3846 | 0 | 0 | 0 | 0
2025-02-12 08:00 | 18.7 | 50.5 | 100 | 22.0272 | 15.4084 | 49.7059 | 0 | 0 | 0 | 0
2025-02-12 09:00 | 22.05 | 44 | 100 | 23.2892 | 16.0608 | 47.2476 | 1.0489 | 1.0489 | 0 | 0
2025-02-12 10:00 | 24.65 | 38.5 | 100 | 24.2332 | 16.468 | 45.0606 | 5.1189 | 5.1189 | 0 | 0
2025-02-12 11:00 | 26.9 | 38 | 100 | 25.0235 | 17.0783 | 44.9493 | 24.8399 | 24.8399 | 0 | 0
2025-02-12 12:00 | 29 | 33.5 | 100 | 25.7421 | 17.317 | 43.0371 | 24.3298 | 24.3298 | 0 | 0
2025-02-12 13:00 | 30 | 27 | 100 | 26.0853 | 17.0281 | 39.8991 | 0.1939 | 0.1939 | 0 | 0
2025-02-12 14:00 | 29.8 | 28.5 | 100 | 26.0164 | 17.1071 | 40.6473 | 6.3756 | 6.3756 | 0 | 0
2025-02-12 15:00 | 28.85 | 34 | 100 | 25.6912 | 17.3146 | 43.2805 | 25.5173 | 25.5173 | 0 | 0
2025-02-12 16:00 | 28.2 | 38.5 | 100 | 25.4671 | 17.4892 | 45.3443 | 40.78 | 40.78 | 0 | 0
2025-02-12 17:00 | 26.35 | 45 | 100 | 24.8292 | 17.4212 | 48.0145 | 50.0985 | 50.0985 | 0 | 0
2025-02-12 18:00 | 23.9 | 54.5 | 100 | 23.9642 | 17.2797 | 51.5514 | 59.8447 | 59.8447 | 0 | 0
2025-02-12 19:00 | 22.9 | 60 | 100 | 23.6046 | 17.2839 | 53.5012 | 67.6955 | 67.6955 | 0 | 0
2025-02-12 20:00 | 22.55 | 57 | 100 | 23.4766 | 16.9889 | 52.2685 | 52.5452 | 52.5452 | 0 | 0
2025-02-12 21:00 | 21.9 | 54.5 | 100 | 23.2373 | 16.6308 | 51.2243 | 36.1531 | 36.1531 | 0 | 0
2025-02-12 22:00 | 21 | 56 | 70 | 22.9039 | 16.4247 | 51.6856 | 21.7142 | 21.7142 | 0 | 0
2025-02-12 23:00 | 20.25 | 55 | 70 | 22.6218 | 16.1278 | 51.2725 | 13.6596 | 13.6596 | 0 | 0
2025-02-13 | 19.55 | 55.5 | 70 | 22.3565 | 15.9308 | 51.4223 | 9.5006 | 9.5006 | 0 | 0
2025-02-13 01:00 | 19.2 | 59 | 70 | 22.2252 | 15.998 | 52.6176 | 14.2798 | 14.2798 | 0 | 0
2025-02-13 02:00 | 19.1 | 63 | 70 | 22.1896 | 16.1676 | 53.9801 | 21.8717 | 21.8717 | 0 | 0
2025-02-13 03:00 | 19.3 | 62 | 70 | 22.2654 | 16.1838 | 53.6586 | 21.4119 | 21.4119 | 0 | 0
2025-02-13 04:00 | 19.15 | 59.5 | 70 | 22.2064 | 16.0069 | 52.7903 | 14.9667 | 14.9667 | 0 | 0
2025-02-13 05:00 | 18.6 | 60 | 70 | 21.9954 | 15.8522 | 52.9289 | 11.7172 | 11.7172 | 0 | 0
2025-02-13 06:00 | 18.2 | 61 | 100 | 21.8416 | 15.771 | 53.2418 | 15.1694 | 15.1694 | 0 | 0
2025-02-13 07:00 | 19.1 | 59 | 100 | 22.1869 | 15.9663 | 52.5993 | 19.1819 | 19.1819 | 0 | 0
2025-02-13 08:00 | 21.75 | 51 | 100 | 23.1807 | 16.3806 | 49.8878 | 22.359 | 22.359 | 0 | 0
2025-02-13 09:00 | 24.7 | 42 | 100 | 24.2505 | 16.7188 | 46.523 | 19.6969 | 19.6969 | 0 | 0
2025-02-13 10:00 | 27.1 | 37.5 | 100 | 25.0928 | 17.0975 | 44.7422 | 24.6028 | 24.6028 | 0 | 0
2025-02-13 11:00 | 28.9 | 35.5 | 100 | 25.706 | 17.4539 | 43.9852 | 33.2154 | 33.2154 | 0 | 0
2025-02-13 12:00 | 30.2 | 33.5 | 100 | 26.1403 | 17.6504 | 43.1611 | 36.1693 | 36.1693 | 0 | 0
2025-02-13 13:00 | 30.95 | 32.5 | 100 | 26.3872 | 17.7699 | 42.7538 | 38.4082 | 38.4082 | 0 | 0
2025-02-13 14:00 | 31.2 | 32 | 100 | 26.4693 | 17.7927 | 42.5325 | 38.2179 | 38.2179 | 0 | 0
2025-02-13 15:00 | 30.2 | 35 | 100 | 26.1377 | 17.7771 | 43.9299 | 44.2372 | 44.2372 | 0 | 0
2025-02-13 16:00 | 28.4 | 38.5 | 100 | 25.5346 | 17.548 | 45.3734 | 42.9146 | 42.9146 | 0 | 0
2025-02-13 17:00 | 26.4 | 45.5 | 100 | 24.8462 | 17.4734 | 48.2368 | 52.7781 | 52.7781 | 0 | 0
2025-02-13 18:00 | 24.5 | 55.5 | 100 | 24.1779 | 17.5417 | 52.0805 | 71.082 | 71.082 | 0 | 0
2025-02-13 19:00 | 23.65 | 58.5 | 100 | 23.8748 | 17.4467 | 53.0845 | 71.7323 | 71.7323 | 0 | 0
2025-02-13 20:00 | 23.65 | 56 | 100 | 23.8747 | 17.2921 | 52.0903 | 62.353 | 62.353 | 0 | 0
2025-02-13 21:00 | 23.85 | 53 | 100 | 23.9463 | 17.1698 | 50.9309 | 53.4487 | 53.4487 | 0 | 0
2025-02-13 22:00 | 23.85 | 51 | 70 | 23.9462 | 17.0434 | 50.1299 | 32.0985 | 32.0985 | 0 | 0
2025-02-13 23:00 | 23.25 | 50.5 | 70 | 23.7298 | 16.8211 | 49.8536 | 26.0364 | 26.0364 | 0 | 0
2025-02-14 | 22.55 | 51.5 | 70 | 23.4752 | 16.6604 | 50.1664 | 23.127 | 23.127 | 0 | 0
2025-02-14 01:00 | 22.05 | 53.5 | 70 | 23.2923 | 16.6193 | 50.8777 | 24.158 | 24.158 | 0 | 0
2025-02-14 02:00 | 21.05 | 57 | 70 | 22.923 | 16.4951 | 52.0698 | 24.5119 | 24.5119 | 0 | 0
2025-02-14 03:00 | 20.3 | 59.5 | 70 | 22.6431 | 16.3847 | 52.8888 | 24.1257 | 24.1257 | 0 | 0
2025-02-14 04:00 | 21 | 67 | 70 | 22.9091 | 17.0273 | 55.6914 | 47.0308 | 47.0308 | 0 | 0
2025-02-14 05:00 | 21.65 | 77.5 | 70 | 23.1539 | 17.8312 | 59.7189 | 77.7026 | 77.7026 | 0 | 0
2025-02-14 06:00 | 21.15 | 81.5 | 100 | 22.9715 | 17.8565 | 60.9704 | 116.473 | 116.473 | 0 | 0
2025-02-14 07:00 | 21.45 | 77 | 100 | 23.0802 | 17.7303 | 59.445 | 106.1983 | 106.1983 | 0 | 0
2025-02-14 08:00 | 23.15 | 66 | 100 | 23.696 | 17.7276 | 55.8769 | 92.5477 | 92.5477 | 0 | 0
2025-02-14 09:00 | 25 | 55 | 100 | 24.3545 | 17.6775 | 51.9713 | 75.1981 | 75.1981 | 0 | 0
2025-02-14 10:00 | 26.35 | 46.5 | 100 | 24.8284 | 17.5327 | 48.6363 | 56.2306 | 56.2306 | 0 | 0
2025-02-14 11:00 | 27.5 | 38.5 | 100 | 25.2292 | 17.2897 | 45.2327 | 33.2049 | 33.2049 | 0 | 0
2025-02-14 12:00 | 28.15 | 33.5 | 100 | 25.4553 | 17.0818 | 42.9812 | 16.2507 | 16.2507 | 0 | 0
2025-02-14 13:00 | 28 | 34 | 100 | 25.4038 | 17.0791 | 43.2129 | 17.2819 | 17.2819 | 0 | 0
2025-02-14 14:00 | 27.1 | 38 | 100 | 25.0924 | 17.1331 | 44.9863 | 27.0514 | 27.0514 | 0 | 0
2025-02-14 15:00 | 26.3 | 42.5 | 100 | 24.8131 | 17.2277 | 46.9067 | 38.6762 | 38.6762 | 0 | 0
2025-02-14 16:00 | 25.75 | 49.5 | 100 | 24.6187 | 17.5495 | 49.8487 | 62.2185 | 62.2185 | 0 | 0
2025-02-14 17:00 | 24.55 | 59 | 100 | 24.1952 | 17.7826 | 53.5291 | 85.4552 | 85.4552 | 0 | 0
2025-02-14 18:00 | 23.35 | 65.5 | 100 | 23.7678 | 17.7671 | 55.7672 | 93.7182 | 93.7182 | 0 | 0
2025-02-14 19:00 | 22.45 | 69.5 | 100 | 23.4435 | 17.6803 | 57.0157 | 95.3655 | 95.3655 | 0 | 0
2025-02-14 20:00 | 21.7 | 71.5 | 100 | 23.17 | 17.5223 | 57.5191 | 91.5594 | 91.5594 | 0 | 0
2025-02-14 21:00 | 21.1 | 73.5 | 100 | 22.9493 | 17.4134 | 58.0601 | 89.6656 | 89.6656 | 0 | 0
2025-02-14 22:00 | 20.4 | 77.5 | 70 | 22.6907 | 17.3664 | 59.2672 | 64.7125 | 64.7125 | 0 | 0
2025-02-14 23:00 | 19.75 | 82.5 | 70 | 22.4494 | 17.3757 | 60.793 | 68.8421 | 68.8421 | 0 | 0
2025-02-15 | 19.25 | 87.5 | 70 | 22.2635 | 17.4294 | 62.3209 | 74.0296 | 74.0296 | 0 | 0
2025-02-15 01:00 | 18.85 | 92.5 | 70 | 22.1148 | 17.511 | 63.8438 | 79.8759 | 79.8759 | 0 | 0
2025-02-15 02:00 | 18.55 | 96.5 | 70 | 22.0031 | 17.5772 | 65.0428 | 84.5136 | 84.5136 | 0 | 0
2025-02-15 03:00 | 18.35 | 98 | 70 | 21.9276 | 17.5651 | 65.4499 | 85.2068 | 85.2068 | 0 | 0
2025-02-15 04:00 | 18.6 | 96.5 | 70 | 22.0222 | 17.597 | 65.0733 | 85.1351 | 85.1351 | 0 | 0
2025-02-15 05:00 | 18.6 | 96 | 70 | 22.0218 | 17.5743 | 64.9064 | 84.129 | 84.129 | 0 | 0
2025-02-15 06:00 | 18.2 | 97.5 | 100 | 21.8695 | 17.4822 | 65.216 | 117.8388 | 117.8388 | 0 | 0
2025-02-15 07:00 | 18.85 | 96.5 | 100 | 22.1176 | 17.6976 | 65.1706 | 125.5852 | 125.5852 | 0 | 0
2025-02-15 08:00 | 20.35 | 91 | 100 | 22.6795 | 18.0312 | 63.9965 | 133.8911 | 133.8911 | 0 | 0
2025-02-15 09:00 | 21.85 | 82 | 100 | 23.2288 | 18.1509 | 61.4602 | 129.188 | 129.188 | 0 | 0
2025-02-15 10:00 | 23 | 74 | 100 | 23.6434 | 18.1394 | 58.94 | 119.3922 | 119.3922 | 0 | 0
2025-02-15 11:00 | 23.6 | 70.5 | 100 | 23.8578 | 18.1553 | 57.8228 | 115.7613 | 115.7613 | 0 | 0
2025-02-15 12:00 | 24 | 68.5 | 100 | 24 | 18.18 | 57.1922 | 114.2964 | 114.2964 | 0 | 0
2025-02-15 13:00 | 24.25 | 67 | 100 | 24.0886 | 18.178 | 56.6925 | 112.3383 | 112.3383 | 0 | 0
2025-02-15 14:00 | 24.6 | 64 | 100 | 24.2123 | 18.1156 | 55.6093 | 105.8639 | 105.8639 | 0 | 0
2025-02-15 15:00 | 24.9 | 60 | 100 | 24.3184 | 17.9647 | 54.0691 | 94.3421 | 94.3421 | 0 | 0
2025-02-15 16:00 | 24.25 | 62.5 | 100 | 24.0888 | 17.8982 | 54.884 | 95.1691 | 95.1691 | 0 | 0
2025-02-15 17:00 | 22.85 | 72.5 | 100 | 23.5891 | 17.9967 | 58.3258 | 111.9888 | 111.9888 | 0 | 0
2025-02-15 18:00 | 21.95 | 81 | 100 | 23.265 | 18.134 | 61.1586 | 127.6262 | 127.6262 | 0 | 0
2025-02-15 19:00 | 21.45 | 85 | 100 | 23.0836 | 18.1554 | 62.399 | 132.9416 | 132.9416 | 0 | 0
2025-02-15 20:00 | 20.8 | 87 | 100 | 22.8447 | 18.006 | 62.813 | 128.8335 | 128.8335 | 0 | 0
2025-02-15 21:00 | 20.4 | 88 | 100 | 22.6965 | 17.9009 | 62.9804 | 125.481 | 125.481 | 0 | 0
2025-02-15 22:00 | 20.35 | 89.5 | 70 | 22.6787 | 17.9565 | 63.4811 | 90.5232 | 90.5232 | 0 | 0
2025-02-15 23:00 | 20.1 | 89.5 | 70 | 22.5853 | 17.858 | 63.367 | 87.6803 | 87.6803 | 0 | 0
2025-02-16 | 19.85 | 88 | 70 | 22.4905 | 17.6862 | 62.7428 | 81.6981 | 81.6981 | 0 | 0
2025-02-16 01:00 | 19.65 | 85.5 | 70 | 22.4136 | 17.4853 | 61.8073 | 74.2524 | 74.2524 | 0 | 0
2025-02-16 02:00 | 19.65 | 83.5 | 70 | 22.4123 | 17.3869 | 61.1236 | 70.0489 | 70.0489 | 0 | 0
2025-02-16 03:00 | 19.75 | 83.5 | 70 | 22.4501 | 17.425 | 61.1636 | 71.1276 | 71.1276 | 0 | 0
2025-02-16 04:00 | 19.7 | 87 | 70 | 22.4334 | 17.578 | 62.3528 | 78.0288 | 78.0288 | 0 | 0
2025-02-16 05:00 | 19.7 | 90.5 | 70 | 22.4356 | 17.7494 | 63.5526 | 85.4056 | 85.4056 | 0 | 0
2025-02-16 06:00 | 19.6 | 90.5 | 100 | 22.3979 | 17.7104 | 63.5028 | 120.3462 | 120.3462 | 0 | 0
2025-02-16 07:00 | 20.05 | 85.5 | 100 | 22.5641 | 17.639 | 61.9605 | 112.2204 | 112.2204 | 0 | 0
2025-02-16 08:00 | 21.45 | 75 | 100 | 23.0794 | 17.6215 | 58.7329 | 99.748 | 99.748 | 0 | 0
2025-02-16 09:00 | 23.1 | 66 | 100 | 23.678 | 17.7088 | 55.8807 | 92.0376 | 92.0376 | 0 | 0
2025-02-16 10:00 | 24.1 | 63.5 | 100 | 24.0355 | 17.9102 | 55.2123 | 96.6596 | 96.6596 | 0 | 0
2025-02-16 11:00 | 24.25 | 64 | 100 | 24.0887 | 17.9935 | 55.4675 | 100.7078 | 100.7078 | 0 | 0
2025-02-16 12:00 | 24.85 | 60.5 | 100 | 24.3007 | 17.9809 | 54.2424 | 95.47 | 95.47 | 0 | 0
2025-02-16 13:00 | 25.35 | 57 | 100 | 24.4766 | 17.9234 | 52.9417 | 88.211 | 88.211 | 0 | 0
2025-02-16 14:00 | 24.9 | 58 | 100 | 24.3187 | 17.8362 | 53.2331 | 86.3092 | 86.3092 | 0 | 0
2025-02-16 15:00 | 24.45 | 60.5 | 100 | 24.1597 | 17.8421 | 54.1328 | 90.1613 | 90.1613 | 0 | 0
2025-02-16 16:00 | 24.6 | 54.5 | 100 | 24.2134 | 17.5082 | 51.7197 | 68.6648 | 68.6648 | 0 | 0
2025-02-16 17:00 | 24.75 | 47.5 | 100 | 24.2675 | 17.0965 | 48.8559 | 42.6683 | 42.6683 | 0 | 0
2025-02-16 18:00 | 24.1 | 49.5 | 100 | 24.0358 | 17.0233 | 49.5866 | 43.2063 | 43.2063 | 0 | 0
2025-02-16 19:00 | 23.05 | 53 | 100 | 23.6577 | 16.9085 | 50.8313 | 44.3333 | 44.3333 | 0 | 0
2025-02-16 20:00 | 22.4 | 55.5 | 100 | 23.4214 | 16.8492 | 51.6928 | 45.6507 | 45.6507 | 0 | 0
2025-02-16 21:00 | 22 | 59.5 | 100 | 23.2759 | 16.9505 | 53.1368 | 54.7628 | 54.7628 | 0 | 0
2025-02-16 22:00 | 21.2 | 68.5 | 70 | 22.9841 | 17.1786 | 56.2925 | 52.3812 | 52.3812 | 0 | 0
2025-02-16 23:00 | 20.8 | 75.5 | 70 | 22.8389 | 17.4085 | 58.7082 | 64.4465 | 64.4465 | 0 | 0
2025-02-17 | 20.5 | 81.5 | 70 | 22.7302 | 17.6084 | 60.7427 | 74.7353 | 74.7353 | 0 | 0
2025-02-17 01:00 | 20.1 | 88 | 70 | 22.5844 | 17.783 | 62.8625 | 84.56 | 84.56 | 0 | 0
2025-02-17 02:00 | 19.9 | 90.5 | 70 | 22.5109 | 17.8283 | 63.6429 | 87.6756 | 87.6756 | 0 | 0
2025-02-17 03:00 | 19.5 | 91.5 | 70 | 22.3608 | 17.7192 | 63.8076 | 85.2534 | 85.2534 | 0 | 0
2025-02-17 04:00 | 20.1 | 85 | 70 | 22.5826 | 17.6335 | 61.8223 | 78.1196 | 78.1196 | 0 | 0
2025-02-17 05:00 | 20.9 | 77 | 70 | 22.8768 | 17.5238 | 59.2926 | 68.9261 | 68.9261 | 0 | 0
2025-02-17 06:00 | 20.65 | 74 | 100 | 22.7822 | 17.2748 | 58.1316 | 85.1838 | 85.1838 | 0 | 0
2025-02-17 07:00 | 20.95 | 68.5 | 100 | 22.8912 | 17.0899 | 56.2291 | 71.4796 | 71.4796 | 0 | 0
2025-02-17 08:00 | 22.1 | 63.5 | 100 | 23.3139 | 17.2137 | 54.6588 | 69.8161 | 69.8161 | 0 | 0
2025-02-17 09:00 | 24.7 | 57 | 100 | 24.2484 | 17.7047 | 52.7521 | 79.5945 | 79.5945 | 0 | 0
2025-02-17 10:00 | 27.4 | 48 | 100 | 25.1873 | 17.9691 | 49.561 | 75.721 | 75.721 | 0 | 0
2025-02-17 11:00 | 29.1 | 40.5 | 100 | 25.7662 | 17.9158 | 46.4403 | 60.3159 | 60.3159 | 0 | 0
2025-02-17 12:00 | 30.2 | 36.5 | 100 | 26.1351 | 17.9057 | 44.6829 | 52.1265 | 52.1265 | 0 | 0
2025-02-17 13:00 | 29.65 | 39 | 100 | 25.9504 | 17.9551 | 45.8279 | 59.0706 | 59.0706 | 0 | 0
2025-02-17 14:00 | 28.95 | 40.5 | 100 | 25.7164 | 17.8684 | 46.4275 | 58.7939 | 58.7939 | 0 | 0
2025-02-17 15:00 | 28.45 | 39.5 | 100 | 25.5503 | 17.6392 | 45.869 | 48.4378 | 48.4378 | 0 | 0
2025-02-17 16:00 | 27.65 | 40.5 | 100 | 25.2787 | 17.48 | 46.2142 | 44.4996 | 44.4996 | 0 | 0
2025-02-17 17:00 | 26.7 | 42.5 | 100 | 24.9516 | 17.3449 | 46.9817 | 43.2268 | 43.2268 | 0 | 0
2025-02-17 18:00 | 25.45 | 44.5 | 100 | 24.5154 | 17.1083 | 47.6858 | 38.1707 | 38.1707 | 0 | 0
2025-02-17 19:00 | 24.3 | 49.5 | 100 | 24.1073 | 17.0878 | 49.6051 | 45.3831 | 45.3831 | 0 | 0
2025-02-17 20:00 | 24 | 53.5 | 100 | 24 | 17.249 | 51.1701 | 57.2542 | 57.2542 | 0 | 0
2025-02-17 21:00 | 23.7 | 55 | 100 | 23.8926 | 17.2457 | 51.7125 | 59.3049 | 59.3049 | 0 | 0
2025-02-17 22:00 | 23 | 58 | 70 | 23.6405 | 17.1969 | 52.7533 | 43.2457 | 43.2457 | 0 | 0
2025-02-17 23:00 | 22.55 | 62 | 70 | 23.4779 | 17.2818 | 54.2013 | 49.3186 | 49.3186 | 0 | 0
2025-02-18 | 21.5 | 68 | 70 | 23.0949 | 17.2567 | 56.1902 | 54.0637 | 54.0637 | 0 | 0
2025-02-18 01:00 | 20.5 | 73 | 70 | 22.7256 | 17.1683 | 57.7284 | 55.9106 | 55.9106 | 0 | 0
2025-02-18 02:00 | 19.65 | 77.5 | 70 | 22.4085 | 17.0888 | 59.064 | 57.3761 | 57.3761 | 0 | 0
2025-02-18 03:00 | 19 | 79.5 | 70 | 22.1628 | 16.9477 | 59.5628 | 55.1425 | 55.1425 | 0 | 0
2025-02-18 04:00 | 19.15 | 84.5 | 70 | 22.2234 | 17.2456 | 61.2969 | 66.9446 | 66.9446 | 0 | 0
2025-02-18 05:00 | 19.45 | 89.5 | 70 | 22.3406 | 17.6026 | 63.1034 | 80.513 | 80.513 | 0 | 0
2025-02-18 06:00 | 19.55 | 88 | 100 | 22.3774 | 17.5689 | 62.628 | 112.0706 | 112.0706 | 0 | 0
2025-02-18 07:00 | 20.05 | 84.5 | 100 | 22.5635 | 17.5896 | 61.6116 | 109.1358 | 109.1358 | 0 | 0
2025-02-18 08:00 | 21.6 | 76 | 100 | 23.135 | 17.7315 | 59.1515 | 105.2709 | 105.2709 | 0 | 0
2025-02-18 09:00 | 22.8 | 69.5 | 100 | 23.5704 | 17.8064 | 57.1307 | 100.339 | 100.339 | 0 | 0
2025-02-18 10:00 | 23.4 | 65 | 100 | 23.7857 | 17.7559 | 55.5789 | 92.4996 | 92.4996 | 0 | 0
2025-02-18 11:00 | 24.45 | 55.5 | 100 | 24.1602 | 17.5255 | 52.0669 | 70.4334 | 70.4334 | 0 | 0
2025-02-18 12:00 | 26.05 | 43.5 | 100 | 24.7257 | 17.2231 | 47.3124 | 40.2882 | 40.2882 | 0 | 0
2025-02-18 13:00 | 26.65 | 40.5 | 100 | 24.9355 | 17.1858 | 46.0713 | 33.7038 | 33.7038 | 0 | 0
2025-02-18 14:00 | 25.15 | 56.5 | 100 | 24.4068 | 17.8228 | 52.6756 | 83.5533 | 83.5533 | 0 | 0
2025-02-18 15:00 | 24.05 | 69.5 | 100 | 24.0177 | 18.2584 | 57.6202 | 118.8993 | 118.8993 | 0 | 0
2025-02-18 16:00 | 23.45 | 72 | 100 | 23.8044 | 18.1889 | 58.3573 | 119.0797 | 119.0797 | 0 | 0
2025-02-18 17:00 | 22.7 | 75.5 | 100 | 23.5356 | 18.1128 | 59.3972 | 120.19 | 120.19 | 0 | 0
2025-02-18 18:00 | 22.25 | 77 | 100 | 23.3729 | 18.0287 | 59.7812 | 118.5305 | 118.5305 | 0 | 0
2025-02-18 19:00 | 21.7 | 78 | 100 | 23.1725 | 17.8769 | 59.9248 | 113.457 | 113.457 | 0 | 0
2025-02-18 20:00 | 21.35 | 81 | 100 | 23.0451 | 17.9058 | 60.8755 | 117.9763 | 117.9763 | 0 | 0
2025-02-18 21:00 | 21.2 | 82.5 | 100 | 22.9905 | 17.9279 | 61.3532 | 120.5131 | 120.5131 | 0 | 0
2025-02-18 22:00 | 20.7 | 85 | 70 | 22.8066 | 17.8658 | 62.0351 | 84.4704 | 84.4704 | 0 | 0
2025-02-18 23:00 | 20.3 | 88.5 | 70 | 22.6595 | 17.8868 | 63.0984 | 87.7191 | 87.7191 | 0 | 0
2025-02-19 | 19.75 | 90.5 | 70 | 22.4544 | 17.7699 | 63.5509 | 85.8207 | 85.8207 | 0 | 0
2025-02-19 01:00 | 18.8 | 93 | 70 | 22.0961 | 17.514 | 63.9897 | 80.3282 | 80.3282 | 0 | 0
2025-02-19 02:00 | 18.2 | 93.5 | 70 | 21.8665 | 17.3008 | 63.9154 | 74.7 | 74.7 | 0 | 0
2025-02-19 03:00 | 18 | 91.5 | 70 | 21.7878 | 17.1318 | 63.1929 | 68.6597 | 68.6597 | 0 | 0
2025-02-19 04:00 | 18.85 | 89.5 | 70 | 22.1126 | 17.3692 | 62.8521 | 73.8681 | 73.8681 | 0 | 0
2025-02-19 05:00 | 19.5 | 89 | 70 | 22.3592 | 17.5984 | 62.9409 | 79.942 | 79.942 | 0 | 0
2025-02-19 06:00 | 19.3 | 88 | 100 | 22.2828 | 17.4726 | 62.5156 | 108.0595 | 108.0595 | 0 | 0
2025-02-19 07:00 | 19.9 | 83 | 100 | 22.5063 | 17.4574 | 61.0246 | 102.1646 | 102.1646 | 0 | 0
2025-02-19 08:00 | 21.35 | 71.5 | 100 | 23.041 | 17.3957 | 57.41 | 86.6216 | 86.6216 | 0 | 0
2025-02-19 09:00 | 22.9 | 58 | 100 | 23.6042 | 17.1655 | 52.7127 | 60.3465 | 60.3465 | 0 | 0
2025-02-19 10:00 | 24.1 | 48.5 | 100 | 24.0358 | 16.9633 | 49.1416 | 38.9622 | 38.9622 | 0 | 0
2025-02-19 11:00 | 24.95 | 44 | 100 | 24.339 | 16.9269 | 47.3881 | 30.4485 | 30.4485 | 0 | 0
2025-02-19 12:00 | 25.3 | 43 | 100 | 24.463 | 16.963 | 47.01 | 30.1446 | 30.1446 | 0 | 0
2025-02-19 13:00 | 25.2 | 44 | 100 | 24.4274 | 17.0001 | 47.4308 | 33.275 | 33.275 | 0 | 0
2025-02-19 14:00 | 24.85 | 46.5 | 100 | 24.3031 | 17.0619 | 48.444 | 39.6799 | 39.6799 | 0 | 0
2025-02-19 15:00 | 24.3 | 50 | 100 | 24.1072 | 17.1199 | 49.8138 | 47.3775 | 47.3775 | 0 | 0
2025-02-19 16:00 | 23.7 | 52 | 100 | 23.8924 | 17.0559 | 50.5303 | 48.1296 | 48.1296 | 0 | 0
2025-02-19 17:00 | 22.75 | 55.5 | 100 | 23.5492 | 16.9629 | 51.7545 | 49.8574 | 49.8574 | 0 | 0
2025-02-19 18:00 | 21.45 | 64 | 100 | 23.0747 | 17.0173 | 54.7161 | 63.2863 | 63.2863 | 0 | 0
2025-02-19 19:00 | 20.3 | 73.5 | 100 | 22.651 | 17.1214 | 57.8586 | 78.7604 | 78.7604 | 0 | 0
2025-02-19 20:00 | 19.5 | 80.5 | 100 | 22.3536 | 17.1823 | 60.0518 | 88.8935 | 88.8935 | 0 | 0
2025-02-19 21:00 | 18.95 | 84.5 | 100 | 22.1472 | 17.1704 | 61.2263 | 92.6372 | 92.6372 | 0 | 0
2025-02-19 22:00 | 18.4 | 87.5 | 70 | 21.9388 | 17.1022 | 62.0386 | 65.1427 | 65.1427 | 0 | 0
2025-02-19 23:00 | 17.65 | 90.5 | 70 | 21.6514 | 16.9507 | 62.7667 | 63.1338 | 63.1338 | 0 | 0
2025-02-20 | 16.85 | 93 | 70 | 21.3412 | 16.7521 | 63.3057 | 59.4652 | 59.4652 | 0 | 0
2025-02-20 01:00 | 16.2 | 95 | 70 | 21.0868 | 16.5844 | 63.7284 | 56.3248 | 56.3248 | 0 | 0
2025-02-20 02:00 | 15.8 | 96.5 | 70 | 20.9294 | 16.4911 | 64.0696 | 54.8271 | 54.8271 | 0 | 0
2025-02-20 03:00 | 16 | 96.5 | 70 | 21.0089 | 16.5692 | 64.1292 | 56.9047 | 56.9047 | 0 | 0
2025-02-20 04:00 | 16.4 | 95 | 70 | 21.1659 | 16.6621 | 63.7943 | 58.434 | 58.434 | 0 | 0
2025-02-20 05:00 | 16.3 | 94.5 | 70 | 21.1259 | 16.6026 | 63.6118 | 56.5139 | 56.5139 | 0 | 0
2025-02-20 06:00 | 15.85 | 95 | 100 | 20.9479 | 16.4494 | 63.6315 | 75.3516 | 75.3516 | 0 | 0
2025-02-20 07:00 | 16.25 | 91 | 100 | 21.103 | 16.436 | 62.5209 | 71.1027 | 71.1027 | 0 | 0
2025-02-20 08:00 | 18.15 | 80.5 | 100 | 21.8371 | 16.6814 | 59.6759 | 69.8214 | 69.8214 | 0 | 0
2025-02-20 09:00 | 20.65 | 66 | 100 | 22.778 | 16.8505 | 55.2707 | 59.5544 | 59.5544 | 0 | 0
2025-02-20 10:00 | 23.15 | 48.5 | 100 | 23.6933 | 16.6644 | 49.0707 | 28.8406 | 28.8406 | 0 | 0
2025-02-20 11:00 | 25.25 | 34.5 | 100 | 24.4475 | 16.3523 | 43.4205 | 0 | 0 | 0 | 0
2025-02-20 12:00 | 26.35 | 30 | 100 | 24.837 | 16.3194 | 41.4311 | 0 | 0 | 0 | 0
2025-02-20 13:00 | 26.55 | 31.5 | 100 | 24.9061 | 16.4836 | 42.0945 | 0 | 0 | 0 | 0
2025-02-20 14:00 | 26.4 | 31.5 | 100 | 24.8537 | 16.4432 | 42.1035 | 0 | 0 | 0 | 0
2025-02-20 15:00 | 25.7 | 30 | 100 | 24.6083 | 16.1461 | 41.49 | 0 | 0 | 0 | 0
2025-02-20 16:00 | 25.15 | 34.5 | 100 | 24.412 | 16.3211 | 43.4501 | 0 | 0 | 0 | 0
2025-02-20 17:00 | 24.65 | 39.5 | 100 | 24.2331 | 16.5256 | 45.5508 | 9.8512 | 9.8512 | 0 | 0
2025-02-20 18:00 | 23.7 | 47 | 100 | 23.8921 | 16.7366 | 48.5539 | 29.4207 | 29.4207 | 0 | 0
2025-02-20 19:00 | 23 | 55 | 100 | 23.6399 | 17.0131 | 51.6191 | 51.1878 | 51.1878 | 0 | 0
2025-02-20 20:00 | 22.15 | 56 | 100 | 23.3298 | 16.7952 | 51.8649 | 44.6405 | 44.6405 | 0 | 0
2025-02-20 21:00 | 21.3 | 56.5 | 100 | 23.0159 | 16.5469 | 51.9384 | 36.4426 | 36.4426 | 0 | 0
2025-02-20 22:00 | 20.95 | 57.5 | 70 | 22.8859 | 16.4884 | 52.2621 | 24.9944 | 24.9944 | 0 | 0
2025-02-20 23:00 | 20.8 | 56 | 70 | 22.8291 | 16.3563 | 51.7044 | 20.3735 | 20.3735 | 0 | 0
2025-02-21 | 20.75 | 54 | 70 | 22.8093 | 16.2296 | 50.9808 | 15.4478 | 15.4478 | 0 | 0
2025-02-21 01:00 | 20.35 | 58 | 70 | 22.6611 | 16.319 | 52.3851 | 21.3464 | 21.3464 | 0 | 0
2025-02-21 02:00 | 19.5 | 66 | 70 | 22.3442 | 16.4537 | 55.0813 | 31.6762 | 31.6762 | 0 | 0
2025-02-21 03:00 | 18.55 | 72.5 | 70 | 21.9853 | 16.4456 | 57.1296 | 36.7642 | 36.7642 | 0 | 0
2025-02-21 04:00 | 19.65 | 74 | 70 | 22.4063 | 16.9123 | 57.8743 | 50.0492 | 50.0492 | 0 | 0
2025-02-21 05:00 | 20.95 | 73.5 | 70 | 22.8937 | 17.3568 | 58.054 | 61.5353 | 61.5353 | 0 | 0
2025-02-21 06:00 | 20.2 | 72 | 100 | 22.6126 | 17.0078 | 57.3033 | 72.6886 | 72.6886 | 0 | 0
2025-02-21 07:00 | 20.45 | 64.5 | 100 | 22.7023 | 16.7019 | 54.6954 | 52.2168 | 52.2168 | 0 | 0
2025-02-21 08:00 | 22.5 | 54.5 | 100 | 23.4577 | 16.8232 | 51.3175 | 43.2091 | 43.2091 | 0 | 0
2025-02-21 09:00 | 25.5 | 45.5 | 100 | 24.5326 | 17.1954 | 48.0978 | 42.6693 | 42.6693 | 0 | 0
2025-02-21 10:00 | 28.05 | 36 | 100 | 25.4189 | 17.2495 | 44.1579 | 27.3439 | 27.3439 | 0 | 0
2025-02-21 11:00 | 29.65 | 28 | 100 | 25.9673 | 17.0221 | 40.4056 | 2.586 | 2.586 | 0 | 0
2025-02-21 12:00 | 30.7 | 23 | 100 | 26.3243 | 16.8374 | 37.8807 | 0 | 0 | 0 | 0
2025-02-21 13:00 | 30.95 | 21 | 100 | 26.4107 | 16.709 | 36.8427 | 0 | 0 | 0 | 0
2025-02-21 14:00 | 30.4 | 21.5 | 100 | 26.2278 | 16.624 | 37.1439 | 0 | 0 | 0 | 0
2025-02-21 15:00 | 29.4 | 24.5 | 100 | 25.8889 | 16.6508 | 38.7074 | 0 | 0 | 0 | 0
2025-02-21 16:00 | 27.95 | 32 | 100 | 25.3888 | 16.901 | 42.3111 | 7.6682 | 7.6682 | 0 | 0
2025-02-21 17:00 | 26.05 | 44.5 | 100 | 24.7252 | 17.2922 | 47.7645 | 44.7385 | 44.7385 | 0 | 0
2025-02-21 18:00 | 24.25 | 59.5 | 100 | 24.0889 | 17.7104 | 53.6669 | 83.5971 | 83.5971 | 0 | 0
2025-02-21 19:00 | 23.15 | 68.5 | 100 | 23.6964 | 17.8727 | 56.8892 | 101.9997 | 101.9997 | 0 | 0
2025-02-21 20:00 | 22.35 | 72.5 | 100 | 23.4079 | 17.8133 | 58.133 | 104.5346 | 104.5346 | 0 | 0
2025-02-21 21:00 | 21.55 | 77 | 100 | 23.117 | 17.7663 | 59.5096 | 107.9457 | 107.9457 | 0 | 0
2025-02-21 22:00 | 20.9 | 80 | 70 | 22.8783 | 17.6823 | 60.3507 | 75.574 | 75.574 | 0 | 0
2025-02-21 23:00 | 20.2 | 82 | 70 | 22.6183 | 17.5205 | 60.7975 | 72.596 | 72.596 | 0 | 0
2025-02-22 | 19.4 | 84.5 | 70 | 22.3184 | 17.3415 | 61.3723 | 69.4911 | 69.4911 | 0 | 0
2025-02-22 01:00 | 18.6 | 87 | 70 | 22.0152 | 17.1554 | 61.9338 | 66.1965 | 66.1965 | 0 | 0
2025-02-22 02:00 | 17.95 | 88 | 70 | 21.7657 | 16.9535 | 62.0478 | 61.3999 | 61.3999 | 0 | 0
2025-02-22 03:00 | 17.35 | 88.5 | 70 | 21.533 | 16.7472 | 62.0261 | 56.204 | 56.204 | 0 | 0
2025-02-22 04:00 | 17.15 | 87.5 | 70 | 21.4541 | 16.6266 | 61.6539 | 52.3249 | 52.3249 | 0 | 0
2025-02-22 05:00 | 17.15 | 87 | 70 | 21.4537 | 16.6046 | 61.4931 | 51.3788 | 51.3788 | 0 | 0
2025-02-22 06:00 | 16.95 | 89 | 100 | 21.377 | 16.6169 | 62.0601 | 75.7489 | 75.7489 | 0 | 0
2025-02-22 07:00 | 17.6 | 88.5 | 100 | 21.6304 | 16.8423 | 62.0817 | 83.7778 | 83.7778 | 0 | 0
2025-02-22 08:00 | 19.7 | 81.5 | 100 | 22.4299 | 17.3079 | 60.4256 | 94.5227 | 94.5227 | 0 | 0
2025-02-22 09:00 | 22.2 | 72 | 100 | 23.3532 | 17.7322 | 57.8635 | 100.355 | 100.355 | 0 | 0
2025-02-22 10:00 | 24.35 | 58 | 100 | 24.1245 | 17.6526 | 53.0496 | 78.768 | 78.768 | 0 | 0
2025-02-22 11:00 | 26.25 | 43.5 | 100 | 24.7952 | 17.286 | 47.3237 | 42.3137 | 42.3137 | 0 | 0
2025-02-22 12:00 | 27.35 | 40.5 | 100 | 25.1763 | 17.3944 | 46.1433 | 40.9751 | 40.9751 | 0 | 0
2025-02-22 13:00 | 27.45 | 41.5 | 100 | 25.2097 | 17.4989 | 46.6191 | 46.6952 | 46.6952 | 0 | 0
2025-02-22 14:00 | 27.1 | 39.5 | 100 | 25.0914 | 17.2438 | 45.6733 | 33.9338 | 33.9338 | 0 | 0
2025-02-22 15:00 | 26.6 | 39.5 | 100 | 24.9188 | 17.0969 | 45.6273 | 28.8237 | 28.8237 | 0 | 0
2025-02-22 16:00 | 26 | 44 | 100 | 24.708 | 17.2421 | 47.5323 | 41.9726 | 41.9726 | 0 | 0
2025-02-22 17:00 | 25.1 | 50 | 100 | 24.3907 | 17.3751 | 49.9437 | 56.646 | 56.646 | 0 | 0
2025-02-22 18:00 | 23.6 | 58.5 | 100 | 23.8569 | 17.4281 | 53.0896 | 71.2556 | 71.2556 | 0 | 0
2025-02-22 19:00 | 22.2 | 66.5 | 100 | 23.3515 | 17.4198 | 55.8173 | 81.5573 | 81.5573 | 0 | 0
2025-02-22 20:00 | 21.45 | 68 | 100 | 23.0764 | 17.2395 | 56.1669 | 76.4662 | 76.4662 | 0 | 0
2025-02-22 21:00 | 20.85 | 65.5 | 100 | 22.8525 | 16.8938 | 55.1145 | 60.3425 | 60.3425 | 0 | 0
2025-02-22 22:00 | 20.3 | 64.5 | 70 | 22.6459 | 16.6512 | 54.6565 | 35.1645 | 35.1645 | 0 | 0
2025-02-22 23:00 | 19.7 | 67 | 70 | 22.4208 | 16.5754 | 55.4357 | 35.4002 | 35.4002 | 0 | 0
2025-02-23 | 19.05 | 69.5 | 70 | 22.175 | 16.4753 | 56.1889 | 34.9794 | 34.9794 | 0 | 0
2025-02-23 01:00 | 18.6 | 70 | 70 | 22.0027 | 16.3426 | 56.2905 | 32.0812 | 32.0812 | 0 | 0
2025-02-23 02:00 | 18.25 | 71.5 | 70 | 21.8689 | 16.2926 | 56.7391 | 32.0421 | 32.0421 | 0 | 0
2025-02-23 03:00 | 18 | 74 | 70 | 21.774 | 16.3226 | 57.5229 | 34.766 | 34.766 | 0 | 0
2025-02-23 04:00 | 18.15 | 77 | 70 | 21.8344 | 16.5172 | 58.5338 | 42.0258 | 42.0258 | 0 | 0
2025-02-23 05:00 | 18.45 | 77.5 | 70 | 21.9505 | 16.6498 | 58.7632 | 45.8281 | 45.8281 | 0 | 0
2025-02-23 06:00 | 18.45 | 76 | 100 | 21.9494 | 16.5783 | 58.2626 | 61.156 | 61.156 | 0 | 0
2025-02-23 07:00 | 19.5 | 72 | 100 | 22.3481 | 16.7586 | 57.1326 | 63.2763 | 63.2763 | 0 | 0
2025-02-23 08:00 | 22.5 | 59.5 | 100 | 23.459 | 17.1185 | 53.233 | 60.9563 | 60.9563 | 0 | 0
2025-02-23 09:00 | 26.55 | 46.5 | 100 | 24.8975 | 17.591 | 48.7069 | 58.8877 | 58.8877 | 0 | 0
2025-02-23 10:00 | 29.85 | 42.5 | 100 | 26.0105 | 18.3072 | 47.5837 | 79.1454 | 79.1454 | 0 | 0
2025-02-23 11:00 | 31.9 | 39 | 100 | 26.677 | 18.6278 | 46.3401 | 85.0108 | 85.0108 | 0 | 0
2025-02-23 12:00 | 33.55 | 32.5 | 100 | 27.212 | 18.4908 | 43.2086 | 65.6946 | 65.6946 | 0 | 0
2025-02-23 13:00 | 34.9 | 27 | 100 | 27.6472 | 18.2893 | 40.3029 | 44.7245 | 44.7245 | 0 | 0
2025-02-23 14:00 | 35.7 | 22 | 100 | 27.9123 | 17.9391 | 37.4172 | 18.4377 | 18.4377 | 0 | 0
2025-02-23 15:00 | 34.85 | 24.5 | 100 | 27.6421 | 18.0043 | 38.8418 | 27.9542 | 27.9542 | 0 | 0
2025-02-23 16:00 | 31.95 | 36.5 | 100 | 26.6991 | 18.4097 | 45.0631 | 71.8224 | 71.8224 | 0 | 0
2025-02-23 17:00 | 29.25 | 45 | 100 | 25.8097 | 18.3185 | 48.6831 | 84.8106 | 84.8106 | 0 | 0
2025-02-23 18:00 | 27.9 | 49 | 100 | 25.3554 | 18.1992 | 50.1904 | 86.9851 | 86.9851 | 0 | 0
2025-02-23 19:00 | 27.05 | 51.5 | 100 | 25.0656 | 18.1067 | 51.0776 | 87.3714 | 87.3714 | 0 | 0
2025-02-23 20:00 | 26.6 | 50.5 | 100 | 24.9124 | 17.8893 | 50.5093 | 77.2148 | 77.2148 | 0 | 0
2025-02-23 21:00 | 26.2 | 51.5 | 100 | 24.774 | 17.8296 | 50.8463 | 76.5114 | 76.5114 | 0 | 0
2025-02-23 22:00 | 25.4 | 57.5 | 70 | 24.4939 | 17.9706 | 53.196 | 63.8411 | 63.8411 | 0 | 0
2025-02-23 23:00 | 24.4 | 67 | 70 | 24.1415 | 18.2303 | 56.7831 | 80.4031 | 80.4031 | 0 | 0
2025-02-24 | 23.3 | 75.5 | 70 | 23.7512 | 18.3354 | 59.7051 | 90.9765 | 90.9765 | 0 | 0
2025-02-24 01:00 | 22.35 | 80.5 | 70 | 23.4103 | 18.2588 | 61.1911 | 92.8534 | 92.8534 | 0 | 0
2025-02-24 02:00 | 21.65 | 81 | 70 | 23.1553 | 18.0182 | 61.0668 | 86.2811 | 86.2811 | 0 | 0
2025-02-24 03:00 | 21.1 | 75.5 | 70 | 22.9503 | 17.5172 | 58.849 | 67.7504 | 67.7504 | 0 | 0
2025-02-24 04:00 | 21.45 | 59 | 70 | 23.0726 | 16.7353 | 52.8986 | 32.7276 | 32.7276 | 0 | 0
2025-02-24 05:00 | 21.9 | 48 | 70 | 23.235 | 16.2452 | 48.8286 | 9.8973 | 9.8973 | 0 | 0
2025-02-24 06:00 | 21.3 | 54.5 | 100 | 23.015 | 16.4333 | 51.2047 | 29.7752 | 29.7752 | 0 | 0
2025-02-24 07:00 | 21.15 | 60 | 100 | 22.9617 | 16.6929 | 53.1954 | 46.2611 | 46.2611 | 0 | 0
2025-02-24 08:00 | 22.6 | 61 | 100 | 23.4958 | 17.2394 | 53.8375 | 67.6223 | 67.6223 | 0 | 0
2025-02-24 09:00 | 24.75 | 60 | 100 | 24.2656 | 17.9135 | 54.0145 | 92.2231 | 92.2231 | 0 | 0
2025-02-24 10:00 | 26.6 | 56.5 | 100 | 24.9088 | 18.3127 | 53.1274 | 103.047 | 103.047 | 0 | 0
2025-02-24 11:00 | 27.85 | 54.5 | 100 | 25.3334 | 18.5938 | 52.6717 | 111.4144 | 111.4144 | 0 | 0
2025-02-24 12:00 | 27.25 | 61.5 | 100 | 25.1259 | 18.8872 | 55.6025 | 134.3635 | 134.3635 | 0 | 0
2025-02-24 13:00 | 25.7 | 70 | 100 | 24.5937 | 18.8957 | 58.5816 | 146.5684 | 146.5684 | 0 | 0
2025-02-24 14:00 | 25.45 | 70 | 100 | 24.5075 | 18.8032 | 58.465 | 142.6427 | 142.6427 | 0 | 0
2025-02-24 15:00 | 25.4 | 70 | 100 | 24.4902 | 18.7845 | 58.4439 | 141.8792 | 141.8792 | 0 | 0
2025-02-24 16:00 | 25.25 | 69.5 | 100 | 24.4384 | 18.6966 | 58.1688 | 137.5542 | 137.5542 | 0 | 0
2025-02-24 17:00 | 24.7 | 71.5 | 100 | 24.2464 | 18.6191 | 58.7396 | 136.8361 | 136.8361 | 0 | 0
2025-02-24 18:00 | 23.65 | 77 | 100 | 23.8761 | 18.5564 | 60.4435 | 140.9129 | 140.9129 | 0 | 0
2025-02-24 19:00 | 23.1 | 80.5 | 100 | 23.6804 | 18.5475 | 61.5327 | 144.6367 | 144.6367 | 0 | 0
2025-02-24 20:00 | 22.85 | 82 | 100 | 23.591 | 18.5354 | 61.9773 | 145.7971 | 145.7971 | 0 | 0
2025-02-24 21:00 | 22.9 | 79 | 100 | 23.6084 | 18.3862 | 60.8481 | 135.9382 | 135.9382 | 0 | 0
2025-02-24 22:00 | 22.95 | 74 | 70 | 23.6254 | 18.1196 | 58.9461 | 83.2179 | 83.2179 | 0 | 0
2025-02-24 23:00 | 22.6 | 73 | 70 | 23.4988 | 17.9327 | 58.426 | 77.0537 | 77.0537 | 0 | 0
2025-02-25 | 22.35 | 76 | 70 | 23.409 | 18.0093 | 59.467 | 81.7634 | 81.7634 | 0 | 0
2025-02-25 01:00 | 22.2 | 83.5 | 70 | 23.3568 | 18.3666 | 62.2185 | 98.1957 | 98.1957 | 0 | 0
2025-02-25 02:00 | 21.8 | 91.5 | 70 | 23.2141 | 18.6364 | 64.9763 | 112.3871 | 112.3871 | 0 | 0
2025-02-25 03:00 | 21.6 | 94 | 70 | 23.1422 | 18.6864 | 65.7783 | 115.7346 | 115.7346 | 0 | 0
2025-02-25 04:00 | 21.95 | 87 | 70 | 23.2671 | 18.4577 | 63.3969 | 103.6211 | 103.6211 | 0 | 0
2025-02-25 05:00 | 22.05 | 77 | 70 | 23.3001 | 17.9528 | 59.7156 | 80.931 | 80.931 | 0 | 0
2025-02-25 06:00 | 21.7 | 72 | 100 | 23.1701 | 17.549 | 57.7209 | 93.4 | 93.4 | 0 | 0
2025-02-25 07:00 | 21.85 | 67.5 | 100 | 23.2236 | 17.3536 | 56.0854 | 80.1527 | 80.1527 | 0 | 0
2025-02-25 08:00 | 22.3 | 62.5 | 100 | 23.3868 | 17.2267 | 54.309 | 68.7562 | 68.7562 | 0 | 0
2025-02-25 09:00 | 22.6 | 59.5 | 100 | 23.4955 | 17.1546 | 53.2239 | 61.9302 | 61.9302 | 0 | 0
2025-02-25 10:00 | 23.05 | 57.5 | 100 | 23.6585 | 17.1861 | 52.5402 | 60.3115 | 60.3115 | 0 | 0
2025-02-25 11:00 | 23.35 | 55.5 | 100 | 23.7666 | 17.1639 | 51.8159 | 56.652 | 56.652 | 0 | 0
2025-02-25 12:00 | 23.1 | 54.5 | 100 | 23.6761 | 17.0208 | 51.382 | 49.9988 | 49.9988 | 0 | 0
2025-02-25 13:00 | 22.95 | 52 | 100 | 23.6212 | 16.8194 | 50.3878 | 39.1625 | 39.1625 | 0 | 0
2025-02-25 14:00 | 23.3 | 45 | 100 | 23.7473 | 16.4945 | 47.6727 | 17.1708 | 17.1708 | 0 | 0
2025-02-25 15:00 | 23.2 | 40 | 100 | 23.7102 | 16.148 | 45.6941 | 0 | 0 | 0 | 0
2025-02-25 16:00 | 21.95 | 46 | 100 | 23.2529 | 16.1489 | 48.0162 | 7.1577 | 7.1577 | 0 | 0
2025-02-25 17:00 | 20.55 | 53.5 | 100 | 22.734 | 16.1433 | 50.7342 | 17.7933 | 17.7933 | 0 | 0
2025-02-25 18:00 | 19.75 | 55.5 | 100 | 22.4327 | 15.9964 | 51.4052 | 15.5031 | 15.5031 | 0 | 0
2025-02-25 19:00 | 19.1 | 58 | 100 | 22.1863 | 15.9168 | 52.2395 | 16.0379 | 16.0379 | 0 | 0
2025-02-25 20:00 | 18.55 | 61.5 | 100 | 21.9773 | 15.9129 | 53.3925 | 20.2204 | 20.2204 | 0 | 0
2025-02-25 21:00 | 18.15 | 65.5 | 100 | 21.8257 | 15.9737 | 54.6909 | 27.0799 | 27.0799 | 0 | 0
2025-02-25 22:00 | 17.8 | 69 | 70 | 21.6925 | 16.021 | 55.8026 | 22.9141 | 22.9141 | 0 | 0
2025-02-25 23:00 | 17.6 | 71 | 70 | 21.6162 | 16.0451 | 56.4297 | 25.0876 | 25.0876 | 0 | 0
2025-02-26 | 17.4 | 73 | 70 | 21.5398 | 16.0674 | 57.052 | 27.2043 | 27.2043 | 0 | 0
2025-02-26 01:00 | 17.15 | 74.5 | 70 | 21.4432 | 16.0474 | 57.5033 | 27.8865 | 27.8865 | 0 | 0
2025-02-26 02:00 | 16.9 | 75.5 | 70 | 21.3459 | 16.0033 | 57.7924 | 27.5919 | 27.5919 | 0 | 0
2025-02-26 03:00 | 16.65 | 76.5 | 70 | 21.2483 | 15.9587 | 58.0749 | 27.2433 | 27.2433 | 0 | 0
2025-02-26 04:00 | 16.75 | 75 | 70 | 21.2864 | 15.9283 | 57.6174 | 25.3698 | 25.3698 | 0 | 0
2025-02-26 05:00 | 16.75 | 74 | 70 | 21.2855 | 15.8837 | 57.3004 | 23.5162 | 23.5162 | 0 | 0
2025-02-26 06:00 | 16.45 | 75 | 100 | 21.168 | 15.8228 | 57.5727 | 32.4562 | 32.4562 | 0 | 0
2025-02-26 07:00 | 17.25 | 71.5 | 100 | 21.4799 | 15.9466 | 56.547 | 32.9097 | 32.9097 | 0 | 0
2025-02-26 08:00 | 18.9 | 62.5 | 100 | 22.1127 | 16.0795 | 53.7381 | 26.9803 | 26.9803 | 0 | 0
2025-02-26 09:00 | 20.1 | 55.5 | 100 | 22.5654 | 16.1111 | 51.394 | 19.0418 | 19.0418 | 0 | 0
2025-02-26 10:00 | 20.85 | 52 | 100 | 22.8459 | 16.1581 | 50.1768 | 15.8482 | 15.8482 | 0 | 0
2025-02-26 11:00 | 21.45 | 49 | 100 | 23.0686 | 16.1746 | 49.1024 | 12.1564 | 12.1564 | 0 | 0
2025-02-26 12:00 | 21.8 | 47.5 | 100 | 23.1979 | 16.1937 | 48.5614 | 10.6907 | 10.6907 | 0 | 0
2025-02-26 13:00 | 21.7 | 48.5 | 100 | 23.1612 | 16.2203 | 48.9418 | 13.1854 | 13.1854 | 0 | 0
2025-02-26 14:00 | 21.55 | 49.5 | 100 | 23.1059 | 16.2321 | 49.3136 | 15.0872 | 15.0872 | 0 | 0
2025-02-26 15:00 | 21.4 | 49.5 | 100 | 23.0502 | 16.1856 | 49.3113 | 13.5593 | 13.5593 | 0 | 0
2025-02-26 16:00 | 20.55 | 54 | 100 | 22.7343 | 16.1709 | 50.9152 | 19.418 | 19.418 | 0 | 0
2025-02-26 17:00 | 19.6 | 60 | 100 | 22.3785 | 16.1827 | 52.9642 | 27.6936 | 27.6936 | 0 | 0
2025-02-26 18:00 | 19.1 | 63 | 100 | 22.1897 | 16.1699 | 53.9487 | 30.9727 | 30.9727 | 0 | 0
2025-02-26 19:00 | 18.65 | 66 | 100 | 22.0191 | 16.167 | 54.913 | 34.4642 | 34.4642 | 0 | 0
2025-02-26 20:00 | 18.15 | 70 | 100 | 21.8291 | 16.1889 | 56.1763 | 39.8247 | 39.8247 | 0 | 0
2025-02-26 21:00 | 18.05 | 70.5 | 100 | 21.7908 | 16.1781 | 56.3246 | 39.9793 | 39.9793 | 0 | 0
2025-02-26 22:00 | 17.95 | 71 | 70 | 21.7524 | 16.1671 | 56.4749 | 28.1018 | 28.1018 | 0 | 0
2025-02-26 23:00 | 17.55 | 73.5 | 70 | 21.5988 | 16.1431 | 57.2334 | 29.4673 | 29.4673 | 0 | 0
2025-02-27 | 17.5 | 73 | 70 | 21.5788 | 16.1023 | 57.0696 | 28.0995 | 28.0995 | 0 | 0
2025-02-27 01:00 | 17.7 | 71 | 70 | 21.6552 | 16.0791 | 56.4528 | 26.0091 | 26.0091 | 0 | 0
2025-02-27 02:00 | 17.55 | 69 | 70 | 21.5951 | 15.9343 | 55.7952 | 20.9266 | 20.9266 | 0 | 0
2025-02-27 03:00 | 17.35 | 68.5 | 70 | 21.5165 | 15.8419 | 55.6224 | 18.3492 | 18.3492 | 0 | 0
2025-02-27 04:00 | 18 | 64 | 70 | 21.7663 | 15.85 | 54.2081 | 14.9141 | 14.9141 | 0 | 0
2025-02-27 05:00 | 18.55 | 60 | 70 | 21.9762 | 15.8377 | 52.9056 | 11.2046 | 11.2046 | 0 | 0
2025-02-27 06:00 | 18.7 | 58 | 100 | 22.0326 | 15.7874 | 52.2335 | 11.7713 | 11.7713 | 0 | 0
2025-02-27 07:00 | 19.6 | 54 | 100 | 22.3747 | 15.8703 | 50.8744 | 9.2589 | 9.2589 | 0 | 0
2025-02-27 08:00 | 20.85 | 52 | 100 | 22.8459 | 16.1566 | 50.1905 | 15.9707 | 15.9707 | 0 | 0
2025-02-27 09:00 | 21.5 | 52.5 | 100 | 23.0886 | 16.3907 | 50.4061 | 24.5568 | 24.5568 | 0 | 0
2025-02-27 10:00 | 21.7 | 54 | 100 | 23.1633 | 16.5405 | 50.9833 | 31.8817 | 31.8817 | 0 | 0
2025-02-27 11:00 | 21.85 | 56 | 100 | 23.2195 | 16.703 | 51.7542 | 40.4962 | 40.4962 | 0 | 0
2025-02-27 12:00 | 21.9 | 58 | 100 | 23.2386 | 16.8341 | 52.5172 | 48.0165 | 48.0165 | 0 | 0
2025-02-27 13:00 | 21.95 | 56.5 | 100 | 23.2565 | 16.7636 | 51.9686 | 43.5063 | 43.5063 | 0 | 0
2025-02-27 14:00 | 21.7 | 55 | 100 | 23.1637 | 16.5954 | 51.381 | 35.5209 | 35.5209 | 0 | 0
2025-02-27 15:00 | 21 | 57 | 100 | 22.9044 | 16.4807 | 52.0429 | 34.2504 | 34.2504 | 0 | 0
2025-02-27 16:00 | 20.3 | 61.5 | 100 | 22.6443 | 16.4931 | 53.5775 | 40.6114 | 40.6114 | 0 | 0
2025-02-27 17:00 | 19.65 | 65 | 100 | 22.4006 | 16.4567 | 54.7175 | 43.6904 | 43.6904 | 0 | 0
2025-02-27 18:00 | 19.15 | 67.5 | 100 | 22.2118 | 16.4116 | 55.5027 | 45.0928 | 45.0928 | 0 | 0
2025-02-27 19:00 | 18.95 | 67.5 | 100 | 22.1353 | 16.343 | 55.4692 | 42.5927 | 42.5927 | 0 | 0
2025-02-27 20:00 | 18.95 | 63.5 | 100 | 22.1326 | 16.1443 | 54.1083 | 30.7424 | 30.7424 | 0 | 0
2025-02-27 21:00 | 19.05 | 60.5 | 100 | 22.1688 | 16.0274 | 53.0923 | 22.9578 | 22.9578 | 0 | 0
2025-02-27 22:00 | 19.05 | 59.5 | 70 | 22.1681 | 15.9762 | 52.7535 | 13.9997 | 13.9997 | 0 | 0
2025-02-27 23:00 | 18.8 | 60 | 70 | 22.0725 | 15.9192 | 52.916 | 13.1305 | 13.1305 | 0 | 0
2025-02-28 | 18.25 | 64 | 70 | 21.8632 | 15.9335 | 54.2271 | 16.9274 | 16.9274 | 0 | 0
2025-02-28 01:00 | 17.6 | 70 | 70 | 21.6154 | 15.997 | 56.137 | 23.3463 | 23.3463 | 0 | 0
2025-02-28 02:00 | 17.2 | 74 | 70 | 21.4623 | 16.0412 | 57.3769 | 27.5377 | 27.5377 | 0 | 0
2025-02-28 03:00 | 17 | 72.5 | 70 | 21.3826 | 15.903 | 56.884 | 23.0512 | 23.0512 | 0 | 0
2025-02-28 04:00 | 17.05 | 70.5 | 70 | 21.4005 | 15.8293 | 56.2559 | 19.7502 | 19.7502 | 0 | 0
2025-02-28 05:00 | 17.25 | 71 | 70 | 21.4794 | 15.9216 | 56.4261 | 22.3209 | 22.3209 | 0 | 0
2025-02-28 06:00 | 17.35 | 70.5 | 100 | 21.5181 | 15.9337 | 56.2689 | 31.6784 | 31.6784 | 0 | 0
2025-02-28 07:00 | 18.2 | 65 | 100 | 21.8446 | 15.9654 | 54.5502 | 26.4154 | 26.4154 | 0 | 0
2025-02-28 08:00 | 19.8 | 57 | 100 | 22.4526 | 16.0914 | 51.9337 | 20.7014 | 20.7014 | 0 | 0
2025-02-28 09:00 | 21.05 | 52.5 | 100 | 22.921 | 16.247 | 50.39 | 19.8149 | 19.8149 | 0 | 0
2025-02-28 10:00 | 21.85 | 49.5 | 100 | 23.2171 | 16.3259 | 49.3207 | 18.1629 | 18.1629 | 0 | 0
2025-02-28 11:00 | 22.4 | 46 | 100 | 23.4188 | 16.2852 | 48.0182 | 11.598 | 11.598 | 0 | 0
2025-02-28 12:00 | 22.6 | 42.5 | 100 | 23.4913 | 16.1304 | 46.68 | 1.0962 | 1.0962 | 0 | 0
2025-02-28 13:00 | 22.55 | 41 | 100 | 23.4726 | 16.0221 | 46.1108 | 0 | 0 | 0 | 0
2025-02-28 14:00 | 22.35 | 41.5 | 100 | 23.3991 | 15.9938 | 46.318 | 0 | 0 | 0 | 0
2025-02-28 15:00 | 21.9 | 43.5 | 100 | 23.2335 | 15.9824 | 47.0971 | 0 | 0 | 0 | 0
2025-02-28 16:00 | 21.4 | 47 | 100 | 23.0491 | 16.0387 | 48.4113 | 5.3515 | 5.3515 | 0 | 0
2025-02-28 17:00 | 20.7 | 51 | 100 | 22.7891 | 16.0506 | 49.8635 | 11.4967 | 11.4967 | 0 | 0
2025-02-28 18:00 | 19.75 | 55.5 | 100 | 22.4326 | 15.994 | 51.4312 | 15.7307 | 15.7307 | 0 | 0
2025-02-28 19:00 | 19.05 | 58.5 | 100 | 22.1674 | 15.9243 | 52.4358 | 17.2234 | 17.2234 | 0 | 0
2025-02-28 20:00 | 18.55 | 59 | 100 | 21.9754 | 15.7869 | 52.5853 | 13.2331 | 13.2331 | 0 | 0
2025-02-28 21:00 | 18.15 | 59.5 | 100 | 21.821 | 15.6819 | 52.7416 | 10.3385 | 10.3385 | 0 | 0
2025-02-28 22:00 | 17.85 | 61.5 | 70 | 21.706 | 15.6799 | 53.3928 | 8.9001 | 8.9001 | 0 | 0
2025-02-28 23:00 | 17.55 | 64.5 | 70 | 21.5914 | 15.7231 | 54.3605 | 12.4007 | 12.4007 | 0 | 0
2025-03-01 | 17.2 | 68.5 | 70 | 21.4577 | 15.7897 | 55.6301 | 17.2307 | 17.2307 | 0 | 0
2025-03-01 01:00 | 16.8 | 72.5 | 70 | 21.3039 | 15.8329 | 56.867 | 21.373 | 21.373 | 0 | 0
2025-03-01 02:00 | 16.2 | 77.5 | 70 | 21.071 | 15.8413 | 58.3594 | 25.2782 | 25.2782 | 0 | 0
2025-03-01 03:00 | 15.6 | 83.5 | 70 | 20.8376 | 15.8791 | 60.1025 | 30.4174 | 30.4174 | 0 | 0
2025-03-01 04:00 | 15.3 | 85.5 | 70 | 20.7194 | 15.8514 | 60.6529 | 31.0744 | 31.0744 | 0 | 0
2025-03-01 05:00 | 15.05 | 86 | 70 | 20.6195 | 15.7803 | 60.7595 | 29.6028 | 29.6028 | 0 | 0
2025-03-01 06:00 | 14.85 | 87.5 | 100 | 20.5403 | 15.7665 | 61.1634 | 43.1678 | 43.1678 | 0 | 0
2025-03-01 07:00 | 15.9 | 83 | 100 | 20.9568 | 15.9684 | 59.9777 | 45.9622 | 45.9622 | 0 | 0
2025-03-01 08:00 | 18.1 | 73 | 100 | 21.812 | 16.3128 | 57.173 | 47.8059 | 47.8059 | 0 | 0
2025-03-01 09:00 | 20.15 | 63 | 100 | 22.5886 | 16.5228 | 54.0846 | 43.5141 | 43.5141 | 0 | 0
2025-03-01 10:00 | 21.75 | 55 | 100 | 23.1821 | 16.6114 | 51.3896 | 36.1174 | 36.1174 | 0 | 0
2025-03-01 11:00 | 22.7 | 50.5 | 100 | 23.5298 | 16.6486 | 49.7845 | 31.0032 | 31.0032 | 0 | 0
2025-03-01 12:00 | 22.95 | 48 | 100 | 23.6205 | 16.573 | 48.8427 | 24.7138 | 24.7138 | 0 | 0
2025-03-01 13:00 | 22.8 | 47 | 100 | 23.5655 | 16.464 | 48.4537 | 19.5917 | 19.5917 | 0 | 0
2025-03-01 14:00 | 22.6 | 47 | 100 | 23.4924 | 16.4026 | 48.4511 | 17.5908 | 17.5908 | 0 | 0
2025-03-01 15:00 | 22.3 | 47.5 | 100 | 23.3824 | 16.34 | 48.6341 | 16.3196 | 16.3196 | 0 | 0
2025-03-01 16:00 | 21.7 | 50 | 100 | 23.1617 | 16.3031 | 49.55 | 18.7574 | 18.7574 | 0 | 0
2025-03-01 17:00 | 20.85 | 55 | 100 | 22.8473 | 16.3187 | 51.3336 | 26.2825 | 26.2825 | 0 | 0
2025-03-01 18:00 | 20.05 | 62.5 | 100 | 22.5505 | 16.46 | 53.9274 | 41.0377 | 41.0377 | 0 | 0
2025-03-01 19:00 | 19.4 | 70 | 100 | 22.3088 | 16.6225 | 56.4253 | 55.9452 | 55.9452 | 0 | 0
2025-03-01 20:00 | 18.85 | 74.5 | 100 | 22.1019 | 16.6506 | 57.8353 | 62.037 | 62.037 | 0 | 0
2025-03-01 21:00 | 18.35 | 77.5 | 100 | 21.912 | 16.6145 | 58.7201 | 63.9425 | 63.9425 | 0 | 0
2025-03-01 22:00 | 17.9 | 80 | 70 | 21.74 | 16.5672 | 59.4373 | 45.4032 | 45.4032 | 0 | 0
2025-03-01 23:00 | 17.3 | 82.5 | 70 | 21.5085 | 16.4606 | 60.1069 | 44.4563 | 44.4563 | 0 | 0
2025-03-02 | 16.5 | 85.5 | 70 | 21.1969 | 16.2953 | 60.8757 | 42.3335 | 42.3335 | 0 | 0
2025-03-02 01:00 | 15.85 | 88.5 | 70 | 20.9419 | 16.1793 | 61.6577 | 41.4126 | 41.4126 | 0 | 0
2025-03-02 02:00 | 15.5 | 90.5 | 70 | 20.8042 | 16.1301 | 62.1876 | 41.4913 | 41.4913 | 0 | 0
2025-03-02 03:00 | 15.3 | 91 | 70 | 20.7246 | 16.0757 | 62.298 | 40.4246 | 40.4246 | 0 | 0
2025-03-02 04:00 | 15.6 | 89.5 | 70 | 20.8432 | 16.1273 | 61.9128 | 40.7673 | 40.7673 | 0 | 0
2025-03-02 05:00 | 16 | 88.5 | 70 | 21.0016 | 16.2356 | 61.6917 | 42.8704 | 42.8704 | 0 | 0
2025-03-02 06:00 | 15.85 | 89.5 | 100 | 20.9429 | 16.2213 | 61.9526 | 61.581 | 61.581 | 0 | 0
2025-03-02 07:00 | 16.55 | 85.5 | 100 | 21.2166 | 16.3141 | 60.8747 | 61.063 | 61.063 | 0 | 0
2025-03-02 08:00 | 18.9 | 75 | 100 | 22.1214 | 16.6935 | 58.0001 | 64.0379 | 64.0379 | 0 | 0
2025-03-02 09:00 | 21.25 | 60.5 | 100 | 22.9991 | 16.7569 | 53.3596 | 48.8137 | 48.8137 | 0 | 0
2025-03-02 10:00 | 22.6 | 45.5 | 100 | 23.492 | 16.314 | 47.8425 | 11.9252 | 11.9252 | 0 | 0
2025-03-02 11:00 | 23.25 | 39.5 | 100 | 23.7283 | 16.1304 | 45.4991 | 0 | 0 | 0 | 0
2025-03-02 12:00 | 23.55 | 37.5 | 100 | 23.8372 | 16.0855 | 44.6983 | 0 | 0 | 0 | 0
2025-03-02 13:00 | 23.6 | 37 | 100 | 23.8553 | 16.0662 | 44.5024 | 0 | 0 | 0 | 0
2025-03-02 14:00 | 23.4 | 40 | 100 | 23.783 | 16.2026 | 45.7139 | 0 | 0 | 0 | 0
2025-03-02 15:00 | 23 | 43 | 100 | 23.6378 | 16.2757 | 46.9036 | 7.0341 | 7.0341 | 0 | 0
2025-03-02 16:00 | 22.25 | 47.5 | 100 | 23.364 | 16.3262 | 48.624 | 15.7304 | 15.7304 | 0 | 0
2025-03-02 17:00 | 21.3 | 55.5 | 100 | 23.0155 | 16.492 | 51.5501 | 32.9145 | 32.9145 | 0 | 0
2025-03-02 18:00 | 20.5 | 60.5 | 100 | 22.7189 | 16.5051 | 53.2682 | 39.9863 | 39.9863 | 0 | 0
2025-03-02 19:00 | 20.1 | 56 | 100 | 22.5656 | 16.1326 | 51.6286 | 21.1273 | 21.1273 | 0 | 0
2025-03-02 20:00 | 19.65 | 55.5 | 100 | 22.3946 | 15.9625 | 51.4288 | 14.6693 | 14.6693 | 0 | 0
2025-03-02 21:00 | 19.1 | 60.5 | 100 | 22.1879 | 16.0419 | 53.1199 | 23.7304 | 23.7304 | 0 | 0
2025-03-02 22:00 | 18.9 | 60 | 70 | 22.1109 | 15.9508 | 52.9362 | 13.9977 | 13.9977 | 0 | 0
2025-03-02 23:00 | 18.85 | 55.5 | 70 | 22.0885 | 15.7075 | 51.4106 | 4.3302 | 4.3302 | 0 | 0
2025-03-03 | 18.6 | 56 | 70 | 21.9925 | 15.653 | 51.5815 | 3.5457 | 3.5457 | 0 | 0
2025-03-03 01:00 | 18.25 | 58 | 70 | 21.8587 | 15.64 | 52.2527 | 5.0339 | 5.0339 | 0 | 0
2025-03-03 02:00 | 17.9 | 56 | 70 | 21.7211 | 15.4302 | 51.6008 | 0 | 0 | 0 | 0
2025-03-03 03:00 | 17.5 | 56 | 70 | 21.5649 | 15.3041 | 51.6182 | 0 | 0 | 0 | 0
2025-03-03 04:00 | 17.1 | 58 | 70 | 21.4096 | 15.2711 | 52.2791 | 0 | 0 | 0 | 0
2025-03-03 05:00 | 16.6 | 60 | 70 | 21.2141 | 15.2033 | 52.9306 | 0 | 0 | 0 | 0
2025-03-03 06:00 | 16.15 | 62.5 | 100 | 21.0378 | 15.1698 | 53.7188 | 0 | 0 | 0 | 0
2025-03-03 07:00 | 17 | 61.5 | 100 | 21.3733 | 15.4034 | 53.3694 | 3.4047 | 3.4047 | 0 | 0
2025-03-03 08:00 | 19 | 54.5 | 100 | 22.1455 | 15.7071 | 51.0382 | 4.4998 | 4.4998 | 0 | 0
2025-03-03 09:00 | 20.5 | 48.5 | 100 | 22.7126 | 15.8543 | 48.9179 | 0.984 | 0.984 | 0 | 0
2025-03-03 10:00 | 21.4 | 45 | 100 | 23.0483 | 15.9282 | 47.6212 | 0 | 0 | 0 | 0
2025-03-03 11:00 | 22.2 | 41.5 | 100 | 23.3438 | 15.9554 | 46.2828 | 0 | 0 | 0 | 0
2025-03-03 12:00 | 22.85 | 39 | 100 | 23.5822 | 15.9866 | 45.2964 | 0 | 0 | 0 | 0
2025-03-03 13:00 | 23.15 | 38.5 | 100 | 23.6918 | 16.0397 | 45.0932 | 0 | 0 | 0 | 0
2025-03-03 14:00 | 23.15 | 39 | 100 | 23.6918 | 16.0704 | 45.2971 | 0 | 0 | 0 | 0
2025-03-03 15:00 | 22.9 | 39 | 100 | 23.6005 | 15.999 | 45.3136 | 0 | 0 | 0 | 0
2025-03-03 16:00 | 22.45 | 39 | 100 | 23.4353 | 15.8702 | 45.3385 | 0 | 0 | 0 | 0
2025-03-03 17:00 | 21.65 | 41 | 100 | 23.1398 | 15.7628 | 46.1484 | 0 | 0 | 0 | 0
2025-03-03 18:00 | 20.45 | 46 | 100 | 22.6923 | 15.6977 | 48.0531 | 0 | 0 | 0 | 0
2025-03-03 19:00 | 19.35 | 51.5 | 100 | 22.2776 | 15.659 | 50.0308 | 0 | 0 | 0 | 0
2025-03-03 20:00 | 18.45 | 56.5 | 100 | 21.935 | 15.6309 | 51.7404 | 4.8746 | 4.8746 | 0 | 0
2025-03-03 21:00 | 17.75 | 59.5 | 100 | 21.6655 | 15.5526 | 52.7316 | 6.0051 | 6.0051 | 0 | 0
2025-03-03 22:00 | 16.95 | 61 | 70 | 21.3532 | 15.3633 | 53.2231 | 1.147 | 1.147 | 0 | 0
2025-03-03 23:00 | 15.9 | 62.5 | 70 | 20.9382 | 15.0884 | 53.7336 | 0 | 0 | 0 | 0
2025-03-04 | 14.8 | 65 | 70 | 20.4986 | 14.8343 | 54.5659 | 0 | 0 | 0 | 0
2025-03-04 01:00 | 13.7 | 68.5 | 70 | 20.0543 | 14.6113 | 55.6834 | 0 | 0 | 0 | 0
2025-03-04 02:00 | 12.85 | 71.5 | 70 | 19.7073 | 14.4418 | 56.6152 | 0 | 0 | 0 | 0
2025-03-04 03:00 | 12.45 | 70 | 70 | 19.5399 | 14.2524 | 56.2646 | 0 | 0 | 0 | 0
2025-03-04 04:00 | 12.85 | 67 | 70 | 19.7028 | 14.2724 | 55.3869 | 0 | 0 | 0 | 0
2025-03-04 05:00 | 13.5 | 65.5 | 70 | 19.9692 | 14.4283 | 54.8671 | 0 | 0 | 0 | 0
2025-03-04 06:00 | 13.8 | 62.5 | 100 | 20.0893 | 14.4082 | 53.9655 | 0 | 0 | 0 | 0
2025-03-04 07:00 | 15.05 | 56.5 | 100 | 20.5916 | 14.5581 | 52.0151 | 0 | 0 | 0 | 0
2025-03-04 08:00 | 17.9 | 45.5 | 100 | 21.713 | 14.9184 | 48.1215 | 0 | 0 | 0 | 0
2025-03-04 09:00 | 21.6 | 32 | 100 | 23.1177 | 15.2132 | 42.751 | 0 | 0 | 0 | 0
2025-03-04 10:00 | 25.05 | 22.5 | 100 | 24.379 | 15.4509 | 38.2958 | 0 | 0 | 0 | 0
2025-03-04 11:00 | 27.3 | 17 | 100 | 25.1773 | 15.5409 | 35.3903 | 0 | 0 | 0 | 0
2025-03-04 12:00 | 28.85 | 14 | 100 | 25.716 | 15.6143 | 33.626 | 0 | 0 | 0 | 0
2025-03-04 13:00 | 29.9 | 14.5 | 100 | 26.0722 | 15.8756 | 33.6494 | 0 | 0 | 0 | 0
2025-03-04 14:00 | 30.2 | 16.5 | 100 | 26.1698 | 16.1233 | 34.6084 | 0 | 0 | 0 | 0
2025-03-04 15:00 | 29.85 | 19.5 | 100 | 26.0475 | 16.3185 | 36.1717 | 0 | 0 | 0 | 0
2025-03-04 16:00 | 28.55 | 22.5 | 100 | 25.6035 | 16.2769 | 37.7876 | 0 | 0 | 0 | 0
2025-03-04 17:00 | 27.15 | 25.5 | 100 | 25.1188 | 16.1816 | 39.3304 | 0 | 0 | 0 | 0
2025-03-04 18:00 | 25.8 | 32.5 | 100 | 24.6426 | 16.3611 | 42.5295 | 0 | 0 | 0 | 0
2025-03-04 19:00 | 24.1 | 45 | 100 | 24.0359 | 16.7346 | 47.7348 | 25.5481 | 25.5481 | 0 | 0
2025-03-04 20:00 | 22.85 | 55.5 | 100 | 23.5855 | 16.9981 | 51.7438 | 50.7935 | 50.7935 | 0 | 0
2025-03-04 21:00 | 22.15 | 62 | 100 | 23.3318 | 17.1464 | 54.0904 | 65.1289 | 65.1289 | 0 | 0
2025-03-04 22:00 | 21.65 | 67.5 | 70 | 23.15 | 17.2835 | 56.0225 | 54.1559 | 54.1559 | 0 | 0
2025-03-04 23:00 | 21.1 | 71.5 | 70 | 22.9484 | 17.3063 | 57.3355 | 58.1911 | 58.1911 | 0 | 0
2025-03-05 | 20.55 | 74.5 | 70 | 22.7451 | 17.2657 | 58.2539 | 59.5931 | 59.5931 | 0 | 0
2025-03-05 01:00 | 20.1 | 76.5 | 70 | 22.5776 | 17.2042 | 58.8279 | 59.5543 | 59.5543 | 0 | 0
2025-03-05 02:00 | 19.85 | 76.5 | 70 | 22.4834 | 17.1128 | 58.7565 | 57.0949 | 57.0949 | 0 | 0
2025-03-05 03:00 | 19.5 | 76.5 | 70 | 22.351 | 16.9848 | 58.6574 | 53.6621 | 53.6621 | 0 | 0
2025-03-05 04:00 | 19.7 | 65.5 | 70 | 22.4199 | 16.4987 | 54.9038 | 32.1157 | 32.1157 | 0 | 0
2025-03-05 05:00 | 20.35 | 49.5 | 70 | 22.6565 | 15.8602 | 49.3107 | 2.0989 | 2.0989 | 0 | 0
2025-03-05 06:00 | 20.4 | 42.5 | 100 | 22.6716 | 15.4882 | 46.7921 | 0 | 0 | 0 | 0
2025-03-05 07:00 | 21 | 37.5 | 100 | 22.8952 | 15.3749 | 44.9023 | 0 | 0 | 0 | 0
2025-03-05 08:00 | 22.65 | 33.5 | 100 | 23.5075 | 15.5849 | 43.1694 | 0 | 0 | 0 | 0
2025-03-05 09:00 | 24.75 | 30.5 | 100 | 24.2701 | 15.9444 | 41.7173 | 0 | 0 | 0 | 0
2025-03-05 10:00 | 26.85 | 28 | 100 | 25.0127 | 16.3069 | 40.4547 | 0 | 0 | 0 | 0
2025-03-05 11:00 | 28.85 | 25.5 | 100 | 25.7018 | 16.6101 | 39.1745 | 0 | 0 | 0 | 0
2025-03-05 12:00 | 30.35 | 23 | 100 | 26.2083 | 16.7586 | 37.8685 | 0 | 0 | 0 | 0
2025-03-05 13:00 | 30.3 | 27.5 | 100 | 26.1838 | 17.1506 | 40.1491 | 5.3212 | 5.3212 | 0 | 0
2025-03-05 14:00 | 28.35 | 40.5 | 100 | 25.5155 | 17.6927 | 46.2906 | 51.7996 | 51.7996 | 0 | 0
2025-03-05 15:00 | 27.15 | 45 | 100 | 25.1045 | 17.6697 | 48.1448 | 59.1224 | 59.1224 | 0 | 0
2025-03-05 16:00 | 27.45 | 40.5 | 100 | 25.2105 | 17.4244 | 46.158 | 42.0583 | 42.0583 | 0 | 0
2025-03-05 17:00 | 27.3 | 37 | 100 | 25.1619 | 17.1144 | 44.5484 | 24.4874 | 24.4874 | 0 | 0
2025-03-05 18:00 | 26.5 | 37 | 100 | 24.8855 | 16.8863 | 44.4946 | 16.6424 | 16.6424 | 0 | 0
2025-03-05 19:00 | 25.15 | 45.5 | 100 | 24.4094 | 17.0895 | 48.0397 | 38.6975 | 38.6975 | 0 | 0
2025-03-05 20:00 | 23.65 | 56 | 100 | 23.8747 | 17.2925 | 52.0852 | 62.3043 | 62.3043 | 0 | 0
2025-03-05 21:00 | 22.55 | 62 | 100 | 23.4779 | 17.2829 | 54.1809 | 70.2648 | 70.2648 | 0 | 0
2025-03-05 22:00 | 21.8 | 67.5 | 70 | 23.2052 | 17.3362 | 56.0673 | 55.604 | 55.604 | 0 | 0
2025-03-05 23:00 | 21.2 | 71 | 70 | 22.9852 | 17.3142 | 57.192 | 58.0726 | 58.0726 | 0 | 0
2025-03-06 | 20.8 | 71 | 70 | 22.8366 | 17.1713 | 57.0834 | 54.2392 | 54.2392 | 0 | 0
2025-03-06 01:00 | 20.3 | 71.5 | 70 | 22.6499 | 17.0184 | 57.1334 | 50.6129 | 50.6129 | 0 | 0
2025-03-06 02:00 | 19.75 | 73 | 70 | 22.4435 | 16.8989 | 57.525 | 48.6902 | 48.6902 | 0 | 0
2025-03-06 03:00 | 19.15 | 75 | 70 | 22.2169 | 16.7832 | 58.068 | 47.241 | 47.241 | 0 | 0
2025-03-06 04:00 | 19.2 | 70 | 70 | 22.2326 | 16.5531 | 56.3777 | 37.3051 | 37.3051 | 0 | 0
2025-03-06 05:00 | 19.65 | 60.5 | 70 | 22.3978 | 16.2231 | 53.168 | 21.0164 | 21.0164 | 0 | 0
2025-03-06 06:00 | 19.7 | 55 | 100 | 22.4133 | 15.9523 | 51.2526 | 13.632 | 13.632 | 0 | 0
2025-03-06 07:00 | 20.65 | 50 | 100 | 22.7698 | 15.9803 | 49.4903 | 7.6326 | 7.6326 | 0 | 0
2025-03-06 08:00 | 22.95 | 44 | 100 | 23.6197 | 16.3268 | 47.2642 | 9.9321 | 9.9321 | 0 | 0
2025-03-06 09:00 | 25.55 | 39 | 100 | 24.5522 | 16.7596 | 45.3077 | 15.8939 | 15.8939 | 0 | 0
2025-03-06 10:00 | 27.9 | 34.5 | 100 | 25.3693 | 17.0922 | 43.4293 | 18.59 | 18.59 | 0 | 0
2025-03-06 11:00 | 29.9 | 30 | 100 | 26.0472 | 17.2665 | 41.3814 | 14.911 | 14.911 | 0 | 0
2025-03-06 12:00 | 31.05 | 28 | 100 | 26.429 | 17.3907 | 40.433 | 14.577 | 14.577 | 0 | 0
2025-03-06 13:00 | 30.85 | 30 | 100 | 26.3597 | 17.5183 | 41.4569 | 23.7894 | 23.7894 | 0 | 0
2025-03-06 14:00 | 29.8 | 32 | 100 | 26.0109 | 17.4084 | 42.386 | 24.5673 | 24.5673 | 0 | 0
2025-03-06 15:00 | 28.65 | 34 | 100 | 25.624 | 17.258 | 43.2692 | 23.6299 | 23.6299 | 0 | 0
2025-03-06 16:00 | 28.2 | 36.5 | 100 | 25.4692 | 17.3317 | 44.4094 | 31.2605 | 31.2605 | 0 | 0
2025-03-06 17:00 | 27.65 | 38 | 100 | 25.2809 | 17.2904 | 45.0462 | 32.7071 | 32.7071 | 0 | 0
2025-03-06 18:00 | 26.4 | 40 | 100 | 24.8492 | 17.0763 | 45.8185 | 28.8533 | 28.8533 | 0 | 0
2025-03-06 19:00 | 25.55 | 40.5 | 100 | 24.5518 | 16.8637 | 45.9633 | 22.3072 | 22.3072 | 0 | 0
2025-03-06 20:00 | 25 | 39 | 100 | 24.3577 | 16.5992 | 45.2998 | 10.6943 | 10.6943 | 0 | 0
2025-03-06 21:00 | 24.45 | 37.5 | 100 | 24.1618 | 16.3398 | 44.6711 | 0 | 0 | 0 | 0
2025-03-06 22:00 | 23.85 | 37 | 70 | 23.9458 | 16.1375 | 44.4835 | 0 | 0 | 0 | 0
2025-03-06 23:00 | 23.2 | 35 | 70 | 23.7095 | 15.8254 | 43.7298 | 0 | 0 | 0 | 0
2025-03-07 | 23.2 | 26.5 | 70 | 23.7082 | 15.269 | 40.3598 | 0 | 0 | 0 | 0
2025-03-07 01:00 | 23.65 | 18.5 | 70 | 23.8722 | 14.834 | 37.0372 | 0 | 0 | 0 | 0
2025-03-07 02:00 | 23.85 | 18 | 70 | 23.9453 | 14.843 | 36.7781 | 0 | 0 | 0 | 0
2025-03-07 03:00 | 23.35 | 21.5 | 70 | 23.7626 | 14.969 | 38.338 | 0 | 0 | 0 | 0
2025-03-07 04:00 | 21.85 | 25.5 | 70 | 23.2085 | 14.8688 | 40.2908 | 0 | 0 | 0 | 0
2025-03-07 05:00 | 20.8 | 27.5 | 70 | 22.8149 | 14.73 | 41.3083 | 0 | 0 | 0 | 0
2025-03-07 06:00 | 20.65 | 29 | 100 | 22.759 | 14.7807 | 41.8917 | 0 | 0 | 0 | 0
2025-03-07 07:00 | 21.8 | 28.5 | 100 | 23.191 | 15.0446 | 41.4285 | 0 | 0 | 0 | 0
2025-03-07 08:00 | 24.95 | 24.5 | 100 | 24.3428 | 15.565 | 39.195 | 0 | 0 | 0 | 0
2025-03-07 09:00 | 28.5 | 20 | 100 | 25.5892 | 16.0548 | 36.593 | 0 | 0 | 0 | 0
2025-03-07 10:00 | 31 | 17.5 | 100 | 26.4342 | 16.393 | 35.002 | 0 | 0 | 0 | 0
2025-03-07 11:00 | 32.65 | 16.5 | 100 | 26.9759 | 16.6544 | 34.2756 | 0 | 0 | 0 | 0
2025-03-07 12:00 | 33.4 | 17 | 100 | 27.2151 | 16.8683 | 34.4883 | 0 | 0 | 0 | 0
2025-03-07 13:00 | 33.25 | 20 | 100 | 27.158 | 17.1467 | 36.1856 | 0 | 0 | 0 | 0
2025-03-07 14:00 | 33.25 | 22 | 100 | 27.1518 | 17.3519 | 37.3088 | 0 | 0 | 0 | 0
2025-03-07 15:00 | 33.35 | 22.5 | 100 | 27.1819 | 17.4264 | 37.5949 | 2.3232 | 2.3232 | 0 | 0
2025-03-07 16:00 | 32.9 | 25.5 | 100 | 27.0303 | 17.6181 | 39.2465 | 16.9178 | 16.9178 | 0 | 0
2025-03-07 17:00 | 31.5 | 30.5 | 100 | 26.5696 | 17.7311 | 41.8173 | 33.16 | 33.16 | 0 | 0
2025-03-07 18:00 | 29.45 | 34 | 100 | 25.8918 | 17.4753 | 43.3753 | 31.8149 | 31.8149 | 0 | 0
2025-03-07 19:00 | 27.95 | 37.5 | 100 | 25.3835 | 17.3334 | 44.8826 | 33.8045 | 33.8045 | 0 | 0
2025-03-07 20:00 | 27.45 | 35.5 | 100 | 25.2146 | 17.0356 | 43.9145 | 19.4697 | 19.4697 | 0 | 0
2025-03-07 21:00 | 26.85 | 30.5 | 100 | 25.0112 | 16.4871 | 41.6402 | 0 | 0 | 0 | 0
2025-03-07 22:00 | 25.75 | 31 | 70 | 24.6256 | 16.2327 | 41.916 | 0 | 0 | 0 | 0
2025-03-07 23:00 | 24.8 | 31.5 | 70 | 24.2878 | 16.0161 | 42.2013 | 0 | 0 | 0 | 0
2025-03-08 | 24.9 | 28.5 | 70 | 24.3241 | 15.8308 | 40.9326 | 0 | 0 | 0 | 0
2025-03-08 01:00 | 25.3 | 24 | 70 | 24.4681 | 15.6047 | 38.9647 | 0 | 0 | 0 | 0
2025-03-08 02:00 | 24.25 | 23 | 70 | 24.0907 | 15.2797 | 38.7553 | 0 | 0 | 0 | 0
2025-03-08 03:00 | 22.85 | 24.5 | 70 | 23.5792 | 15.0441 | 39.6845 | 0 | 0 | 0 | 0
2025-03-08 04:00 | 22.6 | 24 | 70 | 23.4867 | 14.9506 | 39.5525 | 0 | 0 | 0 | 0
2025-03-08 05:00 | 22.8 | 23.5 | 70 | 23.5605 | 14.9668 | 39.3043 | 0 | 0 | 0 | 0
2025-03-08 06:00 | 22.6 | 28 | 100 | 23.4877 | 15.2099 | 41.1067 | 0 | 0 | 0 | 0
2025-03-08 07:00 | 23.2 | 33.5 | 100 | 23.7092 | 15.723 | 43.1697 | 0 | 0 | 0 | 0
2025-03-08 08:00 | 25.15 | 33 | 100 | 24.4124 | 16.2173 | 42.8009 | 0 | 0 | 0 | 0
2025-03-08 09:00 | 27.4 | 28 | 100 | 25.2035 | 16.4375 | 40.4754 | 0 | 0 | 0 | 0
2025-03-08 10:00 | 29.7 | 21.5 | 100 | 25.9941 | 16.4579 | 37.2083 | 0 | 0 | 0 | 0
2025-03-08 11:00 | 32 | 15.5 | 100 | 26.7677 | 16.4034 | 33.8476 | 0 | 0 | 0 | 0
2025-03-08 12:00 | 34 | 11 | 100 | 27.4268 | 16.3272 | 31.0317 | 0 | 0 | 0 | 0
2025-03-08 13:00 | 35.4 | 9 | 100 | 27.8776 | 16.3538 | 29.5985 | 0 | 0 | 0 | 0
2025-03-08 14:00 | 36.15 | 9 | 100 | 28.1116 | 16.4874 | 29.4643 | 0 | 0 | 0 | 0
2025-03-08 15:00 | 36.2 | 9.5 | 100 | 28.1248 | 16.5569 | 29.7696 | 0 | 0 | 0 | 0
2025-03-08 16:00 | 35.75 | 11 | 100 | 27.9782 | 16.6553 | 30.7638 | 0 | 0 | 0 | 0
2025-03-08 17:00 | 34.2 | 15.5 | 100 | 27.4745 | 16.8627 | 33.6197 | 0 | 0 | 0 | 0
2025-03-08 18:00 | 31.3 | 20 | 100 | 26.5282 | 16.6826 | 36.3433 | 0 | 0 | 0 | 0
2025-03-08 19:00 | 28.75 | 22.5 | 100 | 25.6719 | 16.3117 | 37.8284 | 0 | 0 | 0 | 0
2025-03-08 20:00 | 27.1 | 23.5 | 100 | 25.103 | 15.9979 | 38.4873 | 0 | 0 | 0 | 0
2025-03-08 21:00 | 25.8 | 24 | 100 | 24.646 | 15.7225 | 38.8996 | 0 | 0 | 0 | 0
2025-03-08 22:00 | 24.45 | 28 | 70 | 24.1626 | 15.6759 | 40.8071 | 0 | 0 | 0 | 0
2025-03-08 23:00 | 23.7 | 30.5 | 70 | 23.8912 | 15.653 | 41.9381 | 0 | 0 | 0 | 0
2025-03-09 | 23.5 | 30 | 70 | 23.8183 | 15.5674 | 41.7677 | 0 | 0 | 0 | 0
2025-03-09 01:00 | 23.05 | 32 | 70 | 23.6541 | 15.5799 | 42.6303 | 0 | 0 | 0 | 0
2025-03-09 02:00 | 22.65 | 35.5 | 70 | 23.5079 | 15.6959 | 44.0528 | 0 | 0 | 0 | 0
2025-03-09 03:00 | 22.35 | 39 | 70 | 23.3983 | 15.8306 | 45.4325 | 0 | 0 | 0 | 0
2025-03-09 04:00 | 22.1 | 36.5 | 70 | 23.3051 | 15.6067 | 44.4936 | 0 | 0 | 0 | 0
2025-03-09 05:00 | 22 | 33 | 70 | 23.2669 | 15.3651 | 43.1669 | 0 | 0 | 0 | 0
2025-03-09 06:00 | 22.4 | 34 | 100 | 23.4154 | 15.5357 | 43.4867 | 0 | 0 | 0 | 0
2025-03-09 07:00 | 24.2 | 31 | 100 | 24.0723 | 15.8206 | 42.0667 | 0 | 0 | 0 | 0
2025-03-09 08:00 | 26.9 | 26.5 | 100 | 25.0312 | 16.1895 | 39.8478 | 0 | 0 | 0 | 0
2025-03-09 09:00 | 28.5 | 26 | 100 | 25.5826 | 16.5531 | 39.489 | 0 | 0 | 0 | 0
2025-03-09 10:00 | 29.75 | 25 | 100 | 26.0054 | 16.7811 | 38.9424 | 0 | 0 | 0 | 0
2025-03-09 11:00 | 31.35 | 21.5 | 100 | 26.5411 | 16.8472 | 37.0915 | 0 | 0 | 0 | 0
2025-03-09 12:00 | 32.4 | 19.5 | 100 | 26.8872 | 16.8952 | 35.9693 | 0 | 0 | 0 | 0
2025-03-09 13:00 | 31 | 28.5 | 100 | 26.4118 | 17.4137 | 40.7367 | 17.4068 | 17.4068 | 0 | 0
2025-03-09 14:00 | 28.8 | 39 | 100 | 25.6683 | 17.7005 | 45.7027 | 49.9708 | 49.9708 | 0 | 0
2025-03-09 15:00 | 28.2 | 41 | 100 | 25.4645 | 17.6804 | 46.5482 | 53.0299 | 53.0299 | 0 | 0
2025-03-09 16:00 | 27.95 | 39.5 | 100 | 25.3815 | 17.4889 | 45.8119 | 43.2283 | 43.2283 | 0 | 0
2025-03-09 17:00 | 27.2 | 40.5 | 100 | 25.125 | 17.3447 | 46.1657 | 39.8037 | 39.8037 | 0 | 0
2025-03-09 18:00 | 25.85 | 47 | 100 | 24.6545 | 17.4041 | 48.8241 | 53.1913 | 53.1913 | 0 | 0
2025-03-09 19:00 | 24.85 | 52 | 100 | 24.3022 | 17.4255 | 50.7453 | 61.8633 | 61.8633 | 0 | 0
2025-03-09 20:00 | 24.25 | 55.5 | 100 | 24.0891 | 17.4567 | 52.0467 | 68.1728 | 68.1728 | 0 | 0
2025-03-09 21:00 | 23.7 | 58.5 | 100 | 23.8928 | 17.4614 | 53.1188 | 72.5864 | 72.5864 | 0 | 0
2025-03-09 22:00 | 22.95 | 62 | 70 | 23.6231 | 17.4184 | 54.3068 | 53.0165 | 53.0165 | 0 | 0
2025-03-09 23:00 | 22.05 | 66.5 | 70 | 23.2966 | 17.366 | 55.7873 | 55.7425 | 55.7425 | 0 | 0
2025-03-10 | 21.4 | 70 | 70 | 23.0588 | 17.3306 | 56.9063 | 57.835 | 57.835 | 0 | 0
2025-03-10 01:00 | 20.95 | 72 | 70 | 22.8929 | 17.2767 | 57.5086 | 58.1 | 58.1 | 0 | 0
2025-03-10 02:00 | 20.5 | 74 | 70 | 22.7262 | 17.2197 | 58.0983 | 58.2236 | 58.2236 | 0 | 0
2025-03-10 03:00 | 20.05 | 76 | 70 | 22.5585 | 17.1591 | 58.6735 | 58.1955 | 58.1955 | 0 | 0
2025-03-10 04:00 | 20.45 | 69 | 70 | 22.7047 | 16.9392 | 56.3153 | 46.6842 | 46.6842 | 0 | 0
2025-03-10 05:00 | 21.3 | 60 | 70 | 23.0174 | 16.7424 | 53.2292 | 33.7156 | 33.7156 | 0 | 0
2025-03-10 06:00 | 21.35 | 59 | 100 | 23.0356 | 16.704 | 52.8624 | 45.3645 | 45.3645 | 0 | 0
2025-03-10 07:00 | 22.3 | 56 | 100 | 23.3849 | 16.8454 | 51.8737 | 46.2834 | 46.2834 | 0 | 0
2025-03-10 08:00 | 23.85 | 53 | 100 | 23.9463 | 17.1682 | 50.9465 | 53.5988 | 53.5988 | 0 | 0
2025-03-10 09:00 | 25.85 | 49 | 100 | 24.6537 | 17.5458 | 49.6597 | 61.3673 | 61.3673 | 0 | 0
2025-03-10 10:00 | 28.4 | 42 | 100 | 25.5307 | 17.8235 | 47.0188 | 59.6877 | 59.6877 | 0 | 0
2025-03-10 11:00 | 30.15 | 36.5 | 100 | 26.1187 | 17.892 | 44.6725 | 51.5684 | 51.5684 | 0 | 0
2025-03-10 12:00 | 31.4 | 32.5 | 100 | 26.5327 | 17.8916 | 42.8291 | 43.1083 | 43.1083 | 0 | 0
2025-03-10 13:00 | 31.85 | 31.5 | 100 | 26.6796 | 17.9228 | 42.372 | 42.086 | 42.086 | 0 | 0
2025-03-10 14:00 | 31.5 | 32.5 | 100 | 26.565 | 17.9175 | 42.8548 | 44.2499 | 44.2499 | 0 | 0
2025-03-10 15:00 | 30.45 | 35.5 | 100 | 26.2187 | 17.8883 | 44.2405 | 49.7259 | 49.7259 | 0 | 0
2025-03-10 16:00 | 30.05 | 36 | 100 | 26.0868 | 17.8164 | 44.4299 | 48.1403 | 48.1403 | 0 | 0
2025-03-10 17:00 | 29 | 41 | 100 | 25.7324 | 17.922 | 46.6864 | 61.9214 | 61.9214 | 0 | 0
2025-03-10 18:00 | 26.65 | 51.5 | 100 | 24.9289 | 17.9767 | 50.9569 | 82.1403 | 82.1403 | 0 | 0
2025-03-10 19:00 | 25.4 | 55.5 | 100 | 24.4945 | 17.8391 | 52.3357 | 82.8633 | 82.8633 | 0 | 0
2025-03-10 20:00 | 25 | 56 | 100 | 24.3543 | 17.739 | 52.4311 | 79.6369 | 79.6369 | 0 | 0
2025-03-10 21:00 | 24.65 | 56 | 100 | 24.2309 | 17.6224 | 52.3406 | 75.1309 | 75.1309 | 0 | 0
2025-03-10 22:00 | 24.25 | 55 | 70 | 24.0891 | 17.4249 | 51.8431 | 46.3627 | 46.3627 | 0 | 0
2025-03-10 23:00 | 24.05 | 52.5 | 70 | 24.0179 | 17.1999 | 50.7938 | 37.9341 | 37.9341 | 0 | 0
2025-03-11 | 23.75 | 49 | 70 | 23.9102 | 16.8817 | 49.3418 | 26.1674 | 26.1674 | 0 | 0
2025-03-11 01:00 | 23.25 | 46.5 | 70 | 23.7293 | 16.5687 | 48.3031 | 15.8323 | 15.8323 | 0 | 0
2025-03-11 02:00 | 23 | 46 | 70 | 23.6383 | 16.4609 | 48.0936 | 12.7349 | 12.7349 | 0 | 0
2025-03-11 03:00 | 22.5 | 48 | 70 | 23.456 | 16.4313 | 48.844 | 14.1775 | 14.1775 | 0 | 0
2025-03-11 04:00 | 22.9 | 50.5 | 70 | 23.6027 | 16.7078 | 49.8454 | 23.5134 | 23.5134 | 0 | 0
2025-03-11 05:00 | 23.35 | 53 | 70 | 23.7663 | 17.0049 | 50.8826 | 33.5192 | 33.5192 | 0 | 0
2025-03-11 06:00 | 22.9 | 55 | 100 | 23.6036 | 16.9815 | 51.5862 | 49.844 | 49.844 | 0 | 0
2025-03-11 07:00 | 23.75 | 52 | 100 | 23.9104 | 17.0731 | 50.5308 | 48.6418 | 48.6418 | 0 | 0
2025-03-11 08:00 | 25.35 | 46.5 | 100 | 24.4796 | 17.2176 | 48.5047 | 45.1673 | 45.1673 | 0 | 0
2025-03-11 09:00 | 26.35 | 45 | 100 | 24.8292 | 17.4224 | 48.0061 | 50.0146 | 50.0146 | 0 | 0
2025-03-11 10:00 | 27.4 | 42.5 | 100 | 25.1918 | 17.5601 | 47.0591 | 50.6419 | 50.6419 | 0 | 0
2025-03-11 11:00 | 28.45 | 37.5 | 100 | 25.5525 | 17.4837 | 44.9007 | 38.5434 | 38.5434 | 0 | 0
2025-03-11 12:00 | 29.25 | 34 | 100 | 25.8251 | 17.4247 | 43.3215 | 29.4822 | 29.4822 | 0 | 0
2025-03-11 13:00 | 30.1 | 30.5 | 100 | 26.1126 | 17.3575 | 41.6747 | 19.7027 | 19.7027 | 0 | 0
2025-03-11 14:00 | 31.2 | 27 | 100 | 26.4801 | 17.3302 | 39.9527 | 10.6999 | 10.6999 | 0 | 0
2025-03-11 15:00 | 32.3 | 23.5 | 100 | 26.8443 | 17.2719 | 38.1274 | 0 | 0 | 0 | 0
2025-03-11 16:00 | 32.3 | 25.5 | 100 | 26.839 | 17.4671 | 39.2108 | 11.6878 | 11.6878 | 0 | 0
2025-03-11 17:00 | 29.9 | 35.5 | 100 | 26.0383 | 17.7317 | 44.1558 | 43.9353 | 43.9353 | 0 | 0
2025-03-11 18:00 | 27.5 | 44.5 | 100 | 25.2242 | 17.7374 | 48.0163 | 61.2126 | 61.2126 | 0 | 0
2025-03-11 19:00 | 26.95 | 49 | 100 | 25.0333 | 17.8957 | 49.9169 | 74.829 | 74.829 | 0 | 0
2025-03-11 20:00 | 26.6 | 49.5 | 100 | 24.9129 | 17.8201 | 50.0495 | 72.6641 | 72.6641 | 0 | 0
2025-03-11 21:00 | 26.4 | 47 | 100 | 24.8454 | 17.5791 | 48.9048 | 59.3774 | 59.3774 | 0 | 0
2025-03-11 22:00 | 26 | 45.5 | 70 | 24.7074 | 17.348 | 48.1808 | 33.8405 | 33.8405 | 0 | 0
2025-03-11 23:00 | 25.25 | 47.5 | 70 | 24.4442 | 17.2533 | 48.9198 | 33.7527 | 33.7527 | 0 | 0
2025-03-12 | 24.4 | 53 | 70 | 24.1426 | 17.3458 | 51.0561 | 42.183 | 42.183 | 0 | 0
2025-03-12 01:00 | 23.8 | 56.5 | 70 | 23.9285 | 17.3706 | 52.3493 | 46.4558 | 46.4558 | 0 | 0
2025-03-12 02:00 | 23.4 | 58 | 70 | 23.785 | 17.3288 | 52.8618 | 46.9047 | 46.9047 | 0 | 0
2025-03-12 03:00 | 23 | 62 | 70 | 23.6412 | 17.4346 | 54.3341 | 53.5731 | 53.5731 | 0 | 0
2025-03-12 04:00 | 23.5 | 58.5 | 70 | 23.821 | 17.394 | 53.0766 | 49.0557 | 49.0557 | 0 | 0
2025-03-12 05:00 | 24.85 | 46.5 | 70 | 24.3031 | 17.062 | 48.4444 | 27.779 | 27.779 | 0 | 0
2025-03-12 06:00 | 25.5 | 41 | 100 | 24.534 | 16.8814 | 46.1903 | 24.0558 | 24.0558 | 0 | 0
2025-03-12 07:00 | 25.9 | 42 | 100 | 24.674 | 17.0709 | 46.6512 | 32.3579 | 32.3579 | 0 | 0
2025-03-12 08:00 | 27.1 | 41 | 100 | 25.0903 | 17.3568 | 46.3459 | 40.6646 | 40.6646 | 0 | 0
2025-03-12 09:00 | 28.15 | 43 | 100 | 25.4455 | 17.8259 | 47.4302 | 61.5032 | 61.5032 | 0 | 0
2025-03-12 10:00 | 28.45 | 46.5 | 100 | 25.5423 | 18.1899 | 49.1346 | 81.6862 | 81.6862 | 0 | 0
2025-03-12 11:00 | 29.2 | 41 | 100 | 25.7987 | 17.987 | 46.6978 | 63.8979 | 63.8979 | 0 | 0
2025-03-12 12:00 | 30.8 | 32.5 | 100 | 26.3384 | 17.7265 | 42.7451 | 37.0196 | 37.0196 | 0 | 0
2025-03-12 13:00 | 31.5 | 29.5 | 100 | 26.5718 | 17.6423 | 41.2737 | 27.3346 | 27.3346 | 0 | 0
2025-03-12 14:00 | 30.5 | 34 | 100 | 26.2378 | 17.7726 | 43.4847 | 42.214 | 42.214 | 0 | 0
2025-03-12 15:00 | 29.15 | 41.5 | 100 | 25.7815 | 18.0078 | 46.957 | 66.106 | 66.106 | 0 | 0
2025-03-12 16:00 | 28.8 | 41.5 | 100 | 25.6651 | 17.9014 | 46.8873 | 62.1109 | 62.1109 | 0 | 0
2025-03-12 17:00 | 27.9 | 44 | 100 | 25.3602 | 17.8216 | 47.8766 | 63.6457 | 63.6457 | 0 | 0
2025-03-12 18:00 | 25.55 | 59.5 | 100 | 24.5455 | 18.1551 | 54.0817 | 101.362 | 101.362 | 0 | 0
2025-03-12 19:00 | 23.85 | 72 | 100 | 23.9468 | 18.3349 | 58.5498 | 125.4203 | 125.4203 | 0 | 0
2025-03-12 20:00 | 23.15 | 76.5 | 100 | 23.6976 | 18.3379 | 60.0013 | 130.9889 | 130.9889 | 0 | 0
2025-03-12 21:00 | 22.7 | 78 | 100 | 23.5362 | 18.2535 | 60.3713 | 129.1932 | 129.1932 | 0 | 0
2025-03-12 22:00 | 22.25 | 78.5 | 70 | 23.3734 | 18.1113 | 60.3613 | 86.6986 | 86.6986 | 0 | 0
2025-03-12 23:00 | 21.75 | 80.5 | 70 | 23.1917 | 18.0308 | 60.8908 | 85.9821 | 85.9821 | 0 | 0
2025-03-13 | 21.25 | 83 | 70 | 23.0091 | 17.9722 | 61.5897 | 86.2716 | 86.2716 | 0 | 0
2025-03-13 01:00 | 20.95 | 84.5 | 70 | 22.899 | 17.9356 | 62.0027 | 86.3675 | 86.3675 | 0 | 0
2025-03-13 02:00 | 20.85 | 85 | 70 | 22.8622 | 17.9224 | 62.1398 | 86.3894 | 86.3894 | 0 | 0
2025-03-13 03:00 | 20.7 | 84.5 | 70 | 22.8063 | 17.8388 | 61.8988 | 83.6228 | 83.6228 | 0 | 0
2025-03-13 04:00 | 21.1 | 81.5 | 70 | 22.9531 | 17.8357 | 60.993 | 81.2649 | 81.2649 | 0 | 0
2025-03-13 05:00 | 21.6 | 78.5 | 70 | 23.136 | 17.8654 | 60.0997 | 79.7208 | 79.7208 | 0 | 0
2025-03-13 06:00 | 21.45 | 78 | 100 | 23.0806 | 17.7822 | 59.8528 | 109.8993 | 109.8993 | 0 | 0
2025-03-13 07:00 | 22.25 | 73.5 | 100 | 23.3719 | 17.8326 | 58.4788 | 106.5779 | 106.5779 | 0 | 0
2025-03-13 08:00 | 24 | 61.5 | 100 | 24 | 17.7502 | 54.3912 | 87.8053 | 87.8053 | 0 | 0
2025-03-13 09:00 | 25.4 | 50 | 100 | 24.4961 | 17.4717 | 49.9931 | 60.1281 | 60.1281 | 0 | 0
2025-03-13 10:00 | 26.5 | 43 | 100 | 24.8822 | 17.3235 | 47.1546 | 43.034 | 43.034 | 0 | 0
2025-03-13 11:00 | 27.3 | 37 | 100 | 25.1619 | 17.1128 | 44.5596 | 24.6015 | 24.6015 | 0 | 0
2025-03-13 12:00 | 27.35 | 35 | 100 | 25.1807 | 16.9727 | 43.6586 | 15.9876 | 15.9876 | 0 | 0
2025-03-13 13:00 | 26.8 | 39 | 100 | 24.9883 | 17.1168 | 45.4309 | 28.7285 | 28.7285 | 0 | 0
2025-03-13 14:00 | 26.25 | 44 | 100 | 24.795 | 17.3169 | 47.5818 | 44.8664 | 44.8664 | 0 | 0
2025-03-13 15:00 | 25.55 | 50 | 100 | 24.5487 | 17.5167 | 50.0518 | 62.2052 | 62.2052 | 0 | 0
2025-03-13 16:00 | 24.9 | 54.5 | 100 | 24.3194 | 17.6059 | 51.7997 | 72.5252 | 72.5252 | 0 | 0
2025-03-13 17:00 | 23.95 | 61.5 | 100 | 23.9822 | 17.731 | 54.4018 | 87.3735 | 87.3735 | 0 | 0
2025-03-13 18:00 | 22.7 | 71 | 100 | 23.5345 | 17.8546 | 57.7125 | 104.6143 | 104.6143 | 0 | 0
2025-03-13 19:00 | 22 | 75.5 | 100 | 23.2813 | 17.8507 | 59.1477 | 109.8464 | 109.8464 | 0 | 0
2025-03-13 20:00 | 21.5 | 78 | 100 | 23.099 | 17.8009 | 59.874 | 110.6739 | 110.6739 | 0 | 0
2025-03-13 21:00 | 20.9 | 81 | 100 | 22.8788 | 17.7337 | 60.725 | 111.3237 | 111.3237 | 0 | 0
2025-03-13 22:00 | 20.3 | 85 | 70 | 22.6575 | 17.7103 | 61.9036 | 80.3009 | 80.3009 | 0 | 0
2025-03-13 23:00 | 19.75 | 88.5 | 70 | 22.4532 | 17.6713 | 62.8924 | 81.7721 | 81.7721 | 0 | 0
2025-03-14 | 19.25 | 90.5 | 70 | 22.2655 | 17.5727 | 63.3663 | 80.4112 | 80.4112 | 0 | 0
2025-03-14 01:00 | 18.7 | 92 | 70 | 22.0571 | 17.428 | 63.6461 | 77.3913 | 77.3913 | 0 | 0
2025-03-14 02:00 | 18.1 | 93.5 | 70 | 21.8279 | 17.2609 | 63.9037 | 73.7686 | 73.7686 | 0 | 0
2025-03-14 03:00 | 17.45 | 95 | 70 | 21.5774 | 17.073 | 64.1412 | 69.5549 | 69.5549 | 0 | 0
2025-03-14 04:00 | 17 | 95 | 70 | 21.4018 | 16.8968 | 63.9805 | 64.7097 | 64.7097 | 0 | 0
2025-03-14 05:00 | 16.7 | 94.5 | 70 | 21.2836 | 16.7578 | 63.7221 | 60.6053 | 60.6053 | 0 | 0
2025-03-14 06:00 | 16.5 | 95 | 100 | 21.2053 | 16.7012 | 63.8065 | 84.8125 | 84.8125 | 0 | 0
2025-03-14 07:00 | 17.55 | 89.5 | 100 | 21.6118 | 16.8676 | 62.404 | 85.9038 | 85.9038 | 0 | 0
2025-03-14 08:00 | 20.05 | 77.5 | 100 | 22.5594 | 17.2365 | 59.1707 | 87.537 | 87.537 | 0 | 0
2025-03-14 09:00 | 22.6 | 66.5 | 100 | 23.4972 | 17.5612 | 55.9262 | 86.9647 | 86.9647 | 0 | 0
2025-03-14 10:00 | 24.6 | 58.5 | 100 | 24.2129 | 17.7672 | 53.3411 | 84.1854 | 84.1854 | 0 | 0
2025-03-14 11:00 | 26.2 | 52 | 100 | 24.7737 | 17.867 | 51.0343 | 78.352 | 78.352 | 0 | 0
2025-03-14 12:00 | 27.45 | 47.5 | 100 | 25.2047 | 17.9464 | 49.3573 | 74.1754 | 74.1754 | 0 | 0
2025-03-14 13:00 | 28.1 | 48 | 100 | 25.4236 | 18.1903 | 49.763 | 84.6406 | 84.6406 | 0 | 0
2025-03-14 14:00 | 27.9 | 51.5 | 100 | 25.353 | 18.3874 | 51.3255 | 98.4039 | 98.4039 | 0 | 0
2025-03-14 15:00 | 27.15 | 53.5 | 100 | 25.0982 | 18.2841 | 51.9967 | 97.5215 | 97.5215 | 0 | 0
2025-03-14 16:00 | 26.15 | 56.5 | 100 | 24.7543 | 18.1586 | 52.9966 | 97.0879 | 97.0879 | 0 | 0
2025-03-14 17:00 | 24.9 | 62 | 100 | 24.318 | 18.0926 | 54.9059 | 102.3773 | 102.3773 | 0 | 0
2025-03-14 18:00 | 23.6 | 69 | 100 | 23.8577 | 18.064 | 57.2634 | 110.5172 | 110.5172 | 0 | 0
2025-03-14 19:00 | 22.5 | 77.5 | 100 | 23.4638 | 18.1495 | 60.1012 | 124.3772 | 124.3772 | 0 | 0
2025-03-14 20:00 | 21.55 | 87 | 100 | 23.1211 | 18.3002 | 63.1879 | 141.2858 | 141.2858 | 0 | 0
2025-03-14 21:00 | 20.75 | 94 | 100 | 22.8298 | 18.3417 | 65.29 | 150.3531 | 150.3531 | 0 | 0
2025-03-14 22:00 | 19.95 | 97.5 | 70 | 22.5339 | 18.1893 | 66.084 | 103.1593 | 103.1593 | 0 | 0
2025-03-14 23:00 | 19.25 | 98.5 | 70 | 22.271 | 17.9522 | 66.0592 | 96.827 | 96.827 | 0 | 0
2025-03-15 | 18.75 | 98.5 | 70 | 22.081 | 17.7498 | 65.8159 | 90.9356 | 90.9356 | 0 | 0
2025-03-15 01:00 | 18.2 | 99 | 70 | 21.8707 | 17.5503 | 65.7291 | 85.5603 | 85.5603 | 0 | 0
2025-03-15 02:00 | 17.7 | 99.5 | 70 | 21.6782 | 17.3712 | 65.6741 | 80.8191 | 80.8191 | 0 | 0
2025-03-15 03:00 | 17.05 | 100 | 70 | 21.4256 | 17.1316 | 65.5646 | 74.4358 | 74.4358 | 0 | 0
2025-03-15 04:00 | 17.65 | 100 | 70 | 21.6592 | 17.3733 | 65.8086 | 81.1745 | 81.1745 | 0 | 0
2025-03-15 05:00 | 18.75 | 100 | 70 | 22.0821 | 17.8185 | 66.3111 | 93.9272 | 93.9272 | 0 | 0
2025-03-15 06:00 | 18.7 | 99.5 | 100 | 22.0626 | 17.7755 | 66.1153 | 131.8586 | 131.8586 | 0 | 0
2025-03-15 07:00 | 18.75 | 97 | 100 | 22.0799 | 17.6802 | 65.305 | 125.497 | 125.497 | 0 | 0
2025-03-15 08:00 | 20.1 | 86.5 | 100 | 22.5835 | 17.7089 | 62.3255 | 116.0489 | 116.0489 | 0 | 0
2025-03-15 09:00 | 23.15 | 66.5 | 100 | 23.6961 | 17.756 | 56.0945 | 94.5825 | 94.5825 | 0 | 0
2025-03-15 10:00 | 26.4 | 45.5 | 100 | 24.8462 | 17.4737 | 48.2315 | 52.7252 | 52.7252 | 0 | 0
2025-03-15 11:00 | 28.8 | 31 | 100 | 25.6781 | 17.0535 | 41.8392 | 10.2279 | 10.2279 | 0 | 0
2025-03-15 12:00 | 30.4 | 24 | 100 | 26.2232 | 16.8573 | 38.3953 | 0 | 0 | 0 | 0
2025-03-15 13:00 | 31 | 24 | 100 | 26.421 | 17.003 | 38.3867 | 0 | 0 | 0 | 0
2025-03-15 14:00 | 30.3 | 30 | 100 | 26.1795 | 17.3665 | 41.4397 | 18.9387 | 18.9387 | 0 | 0
2025-03-15 15:00 | 29.1 | 38.5 | 100 | 25.769 | 17.751 | 45.4941 | 50.5778 | 50.5778 | 0 | 0
2025-03-15 16:00 | 27.6 | 41.5 | 100 | 25.2608 | 17.5418 | 46.6615 | 48.5379 | 48.5379 | 0 | 0
2025-03-15 17:00 | 25.85 | 49 | 100 | 24.6537 | 17.5451 | 49.6704 | 61.4734 | 61.4734 | 0 | 0
2025-03-15 18:00 | 24.5 | 64 | 100 | 24.177 | 18.0801 | 55.5729 | 104.4305 | 104.4305 | 0 | 0
2025-03-15 19:00 | 23.75 | 69.5 | 100 | 23.9112 | 18.1491 | 57.5008 | 114.4195 | 114.4195 | 0 | 0
2025-03-15 20:00 | 23.25 | 69.5 | 100 | 23.7325 | 17.968 | 57.3062 | 107.0044 | 107.0044 | 0 | 0
2025-03-15 21:00 | 22.4 | 70 | 100 | 23.4254 | 17.6903 | 57.1979 | 96.4868 | 96.4868 | 0 | 0
2025-03-15 22:00 | 21.35 | 71 | 70 | 23.0408 | 17.3681 | 57.2406 | 59.5622 | 59.5622 | 0 | 0
2025-03-15 23:00 | 20.3 | 73 | 70 | 22.6507 | 17.0962 | 57.6669 | 53.9371 | 53.9371 | 0 | 0
2025-03-16 | 19.4 | 71 | 70 | 22.3095 | 16.6733 | 56.7635 | 41.2377 | 41.2377 | 0 | 0
2025-03-16 01:00 | 18.65 | 63 | 70 | 22.0168 | 16.0167 | 53.9517 | 18.2942 | 18.2942 | 0 | 0
2025-03-16 02:00 | 17.95 | 51 | 70 | 21.7366 | 15.2003 | 49.9744 | 0 | 0 | 0 | 0
2025-03-16 03:00 | 17.05 | 38.5 | 70 | 21.3735 | 14.3277 | 46.0757 | 0 | 0 | 0 | 0
2025-03-16 04:00 | 16.75 | 45 | 70 | 21.2604 | 14.5536 | 48.2134 | 0 | 0 | 0 | 0
2025-03-16 05:00 | 16.9 | 56 | 70 | 21.3291 | 15.1139 | 51.6672 | 0 | 0 | 0 | 0
2025-03-16 06:00 | 16.9 | 52 | 100 | 21.3258 | 14.9285 | 50.3933 | 0 | 0 | 0 | 0
2025-03-16 07:00 | 18.5 | 45 | 100 | 21.9459 | 15.067 | 47.8903 | 0 | 0 | 0 | 0
2025-03-16 08:00 | 22.1 | 37.5 | 100 | 23.3056 | 15.6804 | 44.7867 | 0 | 0 | 0 | 0
2025-03-16 09:00 | 26.05 | 28.5 | 100 | 24.7323 | 16.1359 | 40.7546 | 0 | 0 | 0 | 0
2025-03-16 10:00 | 29.2 | 20 | 100 | 25.8275 | 16.2188 | 36.4848 | 0 | 0 | 0 | 0
2025-03-16 11:00 | 31.75 | 14 | 100 | 26.6891 | 16.2113 | 33.0434 | 0 | 0 | 0 | 0
2025-03-16 12:00 | 33.5 | 9 | 100 | 27.2726 | 16.0229 | 29.9538 | 0 | 0 | 0 | 0
2025-03-16 13:00 | 33.6 | 8 | 100 | 27.3082 | 15.9276 | 29.3693 | 0 | 0 | 0 | 0
2025-03-16 14:00 | 32.2 | 16.5 | 100 | 26.8302 | 16.5524 | 34.3411 | 0 | 0 | 0 | 0
2025-03-16 15:00 | 30.85 | 28.5 | 100 | 26.3628 | 17.3769 | 40.7114 | 15.8774 | 15.8774 | 0 | 0
2025-03-16 16:00 | 28.75 | 38.5 | 100 | 25.6521 | 17.648 | 45.4399 | 46.8115 | 46.8115 | 0 | 0
2025-03-16 17:00 | 26.25 | 47.5 | 100 | 24.7933 | 17.5664 | 49.1035 | 59.8657 | 59.8657 | 0 | 0
2025-03-16 18:00 | 25 | 54.5 | 100 | 24.3546 | 17.6402 | 51.8108 | 73.6594 | 73.6594 | 0 | 0
2025-03-16 19:00 | 24.05 | 60 | 100 | 24.0178 | 17.6734 | 53.8112 | 82.8436 | 82.8436 | 0 | 0
2025-03-16 20:00 | 23.35 | 65 | 100 | 23.7678 | 17.7365 | 55.586 | 92.0235 | 92.0235 | 0 | 0
2025-03-16 21:00 | 22.8 | 69.5 | 100 | 23.5704 | 17.8057 | 57.149 | 100.5121 | 100.5121 | 0 | 0
2025-03-16 22:00 | 22.35 | 71.5 | 70 | 23.4077 | 17.7571 | 57.7549 | 70.7388 | 70.7388 | 0 | 0
2025-03-16 23:00 | 22.05 | 74.5 | 70 | 23.2993 | 17.8148 | 58.7736 | 74.8963 | 74.8963 | 0 | 0
2025-03-17 | 21.45 | 80 | 70 | 23.0815 | 17.8897 | 60.5729 | 81.4931 | 81.4931 | 0 | 0
2025-03-17 01:00 | 21.15 | 81 | 70 | 22.9713 | 17.829 | 60.8163 | 80.5623 | 80.5623 | 0 | 0
2025-03-17 02:00 | 21.1 | 78 | 70 | 22.9514 | 17.6516 | 59.7136 | 73.2 | 73.2 | 0 | 0
2025-03-17 03:00 | 20.6 | 77.5 | 70 | 22.7654 | 17.4392 | 59.3626 | 66.9326 | 66.9326 | 0 | 0
2025-03-17 04:00 | 20.95 | 84.5 | 70 | 22.899 | 17.9352 | 62.0008 | 86.3551 | 86.3551 | 0 | 0
2025-03-17 05:00 | 21.6 | 90 | 70 | 23.1406 | 18.4776 | 64.307 | 106.4162 | 106.4162 | 0 | 0
2025-03-17 06:00 | 21.6 | 87 | 100 | 23.1394 | 18.3197 | 63.2053 | 142.0472 | 142.0472 | 0 | 0
2025-03-17 07:00 | 22.15 | 81 | 100 | 23.3378 | 18.2104 | 61.244 | 130.7652 | 130.7652 | 0 | 0
2025-03-17 08:00 | 24 | 65.5 | 100 | 24 | 17.9975 | 55.9886 | 102.9207 | 102.9207 | 0 | 0
2025-03-17 09:00 | 26.1 | 46 | 100 | 24.7419 | 17.4167 | 48.397 | 51.4394 | 51.4394 | 0 | 0
2025-03-17 10:00 | 27.3 | 35 | 100 | 25.1635 | 16.9622 | 43.6364 | 15.3125 | 15.3125 | 0 | 0
2025-03-17 11:00 | 27.05 | 36.5 | 100 | 25.0763 | 17.006 | 44.3021 | 19.7378 | 19.7378 | 0 | 0
2025-03-17 12:00 | 25.8 | 47 | 100 | 24.637 | 17.3928 | 48.7796 | 52.2589 | 52.2589 | 0 | 0
2025-03-17 13:00 | 25.65 | 48.5 | 100 | 24.5841 | 17.4483 | 49.404 | 56.8828 | 56.8828 | 0 | 0
2025-03-17 14:00 | 26.4 | 42 | 100 | 24.8481 | 17.22 | 46.711 | 37.6919 | 37.6919 | 0 | 0
2025-03-17 15:00 | 26.85 | 37.5 | 100 | 25.0066 | 17.02 | 44.763 | 22.5245 | 22.5245 | 0 | 0
2025-03-17 16:00 | 27.15 | 34.5 | 100 | 25.1122 | 16.8774 | 43.4287 | 11.8813 | 11.8813 | 0 | 0
2025-03-17 17:00 | 26.45 | 38 | 100 | 24.8676 | 16.9423 | 44.9558 | 20.7655 | 20.7655 | 0 | 0
2025-03-17 18:00 | 24.55 | 50.5 | 100 | 24.1962 | 17.2324 | 50.0552 | 52.1988 | 52.1988 | 0 | 0
2025-03-17 19:00 | 22.85 | 66 | 100 | 23.5877 | 17.6191 | 55.8226 | 88.7548 | 88.7548 | 0 | 0
2025-03-17 20:00 | 21.9 | 76.5 | 100 | 23.2451 | 17.8697 | 59.4656 | 111.595 | 111.595 | 0 | 0
2025-03-17 21:00 | 21.3 | 82.5 | 100 | 23.0273 | 17.966 | 61.4213 | 122.3185 | 122.3185 | 0 | 0
2025-03-17 22:00 | 20.7 | 86.5 | 70 | 22.8073 | 17.9411 | 62.594 | 87.9687 | 87.9687 | 0 | 0
2025-03-17 23:00 | 19.85 | 90 | 70 | 22.4918 | 17.7843 | 63.4425 | 86.0119 | 86.0119 | 0 | 0
2025-03-18 | 18.85 | 94 | 70 | 22.1159 | 17.5807 | 64.3614 | 83.0123 | 83.0123 | 0 | 0
2025-03-18 01:00 | 18.1 | 97 | 70 | 21.8307 | 17.4199 | 65.0271 | 80.4828 | 80.4828 | 0 | 0
2025-03-18 02:00 | 17.7 | 98.5 | 70 | 21.6773 | 17.3271 | 65.3463 | 78.8739 | 78.8739 | 0 | 0
2025-03-18 03:00 | 17.5 | 99.5 | 70 | 21.6006 | 17.2909 | 65.5856 | 78.5296 | 78.5296 | 0 | 0
2025-03-18 04:00 | 17.7 | 100 | 70 | 21.6786 | 17.3934 | 65.8286 | 81.7353 | 81.7353 | 0 | 0
2025-03-18 05:00 | 17.7 | 100 | 70 | 21.6786 | 17.3935 | 65.8239 | 81.7073 | 81.7073 | 0 | 0
2025-03-18 06:00 | 17.25 | 100 | 100 | 21.5037 | 17.212 | 65.6291 | 109.3991 | 109.3991 | 0 | 0
2025-03-18 07:00 | 17.7 | 99 | 100 | 21.6777 | 17.3488 | 65.4916 | 113.9067 | 113.9067 | 0 | 0
2025-03-18 08:00 | 18.9 | 96.5 | 100 | 22.1367 | 17.7176 | 65.2023 | 126.4864 | 126.4864 | 0 | 0
2025-03-18 09:00 | 21.5 | 81.5 | 100 | 23.1005 | 17.9892 | 61.1346 | 122.0925 | 122.0925 | 0 | 0
2025-03-18 10:00 | 25.05 | 54.5 | 100 | 24.3722 | 17.6581 | 51.8068 | 74.1329 | 74.1329 | 0 | 0
2025-03-18 11:00 | 27.4 | 35 | 100 | 25.1978 | 16.9876 | 43.6564 | 16.4139 | 16.4139 | 0 | 0
2025-03-18 12:00 | 28.2 | 29.5 | 100 | 25.4765 | 16.7683 | 41.1321 | 0 | 0 | 0 | 0
2025-03-18 13:00 | 27.9 | 31.5 | 100 | 25.3722 | 16.8483 | 42.0713 | 4.7896 | 4.7896 | 0 | 0
2025-03-18 14:00 | 27.4 | 32.5 | 100 | 25.1999 | 16.7918 | 42.5286 | 5.0396 | 5.0396 | 0 | 0
2025-03-18 15:00 | 26.9 | 32 | 100 | 25.0275 | 16.6171 | 42.3023 | 0 | 0 | 0 | 0
2025-03-18 16:00 | 26.25 | 34.5 | 100 | 24.7997 | 16.6279 | 43.4148 | 3.6628 | 3.6628 | 0 | 0
2025-03-18 17:00 | 25 | 45.5 | 100 | 24.3564 | 17.0399 | 48.0529 | 37.368 | 37.368 | 0 | 0
2025-03-18 18:00 | 23.55 | 58.5 | 100 | 23.8389 | 17.4109 | 53.0888 | 70.7224 | 70.7224 | 0 | 0
2025-03-18 19:00 | 22.6 | 65.5 | 100 | 23.4969 | 17.5017 | 55.565 | 83.625 | 83.625 | 0 | 0
2025-03-18 20:00 | 21.85 | 70.5 | 100 | 23.2247 | 17.5195 | 57.2236 | 90.5565 | 90.5565 | 0 | 0
2025-03-18 21:00 | 21.1 | 75.5 | 100 | 22.9503 | 17.5188 | 58.8121 | 96.4488 | 96.4488 | 0 | 0
2025-03-18 22:00 | 20.25 | 79.5 | 70 | 22.6356 | 17.4117 | 59.9495 | 67.7405 | 67.7405 | 0 | 0
2025-03-18 23:00 | 19.45 | 83 | 70 | 22.3363 | 17.2863 | 60.8884 | 66.9438 | 66.9438 | 0 | 0
2025-03-19 | 18.75 | 85.5 | 70 | 22.0715 | 17.1418 | 61.4965 | 64.8133 | 64.8133 | 0 | 0
2025-03-19 01:00 | 18 | 86.5 | 70 | 21.7838 | 16.9038 | 61.588 | 59.0753 | 59.0753 | 0 | 0
2025-03-19 02:00 | 17.15 | 88 | 70 | 21.4545 | 16.648 | 61.8236 | 53.3235 | 53.3235 | 0 | 0
2025-03-19 03:00 | 16.3 | 90 | 70 | 21.1219 | 16.4128 | 62.2236 | 48.4755 | 48.4755 | 0 | 0
2025-03-19 04:00 | 16.3 | 86 | 70 | 21.1183 | 16.2425 | 60.9971 | 41.3715 | 41.3715 | 0 | 0
2025-03-19 05:00 | 16.45 | 80.5 | 70 | 21.1727 | 16.0605 | 59.3268 | 32.9155 | 32.9155 | 0 | 0
2025-03-19 06:00 | 16.25 | 78 | 100 | 21.0913 | 15.8803 | 58.5229 | 38.0398 | 38.0398 | 0 | 0
2025-03-19 07:00 | 17.7 | 68 | 100 | 21.6527 | 15.9373 | 55.5151 | 29.1746 | 29.1746 | 0 | 0
2025-03-19 08:00 | 21 | 52 | 100 | 22.902 | 16.2002 | 50.235 | 17.9004 | 17.9004 | 0 | 0
2025-03-19 09:00 | 24.35 | 38.5 | 100 | 24.1258 | 16.3787 | 45.0843 | 2.556 | 2.556 | 0 | 0
2025-03-19 10:00 | 26.85 | 29.5 | 100 | 25.0118 | 16.4168 | 41.1553 | 0 | 0 | 0 | 0
2025-03-19 11:00 | 28.55 | 24 | 100 | 25.6018 | 16.4042 | 38.5 | 0 | 0 | 0 | 0
2025-03-19 12:00 | 29.45 | 22.5 | 100 | 25.9085 | 16.4925 | 37.7032 | 0 | 0 | 0 | 0
2025-03-19 13:00 | 29.5 | 23 | 100 | 25.9246 | 16.5465 | 37.9514 | 0 | 0 | 0 | 0
2025-03-19 14:00 | 28.9 | 25 | 100 | 25.7195 | 16.5717 | 38.9714 | 0 | 0 | 0 | 0
2025-03-19 15:00 | 28.05 | 29.5 | 100 | 25.4254 | 16.7278 | 41.1417 | 0 | 0 | 0 | 0
2025-03-19 16:00 | 27.05 | 35 | 100 | 25.0774 | 16.8875 | 43.6535 | 13.2398 | 13.2398 | 0 | 0
2025-03-19 17:00 | 25.65 | 43.5 | 100 | 24.5859 | 17.1004 | 47.2789 | 36.1252 | 36.1252 | 0 | 0
2025-03-19 18:00 | 24.05 | 56 | 100 | 24.0178 | 17.4223 | 52.2013 | 67.5664 | 67.5664 | 0 | 0
2025-03-19 19:00 | 22.85 | 67.5 | 100 | 23.588 | 17.7066 | 56.4036 | 94.1523 | 94.1523 | 0 | 0
2025-03-19 20:00 | 22 | 74.5 | 100 | 23.281 | 17.7963 | 58.7588 | 106.2879 | 106.2879 | 0 | 0
2025-03-19 21:00 | 21.2 | 78 | 100 | 22.9884 | 17.6893 | 59.7449 | 106.0148 | 106.0148 | 0 | 0
2025-03-19 22:00 | 20.35 | 80 | 70 | 22.6734 | 17.4758 | 60.1488 | 69.7988 | 69.7988 | 0 | 0
2025-03-19 23:00 | 19.25 | 83 | 70 | 22.2604 | 17.2114 | 60.811 | 64.8106 | 64.8106 | 0 | 0
2025-03-20 | 18.2 | 85.5 | 70 | 21.8603 | 16.9329 | 61.3137 | 59.1091 | 59.1091 | 0 | 0
2025-03-20 01:00 | 17.3 | 86.5 | 70 | 21.5119 | 16.6385 | 61.3821 | 51.9828 | 51.9828 | 0 | 0
2025-03-20 02:00 | 16.35 | 87 | 70 | 21.139 | 16.3036 | 61.3086 | 43.5946 | 43.5946 | 0 | 0
2025-03-20 03:00 | 15.6 | 86.5 | 70 | 20.8404 | 16.0032 | 61.0082 | 35.5961 | 35.5961 | 0 | 0
2025-03-20 04:00 | 15.9 | 83 | 70 | 20.9568 | 15.9673 | 60.0026 | 32.3155 | 32.3155 | 0 | 0
2025-03-20 05:00 | 16.35 | 78.5 | 70 | 21.1314 | 15.938 | 58.6871 | 28.388 | 28.388 | 0 | 0
2025-03-20 06:00 | 16.25 | 74 | 100 | 21.0877 | 15.7072 | 57.2833 | 27.7806 | 27.7806 | 0 | 0
2025-03-20 07:00 | 17.7 | 64.5 | 100 | 21.6499 | 15.773 | 54.3697 | 19.4246 | 19.4246 | 0 | 0
2025-03-20 08:00 | 21.4 | 49.5 | 100 | 23.0501 | 16.1842 | 49.3223 | 13.6599 | 13.6599 | 0 | 0
2025-03-20 09:00 | 25.7 | 34 | 100 | 24.6068 | 16.445 | 43.168 | 0 | 0 | 0 | 0
2025-03-20 10:00 | 29.2 | 22.5 | 100 | 25.8241 | 16.4354 | 37.7096 | 0 | 0 | 0 | 0
2025-03-20 11:00 | 31.7 | 16 | 100 | 26.668 | 16.3996 | 34.1181 | 0 | 0 | 0 | 0
2025-03-20 12:00 | 33.1 | 14.5 | 100 | 27.1267 | 16.5406 | 33.1162 | 0 | 0 | 0 | 0
2025-03-20 13:00 | 33.3 | 17.5 | 100 | 27.1816 | 16.8988 | 34.7771 | 0 | 0 | 0 | 0
2025-03-20 14:00 | 32.6 | 21 | 100 | 26.9473 | 17.0979 | 36.7555 | 0 | 0 | 0 | 0
2025-03-20 15:00 | 31.55 | 23.5 | 100 | 26.6018 | 17.0896 | 38.1233 | 0 | 0 | 0 | 0
2025-03-20 16:00 | 30.25 | 29.5 | 100 | 26.1639 | 17.3085 | 41.186 | 15.8409 | 15.8409 | 0 | 0
2025-03-20 17:00 | 28.3 | 40.5 | 100 | 25.4987 | 17.674 | 46.3094 | 51.5311 | 51.5311 | 0 | 0
2025-03-20 18:00 | 26.35 | 50.5 | 100 | 24.8263 | 17.81 | 50.4317 | 73.9396 | 73.9396 | 0 | 0
2025-03-20 19:00 | 25.05 | 58.5 | 100 | 24.3713 | 17.9194 | 53.4847 | 90.3075 | 90.3075 | 0 | 0
2025-03-20 20:00 | 24.1 | 63.5 | 100 | 24.0355 | 17.9087 | 55.2266 | 96.7971 | 96.7971 | 0 | 0
2025-03-20 21:00 | 23.3 | 64 | 100 | 23.7497 | 17.6595 | 55.1702 | 87.5843 | 87.5843 | 0 | 0
2025-03-20 22:00 | 22.4 | 64.5 | 70 | 23.4239 | 17.3756 | 55.1071 | 54.0428 | 54.0428 | 0 | 0
2025-03-20 23:00 | 21.5 | 65.5 | 70 | 23.0939 | 17.1195 | 55.258 | 48.1297 | 48.1297 | 0 | 0
2025-03-21 | 20.7 | 64 | 70 | 22.7957 | 16.7614 | 54.5496 | 37.5407 | 37.5407 | 0 | 0
2025-03-21 01:00 | 19.95 | 59 | 70 | 22.5106 | 16.2429 | 52.6773 | 20.2099 | 20.2099 | 0 | 0
2025-03-21 02:00 | 19.15 | 54 | 70 | 22.2026 | 15.7244 | 50.9154 | 3.4798 | 3.4798 | 0 | 0
2025-03-21 03:00 | 18.45 | 52.5 | 70 | 21.932 | 15.429 | 50.4315 | 0 | 0 | 0 | 0
2025-03-21 04:00 | 18.1 | 53.5 | 70 | 21.797 | 15.3699 | 50.7843 | 0 | 0 | 0 | 0
2025-03-21 05:00 | 17.7 | 56.5 | 70 | 21.6435 | 15.3902 | 51.7857 | 0 | 0 | 0 | 0
2025-03-21 06:00 | 17.8 | 56 | 100 | 21.6821 | 15.3984 | 51.6132 | 0 | 0 | 0 | 0
2025-03-21 07:00 | 20.4 | 42.5 | 100 | 22.6715 | 15.4863 | 46.8088 | 0 | 0 | 0 | 0
2025-03-21 08:00 | 25.4 | 26 | 100 | 24.5031 | 15.7857 | 39.7548 | 0 | 0 | 0 | 0
2025-03-21 09:00 | 30 | 17.5 | 100 | 26.101 | 16.1736 | 35.1362 | 0 | 0 | 0 | 0
2025-03-21 10:00 | 33.05 | 15 | 100 | 27.109 | 16.586 | 33.3908 | 0 | 0 | 0 | 0
2025-03-21 11:00 | 35.1 | 13.5 | 100 | 27.764 | 16.8452 | 32.2854 | 0 | 0 | 0 | 0
2025-03-21 12:00 | 36.3 | 11.5 | 100 | 28.1449 | 16.8439 | 30.9315 | 0 | 0 | 0 | 0
2025-03-21 13:00 | 36.95 | 11 | 100 | 28.3466 | 16.905 | 30.5418 | 0 | 0 | 0 | 0
2025-03-21 14:00 | 37.45 | 11 | 100 | 28.4984 | 16.9989 | 30.4859 | 0 | 0 | 0 | 0
2025-03-21 15:00 | 36.65 | 14 | 100 | 28.2396 | 17.2165 | 32.4685 | 0 | 0 | 0 | 0
2025-03-21 16:00 | 33.55 | 25 | 100 | 27.2367 | 17.7375 | 38.9887 | 19.2827 | 19.2827 | 0 | 0
2025-03-21 17:00 | 30.6 | 35.5 | 100 | 26.2675 | 17.9347 | 44.243 | 51.081 | 51.081 | 0 | 0
2025-03-21 18:00 | 29.1 | 40.5 | 100 | 25.7662 | 17.9154 | 46.4419 | 60.3336 | 60.3336 | 0 | 0
2025-03-21 19:00 | 28.05 | 42 | 100 | 25.4128 | 17.7182 | 46.9505 | 55.6949 | 55.6949 | 0 | 0
2025-03-21 20:00 | 27.4 | 38.5 | 100 | 25.195 | 17.2569 | 45.2449 | 32.4099 | 32.4099 | 0 | 0
2025-03-21 21:00 | 26.95 | 34 | 100 | 25.0435 | 16.7874 | 43.1789 | 7.5847 | 7.5847 | 0 | 0
2025-03-21 22:00 | 26.45 | 30 | 70 | 24.872 | 16.3493 | 41.4029 | 0 | 0 | 0 | 0
2025-03-21 23:00 | 25.75 | 27 | 70 | 24.6271 | 15.9449 | 40.1527 | 0 | 0 | 0 | 0
2025-03-22 | 25.5 | 27 | 70 | 24.5384 | 15.8807 | 40.1892 | 0 | 0 | 0 | 0
2025-03-22 01:00 | 25.45 | 31.5 | 70 | 24.5193 | 16.1925 | 42.1316 | 0 | 0 | 0 | 0
2025-03-22 02:00 | 25.15 | 32.5 | 70 | 24.4125 | 16.1826 | 42.5815 | 0 | 0 | 0 | 0
2025-03-22 03:00 | 24.7 | 30 | 70 | 24.2522 | 15.8872 | 41.5697 | 0 | 0 | 0 | 0
2025-03-22 04:00 | 23.45 | 33.5 | 70 | 23.8005 | 15.7926 | 43.1308 | 0 | 0 | 0 | 0
2025-03-22 05:00 | 22.25 | 37.5 | 70 | 23.361 | 15.7174 | 44.8065 | 0 | 0 | 0 | 0
2025-03-22 06:00 | 22.5 | 35 | 100 | 23.4526 | 15.6323 | 43.8123 | 0 | 0 | 0 | 0
2025-03-22 07:00 | 24.6 | 28 | 100 | 24.2166 | 15.7241 | 40.7292 | 0 | 0 | 0 | 0
2025-03-22 08:00 | 27.6 | 21.5 | 100 | 25.278 | 15.9689 | 37.439 | 0 | 0 | 0 | 0
2025-03-22 09:00 | 30.4 | 16.5 | 100 | 26.2368 | 16.165 | 34.5814 | 0 | 0 | 0 | 0
2025-03-22 10:00 | 32.7 | 12.5 | 100 | 27.0033 | 16.2466 | 32.0743 | 0 | 0 | 0 | 0
2025-03-22 11:00 | 34.45 | 10.5 | 100 | 27.5714 | 16.3683 | 30.6248 | 0 | 0 | 0 | 0
2025-03-22 12:00 | 35.7 | 10 | 100 | 27.9664 | 16.543 | 30.1109 | 0 | 0 | 0 | 0
2025-03-22 13:00 | 36.1 | 10.5 | 100 | 28.0883 | 16.6775 | 30.3585 | 0 | 0 | 0 | 0
2025-03-22 14:00 | 35 | 15 | 100 | 27.727 | 16.9879 | 33.2143 | 0 | 0 | 0 | 0
2025-03-22 15:00 | 33.1 | 20 | 100 | 27.1103 | 17.1094 | 36.2009 | 0 | 0 | 0 | 0
2025-03-22 16:00 | 31.2 | 23.5 | 100 | 26.4876 | 17.0025 | 38.1364 | 0 | 0 | 0 | 0
2025-03-22 17:00 | 29.45 | 29.5 | 100 | 25.8983 | 17.0956 | 41.159 | 8.7613 | 8.7613 | 0 | 0
2025-03-22 18:00 | 27.9 | 35 | 100 | 25.3689 | 17.1248 | 43.7051 | 21.3974 | 21.3974 | 0 | 0
2025-03-22 19:00 | 26.8 | 36.5 | 100 | 24.9899 | 16.9299 | 44.3188 | 17.6336 | 17.6336 | 0 | 0
2025-03-22 20:00 | 26.3 | 34.5 | 100 | 24.8172 | 16.6416 | 43.4134 | 4.0981 | 4.0981 | 0 | 0
2025-03-22 21:00 | 25.9 | 32 | 100 | 24.6781 | 16.3493 | 42.3253 | 0 | 0 | 0 | 0
2025-03-22 22:00 | 25.4 | 30.5 | 70 | 24.5019 | 16.1073 | 41.7106 | 0 | 0 | 0 | 0
2025-03-22 23:00 | 24.9 | 30 | 70 | 24.3239 | 15.9393 | 41.5468 | 0 | 0 | 0 | 0
2025-03-23 | 24.4 | 29.5 | 70 | 24.1445 | 15.7736 | 41.3987 | 0 | 0 | 0 | 0
2025-03-23 01:00 | 24 | 28.5 | 70 | 24 | 15.601 | 41.0479 | 0 | 0 | 0 | 0
2025-03-23 02:00 | 23.65 | 27.5 | 70 | 23.8728 | 15.4438 | 40.7041 | 0 | 0 | 0 | 0
2025-03-23 03:00 | 23.05 | 27 | 70 | 23.6533 | 15.259 | 40.6186 | 0 | 0 | 0 | 0
2025-03-23 04:00 | 23 | 31 | 70 | 23.6356 | 15.5077 | 42.207 | 0 | 0 | 0 | 0
2025-03-23 05:00 | 23.5 | 34 | 70 | 23.8187 | 15.8379 | 43.3344 | 0 | 0 | 0 | 0
2025-03-23 06:00 | 23.9 | 32.5 | 100 | 23.9638 | 15.8474 | 42.6814 | 0 | 0 | 0 | 0
2025-03-23 07:00 | 24.9 | 28.5 | 100 | 24.3241 | 15.8357 | 40.9041 | 0 | 0 | 0 | 0
2025-03-23 08:00 | 26.05 | 28 | 100 | 24.7326 | 16.0958 | 40.554 | 0 | 0 | 0 | 0
2025-03-23 09:00 | 27.1 | 27.5 | 100 | 25.1 | 16.3263 | 40.2411 | 0 | 0 | 0 | 0
2025-03-23 10:00 | 29.4 | 22 | 100 | 25.8924 | 16.4373 | 37.4582 | 0 | 0 | 0 | 0
2025-03-23 11:00 | 31.65 | 19.5 | 100 | 26.6436 | 16.7293 | 35.9943 | 0 | 0 | 0 | 0
2025-03-23 12:00 | 32.75 | 18.5 | 100 | 27.0026 | 16.8784 | 35.3786 | 0 | 0 | 0 | 0
2025-03-23 13:00 | 33.65 | 17.5 | 100 | 27.2931 | 16.9736 | 34.7633 | 0 | 0 | 0 | 0
2025-03-23 14:00 | 32.85 | 21.5 | 100 | 27.026 | 17.2063 | 37.032 | 0 | 0 | 0 | 0
2025-03-23 15:00 | 31.05 | 26.5 | 100 | 26.4322 | 17.2456 | 39.6882 | 6.6395 | 6.6395 | 0 | 0
2025-03-23 16:00 | 29.8 | 31 | 100 | 26.0125 | 17.3192 | 41.9079 | 19.5727 | 19.5727 | 0 | 0
2025-03-23 17:00 | 27.85 | 45.5 | 100 | 25.3419 | 17.9219 | 48.5436 | 69.8929 | 69.8929 | 0 | 0
2025-03-23 18:00 | 26 | 62.5 | 100 | 24.6999 | 18.513 | 55.5147 | 120.0934 | 120.0934 | 0 | 0
2025-03-23 19:00 | 25.15 | 71 | 100 | 24.4033 | 18.7558 | 58.7244 | 141.7621 | 141.7621 | 0 | 0
2025-03-23 20:00 | 24.45 | 76 | 100 | 24.1583 | 18.8019 | 60.4216 | 149.9618 | 149.9618 | 0 | 0
2025-03-23 21:00 | 23.7 | 79.5 | 100 | 23.894 | 18.7222 | 61.4293 | 150.7256 | 150.7256 | 0 | 0
2025-03-23 22:00 | 23.05 | 82 | 70 | 23.6627 | 18.6135 | 62.0661 | 104.2929 | 104.2929 | 0 | 0
2025-03-23 23:00 | 22.45 | 85.5 | 70 | 23.4478 | 18.574 | 63.0854 | 105.8539 | 105.8539 | 0 | 0
2025-03-24 | 22 | 87.5 | 70 | 23.2854 | 18.5048 | 63.5956 | 105.3105 | 105.3105 | 0 | 0
2025-03-24 01:00 | 21.75 | 87.5 | 70 | 23.1944 | 18.405 | 63.4661 | 102.3617 | 102.3617 | 0 | 0
2025-03-24 02:00 | 21.45 | 88.5 | 70 | 23.0851 | 18.3392 | 63.6788 | 101.1564 | 101.1564 | 0 | 0
2025-03-24 03:00 | 21.1 | 91 | 70 | 22.9575 | 18.3296 | 64.4002 | 102.704 | 102.704 | 0 | 0
2025-03-24 04:00 | 21.25 | 91.5 | 70 | 23.013 | 18.4155 | 64.6584 | 105.6218 | 105.6218 | 0 | 0
2025-03-24 05:00 | 21.45 | 90.5 | 70 | 23.0859 | 18.444 | 64.4003 | 105.7167 | 105.7167 | 0 | 0
2025-03-24 06:00 | 21.7 | 88.5 | 100 | 23.1765 | 18.439 | 63.7953 | 148.6072 | 148.6072 | 0 | 0
2025-03-24 07:00 | 23.15 | 81.5 | 100 | 23.6984 | 18.6246 | 61.9087 | 148.7106 | 148.7106 | 0 | 0
2025-03-24 08:00 | 24.75 | 72 | 100 | 24.2638 | 18.6709 | 58.9172 | 139.0814 | 139.0814 | 0 | 0
2025-03-24 09:00 | 25.5 | 65.5 | 100 | 24.5262 | 18.5341 | 56.5511 | 124.7162 | 124.7162 | 0 | 0
2025-03-24 10:00 | 26.4 | 58 | 100 | 24.8395 | 18.3502 | 53.6881 | 106.4687 | 106.4687 | 0 | 0
2025-03-24 11:00 | 27.1 | 52 | 100 | 25.0823 | 18.1637 | 51.2695 | 89.7724 | 89.7724 | 0 | 0
2025-03-24 12:00 | 27.1 | 51 | 100 | 25.083 | 18.0915 | 50.8263 | 85.3648 | 85.3648 | 0 | 0
2025-03-24 13:00 | 26.85 | 49 | 100 | 24.999 | 17.8661 | 49.8757 | 73.4239 | 73.4239 | 0 | 0
2025-03-24 14:00 | 26.5 | 47 | 100 | 24.8799 | 17.6106 | 48.92 | 60.5064 | 60.5064 | 0 | 0
2025-03-24 15:00 | 25.9 | 47 | 100 | 24.6719 | 17.4227 | 48.8101 | 53.5418 | 53.5418 | 0 | 0
2025-03-24 16:00 | 25.1 | 48 | 100 | 24.3912 | 17.2407 | 49.1004 | 48.4854 | 48.4854 | 0 | 0
2025-03-24 17:00 | 24.15 | 51 | 100 | 24.0536 | 17.1385 | 50.1821 | 49.3804 | 49.3804 | 0 | 0
2025-03-24 18:00 | 23.05 | 58 | 100 | 23.6586 | 17.2143 | 52.7576 | 62.3452 | 62.3452 | 0 | 0
2025-03-24 19:00 | 22.2 | 65 | 100 | 23.351 | 17.335 | 55.2383 | 76.2312 | 76.2312 | 0 | 0
2025-03-24 20:00 | 21.65 | 67 | 100 | 23.1498 | 17.2555 | 55.8402 | 75.7052 | 75.7052 | 0 | 0
2025-03-24 21:00 | 21.05 | 68 | 100 | 22.9282 | 17.0995 | 56.0541 | 71.0103 | 71.0103 | 0 | 0
2025-03-24 22:00 | 20.35 | 70.5 | 70 | 22.6681 | 16.9851 | 56.7809 | 48.8076 | 48.8076 | 0 | 0
2025-03-24 23:00 | 19.8 | 73.5 | 70 | 22.4627 | 16.9427 | 57.7012 | 50.1749 | 50.1749 | 0 | 0
2025-03-25 | 19.5 | 75 | 70 | 22.3501 | 16.9097 | 58.1493 | 50.5413 | 50.5413 | 0 | 0
2025-03-25 01:00 | 19.3 | 75 | 70 | 22.2741 | 16.837 | 58.1058 | 48.6733 | 48.6733 | 0 | 0
2025-03-25 02:00 | 19.2 | 75.5 | 70 | 22.2363 | 16.8254 | 58.2567 | 48.795 | 48.795 | 0 | 0
2025-03-25 03:00 | 19.2 | 75.5 | 70 | 22.2363 | 16.8253 | 58.2592 | 48.8105 | 48.8105 | 0 | 0
2025-03-25 04:00 | 19.1 | 72.5 | 70 | 22.1961 | 16.6413 | 57.2174 | 41.65 | 41.65 | 0 | 0
2025-03-25 05:00 | 19.1 | 68 | 70 | 22.193 | 16.4183 | 55.6869 | 32.3036 | 32.3036 | 0 | 0
2025-03-25 06:00 | 19.5 | 64.5 | 100 | 22.3433 | 16.3785 | 54.5421 | 40.5108 | 40.5108 | 0 | 0
2025-03-25 07:00 | 20.65 | 59.5 | 100 | 22.7747 | 16.5012 | 52.9252 | 38.508 | 38.508 | 0 | 0
2025-03-25 08:00 | 22 | 54 | 100 | 23.274 | 16.6326 | 51.0566 | 35.6433 | 35.6433 | 0 | 0
2025-03-25 09:00 | 22.9 | 50 | 100 | 23.6026 | 16.6805 | 49.6175 | 31.459 | 31.459 | 0 | 0
2025-03-25 10:00 | 23.55 | 47.5 | 100 | 23.838 | 16.7269 | 48.6954 | 29.2757 | 29.2757 | 0 | 0
2025-03-25 11:00 | 24 | 46.5 | 100 | 24 | 16.8014 | 48.3378 | 30.3191 | 30.3191 | 0 | 0
2025-03-25 12:00 | 24.2 | 46 | 100 | 24.0717 | 16.8293 | 48.1592 | 30.577 | 30.577 | 0 | 0
2025-03-25 13:00 | 24.15 | 47 | 100 | 24.0538 | 16.8786 | 48.5691 | 34.0005 | 34.0005 | 0 | 0
2025-03-25 14:00 | 23.9 | 49 | 100 | 23.9641 | 16.9288 | 49.3568 | 39.0211 | 39.0211 | 0 | 0
2025-03-25 15:00 | 23.4 | 51 | 100 | 23.7842 | 16.8971 | 50.0949 | 40.9804 | 40.9804 | 0 | 0
2025-03-25 16:00 | 22.55 | 52.5 | 100 | 23.4755 | 16.7182 | 50.5745 | 36.8294 | 36.8294 | 0 | 0
2025-03-25 17:00 | 21.6 | 55 | 100 | 23.1266 | 16.5593 | 51.4112 | 34.762 | 34.762 | 0 | 0
2025-03-25 18:00 | 20.85 | 59.5 | 100 | 22.8495 | 16.5658 | 52.9698 | 41.0327 | 41.0327 | 0 | 0
2025-03-25 19:00 | 20.3 | 62.5 | 100 | 22.6448 | 16.5438 | 53.9668 | 44.0844 | 44.0844 | 0 | 0
2025-03-25 20:00 | 20 | 63.5 | 100 | 22.5322 | 16.4957 | 54.2743 | 43.5768 | 43.5768 | 0 | 0
2025-03-25 21:00 | 19.8 | 64.5 | 100 | 22.4572 | 16.4797 | 54.5929 | 44.2251 | 44.2251 | 0 | 0
2025-03-25 22:00 | 19.55 | 66.5 | 70 | 22.3635 | 16.4971 | 55.2493 | 33.095 | 33.095 | 0 | 0
2025-03-25 23:00 | 19.25 | 69 | 70 | 22.251 | 16.5194 | 56.0632 | 35.7708 | 35.7708 | 0 | 0
2025-03-26 | 18.95 | 70.5 | 70 | 22.1374 | 16.489 | 56.5278 | 36.2632 | 36.2632 | 0 | 0
2025-03-26 01:00 | 18.6 | 72.5 | 70 | 22.0045 | 16.4629 | 57.142 | 37.2352 | 37.2352 | 0 | 0
2025-03-26 02:00 | 18.05 | 76.5 | 70 | 21.7953 | 16.4573 | 58.3626 | 40.1933 | 40.1933 | 0 | 0
2025-03-26 03:00 | 17.65 | 79 | 70 | 21.6421 | 16.4283 | 59.0957 | 41.3315 | 41.3315 | 0 | 0
2025-03-26 04:00 | 17.25 | 79 | 70 | 21.486 | 16.2833 | 59.0196 | 37.6298 | 37.6298 | 0 | 0
2025-03-26 05:00 | 16.65 | 80 | 70 | 21.2512 | 16.1106 | 59.2284 | 33.9722 | 33.9722 | 0 | 0
2025-03-26 06:00 | 16.35 | 81 | 100 | 21.1336 | 16.0452 | 59.4823 | 47.1444 | 47.1444 | 0 | 0
2025-03-26 07:00 | 17.25 | 76.5 | 100 | 21.4839 | 16.1709 | 58.2066 | 46.9031 | 46.9031 | 0 | 0
2025-03-26 08:00 | 19.45 | 67 | 100 | 22.3258 | 16.4884 | 55.4044 | 47.5408 | 47.5408 | 0 | 0
2025-03-26 09:00 | 21.65 | 59.5 | 100 | 23.1469 | 16.8331 | 53.0786 | 50.5141 | 50.5141 | 0 | 0
2025-03-26 10:00 | 23.35 | 54.5 | 100 | 23.7665 | 17.0988 | 51.4573 | 53.2862 | 53.2862 | 0 | 0
2025-03-26 11:00 | 24.7 | 49 | 100 | 24.2496 | 17.181 | 49.4643 | 48.0265 | 48.0265 | 0 | 0
2025-03-26 12:00 | 25.8 | 43.5 | 100 | 24.6384 | 17.1447 | 47.3032 | 37.8035 | 37.8035 | 0 | 0
2025-03-26 13:00 | 26.4 | 42 | 100 | 24.8481 | 17.2168 | 46.7316 | 37.8988 | 37.8988 | 0 | 0
2025-03-26 14:00 | 26.1 | 46.5 | 100 | 24.7417 | 17.4463 | 48.6597 | 54.0292 | 54.0292 | 0 | 0
2025-03-26 15:00 | 25.35 | 51 | 100 | 24.4783 | 17.5187 | 50.4444 | 64.0139 | 64.0139 | 0 | 0
2025-03-26 16:00 | 24.45 | 53 | 100 | 24.1604 | 17.3604 | 51.0888 | 61.0886 | 61.0886 | 0 | 0
2025-03-26 17:00 | 23.35 | 56.5 | 100 | 23.7668 | 17.2198 | 52.2705 | 60.9294 | 60.9294 | 0 | 0
2025-03-26 18:00 | 22.35 | 62 | 100 | 23.4049 | 17.211 | 54.1815 | 68.1239 | 68.1239 | 0 | 0
2025-03-26 19:00 | 21.55 | 67.5 | 100 | 23.1131 | 17.2453 | 56.0408 | 76.431 | 76.431 | 0 | 0
2025-03-26 20:00 | 20.7 | 73.5 | 100 | 22.8006 | 17.2658 | 57.9776 | 84.3753 | 84.3753 | 0 | 0
2025-03-26 21:00 | 19.75 | 78.5 | 100 | 22.4469 | 17.1753 | 59.4467 | 86.4952 | 86.4952 | 0 | 0
2025-03-26 22:00 | 18.8 | 82 | 70 | 22.0881 | 16.9933 | 60.3494 | 58.2795 | 58.2795 | 0 | 0
2025-03-26 23:00 | 17.95 | 85.5 | 70 | 21.7637 | 16.8385 | 61.2513 | 56.6462 | 56.6462 | 0 | 0
2025-03-27 | 17.35 | 88.5 | 70 | 21.533 | 16.7465 | 62.0397 | 56.2846 | 56.2846 | 0 | 0
2025-03-27 01:00 | 16.9 | 90.5 | 70 | 21.3587 | 16.663 | 62.5402 | 55.4133 | 55.4133 | 0 | 0
2025-03-27 02:00 | 16.4 | 92 | 70 | 21.1632 | 16.5357 | 62.8667 | 53.0538 | 53.0538 | 0 | 0
2025-03-27 03:00 | 15.85 | 94 | 70 | 20.947 | 16.4076 | 63.3281 | 51.0042 | 51.0042 | 0 | 0
2025-03-27 04:00 | 15.95 | 93.5 | 70 | 20.9863 | 16.4252 | 63.2012 | 51.1335 | 51.1335 | 0 | 0
2025-03-27 05:00 | 15.85 | 93 | 70 | 20.9461 | 16.3666 | 63.0191 | 49.2304 | 49.2304 | 0 | 0
2025-03-27 06:00 | 15.4 | 95 | 100 | 20.7684 | 16.2755 | 63.4958 | 68.7028 | 68.7028 | 0 | 0
2025-03-27 07:00 | 16.8 | 90 | 100 | 21.319 | 16.6034 | 62.3388 | 76.2645 | 76.2645 | 0 | 0
2025-03-27 08:00 | 19.7 | 77 | 100 | 22.4271 | 17.0823 | 58.8925 | 81.0334 | 81.0334 | 0 | 0
2025-03-27 09:00 | 22.25 | 63 | 100 | 23.3687 | 17.2373 | 54.5014 | 69.991 | 69.991 | 0 | 0
2025-03-27 10:00 | 24.5 | 50 | 100 | 24.1784 | 17.1854 | 49.8281 | 49.518 | 49.518 | 0 | 0
2025-03-27 11:00 | 26.8 | 40 | 100 | 24.9877 | 17.1937 | 45.8614 | 33.0174 | 33.0174 | 0 | 0
2025-03-27 12:00 | 28.4 | 34.5 | 100 | 25.539 | 17.2277 | 43.4917 | 23.6894 | 23.6894 | 0 | 0
2025-03-27 13:00 | 28.5 | 38 | 100 | 25.5688 | 17.5354 | 45.1626 | 41.681 | 41.681 | 0 | 0
2025-03-27 14:00 | 27.45 | 45.5 | 100 | 25.2064 | 17.7965 | 48.4622 | 65.2054 | 65.2054 | 0 | 0
2025-03-27 15:00 | 26.4 | 49.5 | 100 | 24.8441 | 17.7541 | 50.0181 | 70.3656 | 70.3656 | 0 | 0
2025-03-27 16:00 | 25.7 | 48.5 | 100 | 24.6016 | 17.4615 | 49.4396 | 57.7305 | 57.7305 | 0 | 0
2025-03-27 17:00 | 24.75 | 51.5 | 100 | 24.2669 | 17.3603 | 50.521 | 58.6916 | 58.6916 | 0 | 0
2025-03-27 18:00 | 23.55 | 63.5 | 100 | 23.8394 | 17.7148 | 55.0759 | 89.4179 | 89.4179 | 0 | 0
2025-03-27 19:00 | 22.75 | 72.5 | 100 | 23.553 | 17.9588 | 58.3006 | 110.6228 | 110.6228 | 0 | 0
2025-03-27 20:00 | 22.2 | 76.5 | 100 | 23.3546 | 17.9809 | 59.5957 | 116.255 | 116.255 | 0 | 0
2025-03-27 21:00 | 21.55 | 79.5 | 100 | 23.118 | 17.901 | 60.4409 | 116.3971 | 116.3971 | 0 | 0
2025-03-27 22:00 | 20.65 | 82.5 | 70 | 22.7867 | 17.7165 | 61.1599 | 78.5841 | 78.5841 | 0 | 0
2025-03-27 23:00 | 19.55 | 85.5 | 70 | 22.3758 | 17.4473 | 61.7799 | 73.2464 | 73.2464 | 0 | 0
2025-03-28 | 18.55 | 86.5 | 70 | 21.9957 | 17.1124 | 61.7642 | 64.7534 | 64.7534 | 0 | 0
2025-03-28 01:00 | 17.7 | 86 | 70 | 21.6672 | 16.7669 | 61.3438 | 55.1055 | 55.1055 | 0 | 0
2025-03-28 02:00 | 17 | 85.5 | 70 | 21.3936 | 16.4813 | 61.0056 | 47.2594 | 47.2594 | 0 | 0
2025-03-28 03:00 | 16.5 | 86.5 | 70 | 21.1978 | 16.3379 | 61.2024 | 44.2331 | 44.2331 | 0 | 0
2025-03-28 04:00 | 16.65 | 92 | 70 | 21.2618 | 16.6319 | 62.9376 | 55.6028 | 55.6028 | 0 | 0
2025-03-28 05:00 | 16.6 | 94.5 | 70 | 21.2443 | 16.7192 | 63.6895 | 59.5526 | 59.5526 | 0 | 0
2025-03-28 06:00 | 16.25 | 93.5 | 100 | 21.1052 | 16.541 | 63.2708 | 77.3004 | 77.3004 | 0 | 0
2025-03-28 07:00 | 17.1 | 89.5 | 100 | 21.4362 | 16.6962 | 62.2675 | 79.3016 | 79.3016 | 0 | 0
2025-03-28 08:00 | 19.55 | 70.5 | 100 | 22.3661 | 16.7015 | 56.613 | 59.2722 | 59.2722 | 0 | 0
2025-03-28 09:00 | 22.75 | 44.5 | 100 | 23.5467 | 16.2969 | 47.4671 | 9.8882 | 9.8882 | 0 | 0
2025-03-28 10:00 | 25.7 | 29 | 100 | 24.6086 | 16.0806 | 41.0163 | 0 | 0 | 0 | 0
2025-03-28 11:00 | 28.15 | 24 | 100 | 25.4651 | 16.3069 | 38.5378 | 0 | 0 | 0 | 0
2025-03-28 12:00 | 29.9 | 22.5 | 100 | 26.0595 | 16.599 | 37.6722 | 0 | 0 | 0 | 0
2025-03-28 13:00 | 30.65 | 23.5 | 100 | 26.3069 | 16.8693 | 38.1451 | 0 | 0 | 0 | 0
2025-03-28 14:00 | 30.1 | 28.5 | 100 | 26.1161 | 17.1797 | 40.6842 | 9.2937 | 9.2937 | 0 | 0
2025-03-28 15:00 | 28.8 | 34 | 100 | 25.6745 | 17.2948 | 43.3065 | 25.3482 | 25.3482 | 0 | 0
2025-03-28 16:00 | 27.7 | 41.5 | 100 | 25.2948 | 17.5697 | 46.6884 | 49.7531 | 49.7531 | 0 | 0
2025-03-28 17:00 | 26.5 | 48.5 | 100 | 24.8791 | 17.7147 | 49.6036 | 67.2681 | 67.2681 | 0 | 0
2025-03-28 18:00 | 25.05 | 57 | 100 | 24.3716 | 17.8201 | 52.8768 | 84.4544 | 84.4544 | 0 | 0
2025-03-28 19:00 | 24.1 | 65.5 | 100 | 24.0355 | 18.0309 | 56.0523 | 104.6243 | 104.6243 | 0 | 0
2025-03-28 20:00 | 23.35 | 69.5 | 100 | 23.7683 | 18.0031 | 57.3636 | 108.663 | 108.663 | 0 | 0
2025-03-28 21:00 | 22.45 | 77 | 100 | 23.4455 | 18.1029 | 59.8881 | 121.8352 | 121.8352 | 0 | 0
2025-03-28 22:00 | 21.6 | 86.5 | 70 | 23.1392 | 18.2932 | 63.0314 | 98.3318 | 98.3318 | 0 | 0
2025-03-28 23:00 | 20.9 | 93 | 70 | 22.8847 | 18.3514 | 65.0195 | 104.8613 | 104.8613 | 0 | 0
2025-03-29 | 20.4 | 95 | 70 | 22.7004 | 18.2495 | 65.4617 | 103.2628 | 103.2628 | 0 | 0
2025-03-29 01:00 | 20.05 | 94.5 | 70 | 22.5695 | 18.0836 | 65.1086 | 98.0196 | 98.0196 | 0 | 0
2025-03-29 02:00 | 19.7 | 94 | 70 | 22.4379 | 17.919 | 64.7663 | 92.8643 | 92.8643 | 0 | 0
2025-03-29 03:00 | 19.3 | 94.5 | 70 | 22.2872 | 17.7828 | 64.7499 | 89.2854 | 89.2854 | 0 | 0
2025-03-29 04:00 | 19.3 | 95 | 70 | 22.2875 | 17.8068 | 64.9188 | 90.3155 | 90.3155 | 0 | 0
2025-03-29 05:00 | 19.1 | 93 | 70 | 22.2103 | 17.6322 | 64.1514 | 83.9039 | 83.9039 | 0 | 0
2025-03-29 06:00 | 18.6 | 85 | 100 | 22.0137 | 17.0605 | 61.2886 | 89.003 | 89.003 | 0 | 0
2025-03-29 07:00 | 19.7 | 71 | 100 | 22.4233 | 16.7787 | 56.8355 | 62.9151 | 62.9151 | 0 | 0
2025-03-29 08:00 | 22.5 | 56 | 100 | 23.4581 | 16.9118 | 51.8976 | 48.5866 | 48.5866 | 0 | 0
2025-03-29 09:00 | 25.45 | 44 | 100 | 24.5155 | 17.076 | 47.4592 | 35.9609 | 35.9609 | 0 | 0
2025-03-29 10:00 | 27.85 | 35.5 | 100 | 25.3513 | 17.153 | 43.9155 | 23.0802 | 23.0802 | 0 | 0
2025-03-29 11:00 | 29.75 | 29 | 100 | 25.9991 | 17.1346 | 40.9064 | 8.6682 | 8.6682 | 0 | 0
2025-03-29 12:00 | 31.15 | 24.5 | 100 | 26.4691 | 17.0856 | 38.6478 | 0 | 0 | 0 | 0
2025-03-29 13:00 | 31.9 | 23 | 100 | 26.7166 | 17.1254 | 37.8604 | 0 | 0 | 0 | 0
2025-03-29 14:00 | 31.85 | 24.5 | 100 | 26.6968 | 17.2565 | 38.6658 | 2.1595 | 2.1595 | 0 | 0
2025-03-29 15:00 | 30.85 | 28 | 100 | 26.3638 | 17.3287 | 40.4696 | 13.3104 | 13.3104 | 0 | 0
2025-03-29 16:00 | 28.9 | 36 | 100 | 25.7055 | 17.4862 | 44.2801 | 36.2633 | 36.2633 | 0 | 0
2025-03-29 17:00 | 26.65 | 46.5 | 100 | 24.9319 | 17.6182 | 48.7574 | 60.3702 | 60.3702 | 0 | 0
2025-03-29 18:00 | 24.95 | 54.5 | 100 | 24.337 | 17.6222 | 51.8144 | 73.1826 | 73.1826 | 0 | 0
2025-03-29 19:00 | 23.95 | 60 | 100 | 23.9822 | 17.6377 | 53.8015 | 81.6913 | 81.6913 | 0 | 0
2025-03-29 20:00 | 23.2 | 63.5 | 100 | 23.7136 | 17.5931 | 54.9724 | 84.6524 | 84.6524 | 0 | 0
2025-03-29 21:00 | 22.45 | 64 | 100 | 23.442 | 17.362 | 54.9564 | 76.36 | 76.36 | 0 | 0
2025-03-29 22:00 | 21.75 | 64.5 | 70 | 23.1857 | 17.1483 | 54.9702 | 48.2071 | 48.2071 | 0 | 0
2025-03-29 23:00 | 21.05 | 69.5 | 70 | 22.9289 | 17.1782 | 56.6344 | 53.3741 | 53.3741 | 0 | 0
2025-03-30 | 20.25 | 76 | 70 | 22.6336 | 17.2319 | 58.7337 | 60.1807 | 60.1807 | 0 | 0
2025-03-30 01:00 | 19.4 | 82.5 | 70 | 22.317 | 17.2421 | 60.7185 | 65.4898 | 65.4898 | 0 | 0
2025-03-30 02:00 | 18.75 | 87 | 70 | 22.0726 | 17.2117 | 62.0156 | 67.9571 | 67.9571 | 0 | 0
2025-03-30 03:00 | 18.25 | 88 | 70 | 21.8815 | 17.067 | 62.1769 | 64.7083 | 64.7083 | 0 | 0
2025-03-30 04:00 | 18.05 | 84 | 70 | 21.8012 | 16.8062 | 60.8112 | 54.8497 | 54.8497 | 0 | 0
2025-03-30 05:00 | 17.95 | 78.5 | 70 | 21.7582 | 16.5144 | 58.9928 | 43.1552 | 43.1552 | 0 | 0
2025-03-30 06:00 | 18 | 74 | 100 | 21.774 | 16.3224 | 57.5286 | 49.7143 | 49.7143 | 0 | 0
2025-03-30 07:00 | 19.55 | 63 | 100 | 22.3613 | 16.3174 | 54.0454 | 36.6822 | 36.6822 | 0 | 0
2025-03-30 08:00 | 22.75 | 47 | 100 | 23.5473 | 16.4484 | 48.4553 | 19.1121 | 19.1121 | 0 | 0
2025-03-30 09:00 | 26.6 | 33 | 100 | 24.9226 | 16.614 | 42.7392 | 0.0744 | 0.0744 | 0 | 0
2025-03-30 10:00 | 30.3 | 23.5 | 100 | 26.191 | 16.786 | 38.1502 | 0 | 0 | 0 | 0
2025-03-30 11:00 | 32.85 | 18.5 | 100 | 27.0347 | 16.9008 | 35.3717 | 0 | 0 | 0 | 0
2025-03-30 12:00 | 33.95 | 18 | 100 | 27.3863 | 17.0941 | 35.0304 | 0 | 0 | 0 | 0
2025-03-30 13:00 | 34.15 | 19.5 | 100 | 27.4439 | 17.2996 | 35.89 | 0 | 0 | 0 | 0
2025-03-30 14:00 | 33.55 | 21 | 100 | 27.25 | 17.3182 | 36.7563 | 0 | 0 | 0 | 0
2025-03-30 15:00 | 32.25 | 24 | 100 | 26.827 | 17.3069 | 38.4056 | 2.5396 | 2.5396 | 0 | 0
2025-03-30 16:00 | 30.85 | 29.5 | 100 | 26.3608 | 17.4653 | 41.2372 | 21.4654 | 21.4654 | 0 | 0
2025-03-30 17:00 | 29.1 | 37.5 | 100 | 25.7703 | 17.667 | 45.0227 | 45.7212 | 45.7212 | 0 | 0
2025-03-30 18:00 | 27.05 | 50 | 100 | 25.0667 | 17.9992 | 50.4028 | 80.6588 | 80.6588 | 0 | 0
2025-03-30 19:00 | 25.9 | 56.5 | 100 | 24.668 | 18.0739 | 52.917 | 93.7085 | 93.7085 | 0 | 0
2025-03-30 20:00 | 25.35 | 53 | 100 | 24.4778 | 17.6549 | 51.2727 | 72.0458 | 72.0458 | 0 | 0
2025-03-30 21:00 | 24.55 | 50.5 | 100 | 24.1962 | 17.2313 | 50.0633 | 52.2783 | 52.2783 | 0 | 0
2025-03-30 22:00 | 23.75 | 50 | 70 | 23.9103 | 16.9455 | 49.7371 | 28.7888 | 28.7888 | 0 | 0
2025-03-30 23:00 | 23.05 | 50.5 | 70 | 23.6573 | 16.7559 | 49.8512 | 24.6101 | 24.6101 | 0 | 0
2025-03-31 | 22.2 | 50.5 | 70 | 23.3465 | 16.4884 | 49.7748 | 18.108 | 18.108 | 0 | 0
2025-03-31 01:00 | 21.35 | 48.5 | 70 | 23.0311 | 16.1075 | 48.9871 | 7.0718 | 7.0718 | 0 | 0
2025-03-31 02:00 | 20.65 | 46 | 70 | 22.7677 | 15.7532 | 48.0846 | 0 | 0 | 0 | 0
2025-03-31 03:00 | 19.9 | 44 | 70 | 22.4826 | 15.4199 | 47.4248 | 0 | 0 | 0 | 0
2025-03-31 04:00 | 19.5 | 40.5 | 70 | 22.3277 | 15.1144 | 46.2479 | 0 | 0 | 0 | 0
2025-03-31 05:00 | 19.45 | 37.5 | 70 | 22.3067 | 14.938 | 45.2078 | 0 | 0 | 0 | 0
2025-03-31 06:00 | 19.85 | 36 | 100 | 22.4588 | 14.9661 | 44.5973 | 0 | 0 | 0 | 0
2025-03-31 07:00 | 22.1 | 31.5 | 100 | 23.3036 | 15.3067 | 42.524 | 0 | 0 | 0 | 0
2025-03-31 08:00 | 26.05 | 24.5 | 100 | 24.7341 | 15.8312 | 39.0266 | 0 | 0 | 0 | 0
2025-03-31 09:00 | 29.9 | 19 | 100 | 26.0651 | 16.2841 | 35.9204 | 0 | 0 | 0 | 0
2025-03-31 10:00 | 32.65 | 15.5 | 100 | 26.9787 | 16.5484 | 33.7365 | 0 | 0 | 0 | 0
2025-03-31 11:00 | 34.3 | 14 | 100 | 27.511 | 16.7317 | 32.6911 | 0 | 0 | 0 | 0
2025-03-31 12:00 | 35.2 | 14 | 100 | 27.7934 | 16.9155 | 32.5981 | 0 | 0 | 0 | 0
2025-03-31 13:00 | 35.6 | 14 | 100 | 27.9177 | 16.9958 | 32.5661 | 0 | 0 | 0 | 0
2025-03-31 14:00 | 35.45 | 13.5 | 100 | 27.8734 | 16.9045 | 32.285 | 0 | 0 | 0 | 0
2025-03-31 15:00 | 34.6 | 14 | 100 | 27.6058 | 16.7868 | 32.6789 | 0 | 0 | 0 | 0
2025-03-31 16:00 | 32.9 | 18 | 100 | 27.0523 | 16.8545 | 35.1143 | 0 | 0 | 0 | 0
2025-03-31 17:00 | 30.35 | 27.5 | 100 | 26.2005 | 17.1539 | 40.1956 | 6.238 | 6.238 | 0 | 0
2025-03-31 18:00 | 27.65 | 42.5 | 100 | 25.2769 | 17.6312 | 47.1396 | 53.8294 | 53.8294 | 0 | 0
2025-03-31 19:00 | 25.95 | 54.5 | 100 | 24.6861 | 17.9546 | 52.0746 | 85.9991 | 85.9991 | 0 | 0
2025-03-31 20:00 | 25 | 61 | 100 | 24.3532 | 18.063 | 54.5244 | 99.7841 | 99.7841 | 0 | 0
2025-03-31 21:00 | 24.3 | 63.5 | 100 | 24.1064 | 17.9774 | 55.3131 | 99.79 | 99.79 | 0 | 0
2025-03-31 22:00 | 23.95 | 61.5 | 70 | 23.9822 | 17.7314 | 54.3977 | 61.1335 | 61.1335 | 0 | 0
2025-03-31 23:00 | 23.4 | 59.5 | 70 | 23.7851 | 17.4203 | 53.4564 | 50.8149 | 50.8149 | 0 | 0
2025-04-01 | 22.75 | 58.5 | 70 | 23.5498 | 17.1414 | 52.9246 | 42.5207 | 42.5207 | 0 | 0
2025-04-01 01:00 | 22.15 | 57.5 | 70 | 23.3303 | 16.8823 | 52.4364 | 34.9347 | 34.9347 | 0 | 0
2025-04-01 02:00 | 21.45 | 57 | 70 | 23.0718 | 16.6234 | 52.1495 | 27.9533 | 27.9533 | 0 | 0
2025-04-01 03:00 | 20.55 | 58 | 70 | 22.7363 | 16.3838 | 52.413 | 22.9975 | 22.9975 | 0 | 0
2025-04-01 04:00 | 19.8 | 59.5 | 70 | 22.454 | 16.2173 | 52.8744 | 20.3175 | 20.3175 | 0 | 0
2025-04-01 05:00 | 19.25 | 61 | 70 | 22.2456 | 16.1136 | 53.3459 | 19.1167 | 19.1167 | 0 | 0
2025-04-01 06:00 | 19.1 | 59.5 | 100 | 22.1872 | 15.9877 | 52.8204 | 21.1107 | 21.1107 | 0 | 0
2025-04-01 07:00 | 21.05 | 49.5 | 100 | 22.9195 | 16.0718 | 49.3549 | 10.436 | 10.436 | 0 | 0
2025-04-01 08:00 | 25.15 | 35.5 | 100 | 24.4118 | 16.3936 | 43.8547 | 0 | 0 | 0 | 0
2025-04-01 09:00 | 29.2 | 23.5 | 100 | 25.8229 | 16.5159 | 38.2272 | 0 | 0 | 0 | 0
2025-04-01 10:00 | 31.9 | 15 | 100 | 26.7361 | 16.3356 | 33.5806 | 0 | 0 | 0 | 0
2025-04-01 11:00 | 33.45 | 12 | 100 | 27.2472 | 16.3368 | 31.6805 | 0 | 0 | 0 | 0
2025-04-01 12:00 | 33.65 | 13.5 | 100 | 27.3064 | 16.5391 | 32.5027 | 0 | 0 | 0 | 0
2025-04-01 13:00 | 33.05 | 14.5 | 100 | 27.1109 | 16.5212 | 33.1541 | 0 | 0 | 0 | 0
2025-04-01 14:00 | 32.4 | 15.5 | 100 | 26.898 | 16.4868 | 33.7973 | 0 | 0 | 0 | 0
2025-04-01 15:00 | 31.25 | 19 | 100 | 26.5138 | 16.5811 | 35.8015 | 0 | 0 | 0 | 0
2025-04-01 16:00 | 29.9 | 24.5 | 100 | 26.0564 | 16.7704 | 38.7051 | 0 | 0 | 0 | 0
2025-04-01 17:00 | 28.25 | 35 | 100 | 25.4878 | 17.2198 | 43.7509 | 25.0039 | 25.0039 | 0 | 0
2025-04-01 18:00 | 26.4 | 48.5 | 100 | 24.8446 | 17.6818 | 49.5956 | 66.2011 | 66.2011 | 0 | 0
2025-04-01 19:00 | 25.2 | 57 | 100 | 24.4242 | 17.8697 | 52.9315 | 86.5518 | 86.5518 | 0 | 0
2025-04-01 20:00 | 24.35 | 61 | 100 | 24.1243 | 17.8372 | 54.3265 | 90.9439 | 90.9439 | 0 | 0
2025-04-01 21:00 | 23.55 | 64 | 100 | 23.8394 | 17.7443 | 55.2823 | 91.3593 | 91.3593 | 0 | 0
2025-04-01 22:00 | 22.7 | 65.5 | 70 | 23.5332 | 17.5353 | 55.6141 | 59.6243 | 59.6243 | 0 | 0
2025-04-01 23:00 | 21.75 | 66 | 70 | 23.1862 | 17.2314 | 55.5462 | 51.8907 | 51.8907 | 0 | 0
2025-04-02 | 20.9 | 65.5 | 70 | 22.8711 | 16.9084 | 55.1692 | 42.9695 | 42.9695 | 0 | 0
2025-04-02 01:00 | 20.05 | 65 | 70 | 22.552 | 16.5893 | 54.8393 | 34.3948 | 34.3948 | 0 | 0
2025-04-02 02:00 | 19.15 | 63.5 | 70 | 22.209 | 16.2062 | 54.2074 | 23.6397 | 23.6397 | 0 | 0
2025-04-02 03:00 | 18.3 | 60 | 70 | 21.8794 | 15.75 | 52.9808 | 9.7892 | 9.7892 | 0 | 0
2025-04-02 04:00 | 17.9 | 56 | 70 | 21.7209 | 15.4251 | 51.6661 | 0 | 0 | 0 | 0
2025-04-02 05:00 | 17.65 | 52 | 70 | 21.6202 | 15.1529 | 50.3741 | 0 | 0 | 0 | 0
2025-04-02 06:00 | 17.75 | 46.5 | 100 | 21.6549 | 14.9147 | 48.559 | 0 | 0 | 0 | 0
2025-04-02 07:00 | 19.85 | 37.5 | 100 | 22.4596 | 15.0471 | 45.1472 | 0 | 0 | 0 | 0
2025-04-02 08:00 | 23.85 | 28 | 100 | 23.9456 | 15.5286 | 40.8709 | 0 | 0 | 0 | 0
2025-04-02 09:00 | 27.65 | 24 | 100 | 25.2932 | 16.179 | 38.617 | 0 | 0 | 0 | 0
2025-04-02 10:00 | 30.25 | 23 | 100 | 26.1754 | 16.7236 | 37.9206 | 0 | 0 | 0 | 0
2025-04-02 11:00 | 32.1 | 21 | 100 | 26.7864 | 16.9749 | 36.7947 | 0 | 0 | 0 | 0
2025-04-02 12:00 | 33.4 | 20 | 100 | 27.2058 | 17.1755 | 36.206 | 0 | 0 | 0 | 0
2025-04-02 13:00 | 33.85 | 20 | 100 | 27.3481 | 17.2783 | 36.2013 | 0 | 0 | 0 | 0
2025-04-02 14:00 | 33.05 | 20.5 | 100 | 27.093 | 17.143 | 36.5042 | 0 | 0 | 0 | 0
2025-04-02 15:00 | 31.65 | 25 | 100 | 26.6309 | 17.25 | 38.95 | 3.6211 | 3.6211 | 0 | 0
2025-04-02 16:00 | 30.15 | 34 | 100 | 26.1232 | 17.6683 | 43.4697 | 38.9827 | 38.9827 | 0 | 0
2025-04-02 17:00 | 28.15 | 45 | 100 | 25.4435 | 17.9729 | 48.416 | 71.5078 | 71.5078 | 0 | 0
2025-04-02 18:00 | 26.15 | 58.5 | 100 | 24.7534 | 18.2931 | 53.8832 | 105.7707 | 105.7707 | 0 | 0
2025-04-02 19:00 | 24.9 | 71 | 100 | 24.3163 | 18.6611 | 58.6414 | 138.1584 | 138.1584 | 0 | 0
2025-04-02 20:00 | 24.15 | 76.5 | 100 | 24.0529 | 18.7163 | 60.5074 | 147.3138 | 147.3138 | 0 | 0
2025-04-02 21:00 | 23.45 | 77 | 100 | 23.8049 | 18.4792 | 60.3617 | 137.8305 | 137.8305 | 0 | 0
2025-04-02 22:00 | 22.7 | 78 | 70 | 23.5362 | 18.2519 | 60.4033 | 90.6467 | 90.6467 | 0 | 0
2025-04-02 23:00 | 21.95 | 79 | 70 | 23.2643 | 18.0235 | 60.457 | 84.8629 | 84.8629 | 0 | 0
2025-04-03 | 21.15 | 79.5 | 70 | 22.9706 | 17.7484 | 60.3212 | 77.4449 | 77.4449 | 0 | 0
2025-04-03 01:00 | 20.3 | 80 | 70 | 22.6547 | 17.4546 | 60.1894 | 69.6459 | 69.6459 | 0 | 0
2025-04-03 02:00 | 19.45 | 80 | 70 | 22.3343 | 17.1371 | 59.9129 | 60.9657 | 60.9657 | 0 | 0
2025-04-03 03:00 | 18.7 | 79.5 | 70 | 22.048 | 16.8351 | 59.5305 | 52.4979 | 52.4979 | 0 | 0
2025-04-03 04:00 | 18.6 | 75.5 | 70 | 22.0067 | 16.6064 | 58.1703 | 43.4565 | 43.4565 | 0 | 0
2025-04-03 05:00 | 18.5 | 72.5 | 70 | 21.966 | 16.4268 | 57.1469 | 36.4733 | 36.4733 | 0 | 0
2025-04-03 06:00 | 18.5 | 71 | 100 | 21.9649 | 16.3545 | 56.6413 | 47.7412 | 47.7412 | 0 | 0
2025-04-03 07:00 | 20.55 | 63 | 100 | 22.739 | 16.6536 | 54.2049 | 48.914 | 48.914 | 0 | 0
2025-04-03 08:00 | 24.5 | 50 | 100 | 24.1784 | 17.1814 | 49.8636 | 49.8622 | 49.8622 | 0 | 0
2025-04-03 09:00 | 28.6 | 37 | 100 | 25.6036 | 17.4819 | 44.7155 | 38.0203 | 38.0203 | 0 | 0
2025-04-03 10:00 | 32.2 | 26 | 100 | 26.8057 | 17.4896 | 39.4794 | 13.7931 | 13.7931 | 0 | 0
2025-04-03 11:00 | 35.2 | 18.5 | 100 | 27.7746 | 17.4261 | 35.2984 | 0 | 0 | 0 | 0
2025-04-03 12:00 | 37.3 | 14.5 | 100 | 28.4336 | 17.4046 | 32.7731 | 0 | 0 | 0 | 0
2025-04-03 13:00 | 38.15 | 13.5 | 100 | 28.6934 | 17.4503 | 32.0877 | 0 | 0 | 0 | 0
2025-04-03 14:00 | 36.35 | 22 | 100 | 28.1085 | 18.0949 | 37.474 | 24.0245 | 24.0245 | 0 | 0
2025-04-03 15:00 | 32.35 | 36 | 100 | 26.8268 | 18.4792 | 44.8917 | 73.5381 | 73.5381 | 0 | 0
2025-04-03 16:00 | 29.95 | 44 | 100 | 26.0407 | 18.4562 | 48.3954 | 88.5286 | 88.5286 | 0 | 0
2025-04-03 17:00 | 29 | 51 | 100 | 25.7191 | 18.7105 | 51.4874 | 111.0813 | 111.0813 | 0 | 0
2025-04-03 18:00 | 27.4 | 60.5 | 100 | 25.1771 | 18.8677 | 55.2517 | 132.4896 | 132.4896 | 0 | 0
2025-04-03 19:00 | 26.35 | 63 | 100 | 24.8197 | 18.6687 | 55.9031 | 127.6672 | 127.6672 | 0 | 0
2025-04-03 20:00 | 26.25 | 58.5 | 100 | 24.7877 | 18.3279 | 53.9077 | 107.0599 | 107.0599 | 0 | 0
2025-04-03 21:00 | 26.2 | 55 | 100 | 24.7723 | 18.0716 | 52.3706 | 91.4728 | 91.4728 | 0 | 0
2025-04-03 22:00 | 25.7 | 52.5 | 70 | 24.6001 | 17.7348 | 51.1591 | 52.1556 | 52.1556 | 0 | 0
2025-04-03 23:00 | 25 | 49.5 | 70 | 24.3556 | 17.3059 | 49.7484 | 37.6336 | 37.6336 | 0 | 0
2025-04-04 | 24.25 | 47 | 70 | 24.0895 | 16.9055 | 48.6124 | 24.7815 | 24.7815 | 0 | 0
2025-04-04 01:00 | 23.4 | 46 | 70 | 23.7836 | 16.5802 | 48.1381 | 15.7766 | 15.7766 | 0 | 0
2025-04-04 02:00 | 22.65 | 46.5 | 70 | 23.5106 | 16.3827 | 48.2958 | 11.6467 | 11.6467 | 0 | 0
2025-04-04 03:00 | 22.1 | 46.5 | 70 | 23.3084 | 16.2155 | 48.2791 | 7.7407 | 7.7407 | 0 | 0
2025-04-04 04:00 | 22.2 | 41 | 70 | 23.3436 | 15.9131 | 46.1831 | 0 | 0 | 0 | 0
2025-04-04 05:00 | 22.65 | 32 | 70 | 23.5071 | 15.4774 | 42.6639 | 0 | 0 | 0 | 0
2025-04-04 06:00 | 24.05 | 24 | 100 | 24.0182 | 15.3027 | 39.2068 | 0 | 0 | 0 | 0
2025-04-04 07:00 | 27 | 17 | 100 | 25.0725 | 15.4608 | 35.521 | 0 | 0 | 0 | 0
2025-04-04 08:00 | 30.45 | 13 | 100 | 26.26 | 15.8378 | 32.8096 | 0 | 0 | 0 | 0
2025-04-04 09:00 | 33.85 | 10 | 100 | 27.3821 | 16.1922 | 30.4693 | 0 | 0 | 0 | 0
2025-04-04 10:00 | 36.65 | 7.5 | 100 | 28.2732 | 16.3991 | 28.4017 | 0 | 0 | 0 | 0
2025-04-04 11:00 | 38.6 | 7 | 100 | 28.8695 | 16.6649 | 27.7043 | 0 | 0 | 0 | 0
2025-04-04 12:00 | 39.95 | 7 | 100 | 29.27 | 16.8903 | 27.4769 | 0 | 0 | 0 | 0
2025-04-04 13:00 | 40.65 | 7 | 100 | 29.4743 | 17.0051 | 27.3733 | 0 | 0 | 0 | 0
2025-04-04 14:00 | 40.2 | 9 | 100 | 29.3272 | 17.2217 | 28.8568 | 0 | 0 | 0 | 0
2025-04-04 15:00 | 38.7 | 12.5 | 100 | 28.8626 | 17.428 | 31.3933 | 0 | 0 | 0 | 0
2025-04-04 16:00 | 35.95 | 17 | 100 | 28.0117 | 17.4177 | 34.39 | 0 | 0 | 0 | 0
2025-04-04 17:00 | 33.15 | 24 | 100 | 27.1141 | 17.5271 | 38.4434 | 10.1068 | 10.1068 | 0 | 0
2025-04-04 18:00 | 31.25 | 31 | 100 | 26.4877 | 17.7075 | 42.0597 | 33.6211 | 33.6211 | 0 | 0
2025-04-04 19:00 | 29.7 | 34 | 100 | 25.9747 | 17.5443 | 43.4053 | 34.3373 | 34.3373 | 0 | 0
2025-04-04 20:00 | 28.95 | 30.5 | 100 | 25.7294 | 17.0447 | 41.6434 | 9.5072 | 9.5072 | 0 | 0
2025-04-04 21:00 | 28.5 | 26 | 100 | 25.5826 | 16.552 | 39.4924 | 0 | 0 | 0 | 0
2025-04-04 22:00 | 27.75 | 24 | 70 | 25.3277 | 16.2019 | 38.6129 | 0 | 0 | 0 | 0
2025-04-04 23:00 | 26.75 | 22 | 70 | 24.9817 | 15.8009 | 37.8362 | 0 | 0 | 0 | 0
2025-04-05 | 25.75 | 20.5 | 70 | 24.6295 | 15.4514 | 37.3658 | 0 | 0 | 0 | 0
2025-04-05 01:00 | 25 | 22 | 70 | 24.3612 | 15.3869 | 38.1736 | 0 | 0 | 0 | 0
2025-04-05 02:00 | 24.35 | 27 | 70 | 24.1266 | 15.5838 | 40.3919 | 0 | 0 | 0 | 0
2025-04-05 03:00 | 23.65 | 31 | 70 | 23.873 | 15.6768 | 42.1288 | 0 | 0 | 0 | 0
2025-04-05 04:00 | 23.4 | 30 | 70 | 23.7818 | 15.5446 | 41.7625 | 0 | 0 | 0 | 0
2025-04-05 05:00 | 23.85 | 22.5 | 70 | 23.9454 | 15.1495 | 38.6435 | 0 | 0 | 0 | 0
2025-04-05 06:00 | 25.45 | 15 | 100 | 24.5243 | 14.9681 | 35.0568 | 0 | 0 | 0 | 0
2025-04-05 07:00 | 27.9 | 12.5 | 100 | 25.3902 | 15.276 | 33.207 | 0 | 0 | 0 | 0
2025-04-05 08:00 | 30.5 | 11 | 100 | 26.2804 | 15.6568 | 31.7706 | 0 | 0 | 0 | 0
2025-04-05 09:00 | 33.5 | 9 | 100 | 27.2728 | 16.0175 | 29.9706 | 0 | 0 | 0 | 0
2025-04-05 10:00 | 36.3 | 7.5 | 100 | 28.1648 | 16.34 | 28.4686 | 0 | 0 | 0 | 0
2025-04-05 11:00 | 38.15 | 6.5 | 100 | 28.7371 | 16.5229 | 27.452 | 0 | 0 | 0 | 0
2025-04-05 12:00 | 39.25 | 5.5 | 100 | 29.0741 | 16.5605 | 26.5611 | 0 | 0 | 0 | 0
2025-04-05 13:00 | 39.9 | 5 | 100 | 29.2708 | 16.5876 | 26.0872 | 0 | 0 | 0 | 0
2025-04-05 14:00 | 39.3 | 8 | 100 | 29.0711 | 16.9212 | 28.2749 | 0 | 0 | 0 | 0
2025-04-05 15:00 | 37.15 | 14.5 | 100 | 28.3885 | 17.3738 | 32.7801 | 0 | 0 | 0 | 0
2025-04-05 16:00 | 34.5 | 21 | 100 | 27.5478 | 17.5399 | 36.7734 | 2.0332 | 2.0332 | 0 | 0
2025-04-05 17:00 | 32.25 | 30 | 100 | 26.8112 | 17.8858 | 41.6427 | 37.629 | 37.629 | 0 | 0
2025-04-05 18:00 | 30.2 | 39 | 100 | 26.1308 | 18.1144 | 45.9623 | 65.5189 | 65.5189 | 0 | 0
2025-04-05 19:00 | 28.85 | 40.5 | 100 | 25.6831 | 17.8358 | 46.4252 | 57.844 | 57.844 | 0 | 0
2025-04-05 20:00 | 28.2 | 39 | 100 | 25.4666 | 17.5242 | 45.6069 | 43.4583 | 43.4583 | 0 | 0
2025-04-05 21:00 | 27.15 | 39 | 100 | 25.1089 | 17.2171 | 45.4777 | 32.4423 | 32.4423 | 0 | 0
2025-04-05 22:00 | 26.05 | 39 | 70 | 24.7277 | 16.8973 | 45.386 | 14.9236 | 14.9236 | 0 | 0
2025-04-05 23:00 | 25.2 | 37.5 | 70 | 24.4291 | 16.5467 | 44.7106 | 4.7772 | 4.7772 | 0 | 0
2025-04-06 | 24.45 | 33.5 | 70 | 24.1621 | 16.061 | 43.0601 | 0 | 0 | 0 | 0
2025-04-06 01:00 | 23.75 | 30 | 70 | 23.9093 | 15.6367 | 41.7044 | 0 | 0 | 0 | 0
2025-04-06 02:00 | 23.05 | 27.5 | 70 | 23.6533 | 15.2909 | 40.8248 | 0 | 0 | 0 | 0
2025-04-06 03:00 | 22.45 | 24.5 | 70 | 23.4313 | 14.947 | 39.785 | 0 | 0 | 0 | 0
2025-04-06 04:00 | 21.95 | 23.5 | 70 | 23.2451 | 14.7618 | 39.5342 | 0 | 0 | 0 | 0
2025-04-06 05:00 | 21.4 | 24.5 | 70 | 23.0396 | 14.6919 | 40.0679 | 0 | 0 | 0 | 0
2025-04-06 06:00 | 21.85 | 24 | 100 | 23.2079 | 14.7704 | 39.7459 | 0 | 0 | 0 | 0
2025-04-06 07:00 | 24.65 | 19.5 | 100 | 24.2357 | 15.127 | 37.1899 | 0 | 0 | 0 | 0
2025-04-06 08:00 | 29.2 | 13.5 | 100 | 25.8365 | 15.6299 | 33.3431 | 0 | 0 | 0 | 0
2025-04-06 09:00 | 33.5 | 10.5 | 100 | 27.268 | 16.1825 | 30.8225 | 0 | 0 | 0 | 0
2025-04-06 10:00 | 36.35 | 9.5 | 100 | 28.1705 | 16.5985 | 29.705 | 0 | 0 | 0 | 0
2025-04-06 11:00 | 38 | 8.5 | 100 | 28.6795 | 16.7663 | 28.7994 | 0 | 0 | 0 | 0
2025-04-06 12:00 | 38.95 | 8 | 100 | 28.9672 | 16.8631 | 28.3212 | 0 | 0 | 0 | 0
2025-04-06 13:00 | 39.45 | 8.5 | 100 | 29.1117 | 17.0191 | 28.5944 | 0 | 0 | 0 | 0
2025-04-06 14:00 | 39.4 | 9.5 | 100 | 29.0897 | 17.1502 | 29.2928 | 0 | 0 | 0 | 0
2025-04-06 15:00 | 38.45 | 11 | 100 | 28.7986 | 17.1781 | 30.411 | 0 | 0 | 0 | 0
2025-04-06 16:00 | 36.45 | 15.5 | 100 | 28.1715 | 17.3477 | 33.4466 | 0 | 0 | 0 | 0
2025-04-06 17:00 | 33.3 | 28 | 100 | 27.1488 | 17.9695 | 40.6774 | 35.8567 | 35.8567 | 0 | 0
2025-04-06 18:00 | 30.3 | 41.5 | 100 | 26.1589 | 18.3561 | 47.2398 | 79.792 | 79.792 | 0 | 0
2025-04-06 19:00 | 28.9 | 45 | 100 | 25.6939 | 18.2092 | 48.5891 | 80.4843 | 80.4843 | 0 | 0
2025-04-06 20:00 | 28.1 | 47 | 100 | 25.4246 | 18.1119 | 49.3178 | 80.1449 | 80.1449 | 0 | 0
2025-04-06 21:00 | 27.05 | 52 | 100 | 25.0653 | 18.1429 | 51.2993 | 89.5739 | 89.5739 | 0 | 0
2025-04-06 22:00 | 26 | 53 | 70 | 24.7041 | 17.8679 | 51.4436 | 56.2379 | 56.2379 | 0 | 0
2025-04-06 23:00 | 25 | 52 | 70 | 24.3551 | 17.4735 | 50.7826 | 44.6217 | 44.6217 | 0 | 0
2025-04-07 | 24.15 | 51.5 | 70 | 24.0536 | 17.1671 | 50.4189 | 36.1484 | 36.1484 | 0 | 0
2025-04-07 01:00 | 23.35 | 52 | 70 | 23.7662 | 16.9421 | 50.4984 | 30.9903 | 30.9903 | 0 | 0
2025-04-07 02:00 | 22.6 | 53 | 70 | 23.4938 | 16.7619 | 50.7918 | 27.5515 | 27.5515 | 0 | 0
2025-04-07 03:00 | 22.25 | 51.5 | 70 | 23.3652 | 16.5611 | 50.1832 | 21.1045 | 21.1045 | 0 | 0
2025-04-07 04:00 | 22 | 45.5 | 70 | 23.2711 | 16.1266 | 47.8954 | 4.5733 | 4.5733 | 0 | 0
2025-04-07 05:00 | 21.5 | 41 | 70 | 23.0838 | 15.7119 | 46.219 | 0 | 0 | 0 | 0
2025-04-07 06:00 | 21.75 | 38.5 | 100 | 23.1759 | 15.6354 | 45.2554 | 0 | 0 | 0 | 0
2025-04-07 07:00 | 24.4 | 31.5 | 100 | 24.1443 | 15.9109 | 42.2343 | 0 | 0 | 0 | 0
2025-04-07 08:00 | 29 | 23 | 100 | 25.7559 | 16.4227 | 38.008 | 0 | 0 | 0 | 0
2025-04-07 09:00 | 33 | 17 | 100 | 27.0873 | 16.7754 | 34.5411 | 0 | 0 | 0 | 0
2025-04-07 10:00 | 35.55 | 13.5 | 100 | 27.9044 | 16.9268 | 32.2687 | 0 | 0 | 0 | 0
2025-04-07 11:00 | 37.45 | 11 | 100 | 28.4986 | 16.9927 | 30.5035 | 0 | 0 | 0 | 0
2025-04-07 12:00 | 38.45 | 10 | 100 | 28.805 | 17.0475 | 29.7339 | 0 | 0 | 0 | 0
2025-04-07 13:00 | 37.8 | 12 | 100 | 28.5982 | 17.1873 | 31.1217 | 0 | 0 | 0 | 0
2025-04-07 14:00 | 36.4 | 16 | 100 | 28.1537 | 17.399 | 33.7529 | 0 | 0 | 0 | 0
2025-04-07 15:00 | 35.25 | 20.5 | 100 | 27.7815 | 17.6625 | 36.4954 | 4.5692 | 4.5692 | 0 | 0
2025-04-07 16:00 | 34.3 | 22.5 | 100 | 27.4799 | 17.6541 | 37.6362 | 10.1608 | 10.1608 | 0 | 0
2025-04-07 17:00 | 32.55 | 27.5 | 100 | 26.9134 | 17.7237 | 40.3232 | 25.8198 | 25.8198 | 0 | 0
2025-04-07 18:00 | 30.05 | 40 | 100 | 26.08 | 18.1546 | 46.4287 | 69.0077 | 69.0077 | 0 | 0
2025-04-07 19:00 | 28.5 | 49 | 100 | 25.5562 | 18.3932 | 50.3638 | 94.6723 | 94.6723 | 0 | 0
2025-04-07 20:00 | 27.75 | 53 | 100 | 25.3012 | 18.4474 | 51.971 | 103.3722 | 103.3722 | 0 | 0
2025-04-07 21:00 | 27 | 56.5 | 100 | 25.0451 | 18.4472 | 53.2849 | 108.764 | 108.764 | 0 | 0
2025-04-07 22:00 | 26.3 | 59.5 | 70 | 24.8044 | 18.4145 | 54.3492 | 78.3376 | 78.3376 | 0 | 0
2025-04-07 23:00 | 25.5 | 60.5 | 70 | 24.5278 | 18.2035 | 54.494 | 73.3799 | 73.3799 | 0 | 0
2025-04-08 | 24.6 | 59 | 70 | 24.2129 | 17.7956 | 53.5881 | 60.5892 | 60.5892 | 0 | 0
2025-04-08 01:00 | 23.85 | 57 | 70 | 23.9464 | 17.4158 | 52.5888 | 48.4106 | 48.4106 | 0 | 0
2025-04-08 02:00 | 23.45 | 54.5 | 70 | 23.8026 | 17.128 | 51.5168 | 38.4176 | 38.4176 | 0 | 0
2025-04-08 03:00 | 23.3 | 51.5 | 70 | 23.7481 | 16.893 | 50.3095 | 29.3921 | 29.3921 | 0 | 0
2025-04-08 04:00 | 22.8 | 47.5 | 70 | 23.5656 | 16.4894 | 48.6968 | 15.3038 | 15.3038 | 0 | 0
2025-04-08 05:00 | 22.3 | 43 | 70 | 23.3811 | 16.064 | 46.9497 | 0.4975 | 0.4975 | 0 | 0
2025-04-08 06:00 | 22.5 | 39.5 | 100 | 23.4537 | 15.9078 | 45.5901 | 0 | 0 | 0 | 0
2025-04-08 07:00 | 24.4 | 34 | 100 | 24.1441 | 16.0809 | 43.2764 | 0 | 0 | 0 | 0
2025-04-08 08:00 | 27.65 | 28.5 | 100 | 25.2893 | 16.5398 | 40.7043 | 0 | 0 | 0 | 0
2025-04-08 09:00 | 30.55 | 30 | 100 | 26.2617 | 17.4311 | 41.4689 | 21.3766 | 21.3766 | 0 | 0
2025-04-08 10:00 | 32.85 | 33 | 100 | 26.9924 | 18.3414 | 43.3509 | 61.2433 | 61.2433 | 0 | 0
2025-04-08 11:00 | 34.4 | 32.5 | 100 | 27.4731 | 18.7291 | 43.4032 | 75.0818 | 75.0818 | 0 | 0
2025-04-08 12:00 | 34.95 | 32.5 | 100 | 27.6397 | 18.8842 | 43.5399 | 81.2652 | 81.2652 | 0 | 0
2025-04-08 13:00 | 35.1 | 32.5 | 100 | 27.6848 | 18.9264 | 43.5826 | 83.0129 | 83.0129 | 0 | 0
2025-04-08 14:00 | 35.15 | 31.5 | 100 | 27.7041 | 18.834 | 43.0109 | 77.0601 | 77.0601 | 0 | 0
2025-04-08 15:00 | 34.85 | 31 | 100 | 27.6157 | 18.6966 | 42.6523 | 70.551 | 70.551 | 0 | 0
2025-04-08 16:00 | 33.6 | 33.5 | 100 | 27.2242 | 18.5999 | 43.8046 | 72.6599 | 72.6599 | 0 | 0
2025-04-08 17:00 | 31.5 | 40.5 | 100 | 26.5465 | 18.6355 | 47.0515 | 88.9336 | 88.9336 | 0 | 0
2025-04-08 18:00 | 29.8 | 46.5 | 100 | 25.9877 | 18.614 | 49.5763 | 99.3209 | 99.3209 | 0 | 0
2025-04-08 19:00 | 28.85 | 48.5 | 100 | 25.6729 | 18.4678 | 50.2413 | 96.8778 | 96.8778 | 0 | 0
2025-04-08 20:00 | 28.05 | 51 | 100 | 25.4038 | 18.3981 | 51.1578 | 98.2262 | 98.2262 | 0 | 0
2025-04-08 21:00 | 27.25 | 55 | 100 | 25.1309 | 18.4243 | 52.7119 | 105.662 | 105.662 | 0 | 0
2025-04-08 22:00 | 26.55 | 59.5 | 70 | 24.8899 | 18.5011 | 54.4508 | 80.8891 | 80.8891 | 0 | 0
2025-04-08 23:00 | 25.7 | 64.5 | 70 | 24.5957 | 18.537 | 56.2672 | 86.9152 | 86.9152 | 0 | 0
2025-04-09 | 24.75 | 68.5 | 70 | 24.2643 | 18.4499 | 57.5398 | 88.1665 | 88.1665 | 0 | 0
2025-04-09 01:00 | 24 | 70 | 70 | 24 | 18.2685 | 57.8394 | 84.2933 | 84.2933 | 0 | 0
2025-04-09 02:00 | 23.4 | 71 | 70 | 23.7864 | 18.1084 | 57.9984 | 80.6169 | 80.6169 | 0 | 0
2025-04-09 03:00 | 22.9 | 72.5 | 70 | 23.6071 | 18.0125 | 58.3879 | 79.1981 | 79.1981 | 0 | 0
2025-04-09 04:00 | 22.85 | 70 | 70 | 23.5885 | 17.8497 | 57.4081 | 72.4389 | 72.4389 | 0 | 0
2025-04-09 05:00 | 22.7 | 68 | 70 | 23.5338 | 17.6799 | 56.588 | 65.9442 | 65.9442 | 0 | 0
2025-04-09 06:00 | 22.75 | 67.5 | 100 | 23.5518 | 17.6689 | 56.4083 | 93.0948 | 93.0948 | 0 | 0
2025-04-09 07:00 | 24.35 | 61.5 | 100 | 24.1243 | 17.8684 | 54.537 | 92.9495 | 92.9495 | 0 | 0
2025-04-09 08:00 | 26.95 | 52.5 | 100 | 25.0308 | 18.1453 | 51.4976 | 90.5325 | 90.5325 | 0 | 0
2025-04-09 09:00 | 29.3 | 45 | 100 | 25.8262 | 18.3352 | 48.6883 | 85.3412 | 85.3412 | 0 | 0
2025-04-09 10:00 | 31.05 | 40 | 100 | 26.4039 | 18.4563 | 46.6615 | 80.6619 | 80.6619 | 0 | 0
2025-04-09 11:00 | 32.15 | 37 | 100 | 26.7611 | 18.5158 | 45.3673 | 76.864 | 76.864 | 0 | 0
2025-04-09 12:00 | 32.6 | 36 | 100 | 26.9053 | 18.5539 | 44.9426 | 76.2961 | 76.2961 | 0 | 0
2025-04-09 13:00 | 32.6 | 37 | 100 | 26.9025 | 18.6466 | 45.4896 | 82.2001 | 82.2001 | 0 | 0
2025-04-09 14:00 | 32.2 | 39 | 100 | 26.7716 | 18.7115 | 46.4634 | 89.0681 | 89.0681 | 0 | 0
2025-04-09 15:00 | 31.5 | 41.5 | 100 | 26.5442 | 18.7221 | 47.5854 | 94.5995 | 94.5995 | 0 | 0
2025-04-09 16:00 | 30.45 | 47.5 | 100 | 26.1962 | 18.9034 | 50.3092 | 113.2396 | 113.2396 | 0 | 0
2025-04-09 17:00 | 29.1 | 54 | 100 | 25.7479 | 18.9746 | 52.9715 | 127.2323 | 127.2323 | 0 | 0
2025-04-09 18:00 | 27.75 | 59.5 | 100 | 25.2952 | 18.9182 | 54.9662 | 133.3576 | 133.3576 | 0 | 0
2025-04-09 19:00 | 26.7 | 64 | 100 | 24.9382 | 18.8604 | 56.5091 | 137.4032 | 137.4032 | 0 | 0
2025-04-09 20:00 | 25.75 | 67.5 | 100 | 24.6118 | 18.7501 | 57.5828 | 137.4679 | 137.4679 | 0 | 0
2025-04-09 21:00 | 24.75 | 72 | 100 | 24.2638 | 18.667 | 58.9911 | 139.8049 | 139.8049 | 0 | 0
2025-04-09 22:00 | 23.85 | 75.5 | 70 | 23.9469 | 18.5422 | 59.9761 | 97.192 | 97.192 | 0 | 0
2025-04-09 23:00 | 22.95 | 78.5 | 70 | 23.6263 | 18.3749 | 60.7255 | 94.7778 | 94.7778 | 0 | 0
2025-04-10 | 22.1 | 81.5 | 70 | 23.3198 | 18.2174 | 61.4714 | 92.587 | 92.587 | 0 | 0
2025-04-10 01:00 | 21.4 | 83.5 | 70 | 23.0646 | 18.0551 | 61.8965 | 89.4691 | 89.4691 | 0 | 0
2025-04-10 02:00 | 20.75 | 84.5 | 70 | 22.8249 | 17.8563 | 61.9772 | 84.5387 | 84.5387 | 0 | 0
2025-04-10 03:00 | 20 | 86 | 70 | 22.5457 | 17.6424 | 62.1957 | 79.597 | 79.597 | 0 | 0
2025-04-10 04:00 | 19.85 | 87 | 70 | 22.4899 | 17.6346 | 62.4811 | 80.0928 | 80.0928 | 0 | 0
2025-04-10 05:00 | 19.95 | 86.5 | 70 | 22.5272 | 17.6487 | 62.3454 | 80.0999 | 80.0999 | 0 | 0
2025-04-10 06:00 | 20.3 | 82.5 | 100 | 22.6561 | 17.5813 | 61.0832 | 107.4384 | 107.4384 | 0 | 0
2025-04-10 07:00 | 22.2 | 72.5 | 100 | 23.3533 | 17.7553 | 58.1429 | 102.9342 | 102.9342 | 0 | 0
2025-04-10 08:00 | 25.15 | 60 | 100 | 24.406 | 18.0474 | 54.1926 | 98.1968 | 98.1968 | 0 | 0
2025-04-10 09:00 | 28.1 | 48.5 | 100 | 25.4231 | 18.2237 | 50.0324 | 87.372 | 87.372 | 0 | 0
2025-04-10 10:00 | 30.8 | 38 | 100 | 26.3275 | 18.2035 | 45.6012 | 67.2027 | 67.2027 | 0 | 0
2025-04-10 11:00 | 32.85 | 31 | 100 | 26.9983 | 18.1423 | 42.2874 | 49.696 | 49.696 | 0 | 0
2025-04-10 12:00 | 33.45 | 34 | 100 | 27.1762 | 18.6035 | 44.0663 | 74.232 | 74.232 | 0 | 0
2025-04-10 13:00 | 32.9 | 40 | 100 | 26.9871 | 19.0142 | 47.2309 | 103.694 | 103.694 | 0 | 0
2025-04-10 14:00 | 32.35 | 40 | 100 | 26.8159 | 18.845 | 47.0682 | 96.9257 | 96.9257 | 0 | 0
2025-04-10 15:00 | 32.15 | 38.5 | 100 | 26.7572 | 18.646 | 46.2158 | 85.975 | 85.975 | 0 | 0
2025-04-10 16:00 | 31.45 | 35 | 100 | 26.5433 | 18.1203 | 44.2163 | 58.3576 | 58.3576 | 0 | 0
2025-04-10 17:00 | 30.05 | 35 | 100 | 26.0887 | 17.7201 | 43.9936 | 43.5938 | 43.5938 | 0 | 0
2025-04-10 18:00 | 28.15 | 51.5 | 100 | 25.4367 | 18.4628 | 51.4763 | 102.4565 | 102.4565 | 0 | 0
2025-04-10 19:00 | 26.45 | 71.5 | 100 | 24.849 | 19.2706 | 59.6847 | 165.7421 | 165.7421 | 0 | 0
2025-04-10 20:00 | 25.5 | 81.5 | 100 | 24.521 | 19.5436 | 63.3671 | 190.3669 | 190.3669 | 0 | 0
2025-04-10 21:00 | 24.7 | 87.5 | 100 | 24.2441 | 19.5869 | 65.3038 | 199.2037 | 199.2037 | 0 | 0
2025-04-10 22:00 | 23.9 | 91.5 | 70 | 23.965 | 19.4923 | 66.3562 | 139.493 | 139.493 | 0 | 0
2025-04-10 23:00 | 23 | 94.5 | 70 | 23.6472 | 19.288 | 66.9116 | 135.2517 | 135.2517 | 0 | 0
2025-04-11 | 22.05 | 96.5 | 70 | 23.3067 | 19.0015 | 67.0433 | 127.7305 | 127.7305 | 0 | 0
2025-04-11 01:00 | 21.4 | 97 | 70 | 23.0705 | 18.7593 | 66.8248 | 120.6005 | 120.6005 | 0 | 0
2025-04-11 02:00 | 20.9 | 97 | 70 | 22.8868 | 18.5527 | 66.5318 | 114.3416 | 114.3416 | 0 | 0
2025-04-11 03:00 | 20.35 | 95.5 | 70 | 22.6822 | 18.2533 | 65.6996 | 104.3147 | 104.3147 | 0 | 0
2025-04-11 04:00 | 20.4 | 89.5 | 70 | 22.6974 | 17.9735 | 63.6246 | 91.8577 | 91.8577 | 0 | 0
2025-04-11 05:00 | 20.55 | 79.5 | 70 | 22.7478 | 17.5207 | 60.1556 | 71.4913 | 71.4913 | 0 | 0
2025-04-11 06:00 | 21.15 | 68.5 | 100 | 22.9655 | 17.1546 | 56.3826 | 75.098 | 75.098 | 0 | 0
2025-04-11 07:00 | 23.85 | 55 | 100 | 23.9463 | 17.2855 | 51.8406 | 62.0815 | 62.0815 | 0 | 0
2025-04-11 08:00 | 28.05 | 39.5 | 100 | 25.4155 | 17.5114 | 45.8757 | 44.8128 | 44.8128 | 0 | 0
2025-04-11 09:00 | 31.55 | 28.5 | 100 | 26.5905 | 17.5494 | 40.8176 | 22.8837 | 22.8837 | 0 | 0
2025-04-11 10:00 | 33.8 | 22.5 | 100 | 27.324 | 17.5231 | 37.6571 | 6.5288 | 6.5288 | 0 | 0
2025-04-11 11:00 | 35.25 | 20 | 100 | 27.784 | 17.5952 | 36.2387 | 1.6753 | 1.6753 | 0 | 0
2025-04-11 12:00 | 35.9 | 21.5 | 100 | 27.9756 | 17.9185 | 37.1722 | 17.1851 | 17.1851 | 0 | 0
2025-04-11 13:00 | 35.45 | 25.5 | 100 | 27.8209 | 18.256 | 39.5471 | 40.6457 | 40.6457 | 0 | 0
2025-04-11 14:00 | 34.1 | 28 | 100 | 27.398 | 18.1701 | 40.8334 | 44.1608 | 44.1608 | 0 | 0
2025-04-11 15:00 | 32.55 | 31.5 | 100 | 26.9025 | 18.0994 | 42.5566 | 50.0843 | 50.0843 | 0 | 0
2025-04-11 16:00 | 31.15 | 38 | 100 | 26.4404 | 18.2996 | 45.7264 | 71.714 | 71.714 | 0 | 0
2025-04-11 17:00 | 29.95 | 44 | 100 | 26.0407 | 18.4483 | 48.4506 | 89.1188 | 89.1188 | 0 | 0
2025-04-11 18:00 | 28.6 | 52 | 100 | 25.5858 | 18.6486 | 51.8762 | 111.0386 | 111.0386 | 0 | 0
2025-04-11 19:00 | 27.55 | 59 | 100 | 25.2287 | 18.8088 | 54.6975 | 128.578 | 128.578 | 0 | 0
2025-04-11 20:00 | 26.75 | 62 | 100 | 24.9565 | 18.7381 | 55.6954 | 129.9505 | 129.9505 | 0 | 0
2025-04-11 21:00 | 26.05 | 61 | 100 | 24.7178 | 18.4236 | 54.9762 | 115.4008 | 115.4008 | 0 | 0
2025-04-11 22:00 | 25.55 | 57.5 | 70 | 24.5462 | 18.0158 | 53.3103 | 65.7272 | 65.7272 | 0 | 0
2025-04-11 23:00 | 24.8 | 54.5 | 70 | 24.2841 | 17.5656 | 51.8516 | 50.4044 | 50.4044 | 0 | 0
2025-04-12 | 24.05 | 51 | 70 | 24.0179 | 17.095 | 50.2753 | 34.4885 | 34.4885 | 0 | 0
2025-04-12 01:00 | 23.35 | 49 | 70 | 23.7658 | 16.7462 | 49.3882 | 23.6793 | 23.6793 | 0 | 0
2025-04-12 02:00 | 22.6 | 48 | 70 | 23.4926 | 16.4518 | 48.9402 | 15.5007 | 15.5007 | 0 | 0
2025-04-12 03:00 | 22.2 | 45 | 70 | 23.3447 | 16.1477 | 47.7773 | 5.1806 | 5.1806 | 0 | 0
2025-04-12 04:00 | 22.25 | 42.5 | 70 | 23.3624 | 16.0109 | 46.8218 | 0 | 0 | 0 | 0
2025-04-12 05:00 | 22.3 | 40.5 | 70 | 23.3803 | 15.9031 | 46.0524 | 0 | 0 | 0 | 0
2025-04-12 06:00 | 22.95 | 34.5 | 100 | 23.6179 | 15.7085 | 43.6667 | 0 | 0 | 0 | 0
2025-04-12 07:00 | 25.65 | 26 | 100 | 24.5921 | 15.827 | 39.8289 | 0 | 0 | 0 | 0
2025-04-12 08:00 | 30 | 18.5 | 100 | 26.0999 | 16.2405 | 35.7365 | 0 | 0 | 0 | 0
2025-04-12 09:00 | 34.3 | 12.5 | 100 | 27.5173 | 16.5424 | 31.8865 | 0 | 0 | 0 | 0
2025-04-12 10:00 | 37.5 | 9.5 | 100 | 28.5232 | 16.7894 | 29.5782 | 0 | 0 | 0 | 0
2025-04-12 11:00 | 39.2 | 9.5 | 100 | 29.0315 | 17.0997 | 29.3523 | 0 | 0 | 0 | 0
2025-04-12 12:00 | 39.35 | 10.5 | 100 | 29.0683 | 17.2674 | 30.0209 | 0 | 0 | 0 | 0
2025-04-12 13:00 | 38.1 | 12 | 100 | 28.6886 | 17.2307 | 31.1406 | 0 | 0 | 0 | 0
2025-04-12 14:00 | 37.05 | 14.5 | 100 | 28.3589 | 17.3387 | 32.8296 | 0 | 0 | 0 | 0
2025-04-12 15:00 | 36.25 | 17.5 | 100 | 28.1011 | 17.5313 | 34.7328 | 0 | 0 | 0 | 0
2025-04-12 16:00 | 34.8 | 23 | 100 | 27.6331 | 17.8191 | 38.0007 | 18.1353 | 18.1353 | 0 | 0
2025-04-12 17:00 | 33.1 | 31.5 | 100 | 27.0753 | 18.2541 | 42.6323 | 55.5859 | 55.5859 | 0 | 0
2025-04-12 18:00 | 31 | 40.5 | 100 | 26.3868 | 18.4767 | 46.9596 | 83.3643 | 83.3643 | 0 | 0
2025-04-12 19:00 | 29.4 | 46 | 100 | 25.8576 | 18.4399 | 49.2564 | 92.1656 | 92.1656 | 0 | 0
2025-04-12 20:00 | 28.7 | 42 | 100 | 25.6312 | 17.9031 | 47.1627 | 64.0036 | 64.0036 | 0 | 0
2025-04-12 21:00 | 28.3 | 36.5 | 100 | 25.5032 | 17.3472 | 44.5021 | 33.1275 | 33.1275 | 0 | 0
2025-04-12 22:00 | 27.9 | 34.5 | 70 | 25.3695 | 17.0747 | 43.5352 | 13.7769 | 13.7769 | 0 | 0
2025-04-12 23:00 | 27.3 | 34 | 70 | 25.1644 | 16.8689 | 43.2794 | 8.2109 | 8.2109 | 0 | 0
2025-04-13 | 26.6 | 36 | 70 | 24.921 | 16.8257 | 44.156 | 9.9383 | 9.9383 | 0 | 0
2025-04-13 01:00 | 25.95 | 36.5 | 70 | 24.6939 | 16.6788 | 44.3583 | 7.1898 | 7.1898 | 0 | 0
2025-04-13 02:00 | 25.15 | 35.5 | 70 | 24.4118 | 16.3825 | 43.93 | 0 | 0 | 0 | 0
2025-04-13 03:00 | 24.3 | 34.5 | 70 | 24.1082 | 16.0789 | 43.5457 | 0 | 0 | 0 | 0
2025-04-13 04:00 | 25.1 | 32 | 70 | 24.3949 | 16.1212 | 42.4499 | 0 | 0 | 0 | 0
2025-04-13 05:00 | 26.5 | 30 | 70 | 24.8896 | 16.3459 | 41.4939 | 0 | 0 | 0 | 0
2025-04-13 06:00 | 27.75 | 26 | 100 | 25.326 | 16.3551 | 39.5869 | 0 | 0 | 0 | 0
2025-04-13 07:00 | 30.35 | 23 | 100 | 26.2088 | 16.7391 | 37.9539 | 0 | 0 | 0 | 0
2025-04-13 08:00 | 33.25 | 25 | 100 | 27.1426 | 17.6507 | 39.0185 | 17.2329 | 17.2329 | 0 | 0
2025-04-13 09:00 | 35.75 | 24.5 | 100 | 27.916 | 18.2301 | 38.9473 | 36.2033 | 36.2033 | 0 | 0
2025-04-13 10:00 | 37.95 | 21 | 100 | 28.5875 | 18.3602 | 36.9951 | 30.4617 | 30.4617 | 0 | 0
2025-04-13 11:00 | 39.8 | 18 | 100 | 29.1407 | 18.4037 | 35.1542 | 22.0214 | 22.0214 | 0 | 0
2025-04-13 12:00 | 41.2 | 15.5 | 100 | 29.5555 | 18.3622 | 33.4818 | 11.4114 | 11.4114 | 0 | 0
2025-04-13 13:00 | 42.15 | 13 | 100 | 29.8432 | 18.1867 | 31.6778 | 0 | 0 | 0 | 0
2025-04-13 14:00 | 41.6 | 15 | 100 | 29.6714 | 18.3726 | 33.1452 | 9.9623 | 9.9623 | 0 | 0
2025-04-13 15:00 | 39.35 | 18 | 100 | 29.0126 | 18.2976 | 35.1307 | 18.5842 | 18.5842 | 0 | 0
2025-04-13 16:00 | 37.65 | 16 | 100 | 28.5298 | 17.6612 | 33.7498 | 0 | 0 | 0 | 0
2025-04-13 17:00 | 36.15 | 16 | 100 | 28.0778 | 17.338 | 33.7855 | 0 | 0 | 0 | 0
2025-04-13 18:00 | 33.85 | 20.5 | 100 | 27.3465 | 17.3274 | 36.5026 | 0 | 0 | 0 | 0
2025-04-13 19:00 | 31.95 | 26 | 100 | 26.7255 | 17.42 | 39.4968 | 11.9567 | 11.9567 | 0 | 0
2025-04-13 20:00 | 30.8 | 29 | 100 | 26.3456 | 17.402 | 41.0021 | 18.554 | 18.554 | 0 | 0
2025-04-13 21:00 | 30.05 | 28.5 | 100 | 26.0996 | 17.1606 | 40.71 | 9.1494 | 9.1494 | 0 | 0
2025-04-13 22:00 | 29.25 | 27.5 | 70 | 25.8343 | 16.8668 | 40.2063 | 0 | 0 | 0 | 0
2025-04-13 23:00 | 28.35 | 28 | 70 | 25.5293 | 16.6767 | 40.4651 | 0 | 0 | 0 | 0
2025-04-14 | 27.45 | 30 | 70 | 25.2192 | 16.6023 | 41.4235 | 0 | 0 | 0 | 0
2025-04-14 01:00 | 26.75 | 32 | 70 | 24.9755 | 16.5699 | 42.3475 | 0 | 0 | 0 | 0
2025-04-14 02:00 | 26.2 | 34 | 70 | 24.7826 | 16.5696 | 43.2412 | 1.0476 | 1.0476 | 0 | 0
2025-04-14 03:00 | 25.35 | 37.5 | 70 | 24.4822 | 16.584 | 44.7472 | 5.9978 | 5.9978 | 0 | 0
2025-04-14 04:00 | 24.9 | 38.5 | 70 | 24.3223 | 16.5256 | 45.1605 | 5.8905 | 5.8905 | 0 | 0
2025-04-14 05:00 | 24.75 | 37 | 70 | 24.2691 | 16.3804 | 44.5301 | 0.6464 | 0.6464 | 0 | 0
2025-04-14 06:00 | 25.1 | 34 | 100 | 24.3944 | 16.2694 | 43.2542 | 0 | 0 | 0 | 0
2025-04-14 07:00 | 27.9 | 27.5 | 100 | 25.3761 | 16.521 | 40.2411 | 0 | 0 | 0 | 0
2025-04-14 08:00 | 32.35 | 21.5 | 100 | 26.8658 | 17.0819 | 37.0636 | 0 | 0 | 0 | 0
2025-04-14 09:00 | 36.2 | 18.5 | 100 | 28.0806 | 17.652 | 35.3011 | 0 | 0 | 0 | 0
2025-04-14 10:00 | 38.95 | 16.5 | 100 | 28.9079 | 18.0165 | 34.0702 | 3.1524 | 3.1524 | 0 | 0
2025-04-14 11:00 | 40.85 | 13.5 | 100 | 29.4753 | 18.0025 | 32.0182 | 0 | 0 | 0 | 0
2025-04-14 12:00 | 41.9 | 12 | 100 | 29.7838 | 17.9879 | 30.9214 | 0 | 0 | 0 | 0
2025-04-14 13:00 | 42.05 | 12.5 | 100 | 29.8205 | 18.0922 | 31.2975 | 0 | 0 | 0 | 0
2025-04-14 14:00 | 40.7 | 14.5 | 100 | 29.4244 | 18.1111 | 32.7454 | 0 | 0 | 0 | 0
2025-04-14 15:00 | 38.45 | 17.5 | 100 | 28.7559 | 18.0305 | 34.7404 | 7.6044 | 7.6044 | 0 | 0
2025-04-14 16:00 | 36.45 | 21.5 | 100 | 28.1411 | 18.0564 | 37.1876 | 21.5022 | 21.5022 | 0 | 0
2025-04-14 17:00 | 34.65 | 28 | 100 | 27.5669 | 18.3234 | 40.882 | 49.1815 | 49.1815 | 0 | 0
2025-04-14 18:00 | 32.9 | 34.5 | 100 | 27.0036 | 18.4943 | 44.2175 | 71.0954 | 71.0954 | 0 | 0
2025-04-14 19:00 | 31.85 | 36 | 100 | 26.6686 | 18.3322 | 44.7908 | 68.0236 | 68.0236 | 0 | 0
2025-04-14 20:00 | 31.55 | 34 | 100 | 26.5776 | 18.0635 | 43.6754 | 53.4569 | 53.4569 | 0 | 0
2025-04-14 21:00 | 31.05 | 32.5 | 100 | 26.4198 | 17.7878 | 42.8197 | 39.9895 | 39.9895 | 0 | 0
2025-04-14 22:00 | 30.5 | 32.5 | 70 | 26.2406 | 17.6355 | 42.7553 | 24.1747 | 24.1747 | 0 | 0
2025-04-14 23:00 | 29.95 | 33.5 | 70 | 26.0582 | 17.5691 | 43.1976 | 24.0614 | 24.0614 | 0 | 0
2025-04-15 | 29.05 | 35.5 | 70 | 25.7564 | 17.4839 | 44.0791 | 24.8806 | 24.8806 | 0 | 0
2025-04-15 01:00 | 28.1 | 39 | 70 | 25.4329 | 17.4906 | 45.6234 | 29.8961 | 29.8961 | 0 | 0
2025-04-15 02:00 | 27.25 | 40.5 | 70 | 25.1422 | 17.355 | 46.2032 | 28.4571 | 28.4571 | 0 | 0
2025-04-15 03:00 | 26.55 | 39.5 | 70 | 24.9016 | 17.0736 | 45.6813 | 20.2313 | 20.2313 | 0 | 0
2025-04-15 04:00 | 26.25 | 41.5 | 70 | 24.7963 | 17.1308 | 46.5325 | 24.1603 | 24.1603 | 0 | 0
2025-04-15 05:00 | 25.8 | 42 | 70 | 24.639 | 17.0329 | 46.7027 | 22.3443 | 22.3443 | 0 | 0
2025-04-15 06:00 | 25.7 | 38.5 | 100 | 24.6053 | 16.7553 | 45.1838 | 16.0809 | 16.0809 | 0 | 0
2025-04-15 07:00 | 27.65 | 33.5 | 100 | 25.2849 | 16.932 | 43.0313 | 12.3389 | 12.3389 | 0 | 0
2025-04-15 08:00 | 31.75 | 25.5 | 100 | 26.6621 | 17.3233 | 39.2143 | 7.2788 | 7.2788 | 0 | 0
2025-04-15 09:00 | 35.75 | 18 | 100 | 27.9459 | 17.4899 | 35.0035 | 0 | 0 | 0 | 0
2025-04-15 10:00 | 37.75 | 16 | 100 | 28.5593 | 17.6882 | 33.7319 | 0 | 0 | 0 | 0
2025-04-15 11:00 | 37.2 | 21.5 | 100 | 28.3642 | 18.2428 | 37.2332 | 27.6482 | 27.6482 | 0 | 0
2025-04-15 12:00 | 35.7 | 29 | 100 | 27.8801 | 18.7171 | 41.6421 | 66.2596 | 66.2596 | 0 | 0
2025-04-15 13:00 | 35.05 | 33 | 100 | 27.6677 | 18.9628 | 43.8725 | 85.8218 | 85.8218 | 0 | 0
2025-04-15 14:00 | 34.45 | 37 | 100 | 27.471 | 19.1958 | 46.0273 | 104.4747 | 104.4747 | 0 | 0
2025-04-15 15:00 | 33.05 | 44 | 100 | 27.0211 | 19.4362 | 49.453 | 129.0138 | 129.0138 | 0 | 0
2025-04-15 16:00 | 32.35 | 46 | 100 | 26.7995 | 19.3916 | 50.2562 | 130.9922 | 130.9922 | 0 | 0
2025-04-15 17:00 | 31.35 | 51.5 | 100 | 26.4738 | 19.5375 | 52.7075 | 147.16 | 147.16 | 0 | 0
2025-04-15 18:00 | 29.15 | 66.5 | 100 | 25.7467 | 19.9367 | 58.9434 | 188.3982 | 188.3982 | 0 | 0
2025-04-15 19:00 | 27.8 | 76.5 | 100 | 25.2957 | 20.1279 | 62.6926 | 210.7132 | 210.7132 | 0 | 0
2025-04-15 20:00 | 27.1 | 80 | 100 | 25.0615 | 20.0859 | 63.76 | 213.0612 | 213.0612 | 0 | 0
2025-04-15 21:00 | 26.45 | 81.5 | 100 | 24.8434 | 19.9234 | 63.9583 | 207.3232 | 207.3232 | 0 | 0
2025-04-15 22:00 | 25.75 | 83 | 70 | 24.6058 | 19.7375 | 64.1204 | 140.396 | 140.396 | 0 | 0
2025-04-15 23:00 | 25 | 85.5 | 70 | 24.3481 | 19.5891 | 64.657 | 137.6867 | 137.6867 | 0 | 0
2025-04-16 | 24.25 | 88.5 | 70 | 24.0875 | 19.4631 | 65.3736 | 136.0523 | 136.0523 | 0 | 0
2025-04-16 01:00 | 23.55 | 91 | 70 | 23.8417 | 19.3206 | 65.8998 | 133.4747 | 133.4747 | 0 | 0
2025-04-16 02:00 | 23.05 | 91.5 | 70 | 23.6644 | 19.1438 | 65.7721 | 128.3172 | 128.3172 | 0 | 0
2025-04-16 03:00 | 22.85 | 90.5 | 70 | 23.5928 | 19.0069 | 65.266 | 123.3178 | 123.3178 | 0 | 0
2025-04-16 04:00 | 23.4 | 88 | 70 | 23.7883 | 19.0898 | 64.6414 | 123.9904 | 123.9904 | 0 | 0
2025-04-16 05:00 | 24 | 87.5 | 70 | 24 | 19.3039 | 64.8186 | 130.2682 | 130.2682 | 0 | 0
2025-04-16 06:00 | 24.7 | 87.5 | 100 | 24.2441 | 19.5869 | 65.2731 | 198.9045 | 198.9045 | 0 | 0
2025-04-16 07:00 | 26.65 | 79 | 100 | 24.912 | 19.8417 | 63.0107 | 200.461 | 200.461 | 0 | 0
2025-04-16 08:00 | 28.9 | 64.5 | 100 | 25.6686 | 19.6977 | 57.8307 | 174.4263 | 174.4263 | 0 | 0
2025-04-16 09:00 | 30.8 | 52 | 100 | 26.2992 | 19.3956 | 52.6858 | 141.4384 | 141.4384 | 0 | 0
2025-04-16 10:00 | 32.25 | 44.5 | 100 | 26.7726 | 19.2284 | 49.3906 | 120.8057 | 120.8057 | 0 | 0
2025-04-16 11:00 | 33 | 40.5 | 100 | 27.0165 | 19.0972 | 47.4991 | 107.4864 | 107.4864 | 0 | 0
2025-04-16 12:00 | 33.3 | 38 | 100 | 27.1169 | 18.9518 | 46.2217 | 96.3725 | 96.3725 | 0 | 0
2025-04-16 13:00 | 33.3 | 36 | 100 | 27.1233 | 18.7581 | 45.1191 | 84.3895 | 84.3895 | 0 | 0
2025-04-16 14:00 | 33.2 | 34.5 | 100 | 27.0971 | 18.583 | 44.269 | 74.2643 | 74.2643 | 0 | 0
2025-04-16 15:00 | 32.85 | 34 | 100 | 26.9895 | 18.4337 | 43.9203 | 67.4315 | 67.4315 | 0 | 0
2025-04-16 16:00 | 31.8 | 37.5 | 100 | 26.649 | 18.4551 | 45.5644 | 75.8409 | 75.8409 | 0 | 0
2025-04-16 17:00 | 30.15 | 45.5 | 100 | 26.1031 | 18.6427 | 49.2024 | 98.8227 | 98.8227 | 0 | 0
2025-04-16 18:00 | 28.35 | 56.5 | 100 | 25.4978 | 18.9081 | 53.8318 | 128.2464 | 128.2464 | 0 | 0
2025-04-16 19:00 | 27.35 | 61.5 | 100 | 25.1595 | 18.9204 | 55.6811 | 136.2217 | 136.2217 | 0 | 0
2025-04-16 20:00 | 27 | 60.5 | 100 | 25.0422 | 18.7267 | 55.0799 | 126.533 | 126.533 | 0 | 0
2025-04-16 21:00 | 26.6 | 59.5 | 100 | 24.907 | 18.5175 | 54.4778 | 116.3522 | 116.3522 | 0 | 0
2025-04-16 22:00 | 26.15 | 57.5 | 70 | 24.7538 | 18.2249 | 53.4476 | 71.0549 | 71.0549 | 0 | 0
2025-04-16 23:00 | 25.65 | 56 | 70 | 24.5815 | 17.9536 | 52.6515 | 61.9694 | 61.9694 | 0 | 0
2025-04-17 | 25.15 | 55.5 | 70 | 24.407 | 17.7522 | 52.3057 | 55.9941 | 55.9941 | 0 | 0
2025-04-17 01:00 | 24.35 | 58 | 70 | 24.1245 | 17.6458 | 53.13 | 55.6837 | 55.6837 | 0 | 0
2025-04-17 02:00 | 23.55 | 67 | 70 | 23.8397 | 17.924 | 56.4941 | 71.9227 | 71.9227 | 0 | 0
2025-04-17 03:00 | 23.3 | 76 | 70 | 23.7513 | 18.3634 | 59.9226 | 92.3998 | 92.3998 | 0 | 0
2025-04-17 04:00 | 23.1 | 81 | 70 | 23.6805 | 18.5753 | 61.7615 | 102.7382 | 102.7382 | 0 | 0
2025-04-17 05:00 | 22.9 | 85.5 | 70 | 23.6097 | 18.75 | 63.3792 | 111.5532 | 111.5532 | 0 | 0
2025-04-17 06:00 | 23.65 | 84 | 100 | 23.8765 | 18.9624 | 63.2172 | 166.8731 | 166.8731 | 0 | 0
2025-04-17 07:00 | 25.65 | 74.5 | 100 | 24.5748 | 19.1644 | 60.4774 | 164.3134 | 164.3134 | 0 | 0
2025-04-17 08:00 | 27.75 | 62 | 100 | 25.2929 | 19.0991 | 56.0789 | 144.456 | 144.456 | 0 | 0
2025-04-17 09:00 | 29.15 | 52 | 100 | 25.767 | 18.8395 | 52.0064 | 117.8803 | 117.8803 | 0 | 0
2025-04-17 10:00 | 29.9 | 47.5 | 100 | 26.0186 | 18.7285 | 50.0901 | 105.6026 | 105.6026 | 0 | 0
2025-04-17 11:00 | 30.45 | 44 | 100 | 26.2028 | 18.6144 | 48.5274 | 94.6482 | 94.6482 | 0 | 0
2025-04-17 12:00 | 30.85 | 41 | 100 | 26.3376 | 18.482 | 47.1264 | 83.7164 | 83.7164 | 0 | 0
2025-04-17 13:00 | 30.85 | 41.5 | 100 | 26.3366 | 18.5248 | 47.386 | 86.449 | 86.449 | 0 | 0
2025-04-17 14:00 | 30.7 | 41.5 | 100 | 26.2883 | 18.4778 | 47.351 | 84.686 | 84.686 | 0 | 0
2025-04-17 15:00 | 30.25 | 42 | 100 | 26.1417 | 18.3811 | 47.4889 | 81.9286 | 81.9286 | 0 | 0
2025-04-17 16:00 | 29.35 | 43 | 100 | 25.8455 | 18.1863 | 47.7575 | 76.2414 | 76.2414 | 0 | 0
2025-04-17 17:00 | 28 | 48.5 | 100 | 25.3895 | 18.1911 | 50.008 | 86.1395 | 86.1395 | 0 | 0
2025-04-17 18:00 | 26.75 | 57.5 | 100 | 24.9594 | 18.4297 | 53.6671 | 109.9454 | 109.9454 | 0 | 0
2025-04-17 19:00 | 26 | 63.5 | 100 | 24.6995 | 18.5769 | 55.9816 | 124.6518 | 124.6518 | 0 | 0
2025-04-17 20:00 | 25.55 | 66 | 100 | 24.5433 | 18.5803 | 56.8511 | 128.18 | 128.18 | 0 | 0
2025-04-17 21:00 | 25.3 | 66 | 100 | 24.4567 | 18.4901 | 56.7417 | 124.3784 | 124.3784 | 0 | 0
2025-04-17 22:00 | 25 | 66.5 | 70 | 24.3521 | 18.4142 | 56.8261 | 85.3237 | 85.3237 | 0 | 0
2025-04-17 23:00 | 24.65 | 68 | 70 | 24.2293 | 18.382 | 57.3023 | 85.8033 | 85.8033 | 0 | 0
2025-04-18 | 24.4 | 69.5 | 70 | 24.1413 | 18.3834 | 57.8123 | 87.2516 | 87.2516 | 0 | 0
2025-04-18 01:00 | 24.2 | 71.5 | 70 | 24.0707 | 18.4324 | 58.5369 | 90.4863 | 90.4863 | 0 | 0
2025-04-18 02:00 | 24 | 73.5 | 70 | 24 | 18.479 | 59.2519 | 93.6244 | 93.6244 | 0 | 0
2025-04-18 03:00 | 23.75 | 75 | 70 | 23.9115 | 18.4744 | 59.7345 | 94.7983 | 94.7983 | 0 | 0
2025-04-18 04:00 | 23.6 | 77 | 70 | 23.8583 | 18.5356 | 60.4504 | 98.2831 | 98.2831 | 0 | 0
2025-04-18 05:00 | 23.45 | 79.5 | 70 | 23.8052 | 18.6239 | 61.3521 | 102.9573 | 102.9573 | 0 | 0
2025-04-18 06:00 | 23.85 | 79 | 100 | 23.947 | 18.7494 | 61.3563 | 151.8116 | 151.8116 | 0 | 0
2025-04-18 07:00 | 25.2 | 71 | 100 | 24.4206 | 18.773 | 58.7817 | 142.8835 | 142.8835 | 0 | 0
2025-04-18 08:00 | 26.5 | 61.5 | 100 | 24.8717 | 18.62 | 55.3093 | 123.4576 | 123.4576 | 0 | 0
2025-04-18 09:00 | 27.45 | 55 | 100 | 25.1985 | 18.4924 | 52.782 | 108.419 | 108.419 | 0 | 0
2025-04-18 10:00 | 28.25 | 50 | 100 | 25.4717 | 18.3886 | 50.7548 | 96.1543 | 96.1543 | 0 | 0
2025-04-18 11:00 | 28.75 | 46.5 | 100 | 25.6423 | 18.2798 | 49.2609 | 85.8987 | 85.8987 | 0 | 0
2025-04-18 12:00 | 28.9 | 46 | 100 | 25.6927 | 18.2872 | 49.0691 | 85.3947 | 85.3947 | 0 | 0
2025-04-18 13:00 | 28.85 | 47 | 100 | 25.6748 | 18.3495 | 49.5365 | 89.6872 | 89.6872 | 0 | 0
2025-04-18 14:00 | 28.65 | 47 | 100 | 25.6084 | 18.2847 | 49.485 | 87.2142 | 87.2142 | 0 | 0
2025-04-18 15:00 | 28.25 | 47.5 | 100 | 25.4744 | 18.1953 | 49.6125 | 84.6007 | 84.6007 | 0 | 0
2025-04-18 16:00 | 27.4 | 51 | 100 | 25.1849 | 18.1825 | 50.9809 | 89.9354 | 89.9354 | 0 | 0
2025-04-18 17:00 | 26.3 | 55.5 | 100 | 24.8065 | 18.137 | 52.6435 | 95.1892 | 95.1892 | 0 | 0
2025-04-18 18:00 | 25.35 | 57.5 | 100 | 24.4765 | 17.9518 | 53.207 | 90.7894 | 90.7894 | 0 | 0
2025-04-18 19:00 | 24.6 | 60.5 | 100 | 24.2127 | 17.8903 | 54.2219 | 92.62 | 92.62 | 0 | 0
2025-04-18 20:00 | 24.1 | 65 | 100 | 24.0355 | 17.9979 | 55.8806 | 103.0041 | 103.0041 | 0 | 0
2025-04-18 21:00 | 23.65 | 68 | 100 | 23.8755 | 18.0205 | 56.9128 | 107.7847 | 107.7847 | 0 | 0
2025-04-18 22:00 | 23.05 | 71.5 | 70 | 23.6609 | 18.0098 | 58.0555 | 78.2247 | 78.2247 | 0 | 0
2025-04-18 23:00 | 22.45 | 75.5 | 70 | 23.4451 | 18.0172 | 59.3512 | 81.8286 | 81.8286 | 0 | 0
2025-04-19 | 21.95 | 78 | 70 | 23.2639 | 17.9683 | 60.0876 | 82.5025 | 82.5025 | 0 | 0
2025-04-19 01:00 | 21.45 | 80.5 | 70 | 23.0817 | 17.9146 | 60.8042 | 82.9649 | 82.9649 | 0 | 0
2025-04-19 02:00 | 21.05 | 83 | 70 | 22.9353 | 17.8947 | 61.5443 | 84.3253 | 84.3253 | 0 | 0
2025-04-19 03:00 | 20.7 | 85.5 | 70 | 22.8068 | 17.8894 | 62.288 | 86.061 | 86.061 | 0 | 0
2025-04-19 04:00 | 20.85 | 86.5 | 70 | 22.863 | 17.9991 | 62.7115 | 89.9778 | 89.9778 | 0 | 0
2025-04-19 05:00 | 21 | 86.5 | 70 | 22.9185 | 18.0571 | 62.7795 | 91.6724 | 91.6724 | 0 | 0
2025-04-19 06:00 | 21.35 | 85 | 100 | 23.0468 | 18.1157 | 62.3951 | 131.7142 | 131.7142 | 0 | 0
2025-04-19 07:00 | 23.05 | 77.5 | 100 | 23.662 | 18.357 | 60.3685 | 133.2467 | 133.2467 | 0 | 0
2025-04-19 08:00 | 25.2 | 64.5 | 100 | 24.4223 | 18.3583 | 56.0654 | 116.7692 | 116.7692 | 0 | 0
2025-04-19 09:00 | 26.9 | 51.5 | 100 | 25.0145 | 18.0579 | 51.0354 | 85.4402 | 85.4402 | 0 | 0
2025-04-19 10:00 | 28.05 | 42.5 | 100 | 25.4124 | 17.7518 | 47.2155 | 58.3874 | 58.3874 | 0 | 0
2025-04-19 11:00 | 28.75 | 38.5 | 100 | 25.6522 | 17.6451 | 45.455 | 46.9703 | 46.9703 | 0 | 0
2025-04-19 12:00 | 29 | 39 | 100 | 25.735 | 17.7592 | 45.7374 | 52.1689 | 52.1689 | 0 | 0
2025-04-19 13:00 | 29.05 | 40.5 | 100 | 25.7497 | 17.8943 | 46.473 | 60.1982 | 60.1982 | 0 | 0
2025-04-19 14:00 | 29.05 | 41.5 | 100 | 25.7483 | 17.9742 | 46.9599 | 65.2059 | 65.2059 | 0 | 0
2025-04-19 15:00 | 28.65 | 43.5 | 100 | 25.6127 | 18.0108 | 47.8311 | 70.3509 | 70.3509 | 0 | 0
2025-04-19 16:00 | 27.75 | 47 | 100 | 25.3068 | 17.9989 | 49.2513 | 76.0599 | 76.0599 | 0 | 0
2025-04-19 17:00 | 26.5 | 54.5 | 100 | 24.8757 | 18.1354 | 52.2661 | 93.5398 | 93.5398 | 0 | 0
2025-04-19 18:00 | 25.3 | 62 | 100 | 24.4578 | 18.2301 | 55.0772 | 108.3312 | 108.3312 | 0 | 0
2025-04-19 19:00 | 24.55 | 64.5 | 100 | 24.1946 | 18.1262 | 55.838 | 107.5117 | 107.5117 | 0 | 0
2025-04-19 20:00 | 24 | 67.5 | 100 | 24 | 18.1159 | 56.8449 | 111.0262 | 111.0262 | 0 | 0
2025-04-19 21:00 | 23.5 | 70.5 | 100 | 23.8221 | 18.1157 | 57.8381 | 114.792 | 114.792 | 0 | 0
2025-04-19 22:00 | 23.05 | 72.5 | 70 | 23.6611 | 18.0681 | 58.4377 | 80.7133 | 80.7133 | 0 | 0
2025-04-19 23:00 | 22.5 | 75.5 | 70 | 23.4632 | 18.0361 | 59.3662 | 82.3281 | 82.3281 | 0 | 0
2025-04-20 | 21.85 | 78 | 70 | 23.2274 | 17.9316 | 60.0421 | 81.3961 | 81.3961 | 0 | 0
2025-04-20 01:00 | 21.25 | 80 | 70 | 23.0078 | 17.8124 | 60.5393 | 79.6426 | 79.6426 | 0 | 0
2025-04-20 02:00 | 20.75 | 81.5 | 70 | 22.8233 | 17.7012 | 60.8864 | 77.7048 | 77.7048 | 0 | 0
2025-04-20 03:00 | 20.35 | 82.5 | 70 | 22.6748 | 17.6009 | 61.0875 | 75.6469 | 75.6469 | 0 | 0
2025-04-20 04:00 | 20.55 | 81 | 70 | 22.7486 | 17.6004 | 60.6335 | 74.4714 | 74.4714 | 0 | 0
2025-04-20 05:00 | 20.75 | 79.5 | 70 | 22.8223 | 17.5972 | 60.1731 | 73.2351 | 73.2351 | 0 | 0
2025-04-20 06:00 | 21.2 | 77 | 100 | 22.988 | 17.634 | 59.4324 | 103.2027 | 103.2027 | 0 | 0
2025-04-20 07:00 | 23.15 | 67 | 100 | 23.6962 | 17.7823 | 56.342 | 96.9008 | 96.9008 | 0 | 0
2025-04-20 08:00 | 25.45 | 53.5 | 100 | 24.5126 | 17.7198 | 51.5249 | 75.5171 | 75.5171 | 0 | 0
2025-04-20 09:00 | 27.15 | 43.5 | 100 | 25.1056 | 17.5532 | 47.5121 | 52.8072 | 52.8072 | 0 | 0
2025-04-20 10:00 | 28.5 | 37.5 | 100 | 25.5694 | 17.4925 | 44.9441 | 39.4506 | 39.4506 | 0 | 0
2025-04-20 11:00 | 29.5 | 34 | 100 | 25.9084 | 17.4891 | 43.3783 | 32.2879 | 32.2879 | 0 | 0
2025-04-20 12:00 | 30.15 | 32 | 100 | 26.1266 | 17.4973 | 42.4558 | 28.3427 | 28.3427 | 0 | 0
2025-04-20 13:00 | 30.5 | 31 | 100 | 26.2434 | 17.5033 | 41.9878 | 26.435 | 26.435 | 0 | 0
2025-04-20 14:00 | 30.45 | 31.5 | 100 | 26.2261 | 17.5335 | 42.2406 | 28.6733 | 28.6733 | 0 | 0
2025-04-20 15:00 | 30 | 33.5 | 100 | 26.0747 | 17.5838 | 43.2014 | 34.8525 | 34.8525 | 0 | 0
2025-04-20 16:00 | 29.1 | 40.5 | 100 | 25.7663 | 17.9084 | 46.4906 | 60.8465 | 60.8465 | 0 | 0
2025-04-20 17:00 | 27.7 | 51.5 | 100 | 25.2858 | 18.3182 | 51.2909 | 96.0528 | 96.0528 | 0 | 0
2025-04-20 18:00 | 26.25 | 61 | 100 | 24.7865 | 18.4974 | 55.0019 | 117.7757 | 117.7757 | 0 | 0
2025-04-20 19:00 | 25.4 | 67 | 100 | 24.4911 | 18.5911 | 57.203 | 129.9254 | 129.9254 | 0 | 0
2025-04-20 20:00 | 24.95 | 71.5 | 100 | 24.3336 | 18.7112 | 58.8635 | 140.8452 | 140.8452 | 0 | 0
2025-04-20 21:00 | 24.8 | 72.5 | 100 | 24.2812 | 18.718 | 59.1975 | 142.3348 | 142.3348 | 0 | 0
2025-04-20 22:00 | 24.55 | 72.5 | 70 | 24.1937 | 18.6248 | 59.0775 | 96.8469 | 96.8469 | 0 | 0
2025-04-20 23:00 | 24.05 | 75.5 | 70 | 24.0177 | 18.6185 | 60.0492 | 99.2839 | 99.2839 | 0 | 0
2025-04-21 | 23.75 | 77.5 | 70 | 23.9116 | 18.623 | 60.6997 | 101.1353 | 101.1353 | 0 | 0
2025-04-21 01:00 | 23.15 | 79 | 70 | 23.698 | 18.4805 | 60.996 | 98.1705 | 98.1705 | 0 | 0
2025-04-21 02:00 | 22.05 | 81 | 70 | 23.3014 | 18.1706 | 61.2436 | 90.7134 | 90.7134 | 0 | 0
2025-04-21 03:00 | 20.85 | 83 | 70 | 22.8612 | 17.8175 | 61.4556 | 82.102 | 82.102 | 0 | 0
2025-04-21 04:00 | 20.85 | 83.5 | 70 | 22.8615 | 17.8438 | 61.6324 | 83.211 | 83.211 | 0 | 0
2025-04-21 05:00 | 21.15 | 84.5 | 70 | 22.9729 | 18.0122 | 62.1165 | 88.7625 | 88.7625 | 0 | 0
2025-04-21 06:00 | 21.55 | 81.5 | 100 | 23.1188 | 18.0073 | 61.1961 | 123.2479 | 123.2479 | 0 | 0
2025-04-21 07:00 | 23.6 | 70.5 | 100 | 23.8578 | 18.1532 | 57.8599 | 116.1167 | 116.1167 | 0 | 0
2025-04-21 08:00 | 26.15 | 57 | 100 | 24.7541 | 18.1932 | 53.2053 | 99.1293 | 99.1293 | 0 | 0
2025-04-21 09:00 | 28.45 | 44 | 100 | 25.5452 | 17.9934 | 47.9826 | 69.9768 | 69.9768 | 0 | 0
2025-04-21 10:00 | 30.8 | 32 | 100 | 26.3395 | 17.6797 | 42.5 | 34.4265 | 34.4265 | 0 | 0
2025-04-21 11:00 | 33 | 22.5 | 100 | 27.0709 | 17.3429 | 37.5852 | 0 | 0 | 0 | 0
2025-04-21 12:00 | 34.5 | 17.5 | 100 | 27.561 | 17.1598 | 34.7218 | 0 | 0 | 0 | 0
2025-04-21 13:00 | 35 | 15 | 100 | 27.7271 | 16.9859 | 33.2224 | 0 | 0 | 0 | 0
2025-04-21 14:00 | 34.55 | 14 | 100 | 27.5901 | 16.777 | 32.682 | 0 | 0 | 0 | 0
2025-04-21 15:00 | 33.4 | 17 | 100 | 27.2153 | 16.8601 | 34.5171 | 0 | 0 | 0 | 0
2025-04-21 16:00 | 32.1 | 23.5 | 100 | 26.78 | 17.2205 | 38.1386 | 0 | 0 | 0 | 0
2025-04-21 17:00 | 30.45 | 32 | 100 | 26.2252 | 17.581 | 42.4776 | 31.1679 | 31.1679 | 0 | 0
2025-04-21 18:00 | 28.4 | 43.5 | 100 | 25.529 | 17.9375 | 47.7495 | 67.1309 | 67.1309 | 0 | 0
2025-04-21 19:00 | 26.85 | 56 | 100 | 24.9944 | 18.3615 | 53.008 | 104.4664 | 104.4664 | 0 | 0
2025-04-21 20:00 | 25.9 | 64.5 | 100 | 24.6647 | 18.6097 | 56.3334 | 126.9801 | 126.9801 | 0 | 0
2025-04-21 21:00 | 25.2 | 68 | 100 | 24.4214 | 18.5843 | 57.503 | 130.593 | 130.593 | 0 | 0
2025-04-21 22:00 | 24.45 | 69 | 70 | 24.159 | 18.3734 | 57.5917 | 86.1687 | 86.1687 | 0 | 0
2025-04-21 23:00 | 23.45 | 69.5 | 70 | 23.8041 | 18.0398 | 57.3959 | 77.0577 | 77.0577 | 0 | 0
2025-04-22 | 22.4 | 70 | 70 | 23.4254 | 17.6892 | 57.2197 | 67.6837 | 67.6837 | 0 | 0
2025-04-22 01:00 | 21.6 | 69 | 70 | 23.1322 | 17.3463 | 56.6037 | 57.4759 | 57.4759 | 0 | 0
2025-04-22 02:00 | 21 | 66 | 70 | 22.9086 | 16.9709 | 55.3611 | 44.9476 | 44.9476 | 0 | 0
2025-04-22 03:00 | 20.45 | 63 | 70 | 22.7015 | 16.6204 | 54.1827 | 33.3435 | 33.3435 | 0 | 0
2025-04-22 04:00 | 20.85 | 67 | 70 | 22.8532 | 16.9726 | 55.6906 | 45.8691 | 45.8691 | 0 | 0
2025-04-22 05:00 | 21.35 | 73.5 | 70 | 23.0418 | 17.5021 | 58.1822 | 65.5343 | 65.5343 | 0 | 0
2025-04-22 06:00 | 21.85 | 71.5 | 100 | 23.225 | 17.5746 | 57.6014 | 94.0073 | 94.0073 | 0 | 0
2025-04-22 07:00 | 24.15 | 61 | 100 | 24.0534 | 17.77 | 54.2435 | 88.0123 | 88.0123 | 0 | 0
2025-04-22 08:00 | 27.7 | 44.5 | 100 | 25.2921 | 17.8005 | 48.0432 | 63.4032 | 63.4032 | 0 | 0
2025-04-22 09:00 | 31.05 | 28.5 | 100 | 26.428 | 17.4317 | 40.7115 | 17.55 | 17.55 | 0 | 0
2025-04-22 10:00 | 33.45 | 20 | 100 | 27.2214 | 17.1951 | 36.1757 | 0 | 0 | 0 | 0
2025-04-22 11:00 | 35.05 | 17.5 | 100 | 27.7322 | 17.2857 | 34.6859 | 0 | 0 | 0 | 0
2025-04-22 12:00 | 35.6 | 17 | 100 | 27.9042 | 17.349 | 34.3718 | 0 | 0 | 0 | 0
2025-04-22 13:00 | 35.1 | 17.5 | 100 | 27.7477 | 17.2944 | 34.6919 | 0 | 0 | 0 | 0
2025-04-22 14:00 | 34.35 | 20 | 100 | 27.5047 | 17.4 | 36.1762 | 0 | 0 | 0 | 0
2025-04-22 15:00 | 33.75 | 23 | 100 | 27.3063 | 17.5751 | 37.889 | 8.6965 | 8.6965 | 0 | 0
2025-04-22 16:00 | 33.3 | 24.5 | 100 | 27.1598 | 17.6183 | 38.7141 | 14.2719 | 14.2719 | 0 | 0
2025-04-22 17:00 | 32.2 | 28 | 100 | 26.8004 | 17.6832 | 40.5529 | 25.4219 | 25.4219 | 0 | 0
2025-04-22 18:00 | 30.5 | 35 | 100 | 26.2359 | 17.8591 | 43.9974 | 47.6131 | 47.6131 | 0 | 0
2025-04-22 19:00 | 29.25 | 40 | 100 | 25.8167 | 17.9165 | 46.2535 | 59.7899 | 59.7899 | 0 | 0
2025-04-22 20:00 | 28.4 | 42 | 100 | 25.5307 | 17.8206 | 47.0404 | 59.9132 | 59.9132 | 0 | 0
2025-04-22 21:00 | 27.7 | 44.5 | 100 | 25.2921 | 17.7991 | 48.0574 | 63.5492 | 63.5492 | 0 | 0
2025-04-22 22:00 | 26.95 | 48 | 70 | 25.0339 | 17.8228 | 49.4756 | 49.3095 | 49.3095 | 0 | 0
2025-04-22 23:00 | 25.9 | 52.5 | 70 | 24.6697 | 17.8016 | 51.1941 | 53.8158 | 53.8158 | 0 | 0
2025-04-23 | 24.9 | 55 | 70 | 24.3193 | 17.6393 | 52.0037 | 52.1419 | 52.1419 | 0 | 0
2025-04-23 01:00 | 24.35 | 53 | 70 | 24.1248 | 17.3283 | 51.0631 | 41.8739 | 41.8739 | 0 | 0
2025-04-23 02:00 | 24.1 | 50 | 70 | 24.0358 | 17.0543 | 49.8036 | 31.692 | 31.692 | 0 | 0
2025-04-23 03:00 | 23.95 | 47.5 | 70 | 23.9821 | 16.8456 | 48.7766 | 23.8036 | 23.8036 | 0 | 0
2025-04-23 04:00 | 24.05 | 44 | 70 | 24.018 | 16.6488 | 47.3694 | 15.1054 | 15.1054 | 0 | 0
2025-04-23 05:00 | 24.05 | 41 | 70 | 24.018 | 16.452 | 46.1489 | 6.9518 | 6.9518 | 0 | 0
2025-04-23 06:00 | 24.75 | 36.5 | 100 | 24.2692 | 16.35 | 44.2936 | 0 | 0 | 0 | 0
2025-04-23 07:00 | 27.7 | 28.5 | 100 | 25.3064 | 16.5532 | 40.6964 | 0 | 0 | 0 | 0
2025-04-23 08:00 | 31.55 | 21.5 | 100 | 26.6064 | 16.8955 | 37.0764 | 0 | 0 | 0 | 0
2025-04-23 09:00 | 34.6 | 17.5 | 100 | 27.5922 | 17.1825 | 34.7159 | 0 | 0 | 0 | 0
2025-04-23 10:00 | 36.95 | 14.5 | 100 | 28.328 | 17.3356 | 32.7781 | 0 | 0 | 0 | 0
2025-04-23 11:00 | 38.65 | 13 | 100 | 28.8443 | 17.4901 | 31.7167 | 0 | 0 | 0 | 0
2025-04-23 12:00 | 39.15 | 13 | 100 | 28.9909 | 17.5895 | 31.6962 | 0 | 0 | 0 | 0
2025-04-23 13:00 | 38.75 | 13.5 | 100 | 28.8704 | 17.5748 | 32.0545 | 0 | 0 | 0 | 0
2025-04-23 14:00 | 38.2 | 15 | 100 | 28.6987 | 17.6565 | 33.0725 | 0 | 0 | 0 | 0
2025-04-23 15:00 | 37.6 | 16.5 | 100 | 28.5118 | 17.7178 | 34.0592 | 0 | 0 | 0 | 0
2025-04-23 16:00 | 36.75 | 18.5 | 100 | 28.2466 | 17.7739 | 35.3223 | 2.2263 | 2.2263 | 0 | 0
2025-04-23 17:00 | 35.05 | 23 | 100 | 27.7097 | 17.8884 | 37.9823 | 19.8507 | 19.8507 | 0 | 0
2025-04-23 18:00 | 33 | 29.5 | 100 | 27.05 | 18.0366 | 41.4805 | 42.1631 | 42.1631 | 0 | 0
2025-04-23 19:00 | 31.45 | 36.5 | 100 | 26.5398 | 18.2619 | 44.9637 | 66.3032 | 66.3032 | 0 | 0
2025-04-23 20:00 | 30 | 42.5 | 100 | 26.0595 | 18.3466 | 47.6701 | 81.4682 | 81.4682 | 0 | 0
2025-04-23 21:00 | 28.6 | 49 | 100 | 25.5894 | 18.4243 | 50.4093 | 96.1269 | 96.1269 | 0 | 0
2025-04-23 22:00 | 27.55 | 54.5 | 70 | 25.2326 | 18.4886 | 52.606 | 75.3848 | 75.3848 | 0 | 0
2025-04-23 23:00 | 26.6 | 58.5 | 70 | 24.9076 | 18.4477 | 54.0518 | 78.5142 | 78.5142 | 0 | 0
2025-04-24 | 25.65 | 64.5 | 70 | 24.5784 | 18.5171 | 56.2734 | 86.5809 | 86.5809 | 0 | 0
2025-04-24 01:00 | 24.65 | 70.5 | 70 | 24.229 | 18.5363 | 58.3456 | 92.769 | 92.769 | 0 | 0
2025-04-24 02:00 | 23.65 | 75 | 70 | 23.8759 | 18.4363 | 59.702 | 93.782 | 93.782 | 0 | 0
2025-04-24 03:00 | 22.9 | 78 | 70 | 23.6082 | 18.3269 | 60.5258 | 93.0765 | 93.0765 | 0 | 0
2025-04-24 04:00 | 22.95 | 72.5 | 70 | 23.6251 | 18.0295 | 58.4322 | 79.8868 | 79.8868 | 0 | 0
2025-04-24 05:00 | 23.1 | 66.5 | 70 | 23.6781 | 17.7327 | 56.1621 | 66.2733 | 66.2733 | 0 | 0
2025-04-24 06:00 | 23.7 | 65 | 100 | 23.8931 | 17.8552 | 55.7632 | 97.5247 | 97.5247 | 0 | 0
2025-04-24 07:00 | 25.95 | 59 | 100 | 24.6842 | 18.2569 | 54.0423 | 105.2187 | 105.2187 | 0 | 0
2025-04-24 08:00 | 28.7 | 48.5 | 100 | 25.6232 | 18.4176 | 50.2083 | 95.0693 | 95.0693 | 0 | 0
2025-04-24 09:00 | 30.85 | 39.5 | 100 | 26.3406 | 18.3497 | 46.3739 | 75.7997 | 75.7997 | 0 | 0
2025-04-24 10:00 | 32.35 | 35.5 | 100 | 26.8282 | 18.4322 | 44.6268 | 70.6881 | 70.6881 | 0 | 0
2025-04-24 11:00 | 33.4 | 32.5 | 100 | 27.1656 | 18.4427 | 43.2106 | 64.4463 | 64.4463 | 0 | 0
2025-04-24 12:00 | 34 | 31 | 100 | 27.3562 | 18.4593 | 42.4893 | 61.6183 | 61.6183 | 0 | 0
2025-04-24 13:00 | 33.8 | 33 | 100 | 27.2876 | 18.6038 | 43.5859 | 71.9873 | 71.9873 | 0 | 0
2025-04-24 14:00 | 32.9 | 37 | 100 | 26.9961 | 18.7318 | 45.5907 | 85.9741 | 85.9741 | 0 | 0
2025-04-24 15:00 | 31.9 | 41 | 100 | 26.672 | 18.7991 | 47.4571 | 96.9444 | 96.9444 | 0 | 0
2025-04-24 16:00 | 30.9 | 46 | 100 | 26.3433 | 18.9212 | 49.7228 | 111.4675 | 111.4675 | 0 | 0
2025-04-24 17:00 | 29.7 | 52.5 | 100 | 25.9455 | 19.0594 | 52.5046 | 128.5352 | 128.5352 | 0 | 0
2025-04-24 18:00 | 28.35 | 59 | 100 | 25.495 | 19.0917 | 55.0151 | 140.1759 | 140.1759 | 0 | 0
2025-04-24 19:00 | 27.25 | 64.5 | 100 | 25.1235 | 19.0927 | 57.0019 | 148.2406 | 148.2406 | 0 | 0
2025-04-24 20:00 | 26.3 | 69.5 | 100 | 24.7992 | 19.0834 | 58.7186 | 154.6279 | 154.6279 | 0 | 0
2025-04-24 21:00 | 25.4 | 74.5 | 100 | 24.4888 | 19.0675 | 60.3648 | 160.3695 | 160.3695 | 0 | 0
2025-04-24 22:00 | 24.5 | 78.5 | 70 | 24.1756 | 18.9697 | 61.5201 | 112.6794 | 112.6794 | 0 | 0
2025-04-24 23:00 | 23.6 | 80.5 | 70 | 23.8586 | 18.7392 | 61.8365 | 107.3637 | 107.3637 | 0 | 0
2025-04-25 | 22.8 | 81.5 | 70 | 23.573 | 18.4862 | 61.8193 | 100.6301 | 100.6301 | 0 | 0
2025-04-25 01:00 | 22.05 | 84.5 | 70 | 23.3026 | 18.3608 | 62.5801 | 99.2616 | 99.2616 | 0 | 0
2025-04-25 02:00 | 21.35 | 88.5 | 70 | 23.0484 | 18.2982 | 63.699 | 100.4413 | 100.4413 | 0 | 0
2025-04-25 03:00 | 20.75 | 90.5 | 70 | 22.828 | 18.1637 | 64.1158 | 97.9194 | 97.9194 | 0 | 0
2025-04-25 04:00 | 20.9 | 87.5 | 70 | 22.882 | 18.0694 | 63.1186 | 92.9571 | 92.9571 | 0 | 0
2025-04-25 05:00 | 21.2 | 83 | 70 | 22.9907 | 17.9514 | 61.6342 | 86.1444 | 86.1444 | 0 | 0
2025-04-25 06:00 | 22.05 | 75.5 | 100 | 23.2996 | 17.8674 | 59.2183 | 111.0769 | 111.0769 | 0 | 0
2025-04-25 07:00 | 24.95 | 60 | 100 | 24.3359 | 17.978 | 54.1324 | 95.4916 | 95.4916 | 0 | 0
2025-04-25 08:00 | 29.2 | 42.5 | 100 | 25.7967 | 18.1005 | 47.478 | 71.945 | 71.945 | 0 | 0
2025-04-25 09:00 | 33.6 | 26.5 | 100 | 27.2476 | 17.8945 | 39.8772 | 29.5037 | 29.5037 | 0 | 0
2025-04-25 10:00 | 37 | 15.5 | 100 | 28.338 | 17.4624 | 33.4326 | 0 | 0 | 0 | 0
2025-04-25 11:00 | 38.85 | 11.5 | 100 | 28.9138 | 17.3181 | 30.7215 | 0 | 0 | 0 | 0
2025-04-25 12:00 | 39.1 | 15 | 100 | 28.9624 | 17.8416 | 33.0806 | 0 | 0 | 0 | 0
2025-04-25 13:00 | 37.65 | 24 | 100 | 28.4817 | 18.6493 | 38.9098 | 50.4795 | 50.4795 | 0 | 0
2025-04-25 14:00 | 35.85 | 29.5 | 100 | 27.9225 | 18.8068 | 42.0025 | 71.5612 | 71.5612 | 0 | 0
2025-04-25 15:00 | 35 | 30 | 100 | 27.6653 | 18.6272 | 42.1245 | 65.9266 | 65.9266 | 0 | 0
2025-04-25 16:00 | 33.7 | 36.5 | 100 | 27.2448 | 18.9191 | 45.5399 | 92.5194 | 92.5194 | 0 | 0
2025-04-25 17:00 | 31.85 | 46 | 100 | 26.6437 | 19.2279 | 50.0727 | 124.2679 | 124.2679 | 0 | 0
2025-04-25 18:00 | 30.05 | 57 | 100 | 26.0507 | 19.5363 | 54.8667 | 156.4021 | 156.4021 | 0 | 0
2025-04-25 19:00 | 28.5 | 71 | 100 | 25.5303 | 20.0157 | 60.663 | 198.4959 | 198.4959 | 0 | 0
2025-04-25 20:00 | 27.55 | 80 | 100 | 25.2102 | 20.265 | 64.1001 | 221.6927 | 221.6927 | 0 | 0
2025-04-25 21:00 | 26.7 | 85 | 100 | 24.9249 | 20.248 | 65.6675 | 226.9136 | 226.9136 | 0 | 0
2025-04-25 22:00 | 25.95 | 89 | 70 | 24.6711 | 20.1903 | 66.8081 | 160.1796 | 160.1796 | 0 | 0
2025-04-25 23:00 | 25.15 | 92 | 70 | 24.3981 | 20.0396 | 67.4475 | 157.5487 | 157.5487 | 0 | 0
2025-04-26 | 24.45 | 94 | 70 | 24.1567 | 19.8635 | 67.7352 | 153.3434 | 153.3434 | 0 | 0
2025-04-26 01:00 | 23.9 | 95.5 | 70 | 23.965 | 19.7185 | 67.9272 | 149.7679 | 149.7679 | 0 | 0
2025-04-26 02:00 | 23.45 | 93 | 70 | 23.8066 | 19.3913 | 66.6366 | 137.4071 | 137.4071 | 0 | 0
2025-04-26 03:00 | 22.9 | 90.5 | 70 | 23.6107 | 19.0273 | 65.3219 | 124.1146 | 124.1146 | 0 | 0
2025-04-26 04:00 | 22.7 | 77.5 | 70 | 23.5361 | 18.2216 | 60.2592 | 89.722 | 89.722 | 0 | 0
2025-04-26 05:00 | 22.8 | 62.5 | 70 | 23.5688 | 17.3909 | 54.5369 | 53.3914 | 53.3914 | 0 | 0
2025-04-26 06:00 | 23.75 | 55.5 | 100 | 23.9105 | 17.286 | 52.0011 | 62.561 | 62.561 | 0 | 0
2025-04-26 07:00 | 27.1 | 43 | 100 | 25.0889 | 17.4962 | 47.3139 | 50.3557 | 50.3557 | 0 | 0
2025-04-26 08:00 | 31.65 | 31 | 100 | 26.6168 | 17.8135 | 42.1216 | 37.7038 | 37.7038 | 0 | 0
2025-04-26 09:00 | 35.8 | 21 | 100 | 27.9474 | 17.845 | 36.8326 | 12.545 | 12.545 | 0 | 0
2025-04-26 10:00 | 39.1 | 13.5 | 100 | 28.9731 | 17.6408 | 32.0571 | 0 | 0 | 0 | 0
2025-04-26 11:00 | 41.2 | 9 | 100 | 29.6153 | 17.3956 | 28.7654 | 0 | 0 | 0 | 0
2025-04-26 12:00 | 42.45 | 7 | 100 | 29.989 | 17.2957 | 27.1471 | 0 | 0 | 0 | 0
2025-04-26 13:00 | 43.3 | 7 | 100 | 30.2265 | 17.4338 | 27.0518 | 0 | 0 | 0 | 0
2025-04-26 14:00 | 43.55 | 7 | 100 | 30.2958 | 17.4731 | 27.0289 | 0 | 0 | 0 | 0
2025-04-26 15:00 | 42.25 | 9 | 100 | 29.9124 | 17.5764 | 28.6895 | 0 | 0 | 0 | 0
2025-04-26 16:00 | 39.25 | 15 | 100 | 29.0061 | 17.8691 | 33.0937 | 0 | 0 | 0 | 0
2025-04-26 17:00 | 36.3 | 26 | 100 | 28.0736 | 18.5356 | 39.9583 | 52.0231 | 52.0231 | 0 | 0
2025-04-26 18:00 | 33.95 | 34.5 | 100 | 27.3284 | 18.7948 | 44.4791 | 83.0906 | 83.0906 | 0 | 0
2025-04-26 19:00 | 32.55 | 37 | 100 | 26.8869 | 18.6279 | 45.5032 | 81.9096 | 81.9096 | 0 | 0
2025-04-26 20:00 | 31.85 | 39.5 | 100 | 26.6599 | 18.6491 | 46.6475 | 87.8551 | 87.8551 | 0 | 0
2025-04-26 21:00 | 31.1 | 39.5 | 100 | 26.421 | 18.423 | 46.4477 | 78.8729 | 78.8729 | 0 | 0
2025-04-26 22:00 | 30.5 | 34.5 | 70 | 26.2369 | 17.8087 | 43.7796 | 31.7318 | 31.7318 | 0 | 0
2025-04-26 23:00 | 29.65 | 30.5 | 70 | 25.9637 | 17.226 | 41.702 | 11.2998 | 11.2998 | 0 | 0
2025-04-27 | 28.65 | 28.5 | 70 | 25.6307 | 16.7921 | 40.7167 | 0 | 0 | 0 | 0
2025-04-27 01:00 | 27.65 | 26 | 70 | 25.2916 | 16.3305 | 39.5927 | 0 | 0 | 0 | 0
2025-04-27 02:00 | 26.7 | 24 | 70 | 24.9631 | 15.9363 | 38.7878 | 0 | 0 | 0 | 0
2025-04-27 03:00 | 25.9 | 23 | 70 | 24.6819 | 15.6661 | 38.4698 | 0 | 0 | 0 | 0
2025-04-27 04:00 | 26.05 | 23 | 70 | 24.7349 | 15.7029 | 38.4425 | 0 | 0 | 0 | 0
2025-04-27 05:00 | 26.25 | 22.5 | 70 | 24.8058 | 15.7131 | 38.1857 | 0 | 0 | 0 | 0
2025-04-27 06:00 | 26.5 | 21 | 100 | 24.8946 | 15.6558 | 37.4692 | 0 | 0 | 0 | 0
2025-04-27 07:00 | 29.15 | 18 | 100 | 25.8136 | 16.0111 | 35.5951 | 0 | 0 | 0 | 0
2025-04-27 08:00 | 33.45 | 14 | 100 | 27.2411 | 16.5435 | 32.8433 | 0 | 0 | 0 | 0
2025-04-27 09:00 | 37.75 | 10 | 100 | 28.5954 | 16.9105 | 29.8414 | 0 | 0 | 0 | 0
2025-04-27 10:00 | 40.65 | 7.5 | 100 | 29.4703 | 17.0751 | 27.7434 | 0 | 0 | 0 | 0
2025-04-27 11:00 | 42.1 | 6.5 | 100 | 29.8951 | 17.1601 | 26.8099 | 0 | 0 | 0 | 0
2025-04-27 12:00 | 43.2 | 6 | 100 | 30.2099 | 17.2541 | 26.2774 | 0 | 0 | 0 | 0
2025-04-27 13:00 | 43.8 | 6 | 100 | 30.3764 | 17.3475 | 26.2006 | 0 | 0 | 0 | 0
2025-04-27 14:00 | 43.65 | 6.5 | 100 | 30.3291 | 17.4077 | 26.6175 | 0 | 0 | 0 | 0
2025-04-27 15:00 | 42.4 | 8 | 100 | 29.9647 | 17.4459 | 27.916 | 0 | 0 | 0 | 0
2025-04-27 16:00 | 40.5 | 10 | 100 | 29.4062 | 17.4129 | 29.5606 | 0 | 0 | 0 | 0
2025-04-27 17:00 | 37.95 | 16 | 100 | 28.6188 | 17.7243 | 33.7547 | 0 | 0 | 0 | 0
2025-04-27 18:00 | 35 | 26 | 100 | 27.6819 | 18.2006 | 39.7633 | 39.4922 | 39.4922 | 0 | 0
2025-04-27 19:00 | 33.3 | 31.5 | 100 | 27.1377 | 18.3146 | 42.6452 | 57.417 | 57.417 | 0 | 0
2025-04-27 20:00 | 32.45 | 34.5 | 100 | 26.8624 | 18.3651 | 44.12 | 66.1075 | 66.1075 | 0 | 0
2025-04-27 21:00 | 31.55 | 37 | 100 | 26.5706 | 18.3353 | 45.2529 | 70.2787 | 70.2787 | 0 | 0
2025-04-27 22:00 | 30.85 | 34 | 70 | 26.3518 | 17.8648 | 43.5726 | 32.36 | 32.36 | 0 | 0
2025-04-27 23:00 | 30.5 | 33.5 | 70 | 26.2388 | 17.7213 | 43.2721 | 27.9897 | 27.9897 | 0 | 0
2025-04-28 | 29.9 | 32.5 | 70 | 26.0434 | 17.467 | 42.7094 | 20.1834 | 20.1834 | 0 | 0
2025-04-28 01:00 | 29.2 | 29 | 70 | 25.8155 | 16.9775 | 40.9586 | 3.1904 | 3.1904 | 0 | 0
2025-04-28 02:00 | 28.55 | 27 | 70 | 25.5986 | 16.6401 | 40.0089 | 0 | 0 | 0 | 0
2025-04-28 03:00 | 27.7 | 25 | 70 | 25.3097 | 16.2614 | 39.1278 | 0 | 0 | 0 | 0
2025-04-28 04:00 | 27.3 | 24.5 | 70 | 25.1718 | 16.1225 | 38.9391 | 0 | 0 | 0 | 0
2025-04-28 05:00 | 26.9 | 24 | 70 | 25.033 | 15.9858 | 38.7592 | 0 | 0 | 0 | 0
2025-04-28 06:00 | 27.15 | 22 | 100 | 25.1215 | 15.8874 | 37.8129 | 0 | 0 | 0 | 0
2025-04-28 07:00 | 29.65 | 18 | 100 | 25.9829 | 16.1212 | 35.5202 | 0 | 0 | 0 | 0
2025-04-28 08:00 | 34.05 | 13 | 100 | 27.4359 | 16.5543 | 32.1951 | 0 | 0 | 0 | 0
2025-04-28 09:00 | 38 | 8.5 | 100 | 28.6801 | 16.7539 | 28.8322 | 0 | 0 | 0 | 0
2025-04-28 10:00 | 40.25 | 7 | 100 | 29.3584 | 16.9296 | 27.4546 | 0 | 0 | 0 | 0
2025-04-28 11:00 | 41.8 | 6.5 | 100 | 29.81 | 17.1084 | 26.8599 | 0 | 0 | 0 | 0
2025-04-28 12:00 | 42.95 | 6 | 100 | 30.1402 | 17.2111 | 26.3198 | 0 | 0 | 0 | 0
2025-04-28 13:00 | 43.2 | 6.5 | 100 | 30.2045 | 17.3328 | 26.677 | 0 | 0 | 0 | 0
2025-04-28 14:00 | 42.25 | 8 | 100 | 29.9227 | 17.418 | 27.9363 | 0 | 0 | 0 | 0
2025-04-28 15:00 | 40.5 | 10.5 | 100 | 29.4021 | 17.4836 | 29.9226 | 0 | 0 | 0 | 0
2025-04-28 16:00 | 38.55 | 13.5 | 100 | 28.8122 | 17.5203 | 32.1029 | 0 | 0 | 0 | 0
2025-04-28 17:00 | 35.95 | 21.5 | 100 | 27.9907 | 17.9313 | 37.1713 | 17.5508 | 17.5508 | 0 | 0
2025-04-28 18:00 | 33.2 | 33 | 100 | 27.1018 | 18.4309 | 43.4747 | 65.6248 | 65.6248 | 0 | 0
2025-04-28 19:00 | 31.8 | 38 | 100 | 26.6478 | 18.4961 | 45.8575 | 78.9798 | 78.9798 | 0 | 0
2025-04-28 20:00 | 31.05 | 38.5 | 100 | 26.4071 | 18.3178 | 45.9376 | 73.0325 | 73.0325 | 0 | 0
2025-04-28 21:00 | 30.15 | 40.5 | 100 | 26.1119 | 18.2207 | 46.7411 | 73.2031 | 73.2031 | 0 | 0
2025-04-28 22:00 | 29.55 | 39.5 | 70 | 25.9167 | 17.9569 | 46.118 | 42.823 | 42.823 | 0 | 0
2025-04-28 23:00 | 29.15 | 32 | 70 | 25.7946 | 17.2164 | 42.4184 | 13.4862 | 13.4862 | 0 | 0
2025-04-29 | 28.45 | 25.5 | 70 | 25.5663 | 16.4882 | 39.3069 | 0 | 0 | 0 | 0
2025-04-29 01:00 | 27.7 | 23.5 | 70 | 25.3111 | 16.1375 | 38.4399 | 0 | 0 | 0 | 0
2025-04-29 02:00 | 27 | 22 | 70 | 25.0693 | 15.8486 | 37.851 | 0 | 0 | 0 | 0
2025-04-29 03:00 | 26.4 | 21 | 70 | 24.8595 | 15.6284 | 37.5079 | 0 | 0 | 0 | 0
2025-04-29 04:00 | 26.5 | 20.5 | 70 | 24.8949 | 15.6127 | 37.2662 | 0 | 0 | 0 | 0
2025-04-29 05:00 | 26.55 | 20 | 70 | 24.9128 | 15.5849 | 37.0316 | 0 | 0 | 0 | 0
2025-04-29 06:00 | 27.15 | 18.5 | 100 | 25.1241 | 15.6023 | 36.2271 | 0 | 0 | 0 | 0
2025-04-29 07:00 | 29.95 | 15.5 | 100 | 26.088 | 15.9547 | 34.2318 | 0 | 0 | 0 | 0
2025-04-29 08:00 | 34.35 | 11.5 | 100 | 27.5368 | 16.4411 | 31.2916 | 0 | 0 | 0 | 0
2025-04-29 09:00 | 38.4 | 8 | 100 | 28.8038 | 16.7517 | 28.4485 | 0 | 0 | 0 | 0
2025-04-29 10:00 | 40.85 | 7 | 100 | 29.533 | 17.0253 | 27.3743 | 0 | 0 | 0 | 0
2025-04-29 11:00 | 42.35 | 6.5 | 100 | 29.9664 | 17.1933 | 26.7926 | 0 | 0 | 0 | 0
2025-04-29 12:00 | 43.25 | 6.5 | 100 | 30.2186 | 17.338 | 26.6773 | 0 | 0 | 0 | 0
2025-04-29 13:00 | 43.15 | 7.5 | 100 | 30.1795 | 17.4871 | 27.4679 | 0 | 0 | 0 | 0
2025-04-29 14:00 | 42.2 | 9 | 100 | 29.8986 | 17.5641 | 28.702 | 0 | 0 | 0 | 0
2025-04-29 15:00 | 41.05 | 11 | 100 | 29.555 | 17.6584 | 30.2551 | 0 | 0 | 0 | 0
2025-04-29 16:00 | 39.85 | 13.5 | 100 | 29.1909 | 17.7828 | 32.0712 | 0 | 0 | 0 | 0
2025-04-29 17:00 | 37.6 | 21 | 100 | 28.4853 | 18.2662 | 36.9972 | 27.9127 | 27.9127 | 0 | 0
2025-04-29 18:00 | 34.35 | 36 | 100 | 27.4446 | 19.0598 | 45.4592 | 97.3585 | 97.3585 | 0 | 0
2025-04-29 19:00 | 31.6 | 51.5 | 100 | 26.552 | 19.6195 | 52.8503 | 151.1545 | 151.1545 | 0 | 0
2025-04-29 20:00 | 30.35 | 55.5 | 100 | 26.1492 | 19.5205 | 54.2823 | 153.4682 | 153.4682 | 0 | 0
2025-04-29 21:00 | 29.95 | 51.5 | 100 | 26.028 | 19.0632 | 52.125 | 127.1378 | 127.1378 | 0 | 0
2025-04-29 22:00 | 29.5 | 47.5 | 70 | 25.8881 | 18.5943 | 50.0056 | 70.5914 | 70.5914 | 0 | 0
2025-04-29 23:00 | 28.9 | 44 | 70 | 25.6953 | 18.124 | 48.1535 | 53.2262 | 53.2262 | 0 | 0
2025-04-30 | 28 | 42.5 | 70 | 25.3956 | 17.7297 | 47.26 | 40.8635 | 40.8635 | 0 | 0
2025-04-30 01:00 | 27.45 | 39 | 70 | 25.2118 | 17.2959 | 45.5706 | 25.3156 | 25.3156 | 0 | 0
2025-04-30 02:00 | 27.05 | 34.5 | 70 | 25.0778 | 16.838 | 43.5008 | 8.2017 | 8.2017 | 0 | 0
2025-04-30 03:00 | 26.25 | 32.5 | 70 | 24.8008 | 16.4675 | 42.6065 | 0 | 0 | 0 | 0
2025-04-30 04:00 | 25.9 | 31.5 | 70 | 24.6784 | 16.2997 | 42.1842 | 0 | 0 | 0 | 0
2025-04-30 05:00 | 25.85 | 28.5 | 70 | 24.662 | 16.0648 | 40.8831 | 0 | 0 | 0 | 0
2025-04-30 06:00 | 26.45 | 23.5 | 100 | 24.8757 | 15.8358 | 38.6037 | 0 | 0 | 0 | 0
2025-04-30 07:00 | 29.45 | 18 | 100 | 25.9154 | 16.0753 | 35.5572 | 0 | 0 | 0 | 0
2025-04-30 08:00 | 33.3 | 14.5 | 100 | 27.1916 | 16.5631 | 33.1546 | 0 | 0 | 0 | 0
2025-04-30 09:00 | 36.55 | 12.5 | 100 | 28.2175 | 16.995 | 31.5884 | 0 | 0 | 0 | 0
2025-04-30 10:00 | 39.35 | 10 | 100 | 29.0717 | 17.2031 | 29.6632 | 0 | 0 | 0 | 0
2025-04-30 11:00 | 41.15 | 9 | 100 | 29.6011 | 17.3839 | 28.7769 | 0 | 0 | 0 | 0
2025-04-30 12:00 | 42.25 | 9 | 100 | 29.9123 | 17.5791 | 28.683 | 0 | 0 | 0 | 0
2025-04-30 13:00 | 42.75 | 8.5 | 100 | 30.0572 | 17.5855 | 28.2682 | 0 | 0 | 0 | 0
2025-04-30 14:00 | 42.5 | 8 | 100 | 29.9929 | 17.4595 | 27.9137 | 0 | 0 | 0 | 0
2025-04-30 15:00 | 41.5 | 8.5 | 100 | 29.7058 | 17.3639 | 28.39 | 0 | 0 | 0 | 0
2025-04-30 16:00 | 38 | 23 | 100 | 28.5896 | 18.6129 | 38.3278 | 46.3881 | 46.3881 | 0 | 0
2025-04-30 17:00 | 34.45 | 38.5 | 100 | 27.4651 | 19.3417 | 46.9149 | 114.2456 | 114.2456 | 0 | 0
2025-04-30 18:00 | 32.75 | 44.5 | 100 | 26.9274 | 19.3829 | 49.629 | 128.0908 | 128.0908 | 0 | 0
2025-04-30 19:00 | 31.35 | 50 | 100 | 26.4772 | 19.4085 | 51.9504 | 139.2208 | 139.2208 | 0 | 0
2025-04-30 20:00 | 30.75 | 49.5 | 100 | 26.2883 | 19.1667 | 51.442 | 127.9881 | 127.9881 | 0 | 0
2025-04-30 21:00 | 30.1 | 48.5 | 100 | 26.0816 | 18.8707 | 50.6924 | 113.8057 | 113.8057 | 0 | 0
2025-04-30 22:00 | 29.25 | 48 | 70 | 25.8054 | 18.5541 | 50.1577 | 69.9716 | 69.9716 | 0 | 0
2025-04-30 23:00 | 28.4 | 48 | 70 | 25.524 | 18.2802 | 49.9018 | 62.3058 | 62.3058 | 0 | 0
2025-05-01 | 27.6 | 48 | 70 | 25.2552 | 18.0238 | 49.6892 | 55.2954 | 55.2954 | 0 | 0
2025-05-01 01:00 | 26.8 | 46.5 | 70 | 24.9836 | 17.6599 | 48.8343 | 43.8256 | 43.8256 | 0 | 0
2025-05-01 02:00 | 26.2 | 43.5 | 70 | 24.7779 | 17.2582 | 47.4146 | 29.922 | 29.922 | 0 | 0
2025-05-01 03:00 | 25.65 | 39.5 | 70 | 24.5873 | 16.8092 | 45.632 | 14.0075 | 14.0075 | 0 | 0
2025-05-01 04:00 | 25.15 | 38 | 70 | 24.4112 | 16.5599 | 44.9745 | 6.2532 | 6.2532 | 0 | 0
2025-05-01 05:00 | 25 | 35 | 70 | 24.3586 | 16.3078 | 43.7078 | 0 | 0 | 0 | 0
2025-05-01 06:00 | 25.75 | 29 | 100 | 24.6264 | 16.0778 | 41.0955 | 0 | 0 | 0 | 0
2025-05-01 07:00 | 29.05 | 22 | 100 | 25.7744 | 16.3381 | 37.5609 | 0 | 0 | 0 | 0
2025-05-01 08:00 | 33.95 | 15.5 | 100 | 27.3954 | 16.8099 | 33.6416 | 0 | 0 | 0 | 0
2025-05-01 09:00 | 37.6 | 12 | 100 | 28.5385 | 17.1412 | 31.1611 | 0 | 0 | 0 | 0
2025-05-01 10:00 | 39.65 | 10.5 | 100 | 29.1557 | 17.3318 | 29.9719 | 0 | 0 | 0 | 0
2025-05-01 11:00 | 40.9 | 10 | 100 | 29.5206 | 17.4917 | 29.5158 | 0 | 0 | 0 | 0
2025-05-01 12:00 | 41.2 | 11 | 100 | 29.597 | 17.6971 | 30.2213 | 0 | 0 | 0 | 0
2025-05-01 13:00 | 40.5 | 13 | 100 | 29.3806 | 17.8524 | 31.6838 | 0 | 0 | 0 | 0
2025-05-01 14:00 | 38.85 | 17.5 | 100 | 28.8722 | 18.1183 | 34.7642 | 10.7093 | 10.7093 | 0 | 0
2025-05-01 15:00 | 37.1 | 25 | 100 | 28.3152 | 18.6287 | 39.4595 | 52.5815 | 52.5815 | 0 | 0
2025-05-01 16:00 | 35.65 | 30.5 | 100 | 27.8583 | 18.8613 | 42.557 | 76.154 | 76.154 | 0 | 0
2025-05-01 17:00 | 33.95 | 36.5 | 100 | 27.3212 | 18.9944 | 45.6051 | 95.4354 | 95.4354 | 0 | 0
2025-05-01 18:00 | 32.05 | 45.5 | 100 | 26.7075 | 19.2493 | 49.8802 | 124.1322 | 124.1322 | 0 | 0
2025-05-01 19:00 | 30.8 | 49 | 100 | 26.3053 | 19.1427 | 51.2021 | 125.972 | 125.972 | 0 | 0
2025-05-01 20:00 | 30.05 | 48 | 100 | 26.0663 | 18.8143 | 50.4199 | 110.4912 | 110.4912 | 0 | 0
2025-05-01 21:00 | 29.35 | 49.5 | 100 | 25.8361 | 18.707 | 50.9058 | 108.6161 | 108.6161 | 0 | 0
2025-05-01 22:00 | 28.7 | 51 | 70 | 25.6201 | 18.6098 | 51.3958 | 75.0062 | 75.0062 | 0 | 0
2025-05-01 23:00 | 28.05 | 52 | 70 | 25.4028 | 18.4699 | 51.6441 | 72.1927 | 72.1927 | 0 | 0
2025-05-02 | 27.25 | 56.5 | 70 | 25.1297 | 18.529 | 53.4162 | 78.8722 | 78.8722 | 0 | 0
2025-05-02 01:00 | 26.3 | 65 | 70 | 24.8015 | 18.7833 | 56.7759 | 94.967 | 94.967 | 0 | 0
2025-05-02 02:00 | 25.65 | 72 | 70 | 24.5757 | 19.003 | 59.4527 | 108.1045 | 108.1045 | 0 | 0
2025-05-02 03:00 | 25.15 | 74 | 70 | 24.4026 | 18.9414 | 60.0309 | 108.0121 | 108.0121 | 0 | 0
2025-05-02 04:00 | 24.9 | 62 | 70 | 24.318 | 18.0885 | 54.958 | 72.0216 | 72.0216 | 0 | 0
2025-05-02 05:00 | 24.85 | 48.5 | 70 | 24.3028 | 17.1875 | 49.3447 | 33.8633 | 33.8633 | 0 | 0
2025-05-02 06:00 | 26 | 42.5 | 100 | 24.7087 | 17.128 | 46.9443 | 36.1991 | 36.1991 | 0 | 0
2025-05-02 07:00 | 29.1 | 33.5 | 100 | 25.7758 | 17.332 | 43.1223 | 26.1071 | 26.1071 | 0 | 0
2025-05-02 08:00 | 32.75 | 27 | 100 | 26.9784 | 17.7244 | 40.0791 | 24.8045 | 24.8045 | 0 | 0
2025-05-02 09:00 | 35.6 | 24.5 | 100 | 27.8706 | 18.1926 | 38.9247 | 34.7728 | 34.7728 | 0 | 0
2025-05-02 10:00 | 37.45 | 23 | 100 | 28.4292 | 18.4824 | 38.2244 | 41.01 | 41.01 | 0 | 0
2025-05-02 11:00 | 38.6 | 21 | 100 | 28.7758 | 18.5164 | 37.0682 | 36.1091 | 36.1091 | 0 | 0
2025-05-02 12:00 | 39.2 | 20 | 100 | 28.9549 | 18.5292 | 36.4708 | 33.4313 | 33.4313 | 0 | 0
2025-05-02 13:00 | 39.5 | 20 | 100 | 29.0403 | 18.5987 | 36.5106 | 36.072 | 36.072 | 0 | 0
2025-05-02 14:00 | 39.55 | 20 | 100 | 29.0545 | 18.6096 | 36.5208 | 36.556 | 36.556 | 0 | 0
2025-05-02 15:00 | 39.05 | 21 | 100 | 28.9049 | 18.6196 | 37.1409 | 40.2755 | 40.2755 | 0 | 0
2025-05-02 16:00 | 37.9 | 23.5 | 100 | 28.5574 | 18.6502 | 38.6321 | 49.168 | 49.168 | 0 | 0
2025-05-02 17:00 | 36.05 | 28.5 | 100 | 27.9868 | 18.7504 | 41.4409 | 66.8494 | 66.8494 | 0 | 0
2025-05-02 18:00 | 33.75 | 38.5 | 100 | 27.2532 | 19.1303 | 46.676 | 105.3629 | 105.3629 | 0 | 0
2025-05-02 19:00 | 31.95 | 49 | 100 | 26.6673 | 19.5235 | 51.6872 | 142.3294 | 142.3294 | 0 | 0
2025-05-02 20:00 | 30.8 | 54 | 100 | 26.2951 | 19.5567 | 53.7302 | 152.322 | 152.322 | 0 | 0
2025-05-02 21:00 | 29.8 | 56.5 | 100 | 25.9713 | 19.4102 | 54.4916 | 149.9627 | 149.9627 | 0 | 0
2025-05-02 22:00 | 28.85 | 60.5 | 70 | 25.6574 | 19.3805 | 55.9477 | 108.4055 | 108.4055 | 0 | 0
2025-05-02 23:00 | 27.9 | 64 | 70 | 25.3408 | 19.2938 | 57.0975 | 109.371 | 109.371 | 0 | 0
2025-05-03 | 27 | 66.5 | 70 | 25.0379 | 19.1398 | 57.7694 | 107.1609 | 107.1609 | 0 | 0
2025-05-03 01:00 | 26.3 | 68.5 | 70 | 24.7997 | 19.0167 | 58.2951 | 105.3502 | 105.3502 | 0 | 0
2025-05-03 02:00 | 25.8 | 69.5 | 70 | 24.6282 | 18.8974 | 58.4789 | 102.6971 | 102.6971 | 0 | 0
2025-05-03 03:00 | 25.4 | 69.5 | 70 | 24.4903 | 18.7494 | 58.2888 | 98.2799 | 98.2799 | 0 | 0
2025-05-03 04:00 | 25.45 | 65 | 70 | 24.509 | 18.4769 | 56.424 | 86.0771 | 86.0771 | 0 | 0
2025-05-03 05:00 | 25.65 | 60 | 70 | 24.58 | 18.2184 | 54.386 | 73.772 | 73.772 | 0 | 0
2025-05-03 06:00 | 26.6 | 54.5 | 100 | 24.91 | 18.1663 | 52.3175 | 95.0795 | 95.0795 | 0 | 0
2025-05-03 07:00 | 29.3 | 44.5 | 100 | 25.8269 | 18.2907 | 48.4819 | 83.2287 | 83.2287 | 0 | 0
2025-05-03 08:00 | 32.7 | 35 | 100 | 26.9396 | 18.4842 | 44.4446 | 71.805 | 71.805 | 0 | 0
2025-05-03 09:00 | 35.6 | 28.5 | 100 | 27.8525 | 18.6313 | 41.3393 | 62.0421 | 62.0421 | 0 | 0
2025-05-03 10:00 | 37.7 | 24.5 | 100 | 28.4932 | 18.7229 | 39.2375 | 54.6576 | 54.6576 | 0 | 0
2025-05-03 11:00 | 39.05 | 21.5 | 100 | 28.9013 | 18.6852 | 37.475 | 44.218 | 44.218 | 0 | 0
2025-05-03 12:00 | 39.45 | 20.5 | 100 | 29.0224 | 18.6499 | 36.8551 | 39.8071 | 39.8071 | 0 | 0
2025-05-03 13:00 | 39.1 | 21.5 | 100 | 28.9156 | 18.695 | 37.4917 | 44.7885 | 44.7885 | 0 | 0
2025-05-03 14:00 | 38.5 | 23 | 100 | 28.7337 | 18.7367 | 38.4079 | 51.096 | 51.096 | 0 | 0
2025-05-03 15:00 | 37.85 | 24.5 | 100 | 28.5368 | 18.7564 | 39.2836 | 56.3568 | 56.3568 | 0 | 0
2025-05-03 16:00 | 36.85 | 25 | 100 | 28.2417 | 18.5601 | 39.436 | 50.3748 | 50.3748 | 0 | 0
2025-05-03 17:00 | 35.2 | 28.5 | 100 | 27.7321 | 18.5189 | 41.2874 | 58.2095 | 58.2095 | 0 | 0
2025-05-03 18:00 | 33.25 | 36 | 100 | 27.1079 | 18.7361 | 45.149 | 84.2908 | 84.2908 | 0 | 0
2025-05-03 19:00 | 31.8 | 42 | 100 | 26.6379 | 18.8562 | 47.9649 | 101.4255 | 101.4255 | 0 | 0
2025-05-03 20:00 | 30.7 | 47.5 | 100 | 26.2764 | 18.9821 | 50.4209 | 116.8416 | 116.8416 | 0 | 0
2025-05-03 21:00 | 29.6 | 53 | 100 | 25.9123 | 19.065 | 52.7141 | 129.6795 | 129.6795 | 0 | 0
2025-05-03 22:00 | 28.95 | 54 | 70 | 25.6987 | 18.922 | 52.9314 | 87.7111 | 87.7111 | 0 | 0
2025-05-03 23:00 | 28.3 | 52.5 | 70 | 25.4856 | 18.5882 | 51.9871 | 76.3885 | 76.3885 | 0 | 0
2025-05-04 | 27.35 | 50.5 | 70 | 25.1684 | 18.1258 | 50.775 | 61.1694 | 61.1694 | 0 | 0
2025-05-04 01:00 | 26.85 | 46.5 | 70 | 25.0007 | 17.6735 | 48.8626 | 44.3677 | 44.3677 | 0 | 0
2025-05-04 02:00 | 26.55 | 43.5 | 70 | 24.8993 | 17.3621 | 47.4803 | 32.7297 | 32.7297 | 0 | 0
2025-05-04 03:00 | 26.25 | 43 | 70 | 24.7956 | 17.2352 | 47.2199 | 28.9145 | 28.9145 | 0 | 0
2025-05-04 04:00 | 26.5 | 38.5 | 70 | 24.8848 | 16.9812 | 45.2673 | 17.0314 | 17.0314 | 0 | 0
2025-05-04 05:00 | 26.65 | 33 | 70 | 24.9402 | 16.6122 | 42.8296 | 0.999 | 0.999 | 0 | 0
2025-05-04 06:00 | 27.6 | 29 | 100 | 25.2718 | 16.5558 | 40.9934 | 0 | 0 | 0 | 0
2025-05-04 07:00 | 30.7 | 22.5 | 100 | 26.3256 | 16.7746 | 37.6957 | 0 | 0 | 0 | 0
2025-05-04 08:00 | 34.75 | 16.5 | 100 | 27.6435 | 17.0892 | 34.1705 | 0 | 0 | 0 | 0
2025-05-04 09:00 | 38.2 | 12 | 100 | 28.7182 | 17.2544 | 31.121 | 0 | 0 | 0 | 0
2025-05-04 10:00 | 40.6 | 9.5 | 100 | 29.4392 | 17.3576 | 29.1956 | 0 | 0 | 0 | 0
2025-05-04 11:00 | 42.25 | 9 | 100 | 29.9124 | 17.5768 | 28.6889 | 0 | 0 | 0 | 0
2025-05-04 12:00 | 42.95 | 9.5 | 100 | 30.1017 | 17.7806 | 29.0271 | 0 | 0 | 0 | 0
2025-05-04 13:00 | 42.55 | 10.5 | 100 | 29.9804 | 17.8652 | 29.8148 | 0 | 0 | 0 | 0
2025-05-04 14:00 | 41.45 | 12 | 100 | 29.6587 | 17.8847 | 30.9701 | 0 | 0 | 0 | 0
2025-05-04 15:00 | 40 | 15.5 | 100 | 29.2179 | 18.092 | 33.4675 | 3.1719 | 3.1719 | 0 | 0
2025-05-04 16:00 | 37.85 | 22.5 | 100 | 28.5493 | 18.51 | 37.9979 | 41.4256 | 41.4256 | 0 | 0
2025-05-04 17:00 | 35.35 | 31 | 100 | 27.7664 | 18.8267 | 42.8121 | 76.5327 | 76.5327 | 0 | 0
2025-05-04 18:00 | 33.3 | 39 | 100 | 27.1137 | 19.0383 | 46.8323 | 103.021 | 103.021 | 0 | 0
2025-05-04 19:00 | 31.85 | 45 | 100 | 26.6462 | 19.1367 | 49.5679 | 118.9228 | 118.9228 | 0 | 0
2025-05-04 20:00 | 30.85 | 49.5 | 100 | 26.3201 | 19.1979 | 51.5 | 129.5836 | 129.5836 | 0 | 0
2025-05-04 21:00 | 30.15 | 51.5 | 100 | 26.0924 | 19.1294 | 52.2127 | 130.0458 | 130.0458 | 0 | 0
2025-05-04 22:00 | 29.55 | 50.5 | 70 | 25.8999 | 18.8492 | 51.488 | 81.6116 | 81.6116 | 0 | 0
2025-05-04 23:00 | 28.9 | 49.5 | 70 | 25.6881 | 18.5561 | 50.7849 | 72.0527 | 72.0527 | 0 | 0
2025-05-05 | 28.3 | 48.5 | 70 | 25.49 | 18.2831 | 50.1354 | 63.2795 | 63.2795 | 0 | 0
2025-05-05 01:00 | 27.85 | 46.5 | 70 | 25.341 | 17.9865 | 49.0944 | 52.8276 | 52.8276 | 0 | 0
2025-05-05 02:00 | 27.5 | 43 | 70 | 25.2256 | 17.6128 | 47.4212 | 38.6776 | 38.6776 | 0 | 0
2025-05-05 03:00 | 27.2 | 39.5 | 70 | 25.1258 | 17.2579 | 45.7897 | 25.2332 | 25.2332 | 0 | 0
2025-05-05 04:00 | 27.05 | 37 | 70 | 25.0761 | 17.0254 | 44.6466 | 16.2438 | 16.2438 | 0 | 0
2025-05-05 05:00 | 26.9 | 35.5 | 70 | 25.0253 | 16.8693 | 43.961 | 10.4832 | 10.4832 | 0 | 0
2025-05-05 06:00 | 27.7 | 32.5 | 100 | 25.303 | 16.8593 | 42.6152 | 8.5699 | 8.5699 | 0 | 0
2025-05-05 07:00 | 30.45 | 27 | 100 | 26.2346 | 17.1235 | 40.0019 | 5.0332 | 5.0332 | 0 | 0
2025-05-05 08:00 | 34.1 | 21.5 | 100 | 27.4215 | 17.4883 | 37.0953 | 2.5934 | 2.5934 | 0 | 0
2025-05-05 09:00 | 37.35 | 16.5 | 100 | 28.4376 | 17.6545 | 34.0874 | 0 | 0 | 0 | 0
2025-05-05 10:00 | 39.8 | 13 | 100 | 29.1802 | 17.7064 | 31.7144 | 0 | 0 | 0 | 0
2025-05-05 11:00 | 41.25 | 12 | 100 | 29.6023 | 17.8489 | 30.9653 | 0 | 0 | 0 | 0
2025-05-05 12:00 | 41.45 | 13 | 100 | 29.6491 | 18.0372 | 31.6949 | 0 | 0 | 0 | 0
2025-05-05 13:00 | 40.7 | 15 | 100 | 29.4204 | 18.1732 | 33.1301 | 3.8023 | 3.8023 | 0 | 0
2025-05-05 14:00 | 39.15 | 18 | 100 | 28.9554 | 18.2455 | 35.1405 | 17.3032 | 17.3032 | 0 | 0
2025-05-05 15:00 | 37.7 | 20.5 | 100 | 28.5177 | 18.2288 | 36.6837 | 25.0016 | 25.0016 | 0 | 0
2025-05-05 16:00 | 37.35 | 21 | 100 | 28.4117 | 18.2054 | 36.9764 | 25.8144 | 25.8144 | 0 | 0
2025-05-05 17:00 | 36.55 | 24 | 100 | 28.1583 | 18.3653 | 38.7781 | 40.5112 | 40.5112 | 0 | 0
2025-05-05 18:00 | 34.75 | 30 | 100 | 27.5895 | 18.5549 | 42.0928 | 63.5071 | 63.5071 | 0 | 0
2025-05-05 19:00 | 33.2 | 34.5 | 100 | 27.0971 | 18.5749 | 44.3154 | 74.7871 | 74.7871 | 0 | 0
2025-05-05 20:00 | 32.15 | 37.5 | 100 | 26.7598 | 18.553 | 45.6886 | 80.3287 | 80.3287 | 0 | 0
2025-05-05 21:00 | 31.25 | 38.5 | 100 | 26.4713 | 18.3762 | 45.9925 | 75.434 | 75.434 | 0 | 0
2025-05-05 22:00 | 30.4 | 37 | 70 | 26.1997 | 17.9942 | 45.0497 | 40.457 | 40.457 | 0 | 0
2025-05-05 23:00 | 29.6 | 39.5 | 70 | 25.9332 | 17.9701 | 46.1426 | 43.3275 | 43.3275 | 0 | 0
2025-05-06 | 28.85 | 50 | 70 | 25.671 | 18.5782 | 51.0084 | 73.3013 | 73.3013 | 0 | 0
2025-05-06 01:00 | 28.3 | 61.5 | 70 | 25.4756 | 19.2557 | 56.1749 | 105.9214 | 105.9214 | 0 | 0
2025-05-06 02:00 | 27.85 | 66 | 70 | 25.3222 | 19.4158 | 58.0116 | 115.3762 | 115.3762 | 0 | 0
2025-05-06 03:00 | 27.5 | 66 | 70 | 25.2059 | 19.2866 | 57.8284 | 111.4167 | 111.4167 | 0 | 0
2025-05-06 04:00 | 27.5 | 62 | 70 | 25.2093 | 19.0052 | 56.027 | 98.8952 | 98.8952 | 0 | 0
2025-05-06 05:00 | 27.45 | 59 | 70 | 25.1951 | 18.774 | 54.6505 | 88.9381 | 88.9381 | 0 | 0
2025-05-06 06:00 | 28.3 | 57 | 100 | 25.4807 | 18.9244 | 54.0835 | 130.2762 | 130.2762 | 0 | 0
2025-05-06 07:00 | 30.75 | 51 | 100 | 26.2853 | 19.2907 | 52.2081 | 135.9794 | 135.9794 | 0 | 0
2025-05-06 08:00 | 33.25 | 46 | 100 | 27.0758 | 19.6831 | 50.6527 | 143.8165 | 143.8165 | 0 | 0
2025-05-06 09:00 | 34.85 | 42 | 100 | 27.5704 | 19.8156 | 49.0851 | 141.6973 | 141.6973 | 0 | 0
2025-05-06 10:00 | 35.65 | 39.5 | 100 | 27.8165 | 19.8136 | 47.9477 | 136.3703 | 136.3703 | 0 | 0
2025-05-06 11:00 | 36.05 | 39 | 100 | 27.9353 | 19.8852 | 47.8135 | 138.4374 | 138.4374 | 0 | 0
2025-05-06 12:00 | 36.2 | 39 | 100 | 27.9786 | 19.9307 | 47.8791 | 140.5004 | 140.5004 | 0 | 0
2025-05-06 13:00 | 36.05 | 39.5 | 100 | 27.9328 | 19.9363 | 48.1234 | 141.895 | 141.895 | 0 | 0
2025-05-06 14:00 | 35.6 | 41.5 | 100 | 27.7925 | 20.0011 | 49.1325 | 149.058 | 149.058 | 0 | 0
2025-05-06 15:00 | 35.05 | 43 | 100 | 27.625 | 19.9763 | 49.7739 | 151.1066 | 151.1066 | 0 | 0
2025-05-06 16:00 | 34.85 | 43.5 | 100 | 27.564 | 19.9615 | 49.9769 | 151.49 | 151.49 | 0 | 0
2025-05-06 17:00 | 34.1 | 46.5 | 100 | 27.3299 | 20.0067 | 51.3424 | 159.3471 | 159.3471 | 0 | 0
2025-05-06 18:00 | 32.65 | 52 | 100 | 26.8746 | 20.0207 | 53.6403 | 169.9367 | 169.9367 | 0 | 0
2025-05-06 19:00 | 31.95 | 53 | 100 | 26.657 | 19.8673 | 53.8071 | 164.7205 | 164.7205 | 0 | 0
2025-05-06 20:00 | 31.85 | 50.5 | 100 | 26.6324 | 19.618 | 52.4455 | 149.3658 | 149.3658 | 0 | 0
2025-05-06 21:00 | 31.65 | 49.5 | 100 | 26.5725 | 19.4652 | 51.8314 | 140.9213 | 140.9213 | 0 | 0
2025-05-06 22:00 | 31.4 | 49 | 70 | 26.4952 | 19.3394 | 51.4643 | 94.224 | 94.224 | 0 | 0
2025-05-06 23:00 | 31.15 | 49 | 70 | 26.4163 | 19.2563 | 51.363 | 91.7667 | 91.7667 | 0 | 0
2025-05-07 | 30.55 | 51.5 | 70 | 26.2206 | 19.2639 | 52.3828 | 95.0653 | 95.0653 | 0 | 0
2025-05-07 01:00 | 29.6 | 57 | 70 | 25.906 | 19.3771 | 54.6661 | 104.7837 | 104.7837 | 0 | 0
2025-05-07 02:00 | 28.75 | 62 | 70 | 25.6228 | 19.4545 | 56.6288 | 112.4854 | 112.4854 | 0 | 0
2025-05-07 03:00 | 28.2 | 64.5 | 70 | 25.4394 | 19.4376 | 57.5031 | 114.4905 | 114.4905 | 0 | 0
2025-05-07 04:00 | 28.05 | 68 | 70 | 25.3863 | 19.6321 | 59.0251 | 123.9861 | 123.9861 | 0 | 0
2025-05-07 05:00 | 28.15 | 69 | 70 | 25.4181 | 19.7406 | 59.5376 | 128.341 | 128.341 | 0 | 0
2025-05-07 06:00 | 28.75 | 64.5 | 100 | 25.6196 | 19.6398 | 57.7902 | 172.405 | 172.405 | 0 | 0
2025-05-07 07:00 | 29.75 | 60.5 | 100 | 25.9487 | 19.7029 | 56.4206 | 169.2024 | 169.2024 | 0 | 0
2025-05-07 08:00 | 30.8 | 54 | 100 | 26.2951 | 19.5562 | 53.7306 | 152.3264 | 152.3264 | 0 | 0
2025-05-07 09:00 | 31.85 | 45 | 100 | 26.6462 | 19.1406 | 49.5396 | 118.6121 | 118.6121 | 0 | 0
2025-05-07 10:00 | 32.55 | 41 | 100 | 26.8756 | 19.0006 | 47.6549 | 105.0481 | 105.0481 | 0 | 0
2025-05-07 11:00 | 33 | 39.5 | 100 | 27.0196 | 18.9983 | 46.9874 | 101.9741 | 101.9741 | 0 | 0
2025-05-07 12:00 | 33.1 | 38 | 100 | 27.0551 | 18.8858 | 46.1993 | 94.3521 | 94.3521 | 0 | 0
2025-05-07 13:00 | 32.8 | 39 | 100 | 26.9591 | 18.8886 | 46.6627 | 96.6598 | 96.6598 | 0 | 0
2025-05-07 14:00 | 32.35 | 41 | 100 | 26.8132 | 18.9362 | 47.608 | 102.7109 | 102.7109 | 0 | 0
2025-05-07 15:00 | 31.75 | 44 | 100 | 26.6173 | 19.0175 | 48.9996 | 111.9444 | 111.9444 | 0 | 0
2025-05-07 16:00 | 30.9 | 44.5 | 100 | 26.3464 | 18.7921 | 48.972 | 103.5956 | 103.5956 | 0 | 0
2025-05-07 17:00 | 29.8 | 46.5 | 100 | 25.9877 | 18.6087 | 49.6188 | 99.7737 | 99.7737 | 0 | 0
2025-05-07 18:00 | 28.65 | 53 | 100 | 25.6011 | 18.7433 | 52.3464 | 116.3086 | 116.3086 | 0 | 0
2025-05-07 19:00 | 27.85 | 56 | 100 | 25.3319 | 18.6965 | 53.4354 | 119.094 | 119.094 | 0 | 0
2025-05-07 20:00 | 27.35 | 58 | 100 | 25.1623 | 18.669 | 54.1458 | 120.9784 | 120.9784 | 0 | 0
2025-05-07 21:00 | 26.9 | 61.5 | 100 | 25.0077 | 18.7582 | 55.5202 | 129.8261 | 129.8261 | 0 | 0
2025-05-07 22:00 | 26.5 | 63 | 70 | 24.8708 | 18.7189 | 56.0109 | 91.2481 | 91.2481 | 0 | 0
2025-05-07 23:00 | 26.1 | 64 | 70 | 24.7336 | 18.643 | 56.2793 | 90.0538 | 90.0538 | 0 | 0
2025-05-08 | 25.7 | 66 | 70 | 24.5951 | 18.6308 | 56.9683 | 91.6831 | 91.6831 | 0 | 0
2025-05-08 01:00 | 25.3 | 67.5 | 70 | 24.4563 | 18.5826 | 57.4317 | 91.7276 | 91.7276 | 0 | 0
2025-05-08 02:00 | 24.9 | 68.5 | 70 | 24.3168 | 18.5008 | 57.6759 | 90.2586 | 90.2586 | 0 | 0
2025-05-08 03:00 | 24.6 | 70 | 70 | 24.2115 | 18.4847 | 58.1619 | 91.1576 | 91.1576 | 0 | 0
2025-05-08 04:00 | 24.1 | 69 | 70 | 24.0354 | 18.2398 | 57.5473 | 83.1548 | 83.1548 | 0 | 0
2025-05-08 05:00 | 23.65 | 67.5 | 70 | 23.8754 | 17.9867 | 56.7751 | 74.552 | 74.552 | 0 | 0
2025-05-08 06:00 | 24.55 | 65.5 | 100 | 24.1945 | 18.1861 | 56.2955 | 111.8842 | 111.8842 | 0 | 0
2025-05-08 07:00 | 27.05 | 59 | 100 | 25.0602 | 18.6354 | 54.4817 | 121.1577 | 121.1577 | 0 | 0
2025-05-08 08:00 | 29.6 | 52.5 | 100 | 25.913 | 19.0246 | 52.4742 | 127.2181 | 127.2181 | 0 | 0
2025-05-08 09:00 | 31 | 49 | 100 | 26.3688 | 19.2069 | 51.2949 | 128.9084 | 128.9084 | 0 | 0
2025-05-08 10:00 | 31.7 | 47 | 100 | 26.5942 | 19.2657 | 50.5437 | 127.8136 | 127.8136 | 0 | 0
2025-05-08 11:00 | 32.2 | 45.5 | 100 | 26.7543 | 19.2957 | 49.9515 | 126.3243 | 126.3243 | 0 | 0
2025-05-08 12:00 | 32.4 | 45.5 | 100 | 26.8164 | 19.3599 | 50.0318 | 129.0837 | 129.0837 | 0 | 0
2025-05-08 13:00 | 32.35 | 46.5 | 100 | 26.7981 | 19.4331 | 50.5487 | 134.1177 | 134.1177 | 0 | 0
2025-05-08 14:00 | 32.05 | 48.5 | 100 | 26.6997 | 19.511 | 51.486 | 141.1794 | 141.1794 | 0 | 0
2025-05-08 15:00 | 31.45 | 50 | 100 | 26.5086 | 19.4407 | 52.0082 | 140.8181 | 140.8181 | 0 | 0
2025-05-08 16:00 | 30.75 | 48.5 | 100 | 26.2903 | 19.0818 | 50.9527 | 122.8861 | 122.8861 | 0 | 0
2025-05-08 17:00 | 29.75 | 49.5 | 100 | 25.9665 | 18.8345 | 51.0763 | 114.3344 | 114.3344 | 0 | 0
2025-05-08 18:00 | 28.55 | 54 | 100 | 25.5669 | 18.7856 | 52.7822 | 119.7092 | 119.7092 | 0 | 0
2025-05-08 19:00 | 27.75 | 57 | 100 | 25.2975 | 18.7352 | 53.8536 | 122.2431 | 122.2431 | 0 | 0
2025-05-08 20:00 | 27.25 | 60.5 | 100 | 25.1266 | 18.812 | 55.2236 | 130.6255 | 130.6255 | 0 | 0
2025-05-08 21:00 | 26.7 | 65.5 | 100 | 24.9373 | 18.9619 | 57.185 | 144.0482 | 144.0482 | 0 | 0
2025-05-08 22:00 | 26.05 | 70 | 70 | 24.7137 | 19.0229 | 58.8129 | 106.9239 | 106.9239 | 0 | 0
2025-05-08 23:00 | 25.35 | 73 | 70 | 24.472 | 18.9536 | 59.7255 | 107.5601 | 107.5601 | 0 | 0
2025-05-09 | 24.6 | 75.5 | 70 | 24.2109 | 18.8244 | 60.3751 | 105.8901 | 105.8901 | 0 | 0
2025-05-09 01:00 | 23.9 | 77.5 | 70 | 23.9647 | 18.678 | 60.8274 | 103.2056 | 103.2056 | 0 | 0
2025-05-09 02:00 | 23.3 | 78.5 | 70 | 23.7516 | 18.5076 | 60.9259 | 98.9509 | 98.9509 | 0 | 0
2025-05-09 03:00 | 22.7 | 79.5 | 70 | 23.5365 | 18.3351 | 61.0253 | 94.6743 | 94.6743 | 0 | 0
2025-05-09 04:00 | 22.3 | 76.5 | 70 | 23.391 | 18.015 | 59.7137 | 82.9564 | 82.9564 | 0 | 0
2025-05-09 05:00 | 22.1 | 73 | 70 | 23.317 | 17.7452 | 58.3213 | 72.407 | 72.407 | 0 | 0
2025-05-09 06:00 | 22.8 | 69.5 | 100 | 23.5704 | 17.8005 | 57.2317 | 101.2937 | 101.2937 | 0 | 0
2025-05-09 07:00 | 25.1 | 60 | 100 | 24.3885 | 18.0291 | 54.1931 | 97.6731 | 97.6731 | 0 | 0
2025-05-09 08:00 | 27.95 | 51 | 100 | 25.3703 | 18.362 | 51.156 | 97.2127 | 97.2127 | 0 | 0
2025-05-09 09:00 | 30.25 | 46 | 100 | 26.1345 | 18.7143 | 49.4928 | 102.8071 | 102.8071 | 0 | 0
2025-05-09 10:00 | 32.15 | 40.5 | 100 | 26.7519 | 18.8319 | 47.2578 | 97.1163 | 97.1163 | 0 | 0
2025-05-09 11:00 | 33.9 | 34.5 | 100 | 27.3131 | 18.7819 | 44.4574 | 82.4156 | 82.4156 | 0 | 0
2025-05-09 12:00 | 35.15 | 31.5 | 100 | 27.7041 | 18.829 | 43.0358 | 77.3482 | 77.3482 | 0 | 0
2025-05-09 13:00 | 35.35 | 35.5 | 100 | 27.7464 | 19.3065 | 45.4606 | 106.0836 | 106.0836 | 0 | 0
2025-05-09 14:00 | 34.45 | 44 | 100 | 27.4437 | 19.8831 | 50.0661 | 148.747 | 148.747 | 0 | 0
2025-05-09 15:00 | 33.3 | 48.5 | 100 | 27.0829 | 19.9287 | 52.0532 | 159.3478 | 159.3478 | 0 | 0
2025-05-09 16:00 | 32.2 | 51.5 | 100 | 26.7382 | 19.8243 | 53.1302 | 160.0595 | 160.0595 | 0 | 0
2025-05-09 17:00 | 30.7 | 59 | 100 | 26.2533 | 19.9258 | 56.2036 | 176.9529 | 176.9529 | 0 | 0
2025-05-09 18:00 | 29.05 | 70 | 100 | 25.7096 | 20.1542 | 60.5544 | 203.559 | 203.559 | 0 | 0
2025-05-09 19:00 | 27.8 | 80 | 100 | 25.2923 | 20.3652 | 64.2888 | 226.49 | 226.49 | 0 | 0
2025-05-09 20:00 | 27.05 | 85.5 | 100 | 25.0408 | 20.4237 | 66.1561 | 235.8868 | 235.8868 | 0 | 0
2025-05-09 21:00 | 26.55 | 88.5 | 100 | 24.8727 | 20.4084 | 67.0599 | 238.6005 | 238.6005 | 0 | 0
2025-05-09 22:00 | 25.95 | 91.5 | 70 | 24.67 | 20.3442 | 67.8569 | 167.2304 | 167.2304 | 0 | 0
2025-05-09 23:00 | 25.15 | 95 | 70 | 24.3974 | 20.2169 | 68.6715 | 165.685 | 165.685 | 0 | 0
2025-05-10 | 24.3 | 98 | 70 | 24.1043 | 20.0294 | 69.2095 | 161.711 | 161.711 | 0 | 0
2025-05-10 01:00 | 23.55 | 99.5 | 70 | 23.8425 | 19.7938 | 69.219 | 155.0731 | 155.0731 | 0 | 0
2025-05-10 02:00 | 22.85 | 100 | 70 | 23.5949 | 19.5237 | 68.8885 | 146.6614 | 146.6614 | 0 | 0
2025-05-10 03:00 | 22.3 | 100 | 70 | 23.398 | 19.2904 | 68.4938 | 139.2 | 139.2 | 0 | 0
2025-05-10 04:00 | 22.65 | 100 | 70 | 23.5235 | 19.439 | 68.7404 | 143.9153 | 143.9153 | 0 | 0
2025-05-10 05:00 | 23.35 | 99.5 | 70 | 23.772 | 19.7085 | 69.0626 | 152.2659 | 152.2659 | 0 | 0
2025-05-10 06:00 | 23.7 | 99 | 100 | 23.8951 | 19.83 | 69.1288 | 222.6098 | 222.6098 | 0 | 0
2025-05-10 07:00 | 23.95 | 98.5 | 100 | 23.9826 | 19.9083 | 69.1199 | 225.715 | 225.715 | 0 | 0
2025-05-10 08:00 | 25.3 | 89.5 | 100 | 24.4501 | 19.9523 | 66.5129 | 218.0219 | 218.0219 | 0 | 0
2025-05-10 09:00 | 28.1 | 72 | 100 | 25.3986 | 19.9352 | 60.8384 | 195.7368 | 195.7368 | 0 | 0
2025-05-10 10:00 | 31.1 | 56 | 100 | 26.3854 | 19.827 | 54.8714 | 167.2486 | 167.2486 | 0 | 0
2025-05-10 11:00 | 33.6 | 46.5 | 100 | 27.1802 | 19.8472 | 51.0598 | 151.5217 | 151.5217 | 0 | 0
2025-05-10 12:00 | 34.8 | 45.5 | 100 | 27.5412 | 20.1466 | 51.0708 | 162.9812 | 162.9812 | 0 | 0
2025-05-10 13:00 | 34.8 | 49.5 | 100 | 27.5246 | 20.5315 | 53.3873 | 188.2358 | 188.2358 | 0 | 0
2025-05-10 14:00 | 34.2 | 51 | 100 | 27.3428 | 20.4664 | 53.9101 | 188.0809 | 188.0809 | 0 | 0
2025-05-10 15:00 | 33.4 | 51.5 | 100 | 27.1031 | 20.2361 | 53.749 | 178.5033 | 178.5033 | 0 | 0
2025-05-10 16:00 | 32.15 | 53.5 | 100 | 26.7174 | 19.9805 | 54.1587 | 170.4306 | 170.4306 | 0 | 0
2025-05-10 17:00 | 30.9 | 56.5 | 100 | 26.3214 | 19.7951 | 55.0509 | 167.0738 | 167.0738 | 0 | 0
2025-05-10 18:00 | 30 | 62.5 | 100 | 26.0252 | 19.9477 | 57.5361 | 183.2723 | 183.2723 | 0 | 0
2025-05-10 19:00 | 29.25 | 66.5 | 100 | 25.7789 | 19.9732 | 59.0162 | 190.2317 | 190.2317 | 0 | 0
2025-05-10 20:00 | 28.85 | 68 | 100 | 25.6477 | 19.9334 | 59.4763 | 190.4789 | 190.4789 | 0 | 0
2025-05-10 21:00 | 28.55 | 70 | 100 | 25.5478 | 19.9646 | 60.2204 | 194.6214 | 194.6214 | 0 | 0
2025-05-10 22:00 | 28.15 | 72.5 | 70 | 25.4144 | 19.988 | 61.1157 | 139.3467 | 139.3467 | 0 | 0
2025-05-10 23:00 | 27.55 | 75 | 70 | 25.2147 | 19.9285 | 61.8603 | 139.7297 | 139.7297 | 0 | 0
2025-05-11 | 26.9 | 78 | 70 | 24.9963 | 19.8739 | 62.7659 | 140.699 | 140.699 | 0 | 0
2025-05-11 01:00 | 26.3 | 82 | 70 | 24.7926 | 19.8949 | 64.0962 | 144.8219 | 144.8219 | 0 | 0
2025-05-11 02:00 | 25.8 | 85 | 70 | 24.622 | 19.8819 | 65.0242 | 146.9037 | 146.9037 | 0 | 0
2025-05-11 03:00 | 25.25 | 87.5 | 70 | 24.4336 | 19.8107 | 65.6784 | 146.6233 | 146.6233 | 0 | 0
2025-05-11 04:00 | 24.95 | 84 | 70 | 24.3311 | 19.4778 | 64.0383 | 133.1507 | 133.1507 | 0 | 0
2025-05-11 05:00 | 24.8 | 78 | 70 | 24.2802 | 19.0545 | 61.4945 | 114.9644 | 114.9644 | 0 | 0
2025-05-11 06:00 | 25.5 | 72 | 100 | 24.5241 | 18.9468 | 59.3787 | 152.0233 | 152.0233 | 0 | 0
2025-05-11 07:00 | 27.9 | 60 | 100 | 25.3447 | 19.0066 | 55.2658 | 137.9401 | 137.9401 | 0 | 0
2025-05-11 08:00 | 30.85 | 47 | 100 | 26.3253 | 18.9921 | 50.1981 | 115.9586 | 115.9586 | 0 | 0
2025-05-11 09:00 | 33.7 | 35.5 | 100 | 27.2482 | 18.8247 | 44.9588 | 86.1603 | 86.1603 | 0 | 0
2025-05-11 10:00 | 35.9 | 28.5 | 100 | 27.9422 | 18.714 | 41.3936 | 65.0898 | 65.0898 | 0 | 0
2025-05-11 11:00 | 36.95 | 29 | 100 | 28.249 | 19.0539 | 41.9379 | 79.783 | 79.783 | 0 | 0
2025-05-11 12:00 | 37.25 | 31 | 100 | 28.3246 | 19.3654 | 43.2818 | 97.5701 | 97.5701 | 0 | 0
2025-05-11 13:00 | 37.35 | 29.5 | 100 | 28.3621 | 19.2194 | 42.3656 | 87.917 | 87.917 | 0 | 0
2025-05-11 14:00 | 37.05 | 27.5 | 100 | 28.2866 | 18.9049 | 41.0359 | 70.283 | 70.283 | 0 | 0
2025-05-11 15:00 | 36.4 | 28 | 100 | 28.0931 | 18.7871 | 41.2146 | 67.1155 | 67.1155 | 0 | 0
2025-05-11 16:00 | 34.95 | 35 | 100 | 27.6293 | 19.1349 | 45.0523 | 98.0871 | 98.0871 | 0 | 0
2025-05-11 17:00 | 33 | 45.5 | 100 | 27.0011 | 19.5547 | 50.2793 | 137.433 | 137.433 | 0 | 0
2025-05-11 18:00 | 31.55 | 55.5 | 100 | 26.5269 | 19.9404 | 54.8922 | 172.0752 | 172.0752 | 0 | 0
2025-05-11 19:00 | 30.5 | 63.5 | 100 | 26.1815 | 20.2088 | 58.3361 | 196.833 | 196.833 | 0 | 0
2025-05-11 20:00 | 29.95 | 64.5 | 100 | 26.0059 | 20.0829 | 58.486 | 192.4515 | 192.4515 | 0 | 0
2025-05-11 21:00 | 29.5 | 62.5 | 100 | 25.8653 | 19.7655 | 57.2505 | 175.0123 | 175.0123 | 0 | 0
2025-05-11 22:00 | 28.9 | 62 | 70 | 25.6718 | 19.5103 | 56.6869 | 114.0145 | 114.0145 | 0 | 0
2025-05-11 23:00 | 28.15 | 64 | 70 | 25.4235 | 19.3841 | 57.2327 | 112.2135 | 112.2135 | 0 | 0
2025-05-12 | 27.3 | 68.5 | 70 | 25.137 | 19.3872 | 58.8247 | 116.7726 | 116.7726 | 0 | 0
2025-05-12 01:00 | 26.5 | 73 | 70 | 24.865 | 19.389 | 60.3609 | 121.0345 | 121.0345 | 0 | 0
2025-05-12 02:00 | 25.85 | 75 | 70 | 24.6431 | 19.2706 | 60.8508 | 119.1606 | 119.1606 | 0 | 0
2025-05-12 03:00 | 25.3 | 75 | 70 | 24.4542 | 19.0597 | 60.5473 | 112.6864 | 112.6864 | 0 | 0
2025-05-12 04:00 | 25.2 | 71.5 | 70 | 24.4205 | 18.8014 | 59.0408 | 101.7687 | 101.7687 | 0 | 0
2025-05-12 05:00 | 25.2 | 67 | 70 | 24.4217 | 18.5151 | 57.168 | 89.1749 | 89.1749 | 0 | 0
2025-05-12 06:00 | 25.95 | 61 | 100 | 24.6833 | 18.3892 | 54.9292 | 113.8716 | 113.8716 | 0 | 0
2025-05-12 07:00 | 28.6 | 50 | 100 | 25.5882 | 18.4975 | 50.9129 | 101.2529 | 101.2529 | 0 | 0
2025-05-12 08:00 | 31.9 | 38 | 100 | 26.6795 | 18.5267 | 45.8754 | 80.0709 | 80.0709 | 0 | 0
2025-05-12 09:00 | 34.85 | 28 | 100 | 27.628 | 18.3752 | 40.9195 | 51.2323 | 51.2323 | 0 | 0
2025-05-12 10:00 | 37.15 | 22 | 100 | 28.3468 | 18.284 | 37.5722 | 31.2071 | 31.2071 | 0 | 0
2025-05-12 11:00 | 38.8 | 19.5 | 100 | 28.8439 | 18.3658 | 36.1084 | 26.2653 | 26.2653 | 0 | 0
2025-05-12 12:00 | 39.75 | 19.5 | 100 | 29.115 | 18.5871 | 36.2098 | 34.2929 | 34.2929 | 0 | 0
2025-05-12 13:00 | 40.1 | 18.5 | 100 | 29.2218 | 18.5314 | 35.5574 | 28.9766 | 28.9766 | 0 | 0
2025-05-12 14:00 | 39.9 | 16.5 | 100 | 29.1814 | 18.2109 | 34.1537 | 10.7398 | 10.7398 | 0 | 0
2025-05-12 15:00 | 39.15 | 17 | 100 | 28.9627 | 18.1117 | 34.4642 | 9.259 | 9.259 | 0 | 0
2025-05-12 16:00 | 37.9 | 19 | 100 | 28.5856 | 18.0876 | 35.7282 | 15.3025 | 15.3025 | 0 | 0
2025-05-12 17:00 | 36.15 | 22.5 | 100 | 28.0462 | 18.0921 | 37.8098 | 26.3651 | 26.3651 | 0 | 0
2025-05-12 18:00 | 34.15 | 31 | 100 | 27.4024 | 18.4936 | 42.5531 | 63.5985 | 63.5985 | 0 | 0
2025-05-12 19:00 | 32.5 | 38 | 100 | 26.8684 | 18.7029 | 46.0495 | 87.3517 | 87.3517 | 0 | 0
2025-05-12 20:00 | 31.6 | 38 | 100 | 26.5842 | 18.4352 | 45.8168 | 76.7418 | 76.7418 | 0 | 0
2025-05-12 21:00 | 31.05 | 36 | 100 | 26.4124 | 18.095 | 44.658 | 59.4968 | 59.4968 | 0 | 0
2025-05-12 22:00 | 30.25 | 36 | 70 | 26.1525 | 17.8648 | 44.5187 | 35.6138 | 35.6138 | 0 | 0
2025-05-12 23:00 | 29.05 | 41 | 70 | 25.7491 | 17.9281 | 46.758 | 44.1986 | 44.1986 | 0 | 0
2025-05-13 | 28 | 47 | 70 | 25.3911 | 18.0736 | 49.3508 | 55.6618 | 55.6618 | 0 | 0
2025-05-13 01:00 | 27.2 | 47 | 70 | 25.1201 | 17.8193 | 49.1634 | 48.8636 | 48.8636 | 0 | 0
2025-05-13 02:00 | 26.4 | 44.5 | 70 | 24.8468 | 17.3883 | 47.9002 | 34.6283 | 34.6283 | 0 | 0
2025-05-13 03:00 | 25.65 | 44 | 70 | 24.5858 | 17.1242 | 47.5776 | 27.3395 | 27.3395 | 0 | 0
2025-05-13 04:00 | 25.65 | 42.5 | 70 | 24.5863 | 17.0191 | 46.9339 | 22.9317 | 22.9317 | 0 | 0
2025-05-13 05:00 | 25.95 | 39.5 | 70 | 24.6926 | 16.895 | 45.6633 | 16.1876 | 16.1876 | 0 | 0
2025-05-13 06:00 | 27 | 34.5 | 100 | 25.0606 | 16.8233 | 43.5002 | 11.2616 | 11.2616 | 0 | 0
2025-05-13 07:00 | 30.25 | 27.5 | 100 | 26.1677 | 17.1183 | 40.2431 | 5.9152 | 5.9152 | 0 | 0
2025-05-13 08:00 | 34.15 | 21 | 100 | 27.4389 | 17.4488 | 36.8005 | 0 | 0 | 0 | 0
2025-05-13 09:00 | 37.1 | 17.5 | 100 | 28.3571 | 17.726 | 34.7151 | 0 | 0 | 0 | 0
2025-05-13 10:00 | 39.25 | 16 | 100 | 28.9987 | 18.0059 | 33.769 | 1.6509 | 1.6509 | 0 | 0
2025-05-13 11:00 | 40.9 | 14.5 | 100 | 29.4809 | 18.1479 | 32.7654 | 0.6891 | 0.6891 | 0 | 0
2025-05-13 12:00 | 42.05 | 12.5 | 100 | 29.8209 | 18.0837 | 31.3214 | 0 | 0 | 0 | 0
2025-05-13 13:00 | 42.45 | 11.5 | 100 | 29.942 | 18.005 | 30.5723 | 0 | 0 | 0 | 0
2025-05-13 14:00 | 42.05 | 12.5 | 100 | 29.8211 | 18.0802 | 31.3304 | 0 | 0 | 0 | 0
2025-05-13 15:00 | 40.7 | 15 | 100 | 29.4204 | 18.1718 | 33.1345 | 3.859 | 3.859 | 0 | 0
2025-05-13 16:00 | 38.95 | 20 | 100 | 28.8837 | 18.4609 | 36.477 | 31.7147 | 31.7147 | 0 | 0
2025-05-13 17:00 | 36.65 | 27.5 | 100 | 28.1694 | 18.7948 | 40.9666 | 66.3037 | 66.3037 | 0 | 0
2025-05-13 18:00 | 34.15 | 36.5 | 100 | 27.3821 | 19.0504 | 45.6878 | 98.1151 | 98.1151 | 0 | 0
2025-05-13 19:00 | 32.55 | 46 | 100 | 26.8613 | 19.453 | 50.3675 | 134.0992 | 134.0992 | 0 | 0
2025-05-13 20:00 | 31.75 | 48 | 100 | 26.6074 | 19.3689 | 51.0903 | 134.0752 | 134.0752 | 0 | 0
2025-05-13 21:00 | 31.2 | 46 | 100 | 26.4388 | 19.0169 | 49.8373 | 115.5534 | 115.5534 | 0 | 0
2025-05-13 22:00 | 30.35 | 46.5 | 70 | 26.1659 | 18.7854 | 49.7946 | 74.8434 | 74.8434 | 0 | 0
2025-05-13 23:00 | 29.5 | 45.5 | 70 | 25.8912 | 18.4323 | 49.0393 | 63.6256 | 63.6256 | 0 | 0
2025-05-14 | 28.6 | 46.5 | 70 | 25.5924 | 18.2258 | 49.2718 | 59.1964 | 59.1964 | 0 | 0
2025-05-14 01:00 | 27.75 | 47 | 70 | 25.3068 | 17.9939 | 49.2887 | 53.5118 | 53.5118 | 0 | 0
2025-05-14 02:00 | 26.95 | 44.5 | 70 | 25.0364 | 17.5581 | 47.9892 | 38.9627 | 38.9627 | 0 | 0
2025-05-14 03:00 | 26.3 | 41.5 | 70 | 24.8137 | 17.1417 | 46.5673 | 24.7352 | 24.7352 | 0 | 0
2025-05-14 04:00 | 26.55 | 38 | 70 | 24.9025 | 16.9595 | 45.0443 | 15.8037 | 15.8037 | 0 | 0
2025-05-14 05:00 | 27.35 | 33 | 70 | 25.1824 | 16.8046 | 42.8284 | 5.3415 | 5.3415 | 0 | 0
2025-05-14 06:00 | 29.3 | 23.5 | 100 | 25.8569 | 16.5265 | 38.2837 | 0 | 0 | 0 | 0
2025-05-14 07:00 | 32.5 | 17.5 | 100 | 26.9252 | 16.704 | 34.9117 | 0 | 0 | 0 | 0
2025-05-14 08:00 | 35.25 | 22 | 100 | 27.7753 | 17.8232 | 37.4158 | 14.9985 | 14.9985 | 0 | 0
2025-05-14 09:00 | 37.6 | 25 | 100 | 28.4612 | 18.7577 | 39.54 | 57.3853 | 57.3853 | 0 | 0
2025-05-14 10:00 | 39.85 | 21.5 | 100 | 29.1273 | 18.8819 | 37.591 | 51.4557 | 51.4557 | 0 | 0
2025-05-14 11:00 | 41.7 | 16.5 | 100 | 29.6844 | 18.6145 | 34.2577 | 24.2543 | 24.2543 | 0 | 0
2025-05-14 12:00 | 42.75 | 13 | 100 | 30.0079 | 18.3047 | 31.699 | 0 | 0 | 0 | 0
2025-05-14 13:00 | 42.5 | 15 | 100 | 29.9183 | 18.5608 | 33.2102 | 16.7005 | 16.7005 | 0 | 0
2025-05-14 14:00 | 41.2 | 21.5 | 100 | 29.5 | 19.209 | 37.8441 | 64.2924 | 64.2924 | 0 | 0
2025-05-14 15:00 | 39.85 | 25.5 | 100 | 29.0954 | 19.4023 | 40.3703 | 84.3902 | 84.3902 | 0 | 0
2025-05-14 16:00 | 38.35 | 29 | 100 | 28.6508 | 19.434 | 42.3264 | 95.5246 | 95.5246 | 0 | 0
2025-05-14 17:00 | 36.15 | 36 | 100 | 27.9792 | 19.5962 | 46.0398 | 119.4879 | 119.4879 | 0 | 0
2025-05-14 18:00 | 33.9 | 44 | 100 | 27.2792 | 19.7053 | 49.8289 | 141.0401 | 141.0401 | 0 | 0
2025-05-14 19:00 | 32.7 | 48.5 | 100 | 26.9002 | 19.7282 | 51.7681 | 150.488 | 150.488 | 0 | 0
2025-05-14 20:00 | 32.2 | 47.5 | 100 | 26.7489 | 19.4741 | 51.0077 | 137.5543 | 137.5543 | 0 | 0
2025-05-14 21:00 | 31.45 | 45.5 | 100 | 26.5191 | 19.0552 | 49.6608 | 116.0851 | 116.0851 | 0 | 0
2025-05-14 22:00 | 30.75 | 44.5 | 70 | 26.2984 | 18.7466 | 48.9095 | 71.0561 | 71.0561 | 0 | 0
2025-05-14 23:00 | 30.05 | 44.5 | 70 | 26.0724 | 18.5249 | 48.6978 | 64.8408 | 64.8408 | 0 | 0
2025-05-15 | 29.3 | 45 | 70 | 25.8262 | 18.3296 | 48.7336 | 60.0742 | 60.0742 | 0 | 0
2025-05-15 01:00 | 28.45 | 46 | 70 | 25.543 | 18.1405 | 48.9879 | 56.1531 | 56.1531 | 0 | 0
2025-05-15 02:00 | 27.65 | 47 | 70 | 25.273 | 17.9633 | 49.2541 | 52.5821 | 52.5821 | 0 | 0
2025-05-15 03:00 | 27.05 | 47 | 70 | 25.0689 | 17.7739 | 49.1161 | 47.502 | 47.502 | 0 | 0
2025-05-15 04:00 | 26.95 | 45.5 | 70 | 25.0357 | 17.6332 | 48.4206 | 41.9686 | 41.9686 | 0 | 0
2025-05-15 05:00 | 27.2 | 42.5 | 70 | 25.1235 | 17.4888 | 47.1113 | 34.498 | 34.498 | 0 | 0
2025-05-15 06:00 | 28.7 | 33 | 100 | 25.6422 | 17.1781 | 42.8624 | 19.9038 | 19.9038 | 0 | 0
2025-05-15 07:00 | 31.9 | 22 | 100 | 26.7192 | 17.019 | 37.3651 | 0 | 0 | 0 | 0
2025-05-15 08:00 | 34.9 | 19 | 100 | 27.6799 | 17.4086 | 35.6188 | 0 | 0 | 0 | 0
2025-05-15 09:00 | 37.25 | 18.5 | 100 | 28.3961 | 17.8872 | 35.3386 | 6.0373 | 6.0373 | 0 | 0
2025-05-15 10:00 | 39.25 | 17 | 100 | 28.9912 | 18.1448 | 34.4338 | 9.5736 | 9.5736 | 0 | 0
2025-05-15 11:00 | 40.65 | 15.5 | 100 | 29.4016 | 18.2439 | 33.4551 | 7.394 | 7.394 | 0 | 0
2025-05-15 12:00 | 40.35 | 18 | 100 | 29.296 | 18.5273 | 35.2073 | 26.5082 | 26.5082 | 0 | 0
2025-05-15 13:00 | 39.5 | 20.5 | 100 | 29.0365 | 18.6656 | 36.8502 | 40.1053 | 40.1053 | 0 | 0
2025-05-15 14:00 | 39 | 21 | 100 | 28.8906 | 18.6098 | 37.1281 | 39.7539 | 39.7539 | 0 | 0
2025-05-15 15:00 | 38.2 | 23 | 100 | 28.6474 | 18.6657 | 38.347 | 48.1162 | 48.1162 | 0 | 0
2025-05-15 16:00 | 37.45 | 24.5 | 100 | 28.4205 | 18.6581 | 39.2007 | 52.3087 | 52.3087 | 0 | 0
2025-05-15 17:00 | 36.1 | 29 | 100 | 27.9992 | 18.8199 | 41.753 | 70.7852 | 70.7852 | 0 | 0
2025-05-15 18:00 | 33.95 | 39.5 | 100 | 27.3105 | 19.2884 | 47.3052 | 114.0275 | 114.0275 | 0 | 0
2025-05-15 19:00 | 32.35 | 45.5 | 100 | 26.8009 | 19.345 | 50.0035 | 128.3036 | 128.3036 | 0 | 0
2025-05-15 20:00 | 31.45 | 46.5 | 100 | 26.5168 | 19.1419 | 50.1789 | 121.5506 | 121.5506 | 0 | 0
2025-05-15 21:00 | 30.55 | 49.5 | 100 | 26.2245 | 19.1008 | 51.359 | 125.1516 | 125.1516 | 0 | 0
2025-05-15 22:00 | 30.05 | 50.5 | 70 | 26.062 | 19.0173 | 51.6604 | 86.3318 | 86.3318 | 0 | 0
2025-05-15 23:00 | 29.8 | 50.5 | 70 | 25.9811 | 18.9336 | 51.5652 | 83.9048 | 83.9048 | 0 | 0
2025-05-16 | 29.15 | 53.5 | 70 | 25.7649 | 18.9521 | 52.7654 | 87.9501 | 87.9501 | 0 | 0
2025-05-16 01:00 | 28.25 | 55 | 70 | 25.4663 | 18.7597 | 53.1209 | 84.0384 | 84.0384 | 0 | 0
2025-05-16 02:00 | 27.4 | 54.5 | 70 | 25.182 | 18.4345 | 52.5844 | 74.1625 | 74.1625 | 0 | 0
2025-05-16 03:00 | 26.75 | 55 | 70 | 24.961 | 18.2514 | 52.5926 | 69.5392 | 69.5392 | 0 | 0
2025-05-16 04:00 | 26.4 | 52 | 70 | 24.8427 | 17.9235 | 51.1722 | 57.226 | 57.226 | 0 | 0
2025-05-16 05:00 | 26 | 49 | 70 | 24.7059 | 17.5845 | 49.7723 | 44.7835 | 44.7835 | 0 | 0
2025-05-16 06:00 | 26.85 | 46 | 100 | 25.0011 | 17.639 | 48.6226 | 60.9925 | 60.9925 | 0 | 0
2025-05-16 07:00 | 29.5 | 38.5 | 100 | 25.9017 | 17.8609 | 45.612 | 55.4727 | 55.4727 | 0 | 0
2025-05-16 08:00 | 32.45 | 31.5 | 100 | 26.8707 | 18.0801 | 42.4993 | 48.5964 | 48.5964 | 0 | 0
2025-05-16 09:00 | 35.1 | 27.5 | 100 | 27.706 | 18.3904 | 40.6542 | 50.2864 | 50.2864 | 0 | 0
2025-05-16 10:00 | 37.45 | 22.5 | 100 | 28.4322 | 18.4196 | 37.9154 | 37.4356 | 37.4356 | 0 | 0
2025-05-16 11:00 | 38.95 | 19.5 | 100 | 28.887 | 18.403 | 36.1138 | 27.4056 | 27.4056 | 0 | 0
2025-05-16 12:00 | 39.3 | 20.5 | 100 | 28.9798 | 18.6153 | 36.8322 | 38.4447 | 38.4447 | 0 | 0
2025-05-16 13:00 | 39.15 | 19.5 | 100 | 28.9444 | 18.4478 | 36.1414 | 29.1754 | 29.1754 | 0 | 0
2025-05-16 14:00 | 37.95 | 21 | 100 | 28.5876 | 18.3538 | 37.0189 | 30.7518 | 30.7518 | 0 | 0
2025-05-16 15:00 | 36.6 | 24 | 100 | 28.173 | 18.381 | 38.7709 | 40.8085 | 40.8085 | 0 | 0
2025-05-16 16:00 | 35.6 | 26.5 | 100 | 27.8617 | 18.4079 | 40.1574 | 48.7224 | 48.7224 | 0 | 0
2025-05-16 17:00 | 33.65 | 38 | 100 | 27.2243 | 19.0497 | 46.3718 | 101.154 | 101.154 | 0 | 0
2025-05-16 18:00 | 31.6 | 53 | 100 | 26.5484 | 19.7476 | 53.6211 | 159.2517 | 159.2517 | 0 | 0
2025-05-16 19:00 | 30.4 | 61.5 | 100 | 26.1538 | 20.0153 | 57.2802 | 184.9035 | 184.9035 | 0 | 0
2025-05-16 20:00 | 29.65 | 66 | 100 | 25.9078 | 20.085 | 59.028 | 194.7213 | 194.7213 | 0 | 0
2025-05-16 21:00 | 28.85 | 71.5 | 100 | 25.6431 | 20.1859 | 61.1274 | 207.0826 | 207.0826 | 0 | 0
2025-05-16 22:00 | 28.05 | 76.5 | 70 | 25.3775 | 20.2263 | 62.8893 | 150.8885 | 150.8885 | 0 | 0
2025-05-16 23:00 | 27.3 | 78.5 | 70 | 25.129 | 20.065 | 63.2693 | 147.4199 | 147.4199 | 0 | 0
2025-05-17 | 26.55 | 81 | 70 | 24.8772 | 19.9301 | 63.8518 | 145.2382 | 145.2382 | 0 | 0
2025-05-17 01:00 | 26.05 | 84 | 70 | 24.7072 | 19.9199 | 64.794 | 147.4583 | 147.4583 | 0 | 0
2025-05-17 02:00 | 25.8 | 85.5 | 70 | 24.6218 | 19.912 | 65.2548 | 148.4587 | 148.4587 | 0 | 0
2025-05-17 03:00 | 25.75 | 85.5 | 70 | 24.6048 | 19.8918 | 65.2217 | 147.814 | 147.814 | 0 | 0
2025-05-17 04:00 | 25.95 | 83.5 | 70 | 24.6735 | 19.8485 | 64.5172 | 144.7529 | 144.7529 | 0 | 0
2025-05-17 05:00 | 26.2 | 80.5 | 70 | 24.7596 | 19.7584 | 63.4078 | 139.3305 | 139.3305 | 0 | 0
2025-05-17 06:00 | 27.4 | 73.5 | 100 | 25.1662 | 19.7671 | 61.1191 | 190.5928 | 190.5928 | 0 | 0
2025-05-17 07:00 | 30.2 | 62 | 100 | 26.0896 | 19.9816 | 57.4143 | 184.158 | 184.158 | 0 | 0
2025-05-17 08:00 | 32.85 | 51.5 | 100 | 26.9371 | 20.0468 | 53.4594 | 169.9872 | 169.9872 | 0 | 0
2025-05-17 09:00 | 34.25 | 44.5 | 100 | 27.3822 | 19.867 | 50.2605 | 149.0005 | 149.0005 | 0 | 0
2025-05-17 10:00 | 35.15 | 41 | 100 | 27.6631 | 19.8097 | 48.6302 | 139.4243 | 139.4243 | 0 | 0
2025-05-17 11:00 | 35.85 | 38.5 | 100 | 27.8796 | 19.7708 | 47.4311 | 132.4042 | 132.4042 | 0 | 0
2025-05-17 12:00 | 36.15 | 37.5 | 100 | 27.9717 | 19.7565 | 46.9476 | 129.6503 | 129.6503 | 0 | 0
2025-05-17 13:00 | 36.1 | 37.5 | 100 | 27.9572 | 19.7403 | 46.933 | 129.0503 | 129.0503 | 0 | 0
2025-05-17 14:00 | 35.8 | 37.5 | 100 | 27.8697 | 19.6489 | 46.8225 | 125.1858 | 125.1858 | 0 | 0
2025-05-17 15:00 | 35.1 | 38.5 | 100 | 27.6591 | 19.5388 | 47.1577 | 122.7211 | 122.7211 | 0 | 0
2025-05-17 16:00 | 33.95 | 42 | 100 | 27.3014 | 19.5286 | 48.7326 | 129.5918 | 129.5918 | 0 | 0
2025-05-17 17:00 | 32.35 | 50 | 100 | 26.7884 | 19.7429 | 52.4169 | 153.9829 | 153.9829 | 0 | 0
2025-05-17 18:00 | 30.65 | 60.5 | 100 | 26.2346 | 20.0269 | 56.935 | 183.9904 | 183.9904 | 0 | 0
2025-05-17 19:00 | 29.6 | 67.5 | 100 | 25.8895 | 20.1783 | 59.7261 | 201.2708 | 201.2708 | 0 | 0
2025-05-17 20:00 | 29.05 | 69.5 | 100 | 25.7102 | 20.1178 | 60.3228 | 201.226 | 201.226 | 0 | 0
2025-05-17 21:00 | 28.5 | 71.5 | 100 | 25.5297 | 20.051 | 60.9005 | 200.8732 | 200.8732 | 0 | 0
2025-05-17 22:00 | 27.85 | 74 | 70 | 25.3145 | 19.9754 | 61.6221 | 140.4856 | 140.4856 | 0 | 0
2025-05-17 23:00 | 27 | 76.5 | 70 | 25.0308 | 19.8136 | 62.1861 | 137.5413 | 137.5413 | 0 | 0
2025-05-18 | 26.15 | 79 | 70 | 24.7434 | 19.6433 | 62.7262 | 134.2973 | 134.2973 | 0 | 0
2025-05-18 01:00 | 25.45 | 80.5 | 70 | 24.5042 | 19.4617 | 62.9209 | 129.8476 | 129.8476 | 0 | 0
2025-05-18 02:00 | 24.9 | 81 | 70 | 24.3144 | 19.276 | 62.7928 | 124.4402 | 124.4402 | 0 | 0
2025-05-18 03:00 | 24.5 | 81.5 | 70 | 24.1753 | 19.1488 | 62.7611 | 120.9121 | 120.9121 | 0 | 0
2025-05-18 04:00 | 24.5 | 79.5 | 70 | 24.1755 | 19.0284 | 61.9531 | 115.5566 | 115.5566 | 0 | 0
2025-05-18 05:00 | 24.6 | 77.5 | 70 | 24.2106 | 18.9463 | 61.1944 | 111.3386 | 111.3386 | 0 | 0
2025-05-18 06:00 | 25.25 | 74.5 | 100 | 24.437 | 19.0102 | 60.3033 | 158.0629 | 158.0629 | 0 | 0
2025-05-18 07:00 | 27.3 | 66 | 100 | 25.139 | 19.2149 | 57.7007 | 155.7028 | 155.7028 | 0 | 0
2025-05-18 08:00 | 29.85 | 56.5 | 100 | 25.9874 | 19.4271 | 54.5192 | 150.7629 | 150.7629 | 0 | 0
2025-05-18 09:00 | 32.1 | 47 | 100 | 26.7192 | 19.3981 | 50.6931 | 133.2455 | 133.2455 | 0 | 0
2025-05-18 10:00 | 33.95 | 38 | 100 | 27.3158 | 19.1422 | 46.4538 | 104.7239 | 104.7239 | 0 | 0
2025-05-18 11:00 | 35.45 | 31.5 | 100 | 27.794 | 18.9126 | 43.1095 | 80.6871 | 80.6871 | 0 | 0
2025-05-18 12:00 | 36.5 | 28 | 100 | 28.1225 | 18.8153 | 41.2281 | 68.0707 | 68.0707 | 0 | 0
2025-05-18 13:00 | 36.9 | 27.5 | 100 | 28.2427 | 18.8647 | 41.0061 | 68.746 | 68.746 | 0 | 0
2025-05-18 14:00 | 36.45 | 30 | 100 | 28.0975 | 19.0249 | 42.4613 | 81.6754 | 81.6754 | 0 | 0
2025-05-18 15:00 | 35.15 | 37.5 | 100 | 27.6783 | 19.4516 | 46.589 | 116.8701 | 116.8701 | 0 | 0
2025-05-18 16:00 | 33.5 | 45 | 100 | 27.1549 | 19.6695 | 50.2245 | 141.5742 | 141.5742 | 0 | 0
2025-05-18 17:00 | 32 | 49.5 | 100 | 26.6815 | 19.5814 | 51.9935 | 146.0663 | 146.0663 | 0 | 0
2025-05-18 18:00 | 30.6 | 55 | 100 | 26.2296 | 19.5665 | 54.162 | 154.7813 | 154.7813 | 0 | 0
2025-05-18 19:00 | 29.4 | 63 | 100 | 25.8323 | 19.7652 | 57.4529 | 176.0054 | 176.0054 | 0 | 0
2025-05-18 20:00 | 28.45 | 71.5 | 100 | 25.5134 | 20.0316 | 60.8788 | 200.0975 | 200.0975 | 0 | 0
2025-05-18 21:00 | 27.5 | 78 | 100 | 25.1955 | 20.11 | 63.195 | 212.2034 | 212.2034 | 0 | 0
2025-05-18 22:00 | 26.55 | 83.5 | 70 | 24.8757 | 20.0907 | 64.9376 | 152.6228 | 152.6228 | 0 | 0
2025-05-18 23:00 | 25.7 | 88.5 | 70 | 24.5867 | 20.0562 | 66.4403 | 155.5716 | 155.5716 | 0 | 0
2025-05-19 | 24.95 | 93 | 70 | 24.3293 | 20.0144 | 67.7355 | 157.7255 | 157.7255 | 0 | 0
2025-05-19 01:00 | 24.35 | 95.5 | 70 | 24.1219 | 19.9078 | 68.29 | 156.1216 | 156.1216 | 0 | 0
2025-05-19 02:00 | 23.8 | 96 | 70 | 23.93 | 19.7045 | 68.078 | 149.8758 | 149.8758 | 0 | 0
2025-05-19 03:00 | 23.25 | 96 | 70 | 23.7362 | 19.4746 | 67.6823 | 142.4424 | 142.4424 | 0 | 0
2025-05-19 04:00 | 23.35 | 94.5 | 70 | 23.7714 | 19.4331 | 67.1746 | 140.032 | 140.032 | 0 | 0
2025-05-19 05:00 | 23.6 | 93.5 | 70 | 23.8596 | 19.481 | 66.9587 | 140.819 | 140.819 | 0 | 0
2025-05-19 06:00 | 24.35 | 90 | 100 | 24.1222 | 19.5901 | 66.0902 | 202.345 | 202.345 | 0 | 0
2025-05-19 07:00 | 26.65 | 78.5 | 100 | 24.9123 | 19.808 | 62.8428 | 198.8391 | 198.8391 | 0 | 0
2025-05-19 08:00 | 29.6 | 64 | 100 | 25.895 | 19.9146 | 58.042 | 184.1484 | 184.1484 | 0 | 0
2025-05-19 09:00 | 32.65 | 50.5 | 100 | 26.8791 | 19.8898 | 52.8221 | 161.2319 | 161.2319 | 0 | 0
2025-05-19 10:00 | 35.4 | 40.5 | 100 | 27.7387 | 19.837 | 48.4456 | 139.647 | 139.647 | 0 | 0
2025-05-19 11:00 | 37.1 | 36.5 | 100 | 28.25 | 19.936 | 46.7081 | 135.2202 | 135.2202 | 0 | 0
2025-05-19 12:00 | 37.7 | 34 | 100 | 28.435 | 19.8341 | 45.3596 | 125.028 | 125.028 | 0 | 0
2025-05-19 13:00 | 37.45 | 31 | 100 | 28.382 | 19.4159 | 43.3678 | 100.2092 | 100.2092 | 0 | 0
2025-05-19 14:00 | 36.6 | 34.5 | 100 | 28.1175 | 19.5642 | 45.2938 | 114.9712 | 114.9712 | 0 | 0
2025-05-19 15:00 | 35.45 | 43.5 | 100 | 27.7396 | 20.1542 | 50.263 | 160.1758 | 160.1758 | 0 | 0
2025-05-19 16:00 | 33.8 | 54.5 | 100 | 27.2117 | 20.6449 | 55.6694 | 203.0507 | 203.0507 | 0 | 0
2025-05-19 17:00 | 32.15 | 66 | 100 | 26.6836 | 21.0271 | 60.753 | 239.6137 | 239.6137 | 0 | 0
2025-05-19 18:00 | 30.75 | 74.5 | 100 | 26.2371 | 21.1502 | 64.0022 | 257.6638 | 257.6638 | 0 | 0
2025-05-19 19:00 | 29.7 | 79.5 | 100 | 25.9017 | 21.0969 | 65.5785 | 261.5868 | 261.5868 | 0 | 0
2025-05-19 20:00 | 29.1 | 83 | 100 | 25.7072 | 21.0987 | 66.7275 | 266.0545 | 266.0545 | 0 | 0
2025-05-19 21:00 | 28.45 | 87 | 100 | 25.4951 | 21.1023 | 68.0158 | 271.0737 | 271.0737 | 0 | 0
2025-05-19 22:00 | 27.75 | 91.5 | 70 | 25.2648 | 21.1045 | 69.4285 | 193.4959 | 193.4959 | 0 | 0
2025-05-19 23:00 | 27.05 | 95 | 70 | 25.0336 | 21.0284 | 70.3392 | 193.6089 | 193.6089 | 0 | 0
2025-05-20 | 26.55 | 97 | 70 | 24.8675 | 20.9363 | 70.7504 | 191.9811 | 191.9811 | 0 | 0
2025-05-20 01:00 | 25.95 | 99 | 70 | 24.6666 | 20.7982 | 71.0564 | 188.6961 | 188.6961 | 0 | 0
2025-05-20 02:00 | 25.35 | 100 | 70 | 24.4641 | 20.5966 | 70.9374 | 182.5255 | 182.5255 | 0 | 0
2025-05-20 03:00 | 24.9 | 100 | 70 | 24.3108 | 20.4018 | 70.548 | 175.9032 | 175.9032 | 0 | 0
2025-05-20 04:00 | 25.2 | 96.5 | 70 | 24.414 | 20.3262 | 69.3744 | 170.8047 | 170.8047 | 0 | 0
2025-05-20 05:00 | 25.85 | 90 | 70 | 24.6369 | 20.2097 | 67.1968 | 161.9416 | 161.9416 | 0 | 0
2025-05-20 06:00 | 27.15 | 78 | 100 | 25.0795 | 19.9714 | 62.9716 | 205.9361 | 205.9361 | 0 | 0
2025-05-20 07:00 | 30.3 | 59.5 | 100 | 26.1258 | 19.8204 | 56.2561 | 173.3147 | 173.3147 | 0 | 0
2025-05-20 08:00 | 33.55 | 47.5 | 100 | 27.1616 | 19.9186 | 51.636 | 157.2732 | 157.2732 | 0 | 0
2025-05-20 09:00 | 35.85 | 41.5 | 100 | 27.8651 | 20.0803 | 49.2462 | 152.5829 | 152.5829 | 0 | 0
2025-05-20 10:00 | 37.75 | 36.5 | 100 | 28.4335 | 20.132 | 46.9811 | 143.9094 | 143.9094 | 0 | 0
2025-05-20 11:00 | 38.6 | 37 | 100 | 28.6656 | 20.4485 | 47.6831 | 159.1925 | 159.1925 | 0 | 0
2025-05-20 12:00 | 38.4 | 36.5 | 100 | 28.6141 | 20.3288 | 47.2687 | 152.7504 | 152.7504 | 0 | 0
2025-05-20 13:00 | 37.95 | 36.5 | 100 | 28.4893 | 20.1915 | 47.0772 | 146.7217 | 146.7217 | 0 | 0
2025-05-20 14:00 | 37.15 | 39.5 | 100 | 28.2468 | 20.2769 | 48.6318 | 157.352 | 157.352 | 0 | 0
2025-05-20 15:00 | 36.45 | 40 | 100 | 28.0452 | 20.11 | 48.628 | 151.1003 | 151.1003 | 0 | 0
2025-05-20 16:00 | 35.65 | 41 | 100 | 27.8093 | 19.9623 | 48.8803 | 146.7278 | 146.7278 | 0 | 0
2025-05-20 17:00 | 34.4 | 45 | 100 | 27.4248 | 19.9594 | 50.6496 | 154.6544 | 154.6544 | 0 | 0
2025-05-20 18:00 | 32.8 | 53 | 100 | 26.9172 | 20.159 | 54.2788 | 178.2212 | 178.2212 | 0 | 0
2025-05-20 19:00 | 31.05 | 65 | 100 | 26.3499 | 20.5298 | 59.4736 | 214.479 | 214.479 | 0 | 0
2025-05-20 20:00 | 29.75 | 75.5 | 100 | 25.9239 | 20.8265 | 63.7061 | 243.2764 | 243.2764 | 0 | 0
2025-05-20 21:00 | 29.05 | 80 | 100 | 25.6955 | 20.8679 | 65.2887 | 251.0901 | 251.0901 | 0 | 0
2025-05-20 22:00 | 28.25 | 83 | 70 | 25.4353 | 20.7493 | 66.0327 | 174.3381 | 174.3381 | 0 | 0
2025-05-20 23:00 | 27.2 | 87.5 | 70 | 25.0887 | 20.6143 | 67.1992 | 173.5241 | 173.5241 | 0 | 0
2025-05-21 | 26.35 | 91.5 | 70 | 24.8041 | 20.5117 | 68.2401 | 173.2905 | 173.2905 | 0 | 0
2025-05-21 01:00 | 25.7 | 93.5 | 70 | 24.5847 | 20.36 | 68.5577 | 169.7644 | 169.7644 | 0 | 0
2025-05-21 02:00 | 25.15 | 93 | 70 | 24.3978 | 20.0983 | 67.9183 | 160.6918 | 160.6918 | 0 | 0
2025-05-21 03:00 | 24.6 | 91.5 | 70 | 24.2089 | 19.7804 | 66.8981 | 149.1407 | 149.1407 | 0 | 0
2025-05-21 04:00 | 24.45 | 90 | 70 | 24.157 | 19.6311 | 66.1869 | 143.147 | 143.147 | 0 | 0
2025-05-21 05:00 | 24.45 | 87.5 | 70 | 24.1572 | 19.4846 | 65.1798 | 136.4983 | 136.4983 | 0 | 0
2025-05-21 06:00 | 25.4 | 78 | 100 | 24.4877 | 19.2856 | 61.8785 | 174.9193 | 174.9193 | 0 | 0
2025-05-21 07:00 | 28.35 | 62 | 100 | 25.4915 | 19.3093 | 56.4413 | 154.53 | 154.53 | 0 | 0
2025-05-21 08:00 | 32.25 | 45.5 | 100 | 26.7698 | 19.3095 | 49.9871 | 127.1857 | 127.1857 | 0 | 0
2025-05-21 09:00 | 35.95 | 31 | 100 | 27.9451 | 18.9948 | 42.9532 | 83.1108 | 83.1108 | 0 | 0
2025-05-21 10:00 | 38.9 | 22.5 | 100 | 28.8516 | 18.7712 | 38.1471 | 51.0369 | 51.0369 | 0 | 0
2025-05-21 11:00 | 40.9 | 19.5 | 100 | 29.4363 | 18.8529 | 36.3717 | 44.4189 | 44.4189 | 0 | 0
2025-05-21 12:00 | 42 | 20 | 100 | 29.731 | 19.1846 | 36.917 | 58.7817 | 58.7817 | 0 | 0
2025-05-21 13:00 | 42.6 | 22 | 100 | 29.8692 | 19.6201 | 38.5461 | 82.8563 | 82.8563 | 0 | 0
2025-05-21 14:00 | 42.3 | 22 | 100 | 29.7901 | 19.5445 | 38.4788 | 79.8943 | 79.8943 | 0 | 0
2025-05-21 15:00 | 40.8 | 22.5 | 100 | 29.3819 | 19.2387 | 38.5145 | 69.4551 | 69.4551 | 0 | 0
2025-05-21 16:00 | 38.35 | 32.5 | 100 | 28.6272 | 19.845 | 44.6488 | 122.3201 | 122.3201 | 0 | 0
2025-05-21 17:00 | 35.75 | 46 | 100 | 27.8145 | 20.5025 | 51.9108 | 181.1154 | 181.1154 | 0 | 0
2025-05-21 18:00 | 33.65 | 55.5 | 100 | 27.1637 | 20.6805 | 56.1406 | 206.587 | 206.587 | 0 | 0
2025-05-21 19:00 | 32.1 | 63 | 100 | 26.6765 | 20.7613 | 59.1552 | 222.4036 | 222.4036 | 0 | 0
2025-05-21 20:00 | 31.15 | 68 | 100 | 26.3741 | 20.8049 | 61.0541 | 231.8717 | 231.8717 | 0 | 0
2025-05-21 21:00 | 30.45 | 70.5 | 100 | 26.1522 | 20.7285 | 61.7931 | 231.7311 | 231.7311 | 0 | 0
2025-05-21 22:00 | 29.65 | 71.5 | 70 | 25.8989 | 20.4934 | 61.707 | 155.3435 | 155.3435 | 0 | 0
2025-05-21 23:00 | 28.85 | 73 | 70 | 25.641 | 20.2917 | 61.8641 | 150.14 | 150.14 | 0 | 0
2025-05-22 | 28 | 76.5 | 70 | 25.361 | 20.2047 | 62.8931 | 150.5177 | 150.5177 | 0 | 0
2025-05-22 01:00 | 27.1 | 85 | 70 | 25.0576 | 20.4106 | 66.0281 | 164.6778 | 164.6778 | 0 | 0
2025-05-22 02:00 | 26.35 | 93 | 70 | 24.8033 | 20.6047 | 68.8826 | 177.6262 | 177.6262 | 0 | 0
2025-05-22 03:00 | 25.6 | 95 | 70 | 24.5504 | 20.4076 | 69.0999 | 172.5115 | 172.5115 | 0 | 0
2025-05-22 04:00 | 25.6 | 93 | 70 | 24.5511 | 20.2873 | 68.2688 | 166.9578 | 166.9578 | 0 | 0
2025-05-22 05:00 | 25.55 | 92.5 | 70 | 24.5343 | 20.2367 | 68.0201 | 164.8596 | 164.8596 | 0 | 0
2025-05-22 06:00 | 25.95 | 88.5 | 100 | 24.6713 | 20.1588 | 66.6533 | 227.3558 | 227.3558 | 0 | 0
2025-05-22 07:00 | 28.75 | 73 | 100 | 25.6087 | 20.2535 | 61.7952 | 212.6627 | 212.6627 | 0 | 0
2025-05-22 08:00 | 32.5 | 53.5 | 100 | 26.8245 | 20.0999 | 54.3707 | 176.1908 | 176.1908 | 0 | 0
2025-05-22 09:00 | 36.3 | 34.5 | 100 | 28.0304 | 19.4759 | 45.1911 | 111.2539 | 111.2539 | 0 | 0
2025-05-22 10:00 | 39.85 | 19.5 | 100 | 29.1434 | 18.6056 | 36.2392 | 35.3686 | 35.3686 | 0 | 0
2025-05-22 11:00 | 42.3 | 12.5 | 100 | 29.8904 | 18.126 | 31.3424 | 0 | 0 | 0 | 0
2025-05-22 12:00 | 43.65 | 10.5 | 100 | 30.2819 | 18.0648 | 29.7999 | 0 | 0 | 0 | 0
2025-05-22 13:00 | 44.05 | 11.5 | 100 | 30.3773 | 18.3052 | 30.5939 | 0 | 0 | 0 | 0
2025-05-22 14:00 | 43.8 | 13 | 100 | 30.2918 | 18.5022 | 31.7789 | 7.2229 | 7.2229 | 0 | 0
2025-05-22 15:00 | 42.95 | 12.5 | 100 | 30.0687 | 18.2493 | 31.3659 | 0 | 0 | 0 | 0
2025-05-22 16:00 | 41.45 | 14.5 | 100 | 29.6353 | 18.2485 | 32.8267 | 5.1034 | 5.1034 | 0 | 0
2025-05-22 17:00 | 38.95 | 23.5 | 100 | 28.8588 | 18.9033 | 38.8567 | 59.7685 | 59.7685 | 0 | 0
2025-05-22 18:00 | 36 | 36.5 | 100 | 27.9329 | 19.597 | 46.3312 | 121.466 | 121.466 | 0 | 0
2025-05-22 19:00 | 34.05 | 46 | 100 | 27.3167 | 19.9387 | 51.0661 | 155.8883 | 155.8883 | 0 | 0
2025-05-22 20:00 | 32.65 | 54 | 100 | 26.8686 | 20.1934 | 54.7435 | 181.6548 | 181.6548 | 0 | 0
2025-05-22 21:00 | 31.35 | 61.5 | 100 | 26.4506 | 20.3597 | 57.8996 | 201.3797 | 201.3797 | 0 | 0
2025-05-22 22:00 | 30.35 | 62.5 | 70 | 26.136 | 20.0724 | 57.7936 | 132.7659 | 132.7659 | 0 | 0
2025-05-22 23:00 | 29.8 | 56.5 | 70 | 25.9712 | 19.404 | 54.5574 | 105.4609 | 105.4609 | 0 | 0
2025-05-23 | 29.45 | 49.5 | 70 | 25.8687 | 18.7307 | 51.0169 | 77.539 | 77.539 | 0 | 0
2025-05-23 01:00 | 28.75 | 46.5 | 70 | 25.6423 | 18.2668 | 49.365 | 60.8931 | 60.8931 | 0 | 0
2025-05-23 02:00 | 28 | 45 | 70 | 25.3931 | 17.9138 | 48.4787 | 49.5038 | 49.5038 | 0 | 0
2025-05-23 03:00 | 27.45 | 43 | 70 | 25.2086 | 17.5916 | 47.4531 | 38.5739 | 38.5739 | 0 | 0
2025-05-23 04:00 | 27 | 45.5 | 70 | 25.0529 | 17.6404 | 48.4989 | 42.8645 | 42.8645 | 0 | 0
2025-05-23 05:00 | 26.65 | 49.5 | 70 | 24.9302 | 17.8204 | 50.199 | 52.2699 | 52.2699 | 0 | 0
2025-05-23 06:00 | 27.55 | 44 | 100 | 25.2417 | 17.6993 | 47.9174 | 60.7258 | 60.7258 | 0 | 0
2025-05-23 07:00 | 30.8 | 31.5 | 100 | 26.3408 | 17.6144 | 42.3547 | 32.9177 | 32.9177 | 0 | 0
2025-05-23 08:00 | 35.25 | 20.5 | 100 | 27.7821 | 17.6411 | 36.5751 | 5.5028 | 5.5028 | 0 | 0
2025-05-23 09:00 | 39.3 | 13.5 | 100 | 29.0322 | 17.661 | 32.111 | 0 | 0 | 0 | 0
2025-05-23 10:00 | 42.45 | 9.5 | 100 | 29.9639 | 17.6758 | 29.0927 | 0 | 0 | 0 | 0
2025-05-23 11:00 | 44.9 | 7 | 100 | 30.665 | 17.6753 | 26.9398 | 0 | 0 | 0 | 0
2025-05-23 12:00 | 46.3 | 6.5 | 100 | 31.0449 | 17.8092 | 26.4032 | 0 | 0 | 0 | 0
2025-05-23 13:00 | 46.55 | 7.5 | 100 | 31.0944 | 18.0381 | 27.2499 | 0 | 0 | 0 | 0
2025-05-23 14:00 | 45.8 | 8.5 | 100 | 30.8829 | 18.0941 | 28.1404 | 0 | 0 | 0 | 0
2025-05-23 15:00 | 43.5 | 14 | 100 | 30.1999 | 18.5933 | 32.571 | 15.2748 | 15.2748 | 0 | 0
2025-05-23 16:00 | 40.9 | 21 | 100 | 29.423 | 19.0491 | 37.4902 | 57.9138 | 57.9138 | 0 | 0
2025-05-23 17:00 | 38.35 | 29 | 100 | 28.6507 | 19.4222 | 42.3844 | 96.2258 | 96.2258 | 0 | 0
2025-05-23 18:00 | 35.6 | 42 | 100 | 27.7899 | 20.0446 | 49.484 | 152.9665 | 152.9665 | 0 | 0
2025-05-23 19:00 | 34 | 48.5 | 100 | 27.2925 | 20.1569 | 52.4657 | 170.5644 | 170.5644 | 0 | 0
2025-05-23 20:00 | 33.15 | 47.5 | 100 | 27.0404 | 19.7803 | 51.4939 | 151.9209 | 151.9209 | 0 | 0
2025-05-23 21:00 | 32.3 | 47.5 | 100 | 26.7797 | 19.4993 | 51.1133 | 139.664 | 139.664 | 0 | 0
2025-05-23 22:00 | 31.5 | 47 | 70 | 26.5313 | 19.1934 | 50.5243 | 87.9897 | 87.9897 | 0 | 0
2025-05-23 23:00 | 30.6 | 45 | 70 | 26.2492 | 18.7323 | 49.1848 | 72.0872 | 72.0872 | 0 | 0
2025-05-24 | 29.75 | 44 | 70 | 25.9754 | 18.38 | 48.4391 | 60.9761 | 60.9761 | 0 | 0
2025-05-24 01:00 | 28.95 | 45 | 70 | 25.7106 | 18.21 | 48.7141 | 57.5936 | 57.5936 | 0 | 0
2025-05-24 02:00 | 28.2 | 48 | 70 | 25.4572 | 18.2065 | 49.9281 | 61.1312 | 61.1312 | 0 | 0
2025-05-24 03:00 | 27.55 | 50 | 70 | 25.2365 | 18.1469 | 50.666 | 61.8176 | 61.8176 | 0 | 0
2025-05-24 04:00 | 27.3 | 45.5 | 70 | 25.1554 | 17.7327 | 48.5668 | 45.3807 | 45.3807 | 0 | 0
2025-05-24 05:00 | 27.35 | 37 | 70 | 25.1793 | 17.103 | 44.7174 | 18.6682 | 18.6682 | 0 | 0
2025-05-24 06:00 | 28.9 | 28 | 100 | 25.7161 | 16.7998 | 40.5474 | 0 | 0 | 0 | 0
2025-05-24 07:00 | 32.95 | 18 | 100 | 27.0692 | 16.8399 | 35.2058 | 0 | 0 | 0 | 0
2025-05-24 08:00 | 37.6 | 12 | 100 | 28.5394 | 17.119 | 31.2244 | 0 | 0 | 0 | 0
2025-05-24 09:00 | 41.55 | 9.5 | 100 | 29.7113 | 17.5113 | 29.1595 | 0 | 0 | 0 | 0
2025-05-24 10:00 | 44.1 | 7.5 | 100 | 30.4417 | 17.6301 | 27.4163 | 0 | 0 | 0 | 0
2025-05-24 11:00 | 45.7 | 6 | 100 | 30.8938 | 17.6199 | 26.0362 | 0 | 0 | 0 | 0
2025-05-24 12:00 | 46.85 | 5 | 100 | 31.214 | 17.6028 | 25.0564 | 0 | 0 | 0 | 0
2025-05-24 13:00 | 46.9 | 5.5 | 100 | 31.2189 | 17.7062 | 25.4916 | 0 | 0 | 0 | 0
2025-05-24 14:00 | 45.8 | 7 | 100 | 30.9057 | 17.8159 | 26.8805 | 0 | 0 | 0 | 0
2025-05-24 15:00 | 44.05 | 9 | 100 | 30.4096 | 17.872 | 28.6327 | 0 | 0 | 0 | 0
2025-05-24 16:00 | 41.25 | 17 | 100 | 29.5564 | 18.5634 | 34.6567 | 26.1152 | 26.1152 | 0 | 0
2025-05-24 17:00 | 38.2 | 28.5 | 100 | 28.6116 | 19.32 | 42.0189 | 90.803 | 90.803 | 0 | 0
2025-05-24 18:00 | 35.65 | 39.5 | 100 | 27.8162 | 19.8027 | 48.0201 | 137.2034 | 137.2034 | 0 | 0
2025-05-24 19:00 | 33.55 | 51.5 | 100 | 27.1476 | 20.2804 | 53.9031 | 181.6537 | 181.6537 | 0 | 0
2025-05-24 20:00 | 32.25 | 59 | 100 | 26.7327 | 20.4795 | 57.1854 | 203.3467 | 203.3467 | 0 | 0
2025-05-24 21:00 | 31.25 | 64 | 100 | 26.4138 | 20.5234 | 59.1273 | 213.0549 | 213.0549 | 0 | 0
2025-05-24 22:00 | 30.5 | 66 | 70 | 26.1764 | 20.4002 | 59.6342 | 147.1281 | 147.1281 | 0 | 0
2025-05-24 23:00 | 29.75 | 65 | 70 | 25.9411 | 20.0427 | 58.672 | 134.5419 | 134.5419 | 0 | 0
2025-05-25 | 28.85 | 66.5 | 70 | 25.6494 | 19.8194 | 58.8532 | 128.9595 | 128.9595 | 0 | 0
2025-05-25 01:00 | 28.05 | 66 | 70 | 25.3882 | 19.4859 | 58.1725 | 118.0439 | 118.0439 | 0 | 0
2025-05-25 02:00 | 27.35 | 61 | 70 | 25.1598 | 18.8767 | 55.5654 | 94.5733 | 94.5733 | 0 | 0
2025-05-25 03:00 | 26.75 | 53.5 | 70 | 24.9619 | 18.1376 | 52.0046 | 65.4826 | 65.4826 | 0 | 0
2025-05-25 04:00 | 27.05 | 44.5 | 70 | 25.0707 | 17.5807 | 48.0682 | 40.1983 | 40.1983 | 0 | 0
2025-05-25 05:00 | 27.7 | 35 | 70 | 25.3009 | 17.0471 | 43.8233 | 14.5737 | 14.5737 | 0 | 0
2025-05-25 06:00 | 29.3 | 24.5 | 100 | 25.8557 | 16.6003 | 38.8344 | 0 | 0 | 0 | 0
2025-05-25 07:00 | 33.2 | 15 | 100 | 27.1585 | 16.5772 | 33.5107 | 0 | 0 | 0 | 0
2025-05-25 08:00 | 37.25 | 11 | 100 | 28.4395 | 16.9227 | 30.6168 | 0 | 0 | 0 | 0
2025-05-25 09:00 | 40.3 | 15.5 | 100 | 29.3035 | 18.1496 | 33.4996 | 5.6059 | 5.6059 | 0 | 0
2025-05-25 10:00 | 42.85 | 18 | 100 | 29.9798 | 19.0821 | 35.5689 | 48.1728 | 48.1728 | 0 | 0
2025-05-25 11:00 | 44.6 | 15 | 100 | 30.4765 | 18.9957 | 33.4447 | 33.2695 | 33.2695 | 0 | 0
2025-05-25 12:00 | 45.15 | 14 | 100 | 30.6327 | 18.9438 | 32.6891 | 27.2043 | 27.2043 | 0 | 0
2025-05-25 13:00 | 44.05 | 15.5 | 100 | 30.3266 | 18.9565 | 33.7883 | 34.0439 | 34.0439 | 0 | 0
2025-05-25 14:00 | 42.4 | 19 | 100 | 29.8489 | 19.1248 | 36.2654 | 53.6408 | 53.6408 | 0 | 0
2025-05-25 15:00 | 40.85 | 23.5 | 100 | 29.3866 | 19.3835 | 39.2548 | 78.6873 | 78.6873 | 0 | 0
2025-05-25 16:00 | 38.85 | 30.5 | 100 | 28.7804 | 19.7451 | 43.5172 | 113.3556 | 113.3556 | 0 | 0
2025-05-25 17:00 | 36.75 | 41 | 100 | 28.1251 | 20.3086 | 49.4022 | 162.4434 | 162.4434 | 0 | 0
2025-05-25 18:00 | 34.75 | 53 | 100 | 27.4949 | 20.8394 | 55.4394 | 210.0184 | 210.0184 | 0 | 0
2025-05-25 19:00 | 33.2 | 62.5 | 100 | 27.0069 | 21.129 | 59.6848 | 239.5921 | 239.5921 | 0 | 0
2025-05-25 20:00 | 32.1 | 68.5 | 100 | 26.6616 | 21.2103 | 62.0409 | 252.4791 | 252.4791 | 0 | 0
2025-05-25 21:00 | 31.1 | 74 | 100 | 26.3453 | 21.2504 | 64.0523 | 262.1338 | 262.1338 | 0 | 0
2025-05-25 22:00 | 30.2 | 79 | 70 | 26.0583 | 21.2629 | 65.7721 | 188.5475 | 188.5475 | 0 | 0
2025-05-25 23:00 | 29.35 | 83 | 70 | 25.7861 | 21.2017 | 66.9616 | 189.9532 | 189.9532 | 0 | 0
2025-05-26 | 28.55 | 85.5 | 70 | 25.5287 | 21.0427 | 67.4403 | 186.6092 | 186.6092 | 0 | 0
2025-05-26 01:00 | 27.9 | 85.5 | 70 | 25.3192 | 20.7724 | 66.8979 | 177.3877 | 177.3877 | 0 | 0
2025-05-26 02:00 | 27.4 | 82.5 | 70 | 25.1585 | 20.3687 | 65.1648 | 161.2782 | 161.2782 | 0 | 0
2025-05-26 03:00 | 27.05 | 77.5 | 70 | 25.0466 | 19.8975 | 62.7076 | 141.5341 | 141.5341 | 0 | 0
2025-05-26 04:00 | 27.35 | 77.5 | 70 | 25.1462 | 20.0163 | 62.9074 | 145.3475 | 145.3475 | 0 | 0
2025-05-26 05:00 | 28 | 78.5 | 70 | 25.3589 | 20.3412 | 63.8098 | 156.8765 | 156.8765 | 0 | 0
2025-05-26 06:00 | 29.1 | 72 | 100 | 25.7227 | 20.3162 | 61.5732 | 214.3894 | 214.3894 | 0 | 0
2025-05-26 07:00 | 31.5 | 61.5 | 100 | 26.4969 | 20.4161 | 57.9795 | 203.7903 | 203.7903 | 0 | 0
2025-05-26 08:00 | 34.25 | 52 | 100 | 27.3535 | 20.5735 | 54.536 | 195.3333 | 195.3333 | 0 | 0
2025-05-26 09:00 | 36.7 | 44.5 | 100 | 28.0921 | 20.6661 | 51.5002 | 185.3741 | 185.3741 | 0 | 0
2025-05-26 10:00 | 39.35 | 34.5 | 100 | 28.8881 | 20.3808 | 46.3578 | 150.2976 | 150.2976 | 0 | 0
2025-05-26 11:00 | 42.1 | 22.5 | 100 | 29.7319 | 19.5677 | 38.7954 | 82.2871 | 82.2871 | 0 | 0
2025-05-26 12:00 | 43.7 | 16 | 100 | 30.2282 | 18.9665 | 34.1234 | 35.9326 | 35.9326 | 0 | 0
2025-05-26 13:00 | 43.8 | 14 | 100 | 30.2794 | 18.6661 | 32.5631 | 17.0696 | 17.0696 | 0 | 0
2025-05-26 14:00 | 43.6 | 12.5 | 100 | 30.2444 | 18.3808 | 31.3771 | 0.9167 | 0.9167 | 0 | 0
2025-05-26 15:00 | 43.35 | 12 | 100 | 30.183 | 18.2488 | 30.9842 | 0 | 0 | 0 | 0
2025-05-26 16:00 | 42.35 | 13.5 | 100 | 29.8939 | 18.2849 | 32.1125 | 2.1673 | 2.1673 | 0 | 0
2025-05-26 17:00 | 39.85 | 22.5 | 100 | 29.1196 | 18.9997 | 38.3361 | 60.3407 | 60.3407 | 0 | 0
2025-05-26 18:00 | 36.55 | 39 | 100 | 28.0791 | 20.0338 | 48.0668 | 145.7139 | 145.7139 | 0 | 0
2025-05-26 19:00 | 34.55 | 47 | 100 | 27.4612 | 20.2013 | 51.8699 | 169.3567 | 169.3567 | 0 | 0
2025-05-26 20:00 | 33.8 | 47 | 100 | 27.2383 | 19.9526 | 51.495 | 158.1486 | 158.1486 | 0 | 0
2025-05-26 21:00 | 33.3 | 48 | 100 | 27.0844 | 19.8795 | 51.8064 | 156.7075 | 156.7075 | 0 | 0
2025-05-26 22:00 | 32.95 | 47 | 70 | 26.9811 | 19.6725 | 51.0971 | 102.0144 | 102.0144 | 0 | 0
2025-05-26 23:00 | 32.45 | 47.5 | 70 | 26.8262 | 19.5524 | 51.1484 | 99.0326 | 99.0326 | 0 | 0
2025-05-27 | 31.65 | 50.5 | 70 | 26.57 | 19.5481 | 52.3784 | 102.6853 | 102.6853 | 0 | 0
2025-05-27 01:00 | 31 | 51.5 | 70 | 26.3634 | 19.413 | 52.6043 | 99.8288 | 99.8288 | 0 | 0
2025-05-27 02:00 | 30.6 | 50.5 | 70 | 26.2384 | 19.1949 | 51.9296 | 92.1206 | 92.1206 | 0 | 0
2025-05-27 03:00 | 30.2 | 49 | 70 | 26.113 | 18.939 | 51.0248 | 82.7747 | 82.7747 | 0 | 0
2025-05-27 04:00 | 29.95 | 46.5 | 70 | 26.0364 | 18.6524 | 49.7017 | 71.4674 | 71.4674 | 0 | 0
2025-05-27 05:00 | 29.9 | 45.5 | 70 | 26.0219 | 18.5541 | 49.1925 | 67.4369 | 67.4369 | 0 | 0
2025-05-27 06:00 | 31.05 | 44.5 | 100 | 26.3943 | 18.8358 | 49.0499 | 105.8511 | 105.8511 | 0 | 0
2025-05-27 07:00 | 33.15 | 41 | 100 | 27.0611 | 19.1803 | 47.8982 | 113.198 | 113.198 | 0 | 0
2025-05-27 08:00 | 34.9 | 35.5 | 100 | 27.6122 | 19.169 | 45.3491 | 100.9513 | 100.9513 | 0 | 0
2025-05-27 09:00 | 36.05 | 31 | 100 | 27.9746 | 19.0207 | 42.989 | 84.3497 | 84.3497 | 0 | 0
2025-05-27 10:00 | 36.7 | 29.5 | 100 | 28.1734 | 19.0342 | 42.2307 | 81.1093 | 81.1093 | 0 | 0
2025-05-27 11:00 | 37.1 | 29.5 | 100 | 28.2899 | 19.1433 | 42.3331 | 85.5328 | 85.5328 | 0 | 0
2025-05-27 12:00 | 37.2 | 31 | 100 | 28.3102 | 19.3426 | 43.3094 | 97.4947 | 97.4947 | 0 | 0
2025-05-27 13:00 | 37.1 | 34 | 100 | 28.2642 | 19.6529 | 45.17 | 117.8233 | 117.8233 | 0 | 0
2025-05-27 14:00 | 36.8 | 36.5 | 100 | 28.1642 | 19.8396 | 46.6235 | 131.6879 | 131.6879 | 0 | 0
2025-05-27 15:00 | 36.15 | 39 | 100 | 27.964 | 19.9088 | 47.8992 | 140.299 | 140.299 | 0 | 0
2025-05-27 16:00 | 35.35 | 41.5 | 100 | 27.7194 | 19.9174 | 49.0564 | 145.9602 | 145.9602 | 0 | 0
2025-05-27 17:00 | 34.5 | 44 | 100 | 27.4583 | 19.8932 | 50.134 | 149.9707 | 149.9707 | 0 | 0
2025-05-27 18:00 | 33.25 | 49.5 | 100 | 27.0643 | 19.9984 | 52.6212 | 164.9698 | 164.9698 | 0 | 0
2025-05-27 19:00 | 31.8 | 58 | 100 | 26.5978 | 20.2348 | 56.3686 | 190.1135 | 190.1135 | 0 | 0
2025-05-27 20:00 | 30.75 | 67 | 100 | 26.2525 | 20.573 | 60.2831 | 219.5663 | 219.5663 | 0 | 0
2025-05-27 21:00 | 30.05 | 73 | 100 | 26.0224 | 20.7607 | 62.7335 | 236.8315 | 236.8315 | 0 | 0
2025-05-27 22:00 | 29.35 | 74.5 | 70 | 25.7989 | 20.5955 | 62.933 | 161.6393 | 161.6393 | 0 | 0
2025-05-27 23:00 | 28.4 | 74 | 70 | 25.4941 | 20.1879 | 62.0287 | 147.7144 | 147.7144 | 0 | 0
2025-05-28 | 27.65 | 71.5 | 70 | 25.2508 | 19.7238 | 60.4125 | 130.5174 | 130.5174 | 0 | 0
2025-05-28 01:00 | 27.25 | 67 | 70 | 25.1214 | 19.2626 | 58.176 | 111.9081 | 111.9081 | 0 | 0
2025-05-28 02:00 | 26.75 | 64 | 70 | 24.9551 | 18.8731 | 56.6077 | 97.2553 | 97.2553 | 0 | 0
2025-05-28 03:00 | 26.2 | 63.5 | 70 | 24.7681 | 18.6421 | 56.1492 | 89.9324 | 89.9324 | 0 | 0
2025-05-28 04:00 | 26.4 | 62 | 70 | 24.8373 | 18.6113 | 55.5829 | 87.5657 | 87.5657 | 0 | 0
2025-05-28 05:00 | 26.9 | 60 | 70 | 25.0087 | 18.6497 | 54.9072 | 86.6523 | 86.6523 | 0 | 0
2025-05-28 06:00 | 27.7 | 58 | 100 | 25.2798 | 18.7869 | 54.3286 | 126.4804 | 126.4804 | 0 | 0
2025-05-28 07:00 | 29.8 | 52 | 100 | 25.9786 | 19.0493 | 52.3446 | 127.9083 | 127.9083 | 0 | 0
2025-05-28 08:00 | 32.6 | 44 | 100 | 26.8825 | 19.2848 | 49.3313 | 123.5 | 123.5 | 0 | 0
2025-05-28 09:00 | 35.35 | 36.5 | 100 | 27.7419 | 19.4059 | 46.0846 | 113.0376 | 113.0376 | 0 | 0
2025-05-28 10:00 | 37.5 | 30.5 | 100 | 28.3994 | 19.3701 | 43.0763 | 97.291 | 97.291 | 0 | 0
2025-05-28 11:00 | 38.9 | 28 | 100 | 28.8123 | 19.4575 | 41.8431 | 94.2988 | 94.2988 | 0 | 0
2025-05-28 12:00 | 39.35 | 30.5 | 100 | 28.9186 | 19.8912 | 43.6662 | 119.1064 | 119.1064 | 0 | 0
2025-05-28 13:00 | 39.1 | 34 | 100 | 28.8238 | 20.2435 | 45.9317 | 143.3081 | 143.3081 | 0 | 0
2025-05-28 14:00 | 38.4 | 36.5 | 100 | 28.6139 | 20.3253 | 47.2907 | 153.011 | 153.011 | 0 | 0
2025-05-28 15:00 | 37.4 | 41 | 100 | 28.3079 | 20.5169 | 49.7112 | 171.7144 | 171.7144 | 0 | 0
2025-05-28 16:00 | 36.15 | 44 | 100 | 27.9387 | 20.4302 | 50.9299 | 173.9959 | 173.9959 | 0 | 0
2025-05-28 17:00 | 34.55 | 49 | 100 | 27.4531 | 20.3921 | 53.0222 | 181.8797 | 181.8797 | 0 | 0
2025-05-28 18:00 | 32.65 | 62 | 100 | 26.845 | 20.8815 | 59.0199 | 226.801 | 226.801 | 0 | 0
2025-05-28 19:00 | 31.2 | 73.5 | 100 | 26.3769 | 21.252 | 63.8862 | 261.5575 | 261.5575 | 0 | 0
2025-05-28 20:00 | 30.5 | 77.5 | 100 | 26.1539 | 21.2743 | 65.2973 | 268.0041 | 268.0041 | 0 | 0
2025-05-28 21:00 | 29.85 | 79 | 100 | 25.9493 | 21.1204 | 65.4811 | 262.3521 | 262.3521 | 0 | 0
2025-05-28 22:00 | 29.15 | 81.5 | 70 | 25.7251 | 21.0136 | 66.0854 | 182.1633 | 182.1633 | 0 | 0
2025-05-28 23:00 | 28.4 | 84 | 70 | 25.4824 | 20.8783 | 66.6241 | 179.6901 | 179.6901 | 0 | 0
2025-05-29 | 27.7 | 85.5 | 70 | 25.2542 | 20.6903 | 66.7321 | 174.5604 | 174.5604 | 0 | 0
2025-05-29 01:00 | 26.95 | 87.5 | 70 | 25.0061 | 20.5097 | 67.0136 | 170.132 | 170.132 | 0 | 0
2025-05-29 02:00 | 26.2 | 91 | 70 | 24.7542 | 20.4178 | 67.9192 | 169.8293 | 169.8293 | 0 | 0
2025-05-29 03:00 | 25.65 | 93 | 70 | 24.568 | 20.3086 | 68.3184 | 167.7284 | 167.7284 | 0 | 0
2025-05-29 04:00 | 25.9 | 89.5 | 70 | 24.6539 | 20.1998 | 67.0486 | 161.3806 | 161.3806 | 0 | 0
2025-05-29 05:00 | 26.3 | 84.5 | 70 | 24.7911 | 20.0523 | 65.2236 | 152.4722 | 152.4722 | 0 | 0
2025-05-29 06:00 | 27.1 | 78 | 100 | 25.0629 | 19.951 | 62.9567 | 205.2126 | 205.2126 | 0 | 0
2025-05-29 07:00 | 29.9 | 63.5 | 100 | 25.9915 | 19.9849 | 58.0082 | 187.0425 | 187.0425 | 0 | 0
2025-05-29 08:00 | 33.6 | 45.5 | 100 | 27.1834 | 19.7464 | 50.5648 | 146.1995 | 146.1995 | 0 | 0
2025-05-29 09:00 | 36.75 | 32 | 100 | 28.1745 | 19.3288 | 43.801 | 99.3568 | 99.3568 | 0 | 0
2025-05-29 10:00 | 39.4 | 23 | 100 | 28.9895 | 18.9557 | 38.5847 | 59.9319 | 59.9319 | 0 | 0
2025-05-29 11:00 | 41.4 | 19.5 | 100 | 29.5736 | 18.9668 | 36.4595 | 49.0155 | 49.0155 | 0 | 0
2025-05-29 12:00 | 42.35 | 20.5 | 100 | 29.8194 | 19.3368 | 37.371 | 66.7817 | 66.7817 | 0 | 0
2025-05-29 13:00 | 42.7 | 20.5 | 100 | 29.9121 | 19.4205 | 37.4477 | 70.183 | 70.183 | 0 | 0
2025-05-29 14:00 | 42.05 | 21.5 | 100 | 29.729 | 19.4065 | 38.064 | 73.0826 | 73.0826 | 0 | 0
2025-05-29 15:00 | 40.15 | 25.5 | 100 | 29.178 | 19.4698 | 40.4919 | 88.1389 | 88.1389 | 0 | 0
2025-05-29 16:00 | 37.8 | 33.5 | 100 | 28.4662 | 19.798 | 45.1161 | 123.107 | 123.107 | 0 | 0
2025-05-29 17:00 | 35.2 | 46.5 | 100 | 27.6533 | 20.3671 | 51.9328 | 176.1991 | 176.1991 | 0 | 0
2025-05-29 18:00 | 32.9 | 58.5 | 100 | 26.9304 | 20.6732 | 57.322 | 211.5046 | 211.5046 | 0 | 0
2025-05-29 19:00 | 31.6 | 68 | 100 | 26.5117 | 20.9766 | 61.4082 | 240.456 | 240.456 | 0 | 0
2025-05-29 20:00 | 31.1 | 72.5 | 100 | 26.3486 | 21.1351 | 63.3049 | 254.471 | 254.471 | 0 | 0
2025-05-29 21:00 | 30.65 | 72 | 100 | 26.2112 | 20.9195 | 62.7008 | 243.2435 | 243.2435 | 0 | 0
2025-05-29 22:00 | 29.85 | 73.5 | 70 | 25.9587 | 20.7184 | 62.8316 | 164.8975 | 164.8975 | 0 | 0
2025-05-29 23:00 | 29.1 | 74 | 70 | 25.7198 | 20.461 | 62.5264 | 156.7847 | 156.7847 | 0 | 0
2025-05-30 | 28.55 | 73 | 70 | 25.5439 | 20.1745 | 61.6825 | 146.4915 | 146.4915 | 0 | 0
2025-05-30 01:00 | 28 | 74 | 70 | 25.3635 | 20.0315 | 61.7788 | 142.7837 | 142.7837 | 0 | 0
2025-05-30 02:00 | 27.3 | 76 | 70 | 25.1309 | 19.8957 | 62.2194 | 140.2085 | 140.2085 | 0 | 0
2025-05-30 03:00 | 26.6 | 77.5 | 70 | 24.896 | 19.7211 | 62.4246 | 135.936 | 135.936 | 0 | 0
2025-05-30 04:00 | 26.55 | 72 | 70 | 24.8825 | 19.339 | 60.0077 | 119.0291 | 119.0291 | 0 | 0
2025-05-30 05:00 | 26.8 | 63 | 70 | 24.9727 | 18.8222 | 56.1969 | 94.8062 | 94.8062 | 0 | 0
2025-05-30 06:00 | 27.95 | 53 | 100 | 25.3683 | 18.504 | 52.1437 | 107.168 | 107.168 | 0 | 0
2025-05-30 07:00 | 31.4 | 38.5 | 100 | 26.5193 | 18.4157 | 46.0617 | 77.5426 | 77.5426 | 0 | 0
2025-05-30 08:00 | 35.75 | 25 | 100 | 27.9139 | 18.2728 | 39.3058 | 40.2929 | 40.2929 | 0 | 0
2025-05-30 09:00 | 39.5 | 15.5 | 100 | 29.0749 | 17.9802 | 33.4704 | 0 | 0 | 0 | 0
2025-05-30 10:00 | 41.75 | 12.5 | 100 | 29.7381 | 18.0133 | 31.3511 | 0 | 0 | 0 | 0
2025-05-30 11:00 | 42.35 | 16 | 100 | 29.8673 | 18.6687 | 33.9873 | 25.3253 | 25.3253 | 0 | 0
2025-05-30 12:00 | 42.05 | 21.5 | 100 | 29.729 | 19.409 | 38.055 | 72.9674 | 72.9674 | 0 | 0
2025-05-30 13:00 | 41.35 | 22.5 | 100 | 29.5313 | 19.3746 | 38.6401 | 74.9843 | 74.9843 | 0 | 0
2025-05-30 14:00 | 40.45 | 22.5 | 100 | 29.2859 | 19.1484 | 38.4545 | 66.1765 | 66.1765 | 0 | 0
2025-05-30 15:00 | 39.4 | 27 | 100 | 28.9591 | 19.4638 | 41.3241 | 92.1635 | 92.1635 | 0 | 0
2025-05-30 16:00 | 37.55 | 37 | 100 | 28.3741 | 20.1213 | 47.2513 | 145.268 | 145.268 | 0 | 0
2025-05-30 17:00 | 35.7 | 44.5 | 100 | 27.8071 | 20.3336 | 51.0043 | 170.666 | 170.666 | 0 | 0
2025-05-30 18:00 | 34.55 | 48.5 | 100 | 27.4551 | 20.3439 | 52.7396 | 178.8141 | 178.8141 | 0 | 0
2025-05-30 19:00 | 33.3 | 55.5 | 100 | 27.0596 | 20.5548 | 55.9362 | 200.8783 | 200.8783 | 0 | 0
2025-05-30 20:00 | 32.3 | 58.5 | 100 | 26.7494 | 20.4569 | 56.9311 | 201.1851 | 201.1851 | 0 | 0
2025-05-30 21:00 | 31.4 | 60 | 100 | 26.4695 | 20.256 | 57.1589 | 194.2006 | 194.2006 | 0 | 0
2025-05-30 22:00 | 30.45 | 65.5 | 70 | 26.1617 | 20.3433 | 59.3351 | 144.597 | 144.597 | 0 | 0
2025-05-30 23:00 | 29.75 | 70.5 | 70 | 25.9321 | 20.4575 | 61.3122 | 153.328 | 153.328 | 0 | 0
2025-05-31 | 29.45 | 71.5 | 70 | 25.8352 | 20.4151 | 61.587 | 152.9269 | 152.9269 | 0 | 0
2025-05-31 01:00 | 29.3 | 70 | 70 | 25.7896 | 20.247 | 60.7732 | 145.9972 | 145.9972 | 0 | 0
2025-05-31 02:00 | 29.15 | 68 | 70 | 25.7443 | 20.0428 | 59.7281 | 137.4444 | 137.4444 | 0 | 0
2025-05-31 03:00 | 28.5 | 67.5 | 70 | 25.5343 | 19.7623 | 59.0982 | 127.9864 | 127.9864 | 0 | 0
2025-05-31 04:00 | 27.8 | 70 | 70 | 25.3017 | 19.6764 | 59.8299 | 127.6537 | 127.6537 | 0 | 0
2025-05-31 05:00 | 27.65 | 71.5 | 70 | 25.2507 | 19.7238 | 60.4151 | 130.536 | 130.536 | 0 | 0
2025-05-31 06:00 | 28.7 | 65.5 | 100 | 25.602 | 19.6916 | 58.2722 | 176.7289 | 176.7289 | 0 | 0
2025-05-31 07:00 | 31.55 | 54.5 | 100 | 26.5291 | 19.8536 | 54.4041 | 166.9714 | 166.9714 | 0 | 0
2025-05-31 08:00 | 34.8 | 44.5 | 100 | 27.5451 | 20.0425 | 50.5419 | 157.2153 | 157.2153 | 0 | 0
2025-05-31 09:00 | 37.25 | 37 | 100 | 28.2896 | 20.034 | 47.1008 | 140.9612 | 140.9612 | 0 | 0
2025-05-31 10:00 | 38.5 | 33 | 100 | 28.6657 | 19.9499 | 45.0195 | 127.8179 | 127.8179 | 0 | 0
2025-05-31 11:00 | 38.65 | 32.5 | 100 | 28.7108 | 19.9344 | 44.7458 | 125.9062 | 125.9062 | 0 | 0
2025-05-31 12:00 | 38.5 | 33 | 100 | 28.6657 | 19.9495 | 45.0214 | 127.84 | 127.84 | 0 | 0
2025-05-31 13:00 | 38.35 | 34 | 100 | 28.6171 | 20.0221 | 45.622 | 133.489 | 133.489 | 0 | 0
2025-05-31 14:00 | 38.1 | 34 | 100 | 28.5474 | 19.9479 | 45.5281 | 130.3209 | 130.3209 | 0 | 0
2025-05-31 15:00 | 37.55 | 34.5 | 100 | 28.3894 | 19.8427 | 45.6439 | 127.0102 | 127.0102 | 0 | 0
2025-05-31 16:00 | 36.65 | 38 | 100 | 28.1131 | 19.9583 | 47.4848 | 140.0647 | 140.0647 | 0 | 0
2025-05-31 17:00 | 35.3 | 44.5 | 100 | 27.6914 | 20.2044 | 50.789 | 164.5798 | 164.5798 | 0 | 0
2025-05-31 18:00 | 33.5 | 53 | 100 | 27.1278 | 20.4033 | 54.6655 | 189.3143 | 189.3143 | 0 | 0
2025-05-31 19:00 | 32.15 | 58.5 | 100 | 26.7039 | 20.4041 | 56.8215 | 198.4776 | 198.4776 | 0 | 0
2025-05-31 20:00 | 31.35 | 60 | 100 | 26.4541 | 20.2391 | 57.1112 | 193.1755 | 193.1755 | 0 | 0
2025-05-31 21:00 | 30.6 | 60.5 | 100 | 26.2188 | 20.0078 | 56.9191 | 183.303 | 183.303 | 0 | 0
2025-05-31 22:00 | 29.85 | 61.5 | 70 | 25.979 | 19.814 | 56.9865 | 123.2403 | 123.2403 | 0 | 0
2025-05-31 23:00 | 29.15 | 62.5 | 70 | 25.7522 | 19.6361 | 57.0861 | 118.7226 | 118.7226 | 0 | 0
2025-06-01 | 28.35 | 66 | 70 | 25.487 | 19.5996 | 58.2909 | 121.1621 | 121.1621 | 0 | 0
2025-06-01 01:00 | 27.55 | 71 | 70 | 25.2181 | 19.6525 | 60.1106 | 127.6333 | 127.6333 | 0 | 0
2025-06-01 02:00 | 26.85 | 74 | 70 | 24.9823 | 19.5885 | 61.0225 | 128.3603 | 128.3603 | 0 | 0
2025-06-01 03:00 | 26.25 | 75.5 | 70 | 24.779 | 19.4561 | 61.3125 | 125.5182 | 125.5182 | 0 | 0
2025-06-01 04:00 | 26.1 | 76 | 70 | 24.7279 | 19.4302 | 61.4363 | 125.1472 | 125.1472 | 0 | 0
2025-06-01 05:00 | 26 | 77 | 70 | 24.6934 | 19.4559 | 61.8018 | 126.8136 | 126.8136 | 0 | 0
2025-06-01 06:00 | 26.45 | 74.5 | 100 | 24.8473 | 19.4679 | 60.9951 | 178.5222 | 178.5222 | 0 | 0
2025-06-01 07:00 | 28.35 | 65 | 100 | 25.4882 | 19.5281 | 57.8191 | 168.3563 | 168.3563 | 0 | 0
2025-06-01 08:00 | 30.6 | 53.5 | 100 | 26.2326 | 19.4446 | 53.4077 | 146.9549 | 146.9549 | 0 | 0
2025-06-01 09:00 | 32.6 | 44.5 | 100 | 26.8811 | 19.3337 | 49.5793 | 126.1468 | 126.1468 | 0 | 0
2025-06-01 10:00 | 34.6 | 37.5 | 100 | 27.5141 | 19.2858 | 46.3978 | 109.8943 | 109.8943 | 0 | 0
2025-06-01 11:00 | 36.75 | 30 | 100 | 28.1853 | 19.1076 | 42.5398 | 85.0269 | 85.0269 | 0 | 0
2025-06-01 12:00 | 39.1 | 22.5 | 100 | 28.9084 | 18.8203 | 38.1814 | 52.9323 | 52.9323 | 0 | 0
2025-06-01 13:00 | 40.45 | 19.5 | 100 | 29.3116 | 18.7456 | 36.315 | 40.5509 | 40.5509 | 0 | 0
2025-06-01 14:00 | 39.3 | 29 | 100 | 28.9162 | 19.692 | 42.6296 | 106.6283 | 106.6283 | 0 | 0
2025-06-01 15:00 | 37.35 | 37.5 | 100 | 28.3149 | 20.119 | 47.4652 | 145.9499 | 145.9499 | 0 | 0
2025-06-01 16:00 | 36.4 | 38.5 | 100 | 28.0387 | 19.9351 | 47.6879 | 140.1433 | 140.1433 | 0 | 0
2025-06-01 17:00 | 35 | 45 | 100 | 27.6017 | 20.1558 | 50.9336 | 163.3723 | 163.3723 | 0 | 0
2025-06-01 18:00 | 33 | 54 | 100 | 26.9746 | 20.3175 | 54.9283 | 187.1266 | 187.1266 | 0 | 0
2025-06-01 19:00 | 31.7 | 62 | 100 | 26.5572 | 20.53 | 58.368 | 209.9508 | 209.9508 | 0 | 0
2025-06-01 20:00 | 31 | 69 | 100 | 26.3257 | 20.8252 | 61.4493 | 234.2941 | 234.2941 | 0 | 0
2025-06-01 21:00 | 30.45 | 73 | 100 | 26.1473 | 20.9184 | 63.0239 | 244.2935 | 244.2935 | 0 | 0
2025-06-01 22:00 | 29.85 | 74.5 | 70 | 25.9571 | 20.793 | 63.296 | 168.187 | 168.187 | 0 | 0
2025-06-01 23:00 | 28.95 | 77.5 | 70 | 25.6671 | 20.6518 | 64.0388 | 166.1945 | 166.1945 | 0 | 0
2025-06-02 | 28 | 81.5 | 70 | 25.3559 | 20.5454 | 65.1553 | 166.1893 | 166.1893 | 0 | 0
2025-06-02 01:00 | 27.3 | 82.5 | 70 | 25.1256 | 20.3287 | 65.0744 | 159.8225 | 159.8225 | 0 | 0
2025-06-02 02:00 | 26.65 | 80.5 | 70 | 24.911 | 19.9368 | 63.7355 | 145.2789 | 145.2789 | 0 | 0
2025-06-02 03:00 | 26.35 | 74.5 | 70 | 24.8134 | 19.4282 | 60.9537 | 123.8842 | 123.8842 | 0 | 0
2025-06-02 04:00 | 26.55 | 69.5 | 70 | 24.884 | 19.1738 | 58.9011 | 111.4542 | 111.4542 | 0 | 0
2025-06-02 05:00 | 26.85 | 64 | 70 | 24.989 | 18.9101 | 56.6396 | 98.2324 | 98.2324 | 0 | 0
2025-06-02 06:00 | 28.35 | 51.5 | 100 | 25.5034 | 18.5266 | 51.5657 | 105.3787 | 105.3787 | 0 | 0
2025-06-02 07:00 | 31.65 | 37.5 | 100 | 26.6014 | 18.4021 | 45.5836 | 74.715 | 74.715 | 0 | 0
2025-06-02 08:00 | 35.35 | 27 | 100 | 27.7841 | 18.3931 | 40.438 | 49.8915 | 49.8915 | 0 | 0
2025-06-02 09:00 | 38.5 | 20 | 100 | 28.7541 | 18.352 | 36.4388 | 28.0002 | 28.0002 | 0 | 0
2025-06-02 10:00 | 41 | 15 | 100 | 29.5048 | 18.2323 | 33.1551 | 6.1199 | 6.1199 | 0 | 0
2025-06-02 11:00 | 41.1 | 23.5 | 100 | 29.4543 | 19.4542 | 39.2892 | 80.9316 | 80.9316 | 0 | 0
2025-06-02 12:00 | 39.1 | 37.5 | 100 | 28.7977 | 20.6592 | 48.2663 | 170.1451 | 170.1451 | 0 | 0
2025-06-02 13:00 | 38.3 | 38 | 100 | 28.5763 | 20.4677 | 48.2166 | 162.7041 | 162.7041 | 0 | 0
2025-06-02 14:00 | 38.75 | 31.5 | 100 | 28.7455 | 19.8407 | 44.1347 | 119.681 | 119.681 | 0 | 0
2025-06-02 15:00 | 38.7 | 29 | 100 | 28.7492 | 19.5222 | 42.4649 | 99.9454 | 99.9454 | 0 | 0
2025-06-02 16:00 | 37.7 | 34 | 100 | 28.4349 | 19.8276 | 45.394 | 125.436 | 125.436 | 0 | 0
2025-06-02 17:00 | 35.95 | 42.5 | 100 | 27.8889 | 20.211 | 49.927 | 161.0524 | 161.0524 | 0 | 0
2025-06-02 18:00 | 33.7 | 52 | 100 | 27.1907 | 20.3799 | 54.2428 | 186.7695 | 186.7695 | 0 | 0
2025-06-02 19:00 | 31.95 | 61.5 | 100 | 26.6348 | 20.5803 | 58.2863 | 211.7406 | 211.7406 | 0 | 0
2025-06-02 20:00 | 31.05 | 67 | 100 | 26.3454 | 20.6868 | 60.4961 | 225.0316 | 225.0316 | 0 | 0
2025-06-02 21:00 | 30.1 | 71.5 | 100 | 26.0407 | 20.6673 | 62.047 | 230.418 | 230.418 | 0 | 0
2025-06-02 22:00 | 29.15 | 75.5 | 70 | 25.7337 | 20.588 | 63.2681 | 162.4 | 162.4 | 0 | 0
2025-06-02 23:00 | 28.35 | 76 | 70 | 25.4755 | 20.3076 | 62.9268 | 153.5799 | 153.5799 | 0 | 0
2025-06-03 | 27.5 | 78 | 70 | 25.1953 | 20.1085 | 63.2408 | 148.867 | 148.867 | 0 | 0
2025-06-03 01:00 | 26.85 | 81.5 | 70 | 24.9771 | 20.0812 | 64.3314 | 151.0034 | 151.0034 | 0 | 0
2025-06-03 02:00 | 26.3 | 84.5 | 70 | 24.7911 | 20.0517 | 65.235 | 152.5518 | 152.5518 | 0 | 0
2025-06-03 03:00 | 25.8 | 87.5 | 70 | 24.6209 | 20.0348 | 66.1412 | 154.4276 | 154.4276 | 0 | 0
2025-06-03 04:00 | 25.5 | 89.5 | 70 | 24.5183 | 20.0343 | 66.752 | 155.9516 | 155.9516 | 0 | 0
2025-06-03 05:00 | 25.4 | 89.5 | 70 | 24.4842 | 19.9928 | 66.6747 | 154.5738 | 154.5738 | 0 | 0
2025-06-03 06:00 | 26.45 | 83.5 | 100 | 24.8421 | 20.0491 | 64.9031 | 216.5122 | 216.5122 | 0 | 0
2025-06-03 07:00 | 29.05 | 71.5 | 100 | 25.7073 | 20.2606 | 61.3073 | 211.1521 | 211.1521 | 0 | 0
2025-06-03 08:00 | 31.95 | 59 | 100 | 26.6413 | 20.3726 | 56.9732 | 197.9986 | 197.9986 | 0 | 0
2025-06-03 09:00 | 34.65 | 46.5 | 100 | 27.4927 | 20.1865 | 51.6331 | 167.7258 | 167.7258 | 0 | 0
2025-06-03 10:00 | 37.3 | 35.5 | 100 | 28.3125 | 19.88 | 46.1892 | 131.0796 | 131.0796 | 0 | 0
2025-06-03 11:00 | 39.5 | 28.5 | 100 | 28.9752 | 19.6823 | 42.3648 | 105.1239 | 105.1239 | 0 | 0
2025-06-03 12:00 | 40.35 | 28.5 | 100 | 29.207 | 19.9161 | 42.6396 | 115.0267 | 115.0267 | 0 | 0
2025-06-03 13:00 | 39.3 | 37 | 100 | 28.8552 | 20.6588 | 48.0476 | 169.3464 | 169.3464 | 0 | 0
2025-06-03 14:00 | 38.15 | 39.5 | 100 | 28.5248 | 20.5878 | 49.1354 | 171.8414 | 171.8414 | 0 | 0
2025-06-03 15:00 | 37.4 | 38 | 100 | 28.3258 | 20.1855 | 47.8273 | 150.4864 | 150.4864 | 0 | 0
2025-06-03 16:00 | 35.8 | 46.5 | 100 | 27.8262 | 20.5672 | 52.257 | 185.4011 | 185.4011 | 0 | 0
2025-06-03 17:00 | 33.9 | 58.5 | 100 | 27.2263 | 21.0379 | 57.9913 | 228.8869 | 228.8869 | 0 | 0
2025-06-03 18:00 | 32.2 | 69.5 | 100 | 26.6887 | 21.329 | 62.6513 | 259.9169 | 259.9169 | 0 | 0
2025-06-03 19:00 | 30.95 | 77.5 | 100 | 26.2917 | 21.4555 | 65.6904 | 277.1766 | 277.1766 | 0 | 0
2025-06-03 20:00 | 30.25 | 81.5 | 100 | 26.069 | 21.4656 | 67.041 | 282.7684 | 282.7684 | 0 | 0
2025-06-03 21:00 | 29.75 | 83.5 | 100 | 25.9105 | 21.4022 | 67.5551 | 282.0519 | 282.0519 | 0 | 0
2025-06-03 22:00 | 29.2 | 85.5 | 70 | 25.7351 | 21.3133 | 68.0104 | 196.0371 | 196.0371 | 0 | 0
2025-06-03 23:00 | 28.6 | 87.5 | 70 | 25.5422 | 21.1985 | 68.4057 | 193.7267 | 193.7267 | 0 | 0
2025-06-04 | 28.15 | 87 | 70 | 25.3985 | 20.9768 | 67.7866 | 185.6296 | 185.6296 | 0 | 0
2025-06-04 01:00 | 27.8 | 85 | 70 | 25.2872 | 20.6979 | 66.5948 | 174.4584 | 174.4584 | 0 | 0
2025-06-04 02:00 | 27.35 | 83 | 70 | 25.1416 | 20.3819 | 65.3517 | 162.1447 | 162.1447 | 0 | 0
2025-06-04 03:00 | 26.8 | 82 | 70 | 24.9601 | 20.0936 | 64.5089 | 151.7981 | 151.7981 | 0 | 0
2025-06-04 04:00 | 26.6 | 81.5 | 70 | 24.8936 | 19.9812 | 64.1523 | 147.7074 | 147.7074 | 0 | 0
2025-06-04 05:00 | 26.6 | 81 | 70 | 24.8939 | 19.9484 | 63.9339 | 146.2202 | 146.2202 | 0 | 0
2025-06-04 06:00 | 27.15 | 77.5 | 100 | 25.0799 | 19.9377 | 62.7718 | 203.9828 | 203.9828 | 0 | 0
2025-06-04 07:00 | 29.15 | 67.5 | 100 | 25.7451 | 20.0065 | 59.4793 | 193.8326 | 193.8326 | 0 | 0
2025-06-04 08:00 | 31.75 | 56 | 100 | 26.5875 | 20.0498 | 55.2907 | 178.3018 | 178.3018 | 0 | 0
2025-06-04 09:00 | 34.1 | 47 | 100 | 27.328 | 20.0521 | 51.6412 | 162.5921 | 162.5921 | 0 | 0
2025-06-04 10:00 | 36 | 40 | 100 | 27.9157 | 19.969 | 48.4328 | 144.9059 | 144.9059 | 0 | 0
2025-06-04 11:00 | 37.15 | 35.5 | 100 | 28.2699 | 19.8353 | 46.1308 | 129.1344 | 129.1344 | 0 | 0
2025-06-04 12:00 | 37.5 | 34.5 | 100 | 28.3752 | 19.8261 | 45.6328 | 126.4645 | 126.4645 | 0 | 0
2025-06-04 13:00 | 37.1 | 36.5 | 100 | 28.2499 | 19.9302 | 46.744 | 135.6411 | 135.6411 | 0 | 0
2025-06-04 14:00 | 36.3 | 40 | 100 | 28.0021 | 20.0614 | 48.5739 | 149.1626 | 149.1626 | 0 | 0
2025-06-04 15:00 | 35.45 | 42.5 | 100 | 27.7441 | 20.0496 | 49.6949 | 153.9199 | 153.9199 | 0 | 0
2025-06-04 16:00 | 34.4 | 45.5 | 100 | 27.4227 | 20.0059 | 50.9483 | 157.9117 | 157.9117 | 0 | 0
2025-06-04 17:00 | 33 | 53 | 100 | 26.9776 | 20.2272 | 54.3993 | 181.5006 | 181.5006 | 0 | 0
2025-06-04 18:00 | 31.5 | 62.5 | 100 | 26.4945 | 20.4963 | 58.5065 | 209.2752 | 209.2752 | 0 | 0
2025-06-04 19:00 | 30.45 | 69 | 100 | 26.155 | 20.6133 | 61.0634 | 224.2731 | 224.2731 | 0 | 0
2025-06-04 20:00 | 29.8 | 71 | 100 | 25.9472 | 20.5141 | 61.5779 | 222.2922 | 222.2922 | 0 | 0
2025-06-04 21:00 | 29.25 | 71 | 100 | 25.7722 | 20.302 | 61.1949 | 212.2602 | 212.2602 | 0 | 0
2025-06-04 22:00 | 28.65 | 72 | 70 | 25.5777 | 20.1428 | 61.2617 | 144.3308 | 144.3308 | 0 | 0
2025-06-04 23:00 | 27.95 | 74.5 | 70 | 25.3467 | 20.0474 | 61.9471 | 143.5478 | 143.5478 | 0 | 0
2025-06-05 | 27.3 | 77 | 70 | 25.1301 | 19.9632 | 62.6389 | 143.0906 | 143.0906 | 0 | 0
2025-06-05 01:00 | 26.7 | 79 | 70 | 24.9287 | 19.8589 | 63.1205 | 141.497 | 141.497 | 0 | 0
2025-06-05 02:00 | 26.15 | 80.5 | 70 | 24.7426 | 19.7378 | 63.404 | 138.8975 | 138.8975 | 0 | 0
2025-06-05 03:00 | 25.65 | 81.5 | 70 | 24.5722 | 19.6026 | 63.5002 | 135.4042 | 135.4042 | 0 | 0
2025-06-05 04:00 | 25.5 | 79 | 70 | 24.5218 | 19.3866 | 62.3586 | 126.4891 | 126.4891 | 0 | 0
2025-06-05 05:00 | 25.45 | 75.5 | 70 | 24.5057 | 19.1478 | 60.8636 | 116.0271 | 116.0271 | 0 | 0
2025-06-05 06:00 | 26.05 | 70.5 | 100 | 24.7134 | 19.0538 | 59.064 | 155.1976 | 155.1976 | 0 | 0
2025-06-05 07:00 | 28.2 | 60 | 100 | 25.4442 | 19.1096 | 55.4412 | 142.8859 | 142.8859 | 0 | 0
2025-06-05 08:00 | 30.85 | 50 | 100 | 26.3191 | 19.2395 | 51.7596 | 132.2965 | 132.2965 | 0 | 0
2025-06-05 09:00 | 33.3 | 42.5 | 100 | 27.1023 | 19.3704 | 48.7638 | 123.9288 | 123.9288 | 0 | 0
2025-06-05 10:00 | 35.55 | 36 | 100 | 27.8033 | 19.4149 | 45.8423 | 112.0796 | 112.0796 | 0 | 0
2025-06-05 11:00 | 37.3 | 30.5 | 100 | 28.3419 | 19.3162 | 43.0074 | 94.8609 | 94.8609 | 0 | 0
2025-06-05 12:00 | 38.15 | 28.5 | 100 | 28.5974 | 19.3162 | 41.9579 | 89.6732 | 89.6732 | 0 | 0
2025-06-05 13:00 | 37.95 | 31.5 | 100 | 28.5213 | 19.6153 | 43.85 | 109.8436 | 109.8436 | 0 | 0
2025-06-05 14:00 | 37.1 | 37 | 100 | 28.2471 | 19.9878 | 47.0422 | 139.0015 | 139.0015 | 0 | 0
2025-06-05 15:00 | 35.95 | 41.5 | 100 | 27.8939 | 20.1099 | 49.3074 | 154.1738 | 154.1738 | 0 | 0
2025-06-05 16:00 | 34.6 | 48 | 100 | 27.472 | 20.3156 | 52.4574 | 176.2193 | 176.2193 | 0 | 0
2025-06-05 17:00 | 32.9 | 59.5 | 100 | 26.9275 | 20.7622 | 57.8286 | 216.8518 | 216.8518 | 0 | 0
2025-06-05 18:00 | 31.3 | 68.5 | 100 | 26.4191 | 20.9027 | 61.4087 | 237.1716 | 237.1716 | 0 | 0
2025-06-05 19:00 | 30.3 | 72 | 100 | 26.1026 | 20.7838 | 62.4094 | 236.3424 | 236.3424 | 0 | 0
2025-06-05 20:00 | 29.7 | 72 | 100 | 25.914 | 20.5506 | 61.9665 | 225.1048 | 225.1048 | 0 | 0
2025-06-05 21:00 | 29.2 | 71.5 | 100 | 25.7556 | 20.3205 | 61.3739 | 213.498 | 213.498 | 0 | 0
2025-06-05 22:00 | 28.6 | 71.5 | 70 | 25.5621 | 20.0896 | 60.9709 | 141.8935 | 141.8935 | 0 | 0
2025-06-05 23:00 | 28.05 | 70 | 70 | 25.3842 | 19.7736 | 59.9354 | 130.3364 | 130.3364 | 0 | 0
2025-06-06 | 27.6 | 67.5 | 70 | 25.2379 | 19.4294 | 58.5448 | 117.1597 | 117.1597 | 0 | 0
2025-06-06 01:00 | 27 | 67 | 70 | 25.0376 | 19.1728 | 58.0088 | 108.8156 | 108.8156 | 0 | 0
2025-06-06 02:00 | 26.2 | 69 | 70 | 24.7653 | 19.0114 | 58.4802 | 105.8371 | 105.8371 | 0 | 0
2025-06-06 03:00 | 25.4 | 70 | 70 | 24.4902 | 18.7802 | 58.5157 | 99.8125 | 99.8125 | 0 | 0
2025-06-06 04:00 | 24.95 | 70 | 70 | 24.3339 | 18.6141 | 58.307 | 94.8756 | 94.8756 | 0 | 0
2025-06-06 05:00 | 24.95 | 68 | 70 | 24.3343 | 18.4881 | 57.4793 | 89.328 | 89.328 | 0 | 0
2025-06-06 06:00 | 26.15 | 60.5 | 100 | 24.7524 | 18.4252 | 54.7901 | 114.649 | 114.649 | 0 | 0
2025-06-06 07:00 | 29 | 48.5 | 100 | 25.7224 | 18.5114 | 50.33 | 99.2726 | 99.2726 | 0 | 0
2025-06-06 08:00 | 31.9 | 41 | 100 | 26.672 | 18.7984 | 47.4607 | 96.9843 | 96.9843 | 0 | 0
2025-06-06 09:00 | 33.65 | 39.5 | 100 | 27.2192 | 19.1967 | 47.2024 | 110.196 | 110.196 | 0 | 0
2025-06-06 10:00 | 34.55 | 38.5 | 100 | 27.4952 | 19.3732 | 46.9438 | 115.4538 | 115.4538 | 0 | 0
2025-06-06 11:00 | 35.25 | 36 | 100 | 27.7145 | 19.3292 | 45.7236 | 108.139 | 108.139 | 0 | 0
2025-06-06 12:00 | 35.65 | 34 | 100 | 27.8421 | 19.2359 | 44.6625 | 99.7627 | 99.7627 | 0 | 0
2025-06-06 13:00 | 35.5 | 34.5 | 100 | 27.7954 | 19.2447 | 44.9188 | 101.3422 | 101.3422 | 0 | 0
2025-06-06 14:00 | 35.05 | 36.5 | 100 | 27.6528 | 19.3194 | 45.9607 | 109.0273 | 109.0273 | 0 | 0
2025-06-06 15:00 | 34.35 | 41 | 100 | 27.4254 | 19.5574 | 48.3154 | 128.7002 | 128.7002 | 0 | 0
2025-06-06 16:00 | 33.4 | 47 | 100 | 27.118 | 19.8237 | 51.2784 | 151.9819 | 151.9819 | 0 | 0
2025-06-06 17:00 | 32.25 | 53.5 | 100 | 26.7481 | 20.0145 | 54.218 | 172.062 | 172.062 | 0 | 0
2025-06-06 18:00 | 30.9 | 62 | 100 | 26.3098 | 20.2379 | 57.8317 | 195.8987 | 195.8987 | 0 | 0
2025-06-06 19:00 | 29.85 | 70 | 100 | 25.9648 | 20.4609 | 61.0932 | 217.9192 | 217.9192 | 0 | 0
2025-06-06 20:00 | 29.2 | 74.5 | 100 | 25.7513 | 20.538 | 62.7795 | 227.6485 | 227.6485 | 0 | 0
2025-06-06 21:00 | 28.6 | 77.5 | 100 | 25.5549 | 20.5136 | 63.7361 | 230.3349 | 230.3349 | 0 | 0
2025-06-06 22:00 | 27.95 | 80.5 | 70 | 25.3408 | 20.459 | 64.62 | 162.066 | 162.066 | 0 | 0
2025-06-06 23:00 | 27.25 | 83.5 | 70 | 25.1084 | 20.3752 | 65.4325 | 161.8518 | 161.8518 | 0 | 0
2025-06-07 | 26.35 | 86.5 | 70 | 24.807 | 20.1994 | 66.0597 | 158.5437 | 158.5437 | 0 | 0
2025-06-07 01:00 | 25.4 | 90 | 70 | 24.4841 | 20.0232 | 66.8234 | 155.5549 | 155.5549 | 0 | 0
2025-06-07 02:00 | 24.65 | 93.5 | 70 | 24.2259 | 19.9184 | 67.6927 | 154.8166 | 154.8166 | 0 | 0
2025-06-07 03:00 | 24.05 | 95.5 | 70 | 24.0175 | 19.7819 | 68.0416 | 151.8402 | 151.8402 | 0 | 0
2025-06-07 04:00 | 24 | 95 | 70 | 24 | 19.7322 | 67.8048 | 149.8485 | 149.8485 | 0 | 0
2025-06-07 05:00 | 24.1 | 94 | 70 | 24.0349 | 19.7176 | 67.4792 | 148.5935 | 148.5935 | 0 | 0
2025-06-07 06:00 | 24.8 | 89.5 | 100 | 24.2783 | 19.7462 | 66.1738 | 208.6629 | 208.6629 | 0 | 0
2025-06-07 07:00 | 26.75 | 79 | 100 | 24.9455 | 19.8809 | 63.1004 | 202.5133 | 202.5133 | 0 | 0
2025-06-07 08:00 | 29.15 | 65.5 | 100 | 25.7481 | 19.862 | 58.4736 | 183.6474 | 183.6474 | 0 | 0
2025-06-07 09:00 | 31.75 | 51.5 | 100 | 26.5988 | 19.6731 | 52.8966 | 153.1235 | 153.1235 | 0 | 0
2025-06-07 10:00 | 34.1 | 44.5 | 100 | 27.3375 | 19.8198 | 50.1805 | 146.7221 | 146.7221 | 0 | 0
2025-06-07 11:00 | 35.85 | 41.5 | 100 | 27.8652 | 20.084 | 49.223 | 152.3176 | 152.3176 | 0 | 0
2025-06-07 12:00 | 36.6 | 40.5 | 100 | 28.0856 | 20.2162 | 48.9638 | 156.1765 | 156.1765 | 0 | 0
2025-06-07 13:00 | 36.05 | 45.5 | 100 | 27.903 | 20.5568 | 51.7358 | 181.9717 | 181.9717 | 0 | 0
2025-06-07 14:00 | 35.4 | 49 | 100 | 27.7002 | 20.686 | 53.4588 | 194.7805 | 194.7805 | 0 | 0
2025-06-07 15:00 | 35.25 | 52 | 100 | 27.6436 | 20.9239 | 55.1292 | 211.5478 | 211.5478 | 0 | 0
2025-06-07 16:00 | 34.55 | 55 | 100 | 27.4293 | 20.9587 | 56.4089 | 218.489 | 218.489 | 0 | 0
2025-06-07 17:00 | 33.8 | 56.5 | 100 | 27.2047 | 20.8268 | 56.7616 | 214.7309 | 214.7309 | 0 | 0
2025-06-07 18:00 | 32.75 | 63.5 | 100 | 26.8707 | 21.0482 | 59.8498 | 236.5721 | 236.5721 | 0 | 0
2025-06-07 19:00 | 31.4 | 72 | 100 | 26.4416 | 21.2167 | 63.2442 | 257.1937 | 257.1937 | 0 | 0
2025-06-07 20:00 | 30.9 | 75 | 100 | 26.2823 | 21.2487 | 64.3459 | 262.8711 | 262.8711 | 0 | 0
2025-06-07 21:00 | 30.55 | 77 | 100 | 26.1707 | 21.2584 | 65.0439 | 265.9961 | 265.9961 | 0 | 0
2025-06-07 22:00 | 30 | 81.5 | 70 | 25.9921 | 21.3638 | 66.7652 | 193.933 | 193.933 | 0 | 0
2025-06-07 23:00 | 29.45 | 85.5 | 70 | 25.8139 | 21.4186 | 68.1868 | 199.3624 | 199.3624 | 0 | 0
2025-06-08 | 29 | 88 | 70 | 25.6688 | 21.4016 | 68.9511 | 200.9024 | 200.9024 | 0 | 0
2025-06-08 01:00 | 28.55 | 90 | 70 | 25.5235 | 21.3458 | 69.4616 | 200.6071 | 200.6071 | 0 | 0
2025-06-08 02:00 | 28.15 | 92 | 70 | 25.3933 | 21.308 | 70.0025 | 200.8949 | 200.8949 | 0 | 0
2025-06-08 03:00 | 27.65 | 94 | 70 | 25.2301 | 21.2226 | 70.4328 | 199.5002 | 199.5002 | 0 | 0
2025-06-08 04:00 | 27.7 | 94 | 70 | 25.2463 | 21.2442 | 70.479 | 200.2526 | 200.2526 | 0 | 0
2025-06-08 05:00 | 28.05 | 93.5 | 70 | 25.3596 | 21.3629 | 70.5828 | 204.0156 | 204.0156 | 0 | 0
2025-06-08 06:00 | 28.65 | 90.5 | 100 | 25.5547 | 21.4221 | 69.7794 | 290.9476 | 290.9476 | 0 | 0
2025-06-08 07:00 | 30.4 | 80.5 | 100 | 26.1177 | 21.4557 | 66.6296 | 280.356 | 280.356 | 0 | 0
2025-06-08 08:00 | 32.55 | 65 | 100 | 26.8068 | 21.0989 | 60.4849 | 241.1015 | 241.1015 | 0 | 0
2025-06-08 09:00 | 34.65 | 49 | 100 | 27.4828 | 20.432 | 53.0202 | 182.8028 | 182.8028 | 0 | 0
2025-06-08 10:00 | 36.75 | 38.5 | 100 | 28.1392 | 20.0495 | 47.7954 | 144.4126 | 144.4126 | 0 | 0
2025-06-08 11:00 | 38.5 | 30 | 100 | 28.6863 | 19.5977 | 43.0194 | 104.7396 | 104.7396 | 0 | 0
2025-06-08 12:00 | 38.05 | 37.5 | 100 | 28.5108 | 20.3386 | 47.7433 | 155.1481 | 155.1481 | 0 | 0
2025-06-08 13:00 | 36.25 | 53.5 | 100 | 27.9185 | 21.4238 | 56.6838 | 238.2622 | 238.2622 | 0 | 0
2025-06-08 14:00 | 35.1 | 58 | 100 | 27.5743 | 21.4359 | 58.5145 | 246.7046 | 246.7046 | 0 | 0
2025-06-08 15:00 | 34.55 | 58 | 100 | 27.4172 | 21.2343 | 58.1185 | 236.8703 | 236.8703 | 0 | 0
2025-06-08 16:00 | 33.95 | 58 | 100 | 27.2432 | 21.0148 | 57.6997 | 226.2781 | 226.2781 | 0 | 0
2025-06-08 17:00 | 33.3 | 60 | 100 | 27.0451 | 20.9534 | 58.3539 | 226.5526 | 226.5526 | 0 | 0
2025-06-08 18:00 | 32.45 | 64 | 100 | 26.7795 | 20.9769 | 59.9003 | 233.9147 | 233.9147 | 0 | 0
2025-06-08 19:00 | 31.45 | 68.5 | 100 | 26.4651 | 20.9614 | 61.5015 | 239.7708 | 239.7708 | 0 | 0
2025-06-08 20:00 | 31.1 | 71 | 100 | 26.3523 | 21.0208 | 62.5007 | 246.2052 | 246.2052 | 0 | 0
2025-06-08 21:00 | 30.7 | 74.5 | 100 | 26.2219 | 21.1309 | 63.9334 | 256.3909 | 256.3909 | 0 | 0
2025-06-08 22:00 | 30.15 | 77.5 | 70 | 26.0458 | 21.1339 | 64.9582 | 182.3707 | 182.3707 | 0 | 0
2025-06-08 23:00 | 29.65 | 79 | 70 | 25.8869 | 21.0409 | 65.2714 | 180.5353 | 180.5353 | 0 | 0
2025-06-09 | 29.2 | 81 | 70 | 25.7419 | 20.9999 | 65.8527 | 180.9405 | 180.9405 | 0 | 0
2025-06-09 01:00 | 28.8 | 83 | 70 | 25.612 | 20.9758 | 66.4581 | 181.8649 | 181.8649 | 0 | 0
2025-06-09 02:00 | 28.3 | 85 | 70 | 25.4493 | 20.9059 | 66.9602 | 181.1761 | 181.1761 | 0 | 0
2025-06-09 03:00 | 27.8 | 87 | 70 | 25.2854 | 20.8311 | 67.4446 | 180.2996 | 180.2996 | 0 | 0
2025-06-09 04:00 | 27.95 | 86.5 | 70 | 25.3346 | 20.8609 | 67.3455 | 180.8876 | 180.8876 | 0 | 0
2025-06-09 05:00 | 28.2 | 85.5 | 70 | 25.4165 | 20.8974 | 67.1009 | 181.3087 | 181.3087 | 0 | 0
2025-06-09 06:00 | 28.9 | 80.5 | 100 | 25.6472 | 20.8435 | 65.3695 | 250.1326 | 250.1326 | 0 | 0
2025-06-09 07:00 | 31.35 | 63.5 | 100 | 26.4462 | 20.5252 | 58.8674 | 211.4131 | 211.4131 | 0 | 0
2025-06-09 08:00 | 34 | 46 | 100 | 27.302 | 19.9299 | 50.9831 | 154.4935 | 154.4935 | 0 | 0
2025-06-09 09:00 | 35.95 | 37.5 | 100 | 27.9136 | 19.6983 | 46.8563 | 126.8701 | 126.8701 | 0 | 0
2025-06-09 10:00 | 37.95 | 32 | 100 | 28.5182 | 19.6798 | 44.139 | 113.1414 | 113.1414 | 0 | 0
2025-06-09 11:00 | 39.85 | 26 | 100 | 29.0914 | 19.4694 | 40.7048 | 88.3289 | 88.3289 | 0 | 0
2025-06-09 12:00 | 41.05 | 21.5 | 100 | 29.4591 | 19.1729 | 37.8138 | 62.8446 | 62.8446 | 0 | 0
2025-06-09 13:00 | 40.9 | 24.5 | 100 | 29.391 | 19.5439 | 39.936 | 87.1646 | 87.1646 | 0 | 0
2025-06-09 14:00 | 39.1 | 34 | 100 | 28.8239 | 20.2477 | 45.9051 | 142.9896 | 142.9896 | 0 | 0
2025-06-09 15:00 | 38.25 | 36 | 100 | 28.576 | 20.2268 | 46.8709 | 146.9281 | 146.9281 | 0 | 0
2025-06-09 16:00 | 38.55 | 33.5 | 100 | 28.6761 | 20.0249 | 45.3584 | 132.125 | 132.125 | 0 | 0
2025-06-09 17:00 | 38.1 | 33.5 | 100 | 28.5507 | 19.8929 | 45.1879 | 126.4189 | 126.4189 | 0 | 0
2025-06-09 18:00 | 36.95 | 37 | 100 | 28.2044 | 19.9448 | 46.9673 | 136.8506 | 136.8506 | 0 | 0
2025-06-09 19:00 | 35.35 | 44 | 100 | 27.7083 | 20.1738 | 50.4973 | 161.8279 | 161.8279 | 0 | 0
2025-06-09 20:00 | 34.55 | 45 | 100 | 27.4694 | 20.0121 | 50.6938 | 156.5328 | 156.5328 | 0 | 0
2025-06-09 21:00 | 34.3 | 41 | 100 | 27.4105 | 19.5418 | 48.2953 | 128.0237 | 128.0237 | 0 | 0
2025-06-09 22:00 | 33.75 | 39 | 70 | 27.2514 | 19.1771 | 46.9648 | 75.9601 | 75.9601 | 0 | 0
2025-06-09 23:00 | 33 | 40 | 70 | 27.018 | 19.0432 | 47.2753 | 73.5622 | 73.5622 | 0 | 0
2025-06-10 | 32.15 | 41 | 70 | 26.7506 | 18.8733 | 47.5515 | 70.1851 | 70.1851 | 0 | 0
2025-06-10 01:00 | 31.25 | 41.5 | 70 | 26.4647 | 18.6398 | 47.5509 | 64.3484 | 64.3484 | 0 | 0
2025-06-10 02:00 | 30.35 | 43.5 | 70 | 26.1714 | 18.5327 | 48.3106 | 64.0204 | 64.0204 | 0 | 0
2025-06-10 03:00 | 29.75 | 46 | 70 | 25.9722 | 18.5506 | 49.3711 | 67.7133 | 67.7133 | 0 | 0
2025-06-10 04:00 | 29.4 | 49 | 70 | 25.8532 | 18.6792 | 50.7187 | 75.0413 | 75.0413 | 0 | 0
2025-06-10 05:00 | 29 | 52 | 70 | 25.7177 | 18.7827 | 52.0142 | 81.5288 | 81.5288 | 0 | 0
2025-06-10 06:00 | 29.6 | 49.5 | 100 | 25.9177 | 18.7852 | 51.0243 | 112.3165 | 112.3165 | 0 | 0
2025-06-10 07:00 | 31.85 | 42.5 | 100 | 26.6524 | 18.9158 | 48.2449 | 104.8693 | 104.8693 | 0 | 0
2025-06-10 08:00 | 35 | 34 | 100 | 27.6485 | 19.0464 | 44.4785 | 92.1472 | 92.1472 | 0 | 0
2025-06-10 09:00 | 38.1 | 25.5 | 100 | 28.6025 | 18.9437 | 39.9759 | 66.3166 | 66.3166 | 0 | 0
2025-06-10 10:00 | 40.5 | 18.5 | 100 | 29.334 | 18.6238 | 35.5993 | 32.2901 | 32.2901 | 0 | 0
2025-06-10 11:00 | 41.95 | 14.5 | 100 | 29.7732 | 18.3649 | 32.8146 | 8.2211 | 8.2211 | 0 | 0
2025-06-10 12:00 | 42.85 | 14 | 100 | 30.0243 | 18.4748 | 32.4866 | 10.0134 | 10.0134 | 0 | 0
2025-06-10 13:00 | 43.35 | 14 | 100 | 30.1591 | 18.5767 | 32.5206 | 13.6526 | 13.6526 | 0 | 0
2025-06-10 14:00 | 42.95 | 14 | 100 | 30.0515 | 18.4919 | 32.5016 | 10.8504 | 10.8504 | 0 | 0
2025-06-10 15:00 | 41.75 | 16 | 100 | 29.7034 | 18.5402 | 33.9297 | 20.602 | 20.602 | 0 | 0
2025-06-10 16:00 | 40.55 | 17.5 | 100 | 29.3567 | 18.4897 | 34.915 | 24.4027 | 24.4027 | 0 | 0
2025-06-10 17:00 | 39.15 | 20.5 | 100 | 28.9373 | 18.5708 | 36.8464 | 37.5411 | 37.5411 | 0 | 0
2025-06-10 18:00 | 37.05 | 30.5 | 100 | 28.2697 | 19.2451 | 42.9456 | 92.1118 | 92.1118 | 0 | 0
2025-06-10 19:00 | 34.85 | 45 | 100 | 27.5577 | 20.1081 | 50.8519 | 161.073 | 161.073 | 0 | 0
2025-06-10 20:00 | 33.5 | 53 | 100 | 27.1279 | 20.404 | 54.6564 | 189.2133 | 189.2133 | 0 | 0
2025-06-10 21:00 | 32.95 | 51 | 100 | 26.9689 | 20.0348 | 53.2594 | 168.8474 | 168.8474 | 0 | 0
2025-06-10 22:00 | 32.25 | 48 | 70 | 26.763 | 19.5325 | 51.3156 | 98.9209 | 98.9209 | 0 | 0
2025-06-10 23:00 | 31.5 | 47.5 | 70 | 26.5301 | 19.2417 | 50.7437 | 89.5986 | 89.5986 | 0 | 0
2025-06-11 | 30.75 | 50 | 70 | 26.2873 | 19.205 | 51.7247 | 91.6627 | 91.6627 | 0 | 0
2025-06-11 01:00 | 30 | 51.5 | 70 | 26.0441 | 19.0772 | 52.171 | 89.6845 | 89.6845 | 0 | 0
2025-06-11 02:00 | 29.5 | 46.5 | 70 | 25.8897 | 18.5098 | 49.5504 | 67.3175 | 67.3175 | 0 | 0
2025-06-11 03:00 | 28.85 | 39.5 | 70 | 25.6844 | 17.7437 | 46.0256 | 37.6347 | 37.6347 | 0 | 0
2025-06-11 04:00 | 28.8 | 34.5 | 70 | 25.674 | 17.3214 | 43.6302 | 20.0871 | 20.0871 | 0 | 0
2025-06-11 05:00 | 29.2 | 31.5 | 70 | 25.8121 | 17.1823 | 42.2119 | 12.2978 | 12.2978 | 0 | 0
2025-06-11 06:00 | 30 | 29 | 100 | 26.0824 | 17.1818 | 41.0116 | 11.907 | 11.907 | 0 | 0
2025-06-11 07:00 | 31.85 | 25.5 | 100 | 26.6946 | 17.3381 | 39.2642 | 8.6408 | 8.6408 | 0 | 0
2025-06-11 08:00 | 34.45 | 21.5 | 100 | 27.5307 | 17.5702 | 37.111 | 5.4545 | 5.4545 | 0 | 0
2025-06-11 09:00 | 37.45 | 17 | 100 | 28.4646 | 17.7372 | 34.4152 | 0 | 0 | 0 | 0
2025-06-11 10:00 | 39.85 | 15 | 100 | 29.179 | 17.9928 | 33.1094 | 0 | 0 | 0 | 0
2025-06-11 11:00 | 41.35 | 16 | 100 | 29.5929 | 18.4572 | 33.886 | 17.37 | 17.37 | 0 | 0
2025-06-11 12:00 | 42.25 | 16.5 | 100 | 29.8347 | 18.728 | 34.3352 | 28.9245 | 28.9245 | 0 | 0
2025-06-11 13:00 | 42.65 | 15.5 | 100 | 29.9537 | 18.6624 | 33.6224 | 22.7997 | 22.7997 | 0 | 0
2025-06-11 14:00 | 42.35 | 15.5 | 100 | 29.8725 | 18.596 | 33.6022 | 20.5722 | 20.5722 | 0 | 0
2025-06-11 15:00 | 41.4 | 16.5 | 100 | 29.6022 | 18.5363 | 34.2694 | 22.395 | 22.395 | 0 | 0
2025-06-11 16:00 | 40.1 | 19 | 100 | 29.2179 | 18.5935 | 35.9285 | 33.4379 | 33.4379 | 0 | 0
2025-06-11 17:00 | 38.35 | 26.5 | 100 | 28.6675 | 19.1259 | 40.7077 | 76.7731 | 76.7731 | 0 | 0
2025-06-11 18:00 | 36.5 | 34.5 | 100 | 28.0886 | 19.5332 | 45.2663 | 113.8115 | 113.8115 | 0 | 0
2025-06-11 19:00 | 35.15 | 39.5 | 100 | 27.6695 | 19.654 | 47.7785 | 130.0344 | 130.0344 | 0 | 0
2025-06-11 20:00 | 34.15 | 43 | 100 | 27.3579 | 19.6869 | 49.3906 | 138.6075 | 138.6075 | 0 | 0
2025-06-11 21:00 | 33.35 | 44 | 100 | 27.1127 | 19.5262 | 49.6174 | 133.6144 | 133.6144 | 0 | 0
2025-06-11 22:00 | 32.65 | 44.5 | 70 | 26.8965 | 19.3481 | 49.6119 | 88.8809 | 88.8809 | 0 | 0
2025-06-11 23:00 | 31.75 | 45.5 | 70 | 26.6135 | 19.1479 | 49.8024 | 84.3213 | 84.3213 | 0 | 0
2025-06-12 | 30.8 | 46 | 70 | 26.3113 | 18.8853 | 49.7223 | 77.3582 | 77.3582 | 0 | 0
2025-06-12 01:00 | 30.05 | 47 | 70 | 26.068 | 18.7273 | 49.9708 | 74.0961 | 74.0961 | 0 | 0
2025-06-12 02:00 | 29.3 | 51.5 | 70 | 25.8168 | 18.8428 | 51.9012 | 82.8343 | 82.8343 | 0 | 0
2025-06-12 03:00 | 28.45 | 60 | 70 | 25.5268 | 19.1976 | 55.5663 | 102.7551 | 102.7551 | 0 | 0
2025-06-12 04:00 | 28.3 | 64.5 | 70 | 25.4723 | 19.4723 | 57.5783 | 115.7825 | 115.7825 | 0 | 0
2025-06-12 05:00 | 28.3 | 64 | 70 | 25.4728 | 19.4366 | 57.3434 | 114.1334 | 114.1334 | 0 | 0
2025-06-12 06:00 | 28.95 | 57 | 100 | 25.6947 | 19.1492 | 54.3765 | 139.999 | 139.999 | 0 | 0
2025-06-12 07:00 | 31.8 | 44 | 100 | 26.633 | 19.0322 | 49.0259 | 112.6985 | 112.6985 | 0 | 0
2025-06-12 08:00 | 35.6 | 30 | 100 | 27.8457 | 18.789 | 42.2667 | 72.4874 | 72.4874 | 0 | 0
2025-06-12 09:00 | 38.85 | 18.5 | 100 | 28.8655 | 18.2428 | 35.4567 | 18.925 | 18.925 | 0 | 0
2025-06-12 10:00 | 41.15 | 14 | 100 | 29.5558 | 18.1218 | 32.4256 | 0 | 0 | 0 | 0
2025-06-12 11:00 | 42.8 | 12.5 | 100 | 30.0274 | 18.2284 | 31.3401 | 0 | 0 | 0 | 0
2025-06-12 12:00 | 43.9 | 12 | 100 | 30.3306 | 18.3639 | 30.9759 | 0 | 0 | 0 | 0
2025-06-12 13:00 | 44.35 | 12 | 100 | 30.4506 | 18.4506 | 30.9921 | 0.6969 | 0.6969 | 0 | 0
2025-06-12 14:00 | 44 | 13 | 100 | 30.3449 | 18.5451 | 31.7806 | 8.493 | 8.493 | 0 | 0
2025-06-12 15:00 | 42.4 | 17.5 | 100 | 29.8648 | 18.9067 | 35.1189 | 39.5758 | 39.5758 | 0 | 0
2025-06-12 16:00 | 39.9 | 27.5 | 100 | 29.093 | 19.6667 | 41.7927 | 101.5454 | 101.5454 | 0 | 0
2025-06-12 17:00 | 37.65 | 36.5 | 100 | 28.4054 | 20.0985 | 46.9599 | 142.8184 | 142.8184 | 0 | 0
2025-06-12 18:00 | 35.9 | 42.5 | 100 | 27.8745 | 20.1967 | 49.8905 | 160.1877 | 160.1877 | 0 | 0
2025-06-12 19:00 | 34.55 | 50 | 100 | 27.4492 | 20.4885 | 53.5798 | 187.9232 | 187.9232 | 0 | 0
2025-06-12 20:00 | 33.85 | 53 | 100 | 27.2318 | 20.5255 | 54.8673 | 194.9507 | 194.9507 | 0 | 0
2025-06-12 21:00 | 33.25 | 53 | 100 | 27.053 | 20.3159 | 54.5203 | 185.2745 | 185.2745 | 0 | 0
2025-06-12 22:00 | 32.4 | 56 | 70 | 26.7869 | 20.2809 | 55.6492 | 132.0902 | 132.0902 | 0 | 0
2025-06-12 23:00 | 31.65 | 58 | 70 | 26.5517 | 20.1821 | 56.2624 | 131.2118 | 131.2118 | 0 | 0
2025-06-13 | 31 | 59.5 | 70 | 26.3463 | 20.0712 | 56.6568 | 129.3547 | 129.3547 | 0 | 0
2025-06-13 01:00 | 30.5 | 62 | 70 | 26.1843 | 20.0892 | 57.6199 | 132.6305 | 132.6305 | 0 | 0
2025-06-13 02:00 | 29.75 | 64 | 70 | 25.9429 | 19.9685 | 58.1571 | 130.8619 | 130.8619 | 0 | 0
2025-06-13 03:00 | 28.7 | 63 | 70 | 25.6051 | 19.5085 | 57.0948 | 115.4056 | 115.4056 | 0 | 0
2025-06-13 04:00 | 28.6 | 57 | 70 | 25.5797 | 19.0261 | 54.2376 | 94.4718 | 94.4718 | 0 | 0
2025-06-13 05:00 | 28.95 | 53 | 70 | 25.7 | 18.841 | 52.4914 | 84.5837 | 84.5837 | 0 | 0
2025-06-13 06:00 | 29.95 | 49 | 100 | 26.0322 | 18.8581 | 50.9231 | 114.7324 | 114.7324 | 0 | 0
2025-06-13 07:00 | 32.85 | 39 | 100 | 26.9746 | 18.9008 | 46.7003 | 97.5262 | 97.5262 | 0 | 0
2025-06-13 08:00 | 36.4 | 28 | 100 | 28.0931 | 18.7839 | 41.2299 | 67.297 | 67.297 | 0 | 0
2025-06-13 09:00 | 39.45 | 20.5 | 100 | 29.0225 | 18.644 | 36.8774 | 40.0846 | 40.0846 | 0 | 0
2025-06-13 10:00 | 41.95 | 16 | 100 | 29.7582 | 18.586 | 33.9383 | 22.0413 | 22.0413 | 0 | 0
2025-06-13 11:00 | 43.85 | 13.5 | 100 | 30.2987 | 18.5989 | 32.1612 | 12.333 | 12.333 | 0 | 0
2025-06-13 12:00 | 44.95 | 12.5 | 100 | 30.6017 | 18.6541 | 31.4238 | 9.8681 | 9.8681 | 0 | 0
2025-06-13 13:00 | 44.85 | 13.5 | 100 | 30.5618 | 18.8018 | 32.2386 | 19.6001 | 19.6001 | 0 | 0
2025-06-13 14:00 | 42.65 | 20.5 | 100 | 29.8989 | 19.4113 | 37.426 | 69.5592 | 69.5592 | 0 | 0
2025-06-13 15:00 | 40.4 | 27.5 | 100 | 29.2291 | 19.8021 | 41.9453 | 107.224 | 107.224 | 0 | 0
2025-06-13 16:00 | 38.95 | 34.5 | 100 | 28.7791 | 20.2587 | 46.2025 | 145.1781 | 145.1781 | 0 | 0
2025-06-13 17:00 | 36.9 | 46 | 100 | 28.1395 | 20.8868 | 52.555 | 198.9493 | 198.9493 | 0 | 0
2025-06-13 18:00 | 34.85 | 57.5 | 100 | 27.5049 | 21.2958 | 58.0733 | 239.4285 | 239.4285 | 0 | 0
2025-06-13 19:00 | 33.3 | 68.5 | 100 | 27.0165 | 21.6768 | 63.0007 | 275.556 | 275.556 | 0 | 0
2025-06-13 20:00 | 32.35 | 76.5 | 100 | 26.7139 | 21.9479 | 66.4159 | 300.5818 | 300.5818 | 0 | 0
2025-06-13 21:00 | 31.8 | 78 | 100 | 26.547 | 21.8403 | 66.6811 | 297.0545 | 297.0545 | 0 | 0
2025-06-13 22:00 | 31.3 | 77 | 70 | 26.3993 | 21.5604 | 65.7221 | 197.0546 | 197.0546 | 0 | 0
2025-06-13 23:00 | 30.65 | 77 | 70 | 26.2011 | 21.2976 | 65.1671 | 187.8807 | 187.8807 | 0 | 0
2025-06-14 | 30.15 | 76 | 70 | 26.0483 | 21.0228 | 64.2704 | 177.4952 | 177.4952 | 0 | 0
2025-06-14 01:00 | 29.55 | 76 | 70 | 25.86 | 20.7833 | 63.8018 | 169.3682 | 169.3682 | 0 | 0
2025-06-14 02:00 | 28.75 | 78 | 70 | 25.6023 | 20.6066 | 64.1343 | 165.2419 | 165.2419 | 0 | 0
2025-06-14 03:00 | 28.1 | 79 | 70 | 25.391 | 20.4156 | 64.1083 | 159.762 | 159.762 | 0 | 0
2025-06-14 04:00 | 28.3 | 74 | 70 | 25.4616 | 20.1484 | 61.9645 | 146.469 | 146.469 | 0 | 0
2025-06-14 05:00 | 28.7 | 68.5 | 70 | 25.5982 | 19.9103 | 59.6722 | 133.5642 | 133.5642 | 0 | 0
2025-06-14 06:00 | 29.5 | 64 | 100 | 25.8628 | 19.8758 | 58.0125 | 182.7774 | 182.7774 | 0 | 0
2025-06-14 07:00 | 32.25 | 53 | 100 | 26.7494 | 19.969 | 53.9788 | 169.5432 | 169.5432 | 0 | 0
2025-06-14 08:00 | 35.8 | 38.5 | 100 | 27.8649 | 19.7512 | 47.4387 | 132.0571 | 132.0571 | 0 | 0
2025-06-14 09:00 | 39 | 26 | 100 | 28.8548 | 19.2375 | 40.5233 | 79.6731 | 79.6731 | 0 | 0
2025-06-14 10:00 | 41.7 | 17 | 100 | 29.6798 | 18.6769 | 34.66 | 29.1959 | 29.1959 | 0 | 0
2025-06-14 11:00 | 43.6 | 12 | 100 | 30.2503 | 18.3023 | 30.9768 | 0 | 0 | 0 | 0
2025-06-14 12:00 | 44.05 | 12 | 100 | 30.3709 | 18.3892 | 30.9895 | 0 | 0 | 0 | 0
2025-06-14 13:00 | 42.2 | 17.5 | 100 | 29.8109 | 18.8605 | 35.0961 | 37.9389 | 37.9389 | 0 | 0
2025-06-14 14:00 | 39.95 | 24.5 | 100 | 29.1312 | 19.2897 | 39.7363 | 77.6773 | 77.6773 | 0 | 0
2025-06-14 15:00 | 38.9 | 27 | 100 | 28.8195 | 19.3315 | 41.1851 | 86.6352 | 86.6352 | 0 | 0
2025-06-14 16:00 | 37.8 | 31 | 100 | 28.4819 | 19.5096 | 43.5003 | 104.6113 | 104.6113 | 0 | 0
2025-06-14 17:00 | 36.35 | 39 | 100 | 28.0217 | 19.9704 | 47.9867 | 143.0499 | 143.0499 | 0 | 0
2025-06-14 18:00 | 34.75 | 48.5 | 100 | 27.5137 | 20.4115 | 52.8467 | 181.895 | 181.895 | 0 | 0
2025-06-14 19:00 | 33.35 | 56.5 | 100 | 27.0712 | 20.6613 | 56.5134 | 207.5291 | 207.5291 | 0 | 0
2025-06-14 20:00 | 32.5 | 59.5 | 100 | 26.8072 | 20.6143 | 57.5881 | 210.1711 | 210.1711 | 0 | 0
2025-06-14 21:00 | 31.9 | 59 | 100 | 26.626 | 20.3542 | 56.9505 | 197.2436 | 197.2436 | 0 | 0
2025-06-14 22:00 | 31.15 | 58.5 | 70 | 26.3952 | 20.0427 | 56.2527 | 127.5157 | 127.5157 | 0 | 0
2025-06-14 23:00 | 30.25 | 59 | 70 | 26.1108 | 19.7605 | 56.0082 | 119.173 | 119.173 | 0 | 0
2025-06-15 | 29.45 | 57.5 | 70 | 25.8566 | 19.3594 | 54.8768 | 105.2104 | 105.2104 | 0 | 0
2025-06-15 01:00 | 28.7 | 56 | 70 | 25.6139 | 18.9838 | 53.8297 | 92.3113 | 92.3113 | 0 | 0
2025-06-15 02:00 | 27.95 | 55.5 | 70 | 25.3658 | 18.6889 | 53.2986 | 83.14 | 83.14 | 0 | 0
2025-06-15 03:00 | 27.5 | 52 | 70 | 25.2179 | 18.2798 | 51.5481 | 67.6439 | 67.6439 | 0 | 0
2025-06-15 04:00 | 28 | 46 | 70 | 25.3921 | 17.9906 | 48.938 | 52.7524 | 52.7524 | 0 | 0
2025-06-15 05:00 | 28.55 | 39.5 | 70 | 25.5841 | 17.65 | 46.0077 | 35.5656 | 35.5656 | 0 | 0
2025-06-15 06:00 | 29.6 | 31.5 | 100 | 25.9457 | 17.2857 | 42.2649 | 21.5981 | 21.5981 | 0 | 0
2025-06-15 07:00 | 32.35 | 24 | 100 | 26.8596 | 17.3089 | 38.5073 | 4.4704 | 4.4704 | 0 | 0
2025-06-15 08:00 | 35.35 | 19 | 100 | 27.8194 | 17.4925 | 35.6855 | 0 | 0 | 0 | 0
2025-06-15 09:00 | 37.85 | 15.5 | 100 | 28.5929 | 17.6224 | 33.4806 | 0 | 0 | 0 | 0
2025-06-15 10:00 | 39.35 | 16 | 100 | 29.0281 | 18.0113 | 33.8231 | 3.0145 | 3.0145 | 0 | 0
2025-06-15 11:00 | 39.9 | 20 | 100 | 29.1537 | 18.6762 | 36.6212 | 40.304 | 40.304 | 0 | 0
2025-06-15 12:00 | 40 | 23 | 100 | 29.1573 | 19.1004 | 38.7224 | 66.044 | 66.044 | 0 | 0
2025-06-15 13:00 | 39.7 | 25 | 100 | 29.0579 | 19.2853 | 40.0428 | 79.4157 | 79.4157 | 0 | 0
2025-06-15 14:00 | 39.4 | 26.5 | 100 | 28.9629 | 19.3977 | 40.9984 | 88.3539 | 88.3539 | 0 | 0
2025-06-15 15:00 | 38.85 | 28.5 | 100 | 28.7947 | 19.4979 | 42.1988 | 98.0613 | 98.0613 | 0 | 0
2025-06-15 16:00 | 37.55 | 33 | 100 | 28.3984 | 19.6647 | 44.7257 | 116.5689 | 116.5689 | 0 | 0
2025-06-15 17:00 | 36.05 | 40 | 100 | 27.93 | 19.9789 | 48.49 | 146.004 | 146.004 | 0 | 0
2025-06-15 18:00 | 34.55 | 49 | 100 | 27.4529 | 20.389 | 53.0485 | 182.1743 | 182.1743 | 0 | 0
2025-06-15 19:00 | 33.25 | 56 | 100 | 27.0429 | 20.5791 | 56.2052 | 203.2418 | 203.2418 | 0 | 0
2025-06-15 20:00 | 32.45 | 59.5 | 100 | 26.7918 | 20.5939 | 57.5872 | 209.6497 | 209.6497 | 0 | 0
2025-06-15 21:00 | 31.75 | 60.5 | 100 | 26.576 | 20.4221 | 57.6657 | 203.1634 | 203.1634 | 0 | 0
2025-06-15 22:00 | 30.9 | 66 | 70 | 26.301 | 20.5502 | 59.9114 | 152.1664 | 152.1664 | 0 | 0
2025-06-15 23:00 | 30.1 | 72.5 | 70 | 26.0388 | 20.741 | 62.5582 | 164.9344 | 164.9344 | 0 | 0
2025-06-16 | 29.25 | 73 | 70 | 25.7691 | 20.4462 | 62.1866 | 155.5877 | 155.5877 | 0 | 0
2025-06-16 01:00 | 28.4 | 73 | 70 | 25.4951 | 20.1157 | 61.6085 | 144.7878 | 144.7878 | 0 | 0
2025-06-16 02:00 | 27.8 | 73 | 70 | 25.2988 | 19.8838 | 61.2217 | 137.3261 | 137.3261 | 0 | 0
2025-06-16 03:00 | 27.6 | 69 | 70 | 25.2364 | 19.5296 | 59.2984 | 122.4068 | 122.4068 | 0 | 0
2025-06-16 04:00 | 27.8 | 60.5 | 70 | 25.3108 | 18.9993 | 55.5506 | 97.8293 | 97.8293 | 0 | 0
2025-06-16 05:00 | 27.95 | 54.5 | 70 | 25.3668 | 18.6124 | 52.8625 | 80.0794 | 80.0794 | 0 | 0
2025-06-16 06:00 | 28.95 | 49.5 | 100 | 25.7046 | 18.5648 | 50.8672 | 104.2883 | 104.2883 | 0 | 0
2025-06-16 07:00 | 31.4 | 41.5 | 100 | 26.5124 | 18.6779 | 47.6498 | 94.3859 | 94.3859 | 0 | 0
2025-06-16 08:00 | 34.3 | 34 | 100 | 27.4371 | 18.8328 | 44.353 | 84.7614 | 84.7614 | 0 | 0
2025-06-16 09:00 | 37.1 | 28 | 100 | 28.2985 | 18.9628 | 41.4217 | 75.1302 | 75.1302 | 0 | 0
2025-06-16 10:00 | 39.65 | 23.5 | 100 | 29.0559 | 19.0757 | 39.0066 | 66.8063 | 66.8063 | 0 | 0
2025-06-16 11:00 | 41.7 | 22 | 100 | 29.6304 | 19.3863 | 38.3738 | 74.3277 | 74.3277 | 0 | 0
2025-06-16 12:00 | 43.1 | 24 | 100 | 29.9762 | 20.0296 | 40.245 | 107.1359 | 107.1359 | 0 | 0
2025-06-16 13:00 | 43.45 | 27 | 100 | 30.0289 | 20.5585 | 42.6839 | 139.2477 | 139.2477 | 0 | 0
2025-06-16 14:00 | 43.3 | 26.5 | 100 | 29.9972 | 20.4443 | 42.2443 | 132.826 | 132.826 | 0 | 0
2025-06-16 15:00 | 42.7 | 28 | 100 | 29.8278 | 20.4929 | 43.1624 | 139.3697 | 139.3697 | 0 | 0
2025-06-16 16:00 | 40.7 | 31.5 | 100 | 29.2737 | 20.3941 | 44.9171 | 144.5822 | 144.5822 | 0 | 0
2025-06-16 17:00 | 38.5 | 35 | 100 | 28.6516 | 20.1743 | 46.3916 | 143.5932 | 143.5932 | 0 | 0
2025-06-16 18:00 | 36.9 | 41.5 | 100 | 28.1645 | 20.4056 | 49.813 | 168.3944 | 168.3944 | 0 | 0
2025-06-16 19:00 | 35.35 | 49.5 | 100 | 27.6829 | 20.7091 | 53.8019 | 198.0706 | 198.0706 | 0 | 0
2025-06-16 20:00 | 33.85 | 58.5 | 100 | 27.2114 | 21.0175 | 57.9816 | 228.2759 | 228.2759 | 0 | 0
2025-06-16 21:00 | 32.5 | 69 | 100 | 26.7793 | 21.404 | 62.6534 | 263.2242 | 263.2242 | 0 | 0
2025-06-16 22:00 | 31.6 | 76.5 | 70 | 26.4904 | 21.642 | 65.7799 | 199.8647 | 199.8647 | 0 | 0
2025-06-16 23:00 | 30.95 | 80.5 | 70 | 26.2849 | 21.6796 | 67.2124 | 204.8762 | 204.8762 | 0 | 0
2025-06-17 | 30.15 | 87 | 70 | 26.0277 | 21.8184 | 69.648 | 215.4917 | 215.4917 | 0 | 0
2025-06-17 01:00 | 29.55 | 91.5 | 70 | 25.8349 | 21.8755 | 71.2041 | 221.2892 | 221.2892 | 0 | 0
2025-06-17 02:00 | 29.2 | 92 | 70 | 25.7253 | 21.7588 | 71.0885 | 217.4751 | 217.4751 | 0 | 0
2025-06-17 03:00 | 28.6 | 92 | 70 | 25.5364 | 21.5006 | 70.5029 | 208.2413 | 208.2413 | 0 | 0
2025-06-17 04:00 | 28.2 | 90.5 | 70 | 25.4106 | 21.2297 | 69.4471 | 197.5101 | 197.5101 | 0 | 0
2025-06-17 05:00 | 28.4 | 83 | 70 | 25.4834 | 20.8097 | 66.2063 | 176.798 | 176.798 | 0 | 0
2025-06-17 06:00 | 29.85 | 61.5 | 100 | 25.9788 | 19.8094 | 57.0472 | 176.6975 | 176.6975 | 0 | 0
2025-06-17 07:00 | 32.25 | 44.5 | 100 | 26.7724 | 19.2129 | 49.5085 | 122.1064 | 122.1064 | 0 | 0
2025-06-17 08:00 | 35.3 | 35.5 | 100 | 27.7315 | 19.2801 | 45.5134 | 106.2675 | 106.2675 | 0 | 0
2025-06-17 09:00 | 39.1 | 22.5 | 100 | 28.9087 | 18.8083 | 38.2264 | 53.489 | 53.489 | 0 | 0
2025-06-17 10:00 | 42.1 | 16 | 100 | 29.7996 | 18.6056 | 33.9917 | 23.7292 | 23.7292 | 0 | 0
2025-06-17 11:00 | 42.4 | 22.5 | 100 | 29.8112 | 19.6333 | 38.9067 | 85.8248 | 85.8248 | 0 | 0
2025-06-17 12:00 | 41.4 | 29 | 100 | 29.4816 | 20.2694 | 43.3878 | 132.0649 | 132.0649 | 0 | 0
2025-06-17 13:00 | 41.05 | 30 | 100 | 29.38 | 20.3026 | 43.9769 | 136.2953 | 136.2953 | 0 | 0
2025-06-17 14:00 | 40.7 | 31 | 100 | 29.2783 | 20.3322 | 44.5536 | 140.3117 | 140.3117 | 0 | 0
2025-06-17 15:00 | 39.9 | 33.5 | 100 | 29.0437 | 20.413 | 45.9662 | 150.3335 | 150.3335 | 0 | 0
2025-06-17 16:00 | 38.75 | 38 | 100 | 28.6989 | 20.6013 | 48.4716 | 169.5066 | 169.5066 | 0 | 0
2025-06-17 17:00 | 37.45 | 43.5 | 100 | 28.3063 | 20.7998 | 51.3444 | 190.4977 | 190.4977 | 0 | 0
2025-06-17 18:00 | 36.1 | 51 | 100 | 27.8886 | 21.1171 | 55.1473 | 219.999 | 219.999 | 0 | 0
2025-06-17 19:00 | 35.05 | 55 | 100 | 27.5724 | 21.1322 | 56.8061 | 227.7721 | 227.7721 | 0 | 0
2025-06-17 20:00 | 34.1 | 56.5 | 100 | 27.292 | 20.9294 | 57.0194 | 220.5367 | 220.5367 | 0 | 0
2025-06-17 21:00 | 33 | 59 | 100 | 26.9586 | 20.7525 | 57.666 | 216.1771 | 216.1771 | 0 | 0
2025-06-17 22:00 | 31.75 | 63.5 | 70 | 26.5685 | 20.6691 | 59.2097 | 153.4796 | 153.4796 | 0 | 0
2025-06-17 23:00 | 30.65 | 68.5 | 70 | 26.2181 | 20.6502 | 60.9864 | 157.9869 | 157.9869 | 0 | 0
2025-06-18 | 29.8 | 72 | 70 | 25.9453 | 20.5868 | 62.0993 | 159.3122 | 159.3122 | 0 | 0
2025-06-18 01:00 | 29.1 | 72 | 70 | 25.7225 | 20.3151 | 61.6117 | 150.3508 | 150.3508 | 0 | 0
2025-06-18 02:00 | 28.6 | 70 | 70 | 25.5638 | 19.9786 | 60.3469 | 137.5318 | 137.5318 | 0 | 0
2025-06-18 03:00 | 28.35 | 70 | 70 | 25.4823 | 19.8837 | 60.1888 | 134.4685 | 134.4685 | 0 | 0
2025-06-18 04:00 | 28.45 | 65.5 | 70 | 25.5203 | 19.5972 | 58.1644 | 121.0499 | 121.0499 | 0 | 0
2025-06-18 05:00 | 28.6 | 61.5 | 70 | 25.5742 | 19.3591 | 56.3761 | 109.5916 | 109.5916 | 0 | 0
2025-06-18 06:00 | 29.35 | 61.5 | 100 | 25.8183 | 19.6298 | 56.7571 | 168.4119 | 168.4119 | 0 | 0
2025-06-18 07:00 | 31.4 | 56 | 100 | 26.4788 | 19.9245 | 55.1213 | 172.9553 | 172.9553 | 0 | 0
2025-06-18 08:00 | 34 | 48 | 100 | 27.2944 | 20.1109 | 52.1723 | 167.3898 | 167.3898 | 0 | 0
2025-06-18 09:00 | 36.55 | 38.5 | 100 | 28.0817 | 19.9783 | 47.7679 | 142.3684 | 142.3684 | 0 | 0
2025-06-18 10:00 | 38.95 | 29.5 | 100 | 28.8154 | 19.652 | 42.8795 | 106.7603 | 106.7603 | 0 | 0
2025-06-18 11:00 | 41.1 | 23.5 | 100 | 29.4543 | 19.4475 | 39.3138 | 81.242 | 81.242 | 0 | 0
2025-06-18 12:00 | 42.7 | 19.5 | 100 | 29.9233 | 19.268 | 36.7007 | 61.0529 | 61.0529 | 0 | 0
2025-06-18 13:00 | 43.05 | 21 | 100 | 29.9983 | 19.5753 | 37.9217 | 78.449 | 78.449 | 0 | 0
2025-06-18 14:00 | 41.55 | 33 | 100 | 29.481 | 20.8411 | 46.3496 | 168.2131 | 168.2131 | 0 | 0
2025-06-18 15:00 | 39.65 | 40.5 | 100 | 28.9204 | 21.1794 | 50.6174 | 201.8009 | 201.8009 | 0 | 0
2025-06-18 16:00 | 38.2 | 41 | 100 | 28.5284 | 20.7701 | 50.1471 | 183.7406 | 183.7406 | 0 | 0
2025-06-18 17:00 | 36.7 | 46 | 100 | 28.0833 | 20.8159 | 52.4721 | 196.182 | 196.182 | 0 | 0
2025-06-18 18:00 | 35.05 | 55 | 100 | 27.5724 | 21.1327 | 56.8054 | 227.7634 | 227.7634 | 0 | 0
2025-06-18 19:00 | 33.4 | 66 | 100 | 27.0537 | 21.5026 | 61.7574 | 263.5652 | 263.5652 | 0 | 0
2025-06-18 20:00 | 32.65 | 70.5 | 100 | 26.8194 | 21.5866 | 63.5548 | 274.2569 | 274.2569 | 0 | 0
2025-06-18 21:00 | 32.2 | 72.5 | 100 | 26.6804 | 21.5702 | 64.2223 | 276.2125 | 276.2125 | 0 | 0
2025-06-18 22:00 | 31.35 | 79 | 70 | 26.4094 | 21.7316 | 66.8088 | 205.2371 | 205.2371 | 0 | 0
2025-06-18 23:00 | 30.6 | 84.5 | 70 | 26.1703 | 21.8289 | 68.8487 | 213.6118 | 213.6118 | 0 | 0
2025-06-19 | 29.9 | 88.5 | 70 | 25.9483 | 21.8177 | 70.1123 | 216.6427 | 216.6427 | 0 | 0
2025-06-19 01:00 | 29.15 | 94 | 70 | 25.7068 | 21.8723 | 71.9603 | 223.0917 | 223.0917 | 0 | 0
2025-06-19 02:00 | 28.7 | 98 | 70 | 25.5604 | 21.94 | 73.3402 | 228.6825 | 228.6825 | 0 | 0
2025-06-19 03:00 | 28.6 | 98 | 70 | 25.5289 | 21.8961 | 73.2347 | 227.0726 | 227.0726 | 0 | 0
2025-06-19 04:00 | 28.55 | 97 | 70 | 25.5144 | 21.8089 | 72.7275 | 223.1419 | 223.1419 | 0 | 0
2025-06-19 05:00 | 28.3 | 97.5 | 70 | 25.4346 | 21.7312 | 72.6976 | 220.7308 | 220.7308 | 0 | 0
2025-06-19 06:00 | 28.65 | 94.5 | 100 | 25.5492 | 21.6883 | 71.6811 | 309.7267 | 309.7267 | 0 | 0
2025-06-19 07:00 | 30.2 | 85 | 100 | 26.047 | 21.6965 | 68.7052 | 298.9617 | 298.9617 | 0 | 0
2025-06-19 08:00 | 33.1 | 67 | 100 | 26.9628 | 21.473 | 62.0445 | 263.3626 | 263.3626 | 0 | 0
2025-06-19 09:00 | 36.7 | 46.5 | 100 | 28.0807 | 20.8698 | 52.7616 | 199.3876 | 199.3876 | 0 | 0
2025-06-19 10:00 | 39.6 | 34 | 100 | 28.9593 | 20.3894 | 46.1574 | 150.0677 | 150.0677 | 0 | 0
2025-06-19 11:00 | 41.6 | 28 | 100 | 29.544 | 20.1934 | 42.7231 | 125.7106 | 125.7106 | 0 | 0
2025-06-19 12:00 | 43 | 24 | 100 | 29.9505 | 20.0067 | 40.2026 | 105.8864 | 105.8864 | 0 | 0
2025-06-19 13:00 | 43.7 | 22 | 100 | 30.1541 | 19.8873 | 38.8592 | 94.5139 | 94.5139 | 0 | 0
2025-06-19 14:00 | 42.65 | 29 | 100 | 29.8039 | 20.6215 | 43.8809 | 147.5808 | 147.5808 | 0 | 0
2025-06-19 15:00 | 40.35 | 37 | 100 | 29.133 | 20.9814 | 48.5975 | 184.5623 | 184.5623 | 0 | 0
2025-06-19 16:00 | 38 | 43 | 100 | 28.4605 | 20.9264 | 51.3301 | 195.302 | 195.302 | 0 | 0
2025-06-19 17:00 | 35.8 | 53 | 100 | 27.7943 | 21.2084 | 56.1418 | 227.9575 | 227.9575 | 0 | 0
2025-06-19 18:00 | 34.1 | 62 | 100 | 27.2711 | 21.4219 | 60.1006 | 253.4212 | 253.4212 | 0 | 0
2025-06-19 19:00 | 33 | 68 | 100 | 26.9301 | 21.5173 | 62.5139 | 267.2046 | 267.2046 | 0 | 0
2025-06-19 20:00 | 32.25 | 72 | 100 | 26.6966 | 21.5496 | 64.0053 | 274.5202 | 274.5202 | 0 | 0
2025-06-19 21:00 | 31.55 | 77.5 | 100 | 26.4732 | 21.6999 | 66.2255 | 289.5207 | 289.5207 | 0 | 0
2025-06-19 22:00 | 30.8 | 85 | 70 | 26.23 | 21.9496 | 69.28 | 218.325 | 218.325 | 0 | 0
2025-06-19 23:00 | 30 | 91.5 | 70 | 25.9738 | 22.0699 | 71.6405 | 228.1953 | 228.1953 | 0 | 0
2025-06-20 | 29.25 | 95.5 | 70 | 25.7358 | 22.0164 | 72.7558 | 229.4771 | 229.4771 | 0 | 0
2025-06-20 01:00 | 28.65 | 97.5 | 70 | 25.5453 | 21.8854 | 73.0564 | 226.2873 | 226.2873 | 0 | 0
2025-06-20 02:00 | 28.25 | 98 | 70 | 25.4182 | 21.7418 | 72.8719 | 221.4842 | 221.4842 | 0 | 0
2025-06-20 03:00 | 27.9 | 98 | 70 | 25.3065 | 21.5882 | 72.5183 | 215.9618 | 215.9618 | 0 | 0
2025-06-20 04:00 | 28.35 | 95.5 | 70 | 25.4528 | 21.623 | 71.8427 | 215.2987 | 215.2987 | 0 | 0
2025-06-20 05:00 | 28.65 | 94 | 70 | 25.5498 | 21.6548 | 71.4533 | 215.237 | 215.237 | 0 | 0
2025-06-20 06:00 | 28.8 | 90.5 | 100 | 25.6018 | 21.4856 | 69.9845 | 294.8224 | 294.8224 | 0 | 0
2025-06-20 07:00 | 30.15 | 80.5 | 100 | 26.0399 | 21.3516 | 66.4758 | 275.8894 | 275.8894 | 0 | 0
2025-06-20 08:00 | 32.05 | 69 | 100 | 26.6452 | 21.2304 | 62.2688 | 254.2994 | 254.2994 | 0 | 0
2025-06-20 09:00 | 34.45 | 56 | 100 | 27.3959 | 21.0114 | 56.9546 | 223.3672 | 223.3672 | 0 | 0
2025-06-20 10:00 | 37.45 | 40 | 100 | 28.3278 | 20.4224 | 49.1103 | 165.3973 | 165.3973 | 0 | 0
2025-06-20 11:00 | 40.35 | 26 | 100 | 29.2284 | 19.5875 | 40.8974 | 94.4637 | 94.4637 | 0 | 0
2025-06-20 12:00 | 42.5 | 18.5 | 100 | 29.8811 | 19.072 | 35.9097 | 49.9784 | 49.9784 | 0 | 0
2025-06-20 13:00 | 42.8 | 20 | 100 | 29.9442 | 19.3654 | 37.1037 | 66.6861 | 66.6861 | 0 | 0
2025-06-20 14:00 | 40.7 | 32.5 | 100 | 29.2648 | 20.5258 | 45.6057 | 152.6414 | 152.6414 | 0 | 0
2025-06-20 15:00 | 38.85 | 40 | 100 | 28.7115 | 20.8649 | 49.8373 | 185.9381 | 185.9381 | 0 | 0
2025-06-20 16:00 | 37.95 | 41 | 100 | 28.4599 | 20.6896 | 50.0145 | 180.0279 | 180.0279 | 0 | 0
2025-06-20 17:00 | 36.35 | 47.5 | 100 | 27.977 | 20.8525 | 53.1824 | 200.7694 | 200.7694 | 0 | 0
2025-06-20 18:00 | 34.25 | 60 | 100 | 27.3221 | 21.3003 | 59.0878 | 244.1827 | 244.1827 | 0 | 0
2025-06-20 19:00 | 32.75 | 70.5 | 100 | 26.8489 | 21.6259 | 63.6378 | 276.2195 | 276.2195 | 0 | 0
2025-06-20 20:00 | 31.95 | 75.5 | 100 | 26.5978 | 21.707 | 65.5605 | 287.2327 | 287.2327 | 0 | 0
2025-06-20 21:00 | 31.3 | 78 | 100 | 26.3967 | 21.6359 | 66.2534 | 286.9426 | 286.9426 | 0 | 0
2025-06-20 22:00 | 30.7 | 78.5 | 70 | 26.2132 | 21.4295 | 65.9722 | 194.0187 | 194.0187 | 0 | 0
2025-06-20 23:00 | 30.05 | 80.5 | 70 | 26.0089 | 21.311 | 66.3879 | 191.6833 | 191.6833 | 0 | 0
2025-06-21 | 29.35 | 84 | 70 | 25.7844 | 21.2711 | 67.4516 | 193.3859 | 193.3859 | 0 | 0
2025-06-21 01:00 | 28.7 | 87 | 70 | 25.5746 | 21.2068 | 68.2784 | 193.6922 | 193.6922 | 0 | 0
2025-06-21 02:00 | 28.15 | 88 | 70 | 25.3974 | 21.0433 | 68.2522 | 188.8438 | 188.8438 | 0 | 0
2025-06-21 03:00 | 27.7 | 88 | 70 | 25.2517 | 20.8547 | 67.8647 | 182.3452 | 182.3452 | 0 | 0
2025-06-21 04:00 | 27.7 | 87.5 | 70 | 25.2522 | 20.8219 | 67.6425 | 180.8191 | 180.8191 | 0 | 0
2025-06-21 05:00 | 27.95 | 87.5 | 70 | 25.3333 | 20.9263 | 67.8532 | 184.3931 | 184.3931 | 0 | 0
2025-06-21 06:00 | 28.5 | 84.5 | 100 | 25.5139 | 20.9536 | 66.9493 | 261.1206 | 261.1206 | 0 | 0
2025-06-21 07:00 | 29.9 | 77 | 100 | 25.9684 | 20.9955 | 64.5645 | 253.6757 | 253.6757 | 0 | 0
2025-06-21 08:00 | 31.7 | 69.5 | 100 | 26.5384 | 21.1352 | 62.2454 | 250.2147 | 250.2147 | 0 | 0
2025-06-21 09:00 | 33.5 | 62.5 | 100 | 27.0952 | 21.2421 | 59.8962 | 244.9757 | 244.9757 | 0 | 0
2025-06-21 10:00 | 35.5 | 53.5 | 100 | 27.7076 | 21.1533 | 56.2047 | 225.6966 | 225.6966 | 0 | 0
2025-06-21 11:00 | 37.75 | 42.5 | 100 | 28.3956 | 20.7938 | 50.8426 | 187.5653 | 187.5653 | 0 | 0
2025-06-21 12:00 | 39.65 | 33 | 100 | 28.9807 | 20.2829 | 45.4907 | 142.7487 | 142.7487 | 0 | 0
2025-06-21 13:00 | 40.4 | 29 | 100 | 29.2161 | 19.9933 | 43.0117 | 119.8016 | 119.8016 | 0 | 0
2025-06-21 14:00 | 40.1 | 29 | 100 | 29.1351 | 19.9092 | 42.9131 | 116.2843 | 116.2843 | 0 | 0
2025-06-21 15:00 | 39.6 | 29.5 | 100 | 28.9948 | 19.8326 | 43.0933 | 114.4383 | 114.4383 | 0 | 0
2025-06-21 16:00 | 39.05 | 32.5 | 100 | 28.8211 | 20.0443 | 44.9271 | 131.3031 | 131.3031 | 0 | 0
2025-06-21 17:00 | 37.6 | 40 | 100 | 28.3696 | 20.4689 | 49.1894 | 167.617 | 167.617 | 0 | 0
2025-06-21 18:00 | 35.3 | 52 | 100 | 27.6574 | 20.9366 | 55.2118 | 212.9441 | 212.9441 | 0 | 0
2025-06-21 19:00 | 33.2 | 66 | 100 | 26.9954 | 21.4264 | 61.5862 | 259.6226 | 259.6226 | 0 | 0
2025-06-21 20:00 | 31.9 | 77.5 | 100 | 26.5778 | 21.8424 | 66.5377 | 296.7228 | 296.7228 | 0 | 0
2025-06-21 21:00 | 31.3 | 82 | 100 | 26.3875 | 21.9375 | 68.26 | 307.4227 | 307.4227 | 0 | 0
2025-06-21 22:00 | 30.8 | 82.5 | 70 | 26.2354 | 21.7668 | 68.0339 | 209.4894 | 209.4894 | 0 | 0
2025-06-21 23:00 | 30.1 | 85.5 | 70 | 26.0154 | 21.6907 | 68.8415 | 209.3987 | 209.3987 | 0 | 0
2025-06-22 | 29.3 | 89 | 70 | 25.7612 | 21.5968 | 69.7517 | 209.0291 | 209.0291 | 0 | 0
2025-06-22 01:00 | 28.5 | 91 | 70 | 25.506 | 21.3913 | 69.926 | 203.3926 | 203.3926 | 0 | 0
2025-06-22 02:00 | 27.75 | 93 | 70 | 25.2632 | 21.2014 | 70.1336 | 198.3308 | 198.3308 | 0 | 0
2025-06-22 03:00 | 27.1 | 95.5 | 70 | 25.0495 | 21.0814 | 70.6385 | 196.0862 | 196.0862 | 0 | 0
2025-06-22 04:00 | 27.4 | 95 | 70 | 25.1478 | 21.1792 | 70.6977 | 199.1253 | 199.1253 | 0 | 0
2025-06-22 05:00 | 27.85 | 93 | 70 | 25.2955 | 21.244 | 70.2269 | 199.8394 | 199.8394 | 0 | 0
2025-06-22 06:00 | 28.35 | 88 | 100 | 25.4617 | 21.1275 | 68.42 | 273.862 | 273.862 | 0 | 0
2025-06-22 07:00 | 30.25 | 74 | 100 | 26.083 | 20.9129 | 63.3839 | 245.7043 | 245.7043 | 0 | 0
2025-06-22 08:00 | 32.7 | 59.5 | 100 | 26.8674 | 20.6872 | 57.7173 | 213.6083 | 213.6083 | 0 | 0
2025-06-22 09:00 | 35 | 49.5 | 100 | 27.5823 | 20.5935 | 53.5584 | 192.039 | 192.039 | 0 | 0
2025-06-22 10:00 | 37.2 | 40 | 100 | 28.2579 | 20.3446 | 48.9822 | 161.74 | 161.74 | 0 | 0
2025-06-22 11:00 | 39.05 | 30.5 | 100 | 28.8359 | 19.8034 | 43.5761 | 115.6489 | 115.6489 | 0 | 0
2025-06-22 12:00 | 39.75 | 26 | 100 | 29.0638 | 19.4299 | 40.7323 | 87.917 | 87.917 | 0 | 0
2025-06-22 13:00 | 39.6 | 27 | 100 | 29.0145 | 19.5173 | 41.3819 | 94.398 | 94.398 | 0 | 0
2025-06-22 14:00 | 39.1 | 30 | 100 | 28.8533 | 19.7543 | 43.2689 | 112.4902 | 112.4902 | 0 | 0
2025-06-22 15:00 | 38.2 | 34 | 100 | 28.5752 | 19.9724 | 45.5972 | 131.9641 | 131.9641 | 0 | 0
2025-06-22 16:00 | 37.1 | 38.5 | 100 | 28.2382 | 20.1471 | 48.0173 | 150.0104 | 150.0104 | 0 | 0
2025-06-22 17:00 | 35.65 | 45.5 | 100 | 27.7879 | 20.4161 | 51.5882 | 176.6397 | 176.6397 | 0 | 0
2025-06-22 18:00 | 34.1 | 52 | 100 | 27.309 | 20.5172 | 54.4896 | 193.3694 | 193.3694 | 0 | 0
2025-06-22 19:00 | 32.8 | 58.5 | 100 | 26.9003 | 20.6366 | 57.2655 | 209.8781 | 209.8781 | 0 | 0
2025-06-22 20:00 | 31.85 | 66 | 100 | 26.5926 | 20.9106 | 60.5693 | 234.4716 | 234.4716 | 0 | 0
2025-06-22 21:00 | 31.2 | 71 | 100 | 26.3825 | 21.057 | 62.6383 | 248.7411 | 248.7411 | 0 | 0
2025-06-22 22:00 | 30.5 | 74.5 | 70 | 26.1597 | 21.0497 | 63.8364 | 177.2015 | 177.2015 | 0 | 0
2025-06-22 23:00 | 29.75 | 77.5 | 70 | 25.9204 | 20.9708 | 64.7003 | 177.3253 | 177.3253 | 0 | 0
2025-06-23 | 29.1 | 79.5 | 70 | 25.7119 | 20.8522 | 65.133 | 175.0872 | 175.0872 | 0 | 0
2025-06-23 01:00 | 28.55 | 81 | 70 | 25.5341 | 20.7339 | 65.3968 | 172.4145 | 172.4145 | 0 | 0
2025-06-23 02:00 | 28 | 83.5 | 70 | 25.3536 | 20.6797 | 66.1028 | 172.7456 | 172.7456 | 0 | 0
2025-06-23 03:00 | 27.45 | 85.5 | 70 | 25.1723 | 20.5868 | 66.5591 | 171.2691 | 171.2691 | 0 | 0
2025-06-23 04:00 | 28.05 | 85 | 70 | 25.3683 | 20.8014 | 66.8205 | 178.1198 | 178.1198 | 0 | 0
2025-06-23 05:00 | 28.65 | 85 | 70 | 25.5612 | 21.0497 | 67.3217 | 186.6289 | 186.6289 | 0 | 0
2025-06-23 06:00 | 29.15 | 81.5 | 100 | 25.725 | 21.0136 | 66.111 | 260.4944 | 260.4944 | 0 | 0
2025-06-23 07:00 | 31.1 | 71 | 100 | 26.3519 | 21.0188 | 62.5616 | 246.8415 | 246.8415 | 0 | 0
2025-06-23 08:00 | 33.55 | 59 | 100 | 27.1218 | 20.9539 | 58.0248 | 225.6511 | 225.6511 | 0 | 0
2025-06-23 09:00 | 36 | 45.5 | 100 | 27.8883 | 20.5333 | 51.7631 | 181.8246 | 181.8246 | 0 | 0
2025-06-23 10:00 | 37.9 | 33.5 | 100 | 28.4944 | 19.8275 | 45.1537 | 124.3746 | 124.3746 | 0 | 0
2025-06-23 11:00 | 38.8 | 28.5 | 100 | 28.7807 | 19.487 | 42.1717 | 97.343 | 97.343 | 0 | 0
2025-06-23 12:00 | 39.3 | 26 | 100 | 28.9388 | 19.3084 | 40.6278 | 83.2308 | 83.2308 | 0 | 0
2025-06-23 13:00 | 39.8 | 22.5 | 100 | 29.1057 | 18.9826 | 38.3454 | 60.093 | 60.093 | 0 | 0
2025-06-23 14:00 | 39.8 | 21 | 100 | 29.1177 | 18.7819 | 37.3147 | 47.8517 | 47.8517 | 0 | 0
2025-06-23 15:00 | 39.05 | 24.5 | 100 | 28.8799 | 19.0497 | 39.5716 | 68.9326 | 68.9326 | 0 | 0
2025-06-23 16:00 | 37.65 | 31.5 | 100 | 28.4361 | 19.5197 | 43.8032 | 106.863 | 106.863 | 0 | 0
2025-06-23 17:00 | 36.1 | 37.5 | 100 | 27.9569 | 19.7294 | 47.0006 | 129.8353 | 129.8353 | 0 | 0
2025-06-23 18:00 | 34.45 | 46.5 | 100 | 27.4335 | 20.1154 | 51.5697 | 165.1541 | 165.1541 | 0 | 0
2025-06-23 19:00 | 33 | 56 | 100 | 26.968 | 20.4898 | 56.0514 | 199.0717 | 199.0717 | 0 | 0
2025-06-23 20:00 | 32.15 | 60 | 100 | 26.6995 | 20.5268 | 57.6543 | 207.2291 | 207.2291 | 0 | 0
2025-06-23 21:00 | 31.45 | 62.5 | 100 | 26.4789 | 20.4759 | 58.5 | 208.6833 | 208.6833 | 0 | 0
2025-06-23 22:00 | 30.85 | 66 | 70 | 26.2855 | 20.5315 | 59.876 | 151.5308 | 151.5308 | 0 | 0
2025-06-23 23:00 | 30.3 | 70 | 70 | 26.106 | 20.6308 | 61.4805 | 158.8171 | 158.8171 | 0 | 0
2025-06-24 | 29.8 | 72 | 70 | 25.9453 | 20.5869 | 62.1001 | 159.3183 | 159.3183 | 0 | 0
2025-06-24 01:00 | 29.3 | 71 | 70 | 25.788 | 20.3188 | 61.2764 | 149.5589 | 149.5589 | 0 | 0
2025-06-24 02:00 | 28.65 | 70.5 | 70 | 25.5794 | 20.0327 | 60.6171 | 139.8201 | 139.8201 | 0 | 0
2025-06-24 03:00 | 28 | 71 | 70 | 25.3666 | 19.8208 | 60.4406 | 133.4801 | 133.4801 | 0 | 0
2025-06-24 04:00 | 28.1 | 66.5 | 70 | 25.4042 | 19.5396 | 58.4418 | 120.3126 | 120.3126 | 0 | 0
2025-06-24 05:00 | 28.35 | 62.5 | 70 | 25.4909 | 19.3414 | 56.7286 | 110.2032 | 110.2032 | 0 | 0
2025-06-24 06:00 | 28.9 | 60 | 100 | 25.6742 | 19.3535 | 55.8285 | 154.2163 | 154.2163 | 0 | 0
2025-06-24 07:00 | 30.95 | 52.5 | 100 | 26.3454 | 19.4758 | 53.1257 | 147.5666 | 147.5666 | 0 | 0
2025-06-24 08:00 | 33.6 | 44.5 | 100 | 27.1867 | 19.6477 | 50.0447 | 140.593 | 140.593 | 0 | 0
2025-06-24 09:00 | 36.15 | 36.5 | 100 | 27.9765 | 19.6395 | 46.4035 | 123.5887 | 123.5887 | 0 | 0
2025-06-24 10:00 | 38.45 | 26 | 100 | 28.6994 | 19.0824 | 40.4372 | 74.428 | 74.428 | 0 | 0
2025-06-24 11:00 | 39.8 | 19.5 | 100 | 29.1297 | 18.5807 | 36.278 | 35.5016 | 35.5016 | 0 | 0
2025-06-24 12:00 | 40.15 | 20 | 100 | 29.224 | 18.73 | 36.6724 | 42.7228 | 42.7228 | 0 | 0
2025-06-24 13:00 | 39.85 | 24.5 | 100 | 29.1036 | 19.2552 | 39.7488 | 77.0908 | 77.0908 | 0 | 0
2025-06-24 14:00 | 39.1 | 30 | 100 | 28.8533 | 19.7492 | 43.2901 | 112.7476 | 112.7476 | 0 | 0
2025-06-24 15:00 | 38.1 | 34.5 | 100 | 28.5439 | 19.9967 | 45.9044 | 134.6483 | 134.6483 | 0 | 0
2025-06-24 16:00 | 37.1 | 37.5 | 100 | 28.2439 | 20.0332 | 47.4125 | 143.2036 | 143.2036 | 0 | 0
2025-06-24 17:00 | 35.95 | 41 | 100 | 27.896 | 20.0502 | 49.0623 | 151.4743 | 151.4743 | 0 | 0
2025-06-24 18:00 | 34.45 | 48.5 | 100 | 27.4255 | 20.306 | 52.7194 | 177.6454 | 177.6454 | 0 | 0
2025-06-24 19:00 | 33.25 | 56.5 | 100 | 27.0412 | 20.6229 | 56.4836 | 206.204 | 206.204 | 0 | 0
2025-06-24 20:00 | 32.45 | 61 | 100 | 26.7875 | 20.7206 | 58.3837 | 218.022 | 218.022 | 0 | 0
2025-06-24 21:00 | 31.65 | 62.5 | 100 | 26.5403 | 20.5494 | 58.6377 | 212.2416 | 212.2416 | 0 | 0
2025-06-24 22:00 | 30.85 | 62 | 70 | 26.2939 | 20.2137 | 57.8781 | 137.1078 | 137.1078 | 0 | 0
2025-06-24 23:00 | 30.15 | 61.5 | 70 | 26.0743 | 19.9184 | 57.2209 | 127.1666 | 127.1666 | 0 | 0
2025-06-25 | 29.35 | 63.5 | 70 | 25.8152 | 19.7795 | 57.7418 | 124.8987 | 124.8987 | 0 | 0
2025-06-25 01:00 | 28.4 | 64.5 | 70 | 25.505 | 19.5052 | 57.692 | 117.3536 | 117.3536 | 0 | 0
2025-06-25 02:00 | 27.7 | 63 | 70 | 25.2751 | 19.1427 | 56.6486 | 104.7467 | 104.7467 | 0 | 0
2025-06-25 03:00 | 27.35 | 61 | 70 | 25.1598 | 18.8748 | 55.5863 | 94.7225 | 94.7225 | 0 | 0
2025-06-25 04:00 | 27.7 | 54 | 70 | 25.2835 | 18.4897 | 52.5578 | 76.1486 | 76.1486 | 0 | 0
2025-06-25 05:00 | 28.15 | 46.5 | 70 | 25.442 | 18.0728 | 49.2389 | 55.9105 | 55.9105 | 0 | 0
2025-06-25 06:00 | 28.8 | 41.5 | 100 | 25.6653 | 17.8813 | 47.0285 | 63.5931 | 63.5931 | 0 | 0
2025-06-25 07:00 | 30.7 | 34.5 | 100 | 26.3023 | 17.8489 | 43.9069 | 48.4694 | 48.4694 | 0 | 0
2025-06-25 08:00 | 33.2 | 29 | 100 | 27.1147 | 18.0204 | 41.3312 | 42.2353 | 42.2353 | 0 | 0
2025-06-25 09:00 | 35.7 | 24.5 | 100 | 27.9014 | 18.1948 | 39.0352 | 36.8513 | 36.8513 | 0 | 0
2025-06-25 10:00 | 38 | 19.5 | 100 | 28.6123 | 18.1578 | 36.1162 | 20.6005 | 20.6005 | 0 | 0
2025-06-25 11:00 | 40 | 15.5 | 100 | 29.2186 | 18.0746 | 33.5217 | 3.8564 | 3.8564 | 0 | 0
2025-06-25 12:00 | 41.6 | 13.5 | 100 | 29.6872 | 18.1192 | 32.1282 | 0 | 0 | 0 | 0
2025-06-25 13:00 | 42.4 | 14 | 100 | 29.9028 | 18.3589 | 32.528 | 7.6641 | 7.6641 | 0 | 0
2025-06-25 14:00 | 41.6 | 23 | 100 | 29.5937 | 19.497 | 39.1028 | 82.4024 | 82.4024 | 0 | 0
2025-06-25 15:00 | 39.7 | 36 | 100 | 28.9697 | 20.656 | 47.6032 | 167.6249 | 167.6249 | 0 | 0
2025-06-25 16:00 | 37.85 | 44 | 100 | 28.4128 | 20.984 | 51.9039 | 200.4001 | 200.4001 | 0 | 0
2025-06-25 17:00 | 36.25 | 50.5 | 100 | 27.933 | 21.1183 | 54.9593 | 219.3826 | 219.3826 | 0 | 0
2025-06-25 18:00 | 34.5 | 57.5 | 100 | 27.4039 | 21.1641 | 57.8793 | 233.8073 | 233.8073 | 0 | 0
2025-06-25 19:00 | 32.9 | 68 | 100 | 26.9004 | 21.4772 | 62.4542 | 265.4968 | 265.4968 | 0 | 0
2025-06-25 20:00 | 31.85 | 78.5 | 100 | 26.5599 | 21.8987 | 67.0379 | 301.2867 | 301.2867 | 0 | 0
2025-06-25 21:00 | 31.15 | 83 | 100 | 26.3397 | 21.9485 | 68.6497 | 309.63 | 309.63 | 0 | 0
2025-06-25 22:00 | 30.7 | 85 | 70 | 26.1995 | 21.9068 | 69.2044 | 216.9584 | 216.9584 | 0 | 0
2025-06-25 23:00 | 30.15 | 87 | 70 | 26.0277 | 21.8181 | 69.6463 | 215.4801 | 215.4801 | 0 | 0
2025-06-26 | 29.45 | 89 | 70 | 25.8078 | 21.6609 | 69.9268 | 211.5273 | 211.5273 | 0 | 0
2025-06-26 01:00 | 28.8 | 92 | 70 | 25.5996 | 21.5864 | 70.6998 | 211.3303 | 211.3303 | 0 | 0
2025-06-26 02:00 | 28.15 | 94.5 | 70 | 25.3901 | 21.4714 | 71.2101 | 209.2026 | 209.2026 | 0 | 0
2025-06-26 03:00 | 27.65 | 94 | 70 | 25.2298 | 21.2228 | 70.5116 | 200.0478 | 200.0478 | 0 | 0
2025-06-26 04:00 | 27.95 | 93.5 | 70 | 25.3271 | 21.3198 | 70.5673 | 203.0458 | 203.0458 | 0 | 0
2025-06-26 05:00 | 28.35 | 93.5 | 70 | 25.4551 | 21.4924 | 70.9452 | 209.1248 | 209.1248 | 0 | 0
2025-06-26 06:00 | 28.95 | 89.5 | 100 | 25.6504 | 21.4822 | 69.6758 | 293.598 | 293.598 | 0 | 0
2025-06-26 07:00 | 30.7 | 79 | 100 | 26.2121 | 21.4657 | 66.2314 | 279.8059 | 279.8059 | 0 | 0
2025-06-26 08:00 | 32.95 | 66 | 100 | 26.9218 | 21.3304 | 61.3969 | 254.9558 | 254.9558 | 0 | 0
2025-06-26 09:00 | 35.4 | 53.5 | 100 | 27.679 | 21.1159 | 56.1587 | 224.2176 | 224.2176 | 0 | 0
2025-06-26 10:00 | 38.05 | 41 | 100 | 28.4874 | 20.7229 | 50.0615 | 181.4434 | 181.4434 | 0 | 0
2025-06-26 11:00 | 40.45 | 31.5 | 100 | 29.2076 | 20.325 | 44.7974 | 141.166 | 141.166 | 0 | 0
2025-06-26 12:00 | 41.7 | 28.5 | 100 | 29.565 | 20.286 | 43.1382 | 131.4253 | 131.4253 | 0 | 0
2025-06-26 13:00 | 40.7 | 35.5 | 100 | 29.2375 | 20.9035 | 47.7282 | 177.4016 | 177.4016 | 0 | 0
2025-06-26 14:00 | 39.25 | 40 | 100 | 28.8185 | 20.9912 | 50.0621 | 191.9858 | 191.9858 | 0 | 0
2025-06-26 15:00 | 38.55 | 40 | 100 | 28.6304 | 20.7677 | 49.6898 | 181.6415 | 181.6415 | 0 | 0
2025-06-26 16:00 | 37.5 | 41 | 100 | 28.3354 | 20.5441 | 49.7953 | 173.5617 | 173.5617 | 0 | 0
2025-06-26 17:00 | 36.1 | 46 | 100 | 27.914 | 20.6137 | 52.1458 | 186.9897 | 186.9897 | 0 | 0
2025-06-26 18:00 | 34.6 | 56 | 100 | 27.4389 | 21.063 | 57.0864 | 226.2969 | 226.2969 | 0 | 0
2025-06-26 19:00 | 33.45 | 64 | 100 | 27.075 | 21.3505 | 60.7184 | 253.1441 | 253.1441 | 0 | 0
2025-06-26 20:00 | 32.75 | 69.5 | 100 | 26.8518 | 21.5428 | 63.1211 | 270.8319 | 270.8319 | 0 | 0
2025-06-26 21:00 | 32.25 | 72 | 100 | 26.6965 | 21.5488 | 64.0167 | 274.6384 | 274.6384 | 0 | 0
2025-06-26 22:00 | 31.7 | 75.5 | 70 | 26.523 | 21.6059 | 65.352 | 197.5815 | 197.5815 | 0 | 0
2025-06-26 23:00 | 31 | 80.5 | 70 | 26.3002 | 21.7009 | 67.2516 | 205.5619 | 205.5619 | 0 | 0
2025-06-27 | 30.2 | 85.5 | 70 | 26.0459 | 21.7328 | 68.9639 | 211.0962 | 211.0962 | 0 | 0
2025-06-27 01:00 | 29.5 | 89.5 | 70 | 25.8226 | 21.7168 | 70.2056 | 213.8984 | 213.8984 | 0 | 0
2025-06-27 02:00 | 28.9 | 92.5 | 70 | 25.6305 | 21.663 | 71.0213 | 214.4196 | 214.4196 | 0 | 0
2025-06-27 03:00 | 28.45 | 94 | 70 | 25.4863 | 21.5686 | 71.2682 | 212.2194 | 212.2194 | 0 | 0
2025-06-27 04:00 | 28.6 | 88.5 | 70 | 25.5408 | 21.2656 | 68.8954 | 197.1224 | 197.1224 | 0 | 0
2025-06-27 05:00 | 28.95 | 80.5 | 70 | 25.6627 | 20.861 | 65.4907 | 176.3625 | 176.3625 | 0 | 0
2025-06-27 06:00 | 30.15 | 69 | 100 | 26.0608 | 20.497 | 60.8899 | 219.1953 | 219.1953 | 0 | 0
2025-06-27 07:00 | 33 | 53 | 100 | 26.9775 | 20.225 | 54.4226 | 181.7558 | 181.7558 | 0 | 0
2025-06-27 08:00 | 36.6 | 40 | 100 | 28.0878 | 20.1523 | 48.7277 | 153.5639 | 153.5639 | 0 | 0
2025-06-27 09:00 | 40.1 | 28 | 100 | 29.1434 | 19.7781 | 42.2307 | 108.2718 | 108.2718 | 0 | 0
2025-06-27 10:00 | 42.85 | 18.5 | 100 | 29.9743 | 19.1503 | 35.9743 | 53.1778 | 53.1778 | 0 | 0
2025-06-27 11:00 | 44.4 | 15 | 100 | 30.4248 | 18.944 | 33.4468 | 32.0344 | 32.0344 | 0 | 0
2025-06-27 12:00 | 43.25 | 24 | 100 | 30.0146 | 20.0677 | 40.2941 | 108.8223 | 108.8223 | 0 | 0
2025-06-27 13:00 | 41.2 | 33.5 | 100 | 29.3858 | 20.7996 | 46.557 | 167.8291 | 167.8291 | 0 | 0
2025-06-27 14:00 | 40.25 | 35 | 100 | 29.124 | 20.7022 | 47.1693 | 167.1889 | 167.1889 | 0 | 0
2025-06-27 15:00 | 39.4 | 37.5 | 100 | 28.8777 | 20.7436 | 48.4701 | 175.0616 | 175.0616 | 0 | 0
2025-06-27 16:00 | 38 | 41.5 | 100 | 28.4701 | 20.7585 | 50.3815 | 184.6193 | 184.6193 | 0 | 0
2025-06-27 17:00 | 36.15 | 48.5 | 100 | 27.9153 | 20.8832 | 53.6864 | 204.4395 | 204.4395 | 0 | 0
2025-06-27 18:00 | 34.75 | 55.5 | 100 | 27.4841 | 21.0701 | 56.9049 | 225.8472 | 225.8472 | 0 | 0
2025-06-27 19:00 | 33.85 | 59 | 100 | 27.2096 | 21.0619 | 58.2604 | 231.2479 | 231.2479 | 0 | 0
2025-06-27 20:00 | 33.25 | 62 | 100 | 27.023 | 21.1028 | 59.4802 | 237.9606 | 237.9606 | 0 | 0
2025-06-27 21:00 | 32.75 | 65.5 | 100 | 26.864 | 21.2112 | 60.9904 | 248.5515 | 248.5515 | 0 | 0
2025-06-27 22:00 | 32.15 | 68 | 70 | 26.6777 | 21.1876 | 61.8493 | 175.7255 | 175.7255 | 0 | 0
2025-06-27 23:00 | 31.35 | 71.5 | 70 | 26.4269 | 21.1543 | 63.0276 | 178.0921 | 178.0921 | 0 | 0
2025-06-28 | 30.55 | 75.5 | 70 | 26.173 | 21.1431 | 64.3903 | 181.5501 | 181.5501 | 0 | 0
2025-06-28 01:00 | 29.95 | 77.5 | 70 | 25.9829 | 21.0508 | 64.8829 | 180.2338 | 180.2338 | 0 | 0
2025-06-28 02:00 | 29.4 | 79 | 70 | 25.8076 | 20.9374 | 65.1573 | 177.7088 | 177.7088 | 0 | 0
2025-06-28 03:00 | 28.8 | 80.5 | 70 | 25.6148 | 20.8004 | 65.38 | 174.3576 | 174.3576 | 0 | 0
2025-06-28 04:00 | 29.2 | 71.5 | 70 | 25.7552 | 20.3167 | 61.4533 | 150.0234 | 150.0234 | 0 | 0
2025-06-28 05:00 | 30.1 | 64.5 | 70 | 26.0531 | 20.1327 | 58.6635 | 137.1369 | 137.1369 | 0 | 0
2025-06-28 06:00 | 31 | 70 | 100 | 26.3232 | 20.9008 | 62.0018 | 239.9833 | 239.9833 | 0 | 0
2025-06-28 07:00 | 32.85 | 68 | 100 | 26.8859 | 21.4584 | 62.4009 | 264.3967 | 264.3967 | 0 | 0
2025-06-28 08:00 | 35.95 | 53.5 | 100 | 27.834 | 21.3104 | 56.5416 | 233.7839 | 233.7839 | 0 | 0
2025-06-28 09:00 | 39.45 | 36.5 | 100 | 28.8991 | 20.642 | 47.8039 | 167.8236 | 167.8236 | 0 | 0
2025-06-28 10:00 | 42.1 | 25.5 | 100 | 29.7004 | 19.9816 | 41.0685 | 109.7237 | 109.7237 | 0 | 0
2025-06-28 11:00 | 43.2 | 24.5 | 100 | 29.9959 | 20.1283 | 40.6631 | 112.9411 | 112.9411 | 0 | 0
2025-06-28 12:00 | 41.9 | 35 | 100 | 29.5492 | 21.2055 | 47.9965 | 190.3735 | 190.3735 | 0 | 0
2025-06-28 13:00 | 39.75 | 45 | 100 | 28.9094 | 21.7318 | 53.7479 | 238.3024 | 238.3024 | 0 | 0
2025-06-28 14:00 | 38.5 | 49 | 100 | 28.5534 | 21.7465 | 55.5404 | 247.0687 | 247.0687 | 0 | 0
2025-06-28 15:00 | 37.65 | 52 | 100 | 28.3075 | 21.7632 | 56.8508 | 253.6168 | 253.6168 | 0 | 0
2025-06-28 16:00 | 37 | 53 | 100 | 28.1261 | 21.6335 | 57.0005 | 249.0237 | 249.0237 | 0 | 0
2025-06-28 17:00 | 36.25 | 55.5 | 100 | 27.9068 | 21.6113 | 57.9746 | 252.3532 | 252.3532 | 0 | 0
2025-06-28 18:00 | 35 | 61.5 | 100 | 27.5294 | 21.7142 | 60.5429 | 267.4742 | 267.4742 | 0 | 0
2025-06-28 19:00 | 33.85 | 67.5 | 100 | 27.1782 | 21.8041 | 62.9749 | 281.2135 | 281.2135 | 0 | 0
2025-06-28 20:00 | 33.1 | 71 | 100 | 26.9493 | 21.804 | 64.2332 | 286.2741 | 286.2741 | 0 | 0
2025-06-28 21:00 | 32.35 | 74 | 100 | 26.7203 | 21.7486 | 65.1627 | 287.624 | 287.624 | 0 | 0
2025-06-28 22:00 | 31.45 | 78 | 70 | 26.4416 | 21.6963 | 66.4176 | 203.2411 | 203.2411 | 0 | 0
2025-06-28 23:00 | 30.5 | 83 | 70 | 26.1426 | 21.6774 | 68.0406 | 207.0679 | 207.0679 | 0 | 0
2025-06-29 | 29.6 | 88.5 | 70 | 25.8552 | 21.6896 | 69.8428 | 212.2148 | 212.2148 | 0 | 0
2025-06-29 01:00 | 28.85 | 93 | 70 | 25.614 | 21.6752 | 71.2202 | 215.3643 | 215.3643 | 0 | 0
2025-06-29 02:00 | 28.3 | 95.5 | 70 | 25.4368 | 21.6013 | 71.8209 | 214.7121 | 214.7121 | 0 | 0
2025-06-29 03:00 | 27.8 | 96.5 | 70 | 25.2757 | 21.4482 | 71.7787 | 210.0257 | 210.0257 | 0 | 0
2025-06-29 04:00 | 28.15 | 90 | 70 | 25.395 | 21.1753 | 69.1904 | 195.3147 | 195.3147 | 0 | 0
2025-06-29 05:00 | 28.65 | 84 | 70 | 25.5623 | 20.9807 | 66.8838 | 183.5893 | 183.5893 | 0 | 0
2025-06-29 06:00 | 29.1 | 81.5 | 100 | 25.709 | 20.992 | 66.094 | 259.7393 | 259.7393 | 0 | 0
2025-06-29 07:00 | 30.75 | 73 | 100 | 26.2397 | 21.0336 | 63.3173 | 250.6758 | 250.6758 | 0 | 0
2025-06-29 08:00 | 33.05 | 61 | 100 | 26.967 | 20.942 | 58.798 | 228.6632 | 228.6632 | 0 | 0
2025-06-29 09:00 | 35.15 | 49 | 100 | 27.6275 | 20.5923 | 53.3923 | 191.6812 | 191.6812 | 0 | 0
2025-06-29 10:00 | 36.75 | 42 | 100 | 28.1194 | 20.4108 | 50.0465 | 169.6521 | 169.6521 | 0 | 0
2025-06-29 11:00 | 36.85 | 45 | 100 | 28.1307 | 20.7601 | 51.9547 | 191.8264 | 191.8264 | 0 | 0
2025-06-29 12:00 | 36.2 | 50 | 100 | 27.9216 | 21.051 | 54.6223 | 215.2023 | 215.2023 | 0 | 0
2025-06-29 13:00 | 36.15 | 48.5 | 100 | 27.9153 | 20.8832 | 53.6899 | 204.4787 | 204.4787 | 0 | 0
2025-06-29 14:00 | 36.15 | 45.5 | 100 | 27.9306 | 20.5779 | 51.8837 | 184.5652 | 184.5652 | 0 | 0
2025-06-29 15:00 | 36.35 | 42.5 | 100 | 28.0031 | 20.3324 | 50.1711 | 167.4222 | 167.4222 | 0 | 0
2025-06-29 16:00 | 35.9 | 44.5 | 100 | 27.8643 | 20.3923 | 51.1556 | 174.2044 | 174.2044 | 0 | 0
2025-06-29 17:00 | 34.95 | 50 | 100 | 27.5651 | 20.6183 | 53.8782 | 195.0539 | 195.0539 | 0 | 0
2025-06-29 18:00 | 33.9 | 56.5 | 100 | 27.2332 | 20.8546 | 56.9216 | 217.4744 | 217.4744 | 0 | 0
2025-06-29 19:00 | 32.6 | 64.5 | 100 | 26.8221 | 21.0694 | 60.3673 | 240.4219 | 240.4219 | 0 | 0
2025-06-29 20:00 | 31.7 | 69 | 100 | 26.5392 | 21.0928 | 62.0406 | 248.1038 | 248.1038 | 0 | 0
2025-06-29 21:00 | 31.1 | 71 | 100 | 26.3516 | 21.017 | 62.5954 | 247.194 | 247.194 | 0 | 0
2025-06-29 22:00 | 30.45 | 73.5 | 70 | 26.1459 | 20.9525 | 63.3382 | 173.2564 | 173.2564 | 0 | 0
2025-06-29 23:00 | 29.7 | 76 | 70 | 25.907 | 20.8411 | 63.9737 | 171.7941 | 171.7941 | 0 | 0
2025-06-30 | 28.9 | 77.5 | 70 | 25.6507 | 20.6295 | 64.0737 | 166.0452 | 166.0452 | 0 | 0
2025-06-30 01:00 | 28.2 | 78.5 | 70 | 25.4238 | 20.4191 | 64.0161 | 159.9507 | 159.9507 | 0 | 0
2025-06-30 02:00 | 27.6 | 80.5 | 70 | 25.2259 | 20.3146 | 64.4819 | 158.2494 | 158.2494 | 0 | 0
2025-06-30 03:00 | 27.15 | 82 | 70 | 25.0762 | 20.2332 | 64.819 | 156.8386 | 156.8386 | 0 | 0
2025-06-30 04:00 | 27.85 | 78.5 | 70 | 25.3097 | 20.2798 | 63.7644 | 155.349 | 155.349 | 0 | 0
2025-06-30 05:00 | 28.7 | 73.5 | 70 | 25.5917 | 20.2661 | 62.0653 | 150.3733 | 150.3733 | 0 | 0
2025-06-30 06:00 | 29.2 | 68 | 100 | 25.7603 | 20.0592 | 59.8034 | 197.6737 | 197.6737 | 0 | 0
2025-06-30 07:00 | 31.05 | 57 | 100 | 26.3671 | 19.8806 | 55.4775 | 173.083 | 173.083 | 0 | 0
2025-06-30 08:00 | 33.85 | 44.5 | 100 | 27.2621 | 19.7267 | 50.1678 | 144.2782 | 144.2782 | 0 | 0
2025-06-30 09:00 | 36.25 | 37 | 100 | 28.003 | 19.7206 | 46.7591 | 128.4483 | 128.4483 | 0 | 0
2025-06-30 10:00 | 37.65 | 34.5 | 100 | 28.4175 | 19.8644 | 45.7269 | 128.8225 | 128.8225 | 0 | 0
2025-06-30 11:00 | 38.05 | 35.5 | 100 | 28.5234 | 20.0978 | 46.5271 | 141.3319 | 141.3319 | 0 | 0
2025-06-30 12:00 | 38.1 | 37 | 100 | 28.5274 | 20.2844 | 47.5223 | 153.0973 | 153.0973 | 0 | 0
2025-06-30 13:00 | 38.1 | 38.5 | 100 | 28.5174 | 20.4545 | 48.4978 | 164.1855 | 164.1855 | 0 | 0
2025-06-30 14:00 | 37.85 | 41 | 100 | 28.4321 | 20.654 | 49.9864 | 178.8316 | 178.8316 | 0 | 0
2025-06-30 15:00 | 37.5 | 43.5 | 100 | 28.3199 | 20.8133 | 51.3919 | 191.4889 | 191.4889 | 0 | 0
2025-06-30 16:00 | 36.95 | 46.5 | 100 | 28.1499 | 20.9489 | 52.9531 | 203.8484 | 203.8484 | 0 | 0
2025-06-30 17:00 | 36 | 52 | 100 | 27.8552 | 21.1788 | 55.703 | 225.1185 | 225.1185 | 0 | 0
2025-06-30 18:00 | 34.65 | 61.5 | 100 | 27.4303 | 21.5823 | 60.2688 | 260.9268 | 260.9268 | 0 | 0
2025-06-30 19:00 | 33.5 | 69.5 | 100 | 27.0703 | 21.8369 | 63.7716 | 285.8124 | 285.8124 | 0 | 0
2025-06-30 20:00 | 32.7 | 74 | 100 | 26.8232 | 21.8892 | 65.4768 | 294.7914 | 294.7914 | 0 | 0
2025-06-30 21:00 | 31.95 | 77.5 | 100 | 26.5922 | 21.862 | 66.6193 | 298.1307 | 298.1307 | 0 | 0
2025-06-30 22:00 | 31.2 | 81.5 | 70 | 26.3581 | 21.858 | 67.9539 | 212.1957 | 212.1957 | 0 | 0
2025-06-30 23:00 | 30.45 | 84.5 | 70 | 26.1243 | 21.7655 | 68.7296 | 211.5252 | 211.5252 | 0 | 0
2025-07-01 | 29.75 | 84 | 70 | 25.9093 | 21.4368 | 67.8415 | 199.4521 | 199.4521 | 0 | 0
2025-07-01 01:00 | 29 | 82 | 70 | 25.6765 | 20.9859 | 66.2493 | 182.0779 | 182.0779 | 0 | 0
2025-07-01 02:00 | 28.25 | 82 | 70 | 25.4361 | 20.68 | 65.6433 | 171.6502 | 171.6502 | 0 | 0
2025-07-01 03:00 | 27.6 | 84 | 70 | 25.2227 | 20.5491 | 66.0326 | 168.9192 | 168.9192 | 0 | 0
2025-07-01 04:00 | 27.5 | 80.5 | 70 | 25.193 | 20.2754 | 64.3956 | 156.8276 | 156.8276 | 0 | 0
2025-07-01 05:00 | 27.65 | 74 | 70 | 25.2483 | 19.8943 | 61.5873 | 138.6653 | 138.6653 | 0 | 0
2025-07-01 06:00 | 28.5 | 66.5 | 100 | 25.5354 | 19.6874 | 58.6707 | 178.5605 | 178.5605 | 0 | 0
2025-07-01 07:00 | 30.8 | 55 | 100 | 26.2928 | 19.6296 | 54.3263 | 158.5483 | 158.5483 | 0 | 0
2025-07-01 08:00 | 33.6 | 44 | 100 | 27.1884 | 19.5998 | 49.7709 | 137.6329 | 137.6329 | 0 | 0
2025-07-01 09:00 | 36.2 | 35.5 | 100 | 27.9961 | 19.5463 | 45.8156 | 117.4334 | 117.4334 | 0 | 0
2025-07-01 10:00 | 38.5 | 29 | 100 | 28.693 | 19.4623 | 42.43 | 97.9554 | 97.9554 | 0 | 0
2025-07-01 11:00 | 40.5 | 24.5 | 100 | 29.2823 | 19.4241 | 39.8978 | 83.7516 | 83.7516 | 0 | 0
2025-07-01 12:00 | 41.8 | 23 | 100 | 29.6471 | 19.5513 | 39.1397 | 84.2995 | 84.2995 | 0 | 0
2025-07-01 13:00 | 42.15 | 22 | 100 | 29.7505 | 19.4948 | 38.4872 | 78.9496 | 78.9496 | 0 | 0
2025-07-01 14:00 | 41.75 | 21.5 | 100 | 29.6489 | 19.3233 | 38.0334 | 70.5849 | 70.5849 | 0 | 0
2025-07-01 15:00 | 41 | 24 | 100 | 29.4227 | 19.4825 | 39.6807 | 84.9098 | 84.9098 | 0 | 0
2025-07-01 16:00 | 40.1 | 27.5 | 100 | 29.1476 | 19.7092 | 41.9046 | 104.4461 | 104.4461 | 0 | 0
2025-07-01 17:00 | 38.5 | 34 | 100 | 28.6585 | 20.0561 | 45.7385 | 136.1072 | 136.1072 | 0 | 0
2025-07-01 18:00 | 36.3 | 46.5 | 100 | 27.968 | 20.7309 | 52.5676 | 193.5176 | 193.5176 | 0 | 0
2025-07-01 19:00 | 34.5 | 58 | 100 | 27.4018 | 21.2095 | 58.1626 | 236.8464 | 236.8464 | 0 | 0
2025-07-01 20:00 | 33.35 | 65 | 100 | 27.0422 | 21.3971 | 61.1934 | 257.0932 | 257.0932 | 0 | 0
2025-07-01 21:00 | 32.35 | 72 | 100 | 26.7261 | 21.5886 | 64.1122 | 276.739 | 276.739 | 0 | 0
2025-07-01 22:00 | 31.35 | 81 | 70 | 26.4044 | 21.8825 | 67.8374 | 212.5874 | 212.5874 | 0 | 0
2025-07-01 23:00 | 30.6 | 88 | 70 | 26.163 | 22.0813 | 70.581 | 225.8457 | 225.8457 | 0 | 0
2025-07-02 | 29.85 | 91 | 70 | 25.9284 | 21.9703 | 71.2728 | 224.3391 | 224.3391 | 0 | 0
2025-07-02 01:00 | 29 | 92 | 70 | 25.6626 | 21.6728 | 70.8969 | 214.4217 | 214.4217 | 0 | 0
2025-07-02 02:00 | 28.25 | 92.5 | 70 | 25.4243 | 21.3835 | 70.4068 | 204.5508 | 204.5508 | 0 | 0
2025-07-02 03:00 | 27.65 | 92.5 | 70 | 25.2311 | 21.1259 | 69.8518 | 195.5364 | 195.5364 | 0 | 0
2025-07-02 04:00 | 27.8 | 88.5 | 70 | 25.2836 | 20.9293 | 68.1999 | 185.5038 | 185.5038 | 0 | 0
2025-07-02 05:00 | 28 | 84 | 70 | 25.3531 | 20.7129 | 66.3407 | 174.39 | 174.39 | 0 | 0
2025-07-02 06:00 | 28.5 | 78 | 100 | 25.5216 | 20.5053 | 63.9854 | 231.682 | 231.682 | 0 | 0
2025-07-02 07:00 | 30.7 | 66 | 100 | 26.2388 | 20.4743 | 59.7816 | 213.8741 | 213.8741 | 0 | 0
2025-07-02 08:00 | 33.4 | 54.5 | 100 | 27.0926 | 20.499 | 55.4706 | 196.9284 | 196.9284 | 0 | 0
2025-07-02 09:00 | 35.6 | 46 | 100 | 27.7711 | 20.4492 | 51.8607 | 179.17 | 179.17 | 0 | 0
2025-07-02 10:00 | 37.4 | 39.5 | 100 | 28.3167 | 20.35 | 48.7849 | 161.2954 | 161.2954 | 0 | 0
2025-07-02 11:00 | 38.75 | 36 | 100 | 28.7133 | 20.3692 | 47.1441 | 154.3225 | 154.3225 | 0 | 0
2025-07-02 12:00 | 39.5 | 36.5 | 100 | 28.9124 | 20.6569 | 47.8309 | 168.5579 | 168.5579 | 0 | 0
2025-07-02 13:00 | 39.5 | 39.5 | 100 | 28.8887 | 21.0126 | 49.8651 | 191.9024 | 191.9024 | 0 | 0
2025-07-02 14:00 | 39 | 41.5 | 100 | 28.7405 | 21.0827 | 50.9293 | 199.673 | 199.673 | 0 | 0
2025-07-02 15:00 | 38.25 | 44 | 100 | 28.5214 | 21.1164 | 52.1342 | 206.6054 | 206.6054 | 0 | 0
2025-07-02 16:00 | 37.15 | 48 | 100 | 28.1965 | 21.1743 | 53.9981 | 217.3076 | 217.3076 | 0 | 0
2025-07-02 17:00 | 35.6 | 55 | 100 | 27.7282 | 21.3288 | 57.202 | 237.5233 | 237.5233 | 0 | 0
2025-07-02 18:00 | 33.95 | 65.5 | 100 | 27.2145 | 21.6706 | 61.946 | 271.4169 | 271.4169 | 0 | 0
2025-07-02 19:00 | 32.8 | 73.5 | 100 | 26.854 | 21.8891 | 65.2952 | 294.021 | 294.021 | 0 | 0
2025-07-02 20:00 | 32.15 | 77 | 100 | 26.6529 | 21.9048 | 66.5368 | 299.5581 | 299.5581 | 0 | 0
2025-07-02 21:00 | 31.75 | 78.5 | 100 | 26.5302 | 21.8571 | 66.9378 | 299.1142 | 299.1142 | 0 | 0
2025-07-02 22:00 | 31.45 | 80 | 70 | 26.4369 | 21.8487 | 67.4216 | 210.4281 | 210.4281 | 0 | 0
2025-07-02 23:00 | 31.15 | 82.5 | 70 | 26.3409 | 21.9115 | 68.3972 | 214.9438 | 214.9438 | 0 | 0
2025-07-03 | 30.75 | 85 | 70 | 26.2146 | 21.9282 | 69.2542 | 217.7263 | 217.7263 | 0 | 0
2025-07-03 01:00 | 30.25 | 86.5 | 70 | 26.0593 | 21.8246 | 69.5034 | 215.3135 | 215.3135 | 0 | 0
2025-07-03 02:00 | 29.75 | 87 | 70 | 25.9043 | 21.649 | 69.2661 | 209.4464 | 209.4464 | 0 | 0
2025-07-03 03:00 | 29.2 | 87 | 70 | 25.7326 | 21.4163 | 68.755 | 201.2358 | 201.2358 | 0 | 0
2025-07-03 04:00 | 29 | 88.5 | 70 | 25.6675 | 21.435 | 69.2692 | 203.1209 | 203.1209 | 0 | 0
2025-07-03 05:00 | 29.05 | 90 | 70 | 25.6812 | 21.5587 | 70.0094 | 208.6906 | 208.6906 | 0 | 0
2025-07-03 06:00 | 29.5 | 86.5 | 100 | 25.8274 | 21.5084 | 68.7845 | 291.3854 | 291.3854 | 0 | 0
2025-07-03 07:00 | 31.1 | 75.5 | 100 | 26.3417 | 21.3645 | 64.8338 | 270.1391 | 270.1391 | 0 | 0
2025-07-03 08:00 | 33.3 | 61.5 | 100 | 27.0395 | 21.0795 | 59.2297 | 235.8338 | 235.8338 | 0 | 0
2025-07-03 09:00 | 35.5 | 49.5 | 100 | 27.726 | 20.7623 | 53.8751 | 200.3062 | 200.3062 | 0 | 0
2025-07-03 10:00 | 37.85 | 39 | 100 | 28.4452 | 20.4354 | 48.6814 | 164.0783 | 164.0783 | 0 | 0
2025-07-03 11:00 | 39.9 | 32 | 100 | 29.0561 | 20.2274 | 44.9306 | 138.287 | 138.287 | 0 | 0
2025-07-03 12:00 | 40.7 | 32.5 | 100 | 29.2648 | 20.524 | 45.6152 | 152.7562 | 152.7562 | 0 | 0
2025-07-03 13:00 | 40.1 | 38 | 100 | 29.0589 | 21.023 | 49.1666 | 189.0211 | 189.0211 | 0 | 0
2025-07-03 14:00 | 39.1 | 42 | 100 | 28.7633 | 21.1724 | 51.3194 | 204.9851 | 204.9851 | 0 | 0
2025-07-03 15:00 | 38.15 | 46 | 100 | 28.481 | 21.3022 | 53.363 | 219.49 | 219.49 | 0 | 0
2025-07-03 16:00 | 36.7 | 53 | 100 | 28.0442 | 21.5268 | 56.7808 | 243.7082 | 243.7082 | 0 | 0
2025-07-03 17:00 | 35.2 | 60 | 100 | 27.5924 | 21.6522 | 59.8283 | 261.8617 | 261.8617 | 0 | 0
2025-07-03 18:00 | 33.85 | 68 | 100 | 27.1765 | 21.8471 | 63.2451 | 284.0619 | 284.0619 | 0 | 0
2025-07-03 19:00 | 32.65 | 77 | 100 | 26.7995 | 22.1083 | 67.0105 | 310.1166 | 310.1166 | 0 | 0
2025-07-03 20:00 | 32 | 83 | 100 | 26.5923 | 22.3055 | 69.4914 | 328.1577 | 328.1577 | 0 | 0
2025-07-03 21:00 | 31.7 | 86 | 100 | 26.4962 | 22.4045 | 70.7111 | 337.0757 | 337.0757 | 0 | 0
2025-07-03 22:00 | 31.5 | 87 | 70 | 26.4347 | 22.3929 | 71.0063 | 236.3919 | 236.3919 | 0 | 0
2025-07-03 23:00 | 31.15 | 87.5 | 70 | 26.3295 | 22.2802 | 70.8935 | 232.6691 | 232.6691 | 0 | 0
2025-07-04 | 30.6 | 88 | 70 | 26.163 | 22.0812 | 70.5802 | 225.84 | 225.84 | 0 | 0
2025-07-04 01:00 | 30.05 | 87.5 | 70 | 25.9961 | 21.8108 | 69.794 | 215.6763 | 215.6763 | 0 | 0
2025-07-04 02:00 | 29.55 | 86.5 | 70 | 25.8429 | 21.529 | 68.8413 | 204.7881 | 204.7881 | 0 | 0
2025-07-04 03:00 | 29.05 | 85.5 | 70 | 25.6875 | 21.2502 | 67.9156 | 194.1202 | 194.1202 | 0 | 0
2025-07-04 04:00 | 28.85 | 84 | 70 | 25.6262 | 21.0635 | 67.0403 | 186.3468 | 186.3468 | 0 | 0
2025-07-04 05:00 | 28.8 | 82 | 70 | 25.6129 | 20.9046 | 66.0659 | 179.141 | 179.141 | 0 | 0
2025-07-04 06:00 | 29.25 | 78 | 100 | 25.7617 | 20.8062 | 64.5495 | 246.0228 | 246.0228 | 0 | 0
2025-07-04 07:00 | 30.9 | 69 | 100 | 26.2946 | 20.7851 | 61.4136 | 232.8332 | 232.8332 | 0 | 0
2025-07-04 08:00 | 33.1 | 57 | 100 | 26.9949 | 20.6143 | 56.6449 | 206.3854 | 206.3854 | 0 | 0
2025-07-04 09:00 | 35.25 | 46 | 100 | 27.67 | 20.3337 | 51.6714 | 173.8072 | 173.8072 | 0 | 0
2025-07-04 10:00 | 37.3 | 37 | 100 | 28.3036 | 20.0431 | 47.157 | 142.0442 | 142.0442 | 0 | 0
2025-07-04 11:00 | 39.3 | 30 | 100 | 28.9085 | 19.8087 | 43.3407 | 114.9319 | 114.9319 | 0 | 0
2025-07-04 12:00 | 41.3 | 24 | 100 | 29.5035 | 19.5641 | 39.7387 | 87.8193 | 87.8193 | 0 | 0
2025-07-04 13:00 | 42.65 | 20 | 100 | 29.9046 | 19.3268 | 37.0852 | 65.4211 | 65.4211 | 0 | 0
2025-07-04 14:00 | 41.6 | 30 | 100 | 29.5238 | 20.4576 | 44.2018 | 143.2738 | 143.2738 | 0 | 0
2025-07-04 15:00 | 39.3 | 43 | 100 | 28.8085 | 21.3528 | 52.1055 | 215.676 | 215.676 | 0 | 0
2025-07-04 16:00 | 37.8 | 48 | 100 | 28.3736 | 21.3979 | 54.4126 | 227.983 | 227.983 | 0 | 0
2025-07-04 17:00 | 36.45 | 53 | 100 | 27.9755 | 21.4384 | 56.5986 | 239.2847 | 239.2847 | 0 | 0
2025-07-04 18:00 | 35 | 59.5 | 100 | 27.5383 | 21.532 | 59.3794 | 254.9967 | 254.9967 | 0 | 0
2025-07-04 19:00 | 33.7 | 69.5 | 100 | 27.1281 | 21.9161 | 63.9305 | 289.653 | 289.653 | 0 | 0
2025-07-04 20:00 | 32.85 | 76.5 | 100 | 26.8594 | 22.1504 | 66.9236 | 311.4785 | 311.4785 | 0 | 0
2025-07-04 21:00 | 32.45 | 78 | 100 | 26.7384 | 22.1065 | 67.3276 | 311.1236 | 311.1236 | 0 | 0
2025-07-04 22:00 | 32.1 | 78.5 | 70 | 26.6342 | 22.0012 | 67.2531 | 214.453 | 214.453 | 0 | 0
2025-07-04 23:00 | 31.6 | 80.5 | 70 | 26.4806 | 21.9487 | 67.8074 | 214.4037 | 214.4037 | 0 | 0
2025-07-05 | 31.05 | 84.5 | 70 | 26.3064 | 22.018 | 69.2916 | 220.4787 | 220.4787 | 0 | 0
2025-07-05 01:00 | 30.55 | 88.5 | 70 | 26.1469 | 22.0956 | 70.7655 | 226.7252 | 226.7252 | 0 | 0
2025-07-05 02:00 | 30.15 | 90.5 | 70 | 26.0213 | 22.0652 | 71.3277 | 227.2854 | 227.2854 | 0 | 0
2025-07-05 03:00 | 29.8 | 91 | 70 | 25.9131 | 21.949 | 71.211 | 223.48 | 223.48 | 0 | 0
2025-07-05 04:00 | 29.7 | 90.5 | 70 | 25.8831 | 21.871 | 70.8728 | 220.262 | 220.262 | 0 | 0
2025-07-05 05:00 | 29.65 | 90 | 70 | 25.8684 | 21.8153 | 70.5846 | 217.8224 | 217.8224 | 0 | 0
2025-07-05 06:00 | 30 | 86 | 100 | 25.9835 | 21.6841 | 69.0078 | 299.6174 | 299.6174 | 0 | 0
2025-07-05 07:00 | 31.5 | 75 | 100 | 26.4642 | 21.4866 | 64.9135 | 275.4898 | 275.4898 | 0 | 0
2025-07-05 08:00 | 33.55 | 61 | 100 | 27.1149 | 21.1293 | 59.1274 | 237.357 | 237.357 | 0 | 0
2025-07-05 09:00 | 35.6 | 49 | 100 | 27.757 | 20.748 | 53.6302 | 198.5817 | 198.5817 | 0 | 0
2025-07-05 10:00 | 37.6 | 40.5 | 100 | 28.3665 | 20.5238 | 49.5093 | 171.2245 | 171.2245 | 0 | 0
2025-07-05 11:00 | 39.3 | 35.5 | 100 | 28.8665 | 20.4787 | 47.0516 | 157.8977 | 157.8977 | 0 | 0
2025-07-05 12:00 | 40.1 | 34.5 | 100 | 29.0887 | 20.5972 | 46.7387 | 160.9465 | 160.9465 | 0 | 0
2025-07-05 13:00 | 39.9 | 36.5 | 100 | 29.0189 | 20.7806 | 48.026 | 174.1782 | 174.1782 | 0 | 0
2025-07-05 14:00 | 39.4 | 37.5 | 100 | 28.8778 | 20.7447 | 48.4612 | 174.9561 | 174.9561 | 0 | 0
2025-07-05 15:00 | 38.35 | 42 | 100 | 28.5622 | 20.9289 | 50.8884 | 193.4547 | 193.4547 | 0 | 0
2025-07-05 16:00 | 36.4 | 52 | 100 | 27.967 | 21.3211 | 55.957 | 231.7702 | 231.7702 | 0 | 0
2025-07-05 17:00 | 34.45 | 62 | 100 | 27.3714 | 21.5532 | 60.3825 | 260.0664 | 260.0664 | 0 | 0
2025-07-05 18:00 | 32.9 | 73.5 | 100 | 26.8832 | 21.929 | 65.3828 | 296.0447 | 296.0447 | 0 | 0
2025-07-05 19:00 | 31.95 | 82 | 100 | 26.5803 | 22.2084 | 68.9223 | 321.7543 | 321.7543 | 0 | 0
2025-07-05 20:00 | 31.7 | 81.5 | 100 | 26.5078 | 22.0662 | 68.4173 | 313.685 | 313.685 | 0 | 0
2025-07-05 21:00 | 31.7 | 75 | 100 | 26.5243 | 21.5668 | 65.0931 | 279.5969 | 279.5969 | 0 | 0
2025-07-05 22:00 | 31.7 | 68.5 | 70 | 26.5407 | 21.0538 | 61.7548 | 171.5986 | 171.5986 | 0 | 0
2025-07-05 23:00 | 31.5 | 66.5 | 70 | 26.4847 | 20.8173 | 60.583 | 161.5792 | 161.5792 | 0 | 0
2025-07-06 | 31.05 | 68 | 70 | 26.343 | 20.7641 | 61.0258 | 161.346 | 161.346 | 0 | 0
2025-07-06 01:00 | 30.55 | 69 | 70 | 26.186 | 20.6496 | 61.1722 | 158.5495 | 158.5495 | 0 | 0
2025-07-06 02:00 | 30.25 | 68.5 | 70 | 26.0931 | 20.4962 | 60.7178 | 152.9806 | 152.9806 | 0 | 0
2025-07-06 03:00 | 29.85 | 68.5 | 70 | 25.967 | 20.3441 | 60.4467 | 147.9571 | 147.9571 | 0 | 0
2025-07-06 04:00 | 29.55 | 69 | 70 | 25.8708 | 20.2672 | 60.4894 | 145.938 | 145.938 | 0 | 0
2025-07-06 05:00 | 29.45 | 68.5 | 70 | 25.8397 | 20.1918 | 60.1842 | 142.9986 | 142.9986 | 0 | 0
2025-07-06 06:00 | 29.8 | 66 | 100 | 25.9553 | 20.1365 | 59.2001 | 198.1298 | 198.1298 | 0 | 0
2025-07-06 07:00 | 31.3 | 59 | 100 | 26.4407 | 20.1352 | 56.6183 | 187.5378 | 187.5378 | 0 | 0
2025-07-06 08:00 | 33.3 | 51 | 100 | 27.0743 | 20.1492 | 53.4926 | 174.7982 | 174.7982 | 0 | 0
2025-07-06 09:00 | 35.3 | 45 | 100 | 27.689 | 20.25 | 51.1163 | 168.1878 | 168.1878 | 0 | 0
2025-07-06 10:00 | 37.15 | 40 | 100 | 28.2436 | 20.325 | 48.9837 | 161.3229 | 161.3229 | 0 | 0
2025-07-06 11:00 | 38.35 | 38 | 100 | 28.5897 | 20.4779 | 48.2751 | 163.8148 | 163.8148 | 0 | 0
2025-07-06 12:00 | 38.5 | 39 | 100 | 28.6238 | 20.6382 | 49.0047 | 173.4179 | 173.4179 | 0 | 0
2025-07-06 13:00 | 37.95 | 41 | 100 | 28.4598 | 20.6883 | 50.0251 | 180.1508 | 180.1508 | 0 | 0
2025-07-06 14:00 | 37.1 | 44.5 | 100 | 28.2033 | 20.7903 | 51.7828 | 192.208 | 192.208 | 0 | 0
2025-07-06 15:00 | 36.05 | 50.5 | 100 | 27.877 | 21.0492 | 54.8252 | 215.9902 | 215.9902 | 0 | 0
2025-07-06 16:00 | 34.9 | 55.5 | 100 | 27.5272 | 21.1244 | 57.006 | 228.4371 | 228.4371 | 0 | 0
2025-07-06 17:00 | 33.85 | 58.5 | 100 | 27.2114 | 21.0176 | 57.982 | 228.2802 | 228.2802 | 0 | 0
2025-07-06 18:00 | 32.9 | 59.5 | 100 | 26.9271 | 20.7576 | 57.885 | 217.4606 | 217.4606 | 0 | 0
2025-07-06 19:00 | 32.1 | 60 | 100 | 26.6842 | 20.508 | 57.6291 | 206.4444 | 206.4444 | 0 | 0
2025-07-06 20:00 | 31.65 | 62 | 100 | 26.5416 | 20.5089 | 58.3782 | 209.5384 | 209.5384 | 0 | 0
2025-07-06 21:00 | 31.4 | 64 | 100 | 26.46 | 20.5786 | 59.236 | 215.7908 | 215.7908 | 0 | 0
2025-07-06 22:00 | 31.1 | 65.5 | 70 | 26.364 | 20.5863 | 59.7946 | 152.8391 | 152.8391 | 0 | 0
2025-07-06 23:00 | 30.6 | 66.5 | 70 | 26.2066 | 20.476 | 59.9608 | 150.2389 | 150.2389 | 0 | 0
2025-07-07 | 30 | 68.5 | 70 | 26.0144 | 20.4016 | 60.5446 | 149.8134 | 149.8134 | 0 | 0
2025-07-07 01:00 | 29.35 | 70.5 | 70 | 25.8047 | 20.3019 | 61.0732 | 148.5143 | 148.5143 | 0 | 0
2025-07-07 02:00 | 28.65 | 71 | 70 | 25.5787 | 20.069 | 60.848 | 141.4403 | 141.4403 | 0 | 0
2025-07-07 03:00 | 28 | 71.5 | 70 | 25.366 | 19.8558 | 60.6662 | 135.0501 | 135.0501 | 0 | 0
2025-07-07 04:00 | 27.9 | 70.5 | 70 | 25.3342 | 19.7477 | 60.1515 | 130.6821 | 130.6821 | 0 | 0
2025-07-07 05:00 | 28.05 | 68.5 | 70 | 25.3856 | 19.6633 | 59.3284 | 126.1188 | 126.1188 | 0 | 0
2025-07-07 06:00 | 28.55 | 65 | 100 | 25.5536 | 19.5975 | 57.991 | 172.2781 | 172.2781 | 0 | 0
2025-07-07 07:00 | 30.2 | 58 | 100 | 26.0966 | 19.662 | 55.5094 | 164.5977 | 164.5977 | 0 | 0
2025-07-07 08:00 | 32.4 | 49.5 | 100 | 26.805 | 19.71 | 52.229 | 152.4959 | 152.4959 | 0 | 0
2025-07-07 09:00 | 34.5 | 40.5 | 100 | 27.4721 | 19.5467 | 48.1452 | 128.223 | 128.223 | 0 | 0
2025-07-07 10:00 | 36.4 | 32.5 | 100 | 28.0699 | 19.2778 | 44.0417 | 99.1698 | 99.1698 | 0 | 0
2025-07-07 11:00 | 37.85 | 28 | 100 | 28.515 | 19.1646 | 41.6019 | 83.196 | 83.196 | 0 | 0
2025-07-07 12:00 | 38.35 | 29.5 | 100 | 28.6474 | 19.4812 | 42.7148 | 100.047 | 100.047 | 0 | 0
2025-07-07 13:00 | 37.95 | 34.5 | 100 | 28.5019 | 19.954 | 45.8347 | 132.5818 | 132.5818 | 0 | 0
2025-07-07 14:00 | 37.5 | 37 | 100 | 28.3599 | 20.1021 | 47.2554 | 144.8932 | 144.8932 | 0 | 0
2025-07-07 15:00 | 37 | 39.5 | 100 | 28.2041 | 20.2226 | 48.6102 | 155.802 | 155.802 | 0 | 0
2025-07-07 16:00 | 36.15 | 42.5 | 100 | 27.9461 | 20.2706 | 50.0549 | 164.3046 | 164.3046 | 0 | 0
2025-07-07 17:00 | 34.95 | 46.5 | 100 | 27.5803 | 20.2809 | 51.827 | 172.691 | 172.691 | 0 | 0
2025-07-07 18:00 | 33.55 | 53 | 100 | 27.1424 | 20.4157 | 54.741 | 190.632 | 190.632 | 0 | 0
2025-07-07 19:00 | 32.55 | 58 | 100 | 26.8264 | 20.502 | 56.8504 | 202.9231 | 202.9231 | 0 | 0
2025-07-07 20:00 | 31.9 | 62.5 | 100 | 26.6168 | 20.6429 | 58.7971 | 216.5528 | 216.5528 | 0 | 0
2025-07-07 21:00 | 31.4 | 66.5 | 100 | 26.4541 | 20.7797 | 60.509 | 228.9754 | 228.9754 | 0 | 0
2025-07-07 22:00 | 30.95 | 68.5 | 70 | 26.3111 | 20.7652 | 61.1972 | 161.8116 | 161.8116 | 0 | 0
2025-07-07 23:00 | 30.4 | 69 | 70 | 26.1392 | 20.5929 | 61.0561 | 156.5572 | 156.5572 | 0 | 0
2025-07-08 | 29.75 | 69.5 | 70 | 25.9336 | 20.3809 | 60.8556 | 150.0895 | 150.0895 | 0 | 0
2025-07-08 01:00 | 29.05 | 70.5 | 70 | 25.7086 | 20.1865 | 60.8698 | 144.7303 | 144.7303 | 0 | 0
2025-07-08 02:00 | 28.5 | 71.5 | 70 | 25.5294 | 20.0471 | 60.9802 | 141.1856 | 141.1856 | 0 | 0
2025-07-08 03:00 | 28.05 | 73 | 70 | 25.3809 | 19.9804 | 61.379 | 140.4064 | 140.4064 | 0 | 0
2025-07-08 04:00 | 28.1 | 72 | 70 | 25.3983 | 19.9295 | 60.9539 | 137.8432 | 137.8432 | 0 | 0
2025-07-08 05:00 | 28.25 | 69.5 | 70 | 25.4502 | 19.81 | 59.899 | 131.6602 | 131.6602 | 0 | 0
2025-07-08 06:00 | 28.55 | 66.5 | 100 | 25.5518 | 19.7071 | 58.6844 | 179.2414 | 179.2414 | 0 | 0
2025-07-08 07:00 | 30.1 | 59.5 | 100 | 26.0621 | 19.7452 | 56.1915 | 170.5646 | 170.5646 | 0 | 0
2025-07-08 08:00 | 32.25 | 51 | 100 | 26.7547 | 19.7914 | 52.949 | 158.6561 | 158.6561 | 0 | 0
2025-07-08 09:00 | 34.25 | 42 | 100 | 27.3915 | 19.6168 | 48.8958 | 134.1476 | 134.1476 | 0 | 0
2025-07-08 10:00 | 36 | 34 | 100 | 27.9452 | 19.3274 | 44.8266 | 104.6145 | 104.6145 | 0 | 0
2025-07-08 11:00 | 37.4 | 29.5 | 100 | 28.3766 | 19.2207 | 42.44 | 89.2053 | 89.2053 | 0 | 0
2025-07-08 12:00 | 38.1 | 28.5 | 100 | 28.5832 | 19.294 | 41.9854 | 89.6134 | 89.6134 | 0 | 0
2025-07-08 13:00 | 38.15 | 28 | 100 | 28.6007 | 19.2469 | 41.6767 | 86.4469 | 86.4469 | 0 | 0
2025-07-08 14:00 | 37.95 | 26.5 | 100 | 28.5532 | 19.0114 | 40.6567 | 73.0703 | 73.0703 | 0 | 0
2025-07-08 15:00 | 37.5 | 26.5 | 100 | 28.4234 | 18.8919 | 40.5634 | 68.4577 | 68.4577 | 0 | 0
2025-07-08 16:00 | 36.75 | 28.5 | 100 | 28.1935 | 18.9246 | 41.665 | 75.0967 | 75.0967 | 0 | 0
2025-07-08 17:00 | 35.8 | 31 | 100 | 27.9007 | 18.942 | 42.9731 | 82.1142 | 82.1142 | 0 | 0
2025-07-08 18:00 | 34.8 | 32.5 | 100 | 27.5946 | 18.8208 | 43.6161 | 80.8904 | 80.8904 | 0 | 0
2025-07-08 19:00 | 33.75 | 35 | 100 | 27.2654 | 18.7742 | 44.782 | 84.6997 | 84.6997 | 0 | 0
2025-07-08 20:00 | 32.6 | 40.5 | 100 | 26.8925 | 18.9577 | 47.4795 | 103.654 | 103.654 | 0 | 0
2025-07-08 21:00 | 31.55 | 46.5 | 100 | 26.5482 | 19.1657 | 50.2872 | 123.6814 | 123.6814 | 0 | 0
2025-07-08 22:00 | 30.7 | 50 | 70 | 26.2713 | 19.1843 | 51.7427 | 91.4571 | 91.4571 | 0 | 0
2025-07-08 23:00 | 29.95 | 52.5 | 70 | 26.0262 | 19.1366 | 52.6798 | 93.0169 | 93.0169 | 0 | 0
2025-07-09 | 29.2 | 54.5 | 70 | 25.7797 | 19.0392 | 53.3395 | 92.4236 | 92.4236 | 0 | 0
2025-07-09 01:00 | 28.45 | 54.5 | 70 | 25.5331 | 18.7829 | 53.0413 | 84.9288 | 84.9288 | 0 | 0
2025-07-09 02:00 | 27.75 | 53 | 70 | 25.3012 | 18.435 | 52.0995 | 73.287 | 73.287 | 0 | 0
2025-07-09 03:00 | 27.15 | 51.5 | 70 | 25.0997 | 18.1257 | 51.2359 | 62.9906 | 62.9906 | 0 | 0
2025-07-09 04:00 | 27.15 | 50 | 70 | 25.1008 | 18.0168 | 50.5631 | 58.3004 | 58.3004 | 0 | 0
2025-07-09 05:00 | 27.25 | 48.5 | 70 | 25.136 | 17.939 | 49.9128 | 54.4566 | 54.4566 | 0 | 0
2025-07-09 06:00 | 27.8 | 44.5 | 100 | 25.3261 | 17.8124 | 48.2116 | 66.0952 | 66.0952 | 0 | 0
2025-07-09 07:00 | 29.85 | 37.5 | 100 | 26.0188 | 17.8675 | 45.2566 | 54.9943 | 54.9943 | 0 | 0
2025-07-09 08:00 | 32.45 | 31.5 | 100 | 26.8709 | 18.0655 | 42.574 | 49.4306 | 49.4306 | 0 | 0
2025-07-09 09:00 | 34.8 | 27 | 100 | 27.6171 | 18.242 | 40.3865 | 44.8938 | 44.8938 | 0 | 0
2025-07-09 10:00 | 36.75 | 23 | 100 | 28.2232 | 18.2892 | 38.2163 | 35.6239 | 35.6239 | 0 | 0
2025-07-09 11:00 | 37.95 | 21.5 | 100 | 28.5849 | 18.4013 | 37.3982 | 35.2073 | 35.2073 | 0 | 0
2025-07-09 12:00 | 38.45 | 22.5 | 100 | 28.723 | 18.648 | 38.1202 | 47.3807 | 47.3807 | 0 | 0
2025-07-09 13:00 | 38.65 | 23 | 100 | 28.777 | 18.7606 | 38.4856 | 53.1645 | 53.1645 | 0 | 0
2025-07-09 14:00 | 38.55 | 23.5 | 100 | 28.7449 | 18.7976 | 38.8051 | 56.1533 | 56.1533 | 0 | 0
2025-07-09 15:00 | 38.1 | 25.5 | 100 | 28.6027 | 18.9288 | 40.0393 | 67.087 | 67.087 | 0 | 0
2025-07-09 16:00 | 37.15 | 29 | 100 | 28.3073 | 19.0906 | 42.0729 | 82.9867 | 82.9867 | 0 | 0
2025-07-09 17:00 | 36 | 33 | 100 | 27.9501 | 19.2165 | 44.2374 | 98.0056 | 98.0056 | 0 | 0
2025-07-09 18:00 | 34.8 | 38.5 | 100 | 27.5698 | 19.4376 | 47.1097 | 119.5443 | 119.5443 | 0 | 0
2025-07-09 19:00 | 33.6 | 44.5 | 100 | 27.1867 | 19.6469 | 50.0475 | 140.624 | 140.624 | 0 | 0
2025-07-09 20:00 | 32.65 | 48 | 100 | 26.8861 | 19.6588 | 51.5432 | 147.6284 | 147.6284 | 0 | 0
2025-07-09 21:00 | 31.75 | 50 | 100 | 26.6023 | 19.5351 | 52.1952 | 145.7598 | 145.7598 | 0 | 0
2025-07-09 22:00 | 30.8 | 52.5 | 70 | 26.298 | 19.4254 | 53.0501 | 101.6893 | 101.6893 | 0 | 0
2025-07-09 23:00 | 29.9 | 56 | 70 | 26.0042 | 19.3983 | 54.3767 | 104.8875 | 104.8875 | 0 | 0
2025-07-10 | 29.15 | 59.5 | 70 | 25.7564 | 19.4057 | 55.708 | 108.9424 | 108.9424 | 0 | 0
2025-07-10 01:00 | 28.45 | 60 | 70 | 25.5267 | 19.1938 | 55.6086 | 103.0624 | 103.0624 | 0 | 0
2025-07-10 02:00 | 27.8 | 57 | 70 | 25.3142 | 18.7455 | 53.9463 | 86.5987 | 86.5987 | 0 | 0
2025-07-10 03:00 | 27.2 | 52.5 | 70 | 25.1159 | 18.2146 | 51.7005 | 66.5832 | 66.5832 | 0 | 0
2025-07-10 04:00 | 27.4 | 45.5 | 70 | 25.1895 | 17.763 | 48.5925 | 46.2412 | 46.2412 | 0 | 0
2025-07-10 05:00 | 27.9 | 39.5 | 70 | 25.3648 | 17.4562 | 45.9276 | 30.7724 | 30.7724 | 0 | 0
2025-07-10 06:00 | 28.75 | 35.5 | 100 | 25.6561 | 17.3826 | 44.1455 | 33.5553 | 33.5553 | 0 | 0
2025-07-10 07:00 | 30.8 | 31 | 100 | 26.3419 | 17.5655 | 42.1174 | 30.4079 | 30.4079 | 0 | 0
2025-07-10 08:00 | 33.1 | 28.5 | 100 | 27.0848 | 17.9467 | 41.0263 | 38.0633 | 38.0633 | 0 | 0
2025-07-10 09:00 | 35.3 | 26 | 100 | 27.7735 | 18.2629 | 39.8668 | 43.0757 | 43.0757 | 0 | 0
2025-07-10 10:00 | 37.15 | 23.5 | 100 | 28.3387 | 18.4488 | 38.5793 | 42.863 | 42.863 | 0 | 0
2025-07-10 11:00 | 38.35 | 24 | 100 | 28.6842 | 18.8117 | 39.089 | 57.9444 | 57.9444 | 0 | 0
2025-07-10 12:00 | 38.95 | 25 | 100 | 28.848 | 19.0905 | 39.8728 | 71.6917 | 71.6917 | 0 | 0
2025-07-10 13:00 | 39.35 | 23 | 100 | 28.9756 | 18.936 | 38.6059 | 59.8275 | 59.8275 | 0 | 0
2025-07-10 14:00 | 39.55 | 20.5 | 100 | 29.0512 | 18.6553 | 36.9355 | 41.5278 | 41.5278 | 0 | 0
2025-07-10 15:00 | 39.1 | 21 | 100 | 28.9197 | 18.6119 | 37.2199 | 41.6175 | 41.6175 | 0 | 0
2025-07-10 16:00 | 38.45 | 22.5 | 100 | 28.7231 | 18.6461 | 38.131 | 47.5131 | 47.5131 | 0 | 0
2025-07-10 17:00 | 37.4 | 25.5 | 100 | 28.4003 | 18.7472 | 39.9048 | 60.0845 | 60.0845 | 0 | 0
2025-07-10 18:00 | 35.75 | 32 | 100 | 27.8811 | 19.0373 | 43.5604 | 88.2932 | 88.2932 | 0 | 0
2025-07-10 19:00 | 34.15 | 42 | 100 | 27.3615 | 19.5836 | 48.8663 | 132.9105 | 132.9105 | 0 | 0
2025-07-10 20:00 | 32.85 | 53 | 100 | 26.9322 | 20.1737 | 54.3342 | 179.3179 | 179.3179 | 0 | 0
2025-07-10 21:00 | 31.8 | 61 | 100 | 26.5901 | 20.4825 | 57.9431 | 206.5803 | 206.5803 | 0 | 0
2025-07-10 22:00 | 31 | 61.5 | 70 | 26.3418 | 20.2305 | 57.6983 | 136.9162 | 136.9162 | 0 | 0
2025-07-10 23:00 | 30.45 | 59 | 70 | 26.1742 | 19.8311 | 56.1291 | 121.5129 | 121.5129 | 0 | 0
2025-07-11 | 29.85 | 60.5 | 70 | 25.9805 | 19.7334 | 56.546 | 120.0956 | 120.0956 | 0 | 0
2025-07-11 01:00 | 29.2 | 64 | 70 | 25.7661 | 19.7633 | 57.8763 | 124.7166 | 124.7166 | 0 | 0
2025-07-11 02:00 | 28.4 | 66.5 | 70 | 25.5027 | 19.6513 | 58.5998 | 123.7235 | 123.7235 | 0 | 0
2025-07-11 03:00 | 27.5 | 66 | 70 | 25.2058 | 19.2832 | 57.8852 | 111.8229 | 111.8229 | 0 | 0
2025-07-11 04:00 | 27.6 | 64 | 70 | 25.2409 | 19.1788 | 57.0326 | 106.6601 | 106.6601 | 0 | 0
2025-07-11 05:00 | 28.1 | 63.5 | 70 | 25.4074 | 19.3245 | 57.0517 | 110.5823 | 110.5823 | 0 | 0
2025-07-11 06:00 | 29.15 | 61 | 100 | 25.7542 | 19.5195 | 56.4164 | 162.8241 | 162.8241 | 0 | 0
2025-07-11 07:00 | 31.95 | 58 | 100 | 26.6438 | 20.2876 | 56.4701 | 192.7305 | 192.7305 | 0 | 0
2025-07-11 08:00 | 35.3 | 50.5 | 100 | 27.6642 | 20.7922 | 54.3293 | 203.335 | 203.335 | 0 | 0
2025-07-11 09:00 | 38.3 | 36.5 | 100 | 28.5863 | 20.2931 | 47.2563 | 151.7682 | 151.7682 | 0 | 0
2025-07-11 10:00 | 40.75 | 25.5 | 100 | 29.3414 | 19.6277 | 40.6527 | 94.5995 | 94.5995 | 0 | 0
2025-07-11 11:00 | 42.45 | 19.5 | 100 | 29.8568 | 19.2099 | 36.6519 | 58.7157 | 58.7157 | 0 | 0
2025-07-11 12:00 | 42.5 | 23 | 100 | 29.832 | 19.7329 | 39.3016 | 91.3307 | 91.3307 | 0 | 0
2025-07-11 13:00 | 40.55 | 31 | 100 | 29.2386 | 20.2912 | 44.4822 | 138.2707 | 138.2707 | 0 | 0
2025-07-11 14:00 | 38.95 | 36.5 | 100 | 28.7642 | 20.4902 | 47.5613 | 160.7987 | 160.7987 | 0 | 0
2025-07-11 15:00 | 38.5 | 43 | 100 | 28.596 | 21.0911 | 51.6119 | 202.9615 | 202.9615 | 0 | 0
2025-07-11 16:00 | 37.8 | 49 | 100 | 28.3674 | 21.5051 | 55.033 | 234.8858 | 234.8858 | 0 | 0
2025-07-11 17:00 | 36.85 | 53.5 | 100 | 28.0828 | 21.6327 | 57.1725 | 249.4591 | 249.4591 | 0 | 0
2025-07-11 18:00 | 35.8 | 57.5 | 100 | 27.7724 | 21.6418 | 58.7996 | 256.8359 | 256.8359 | 0 | 0
2025-07-11 19:00 | 34.65 | 63 | 100 | 27.4246 | 21.7193 | 61.083 | 269.6172 | 269.6172 | 0 | 0
2025-07-11 20:00 | 33.6 | 70 | 100 | 27.0979 | 21.9202 | 64.092 | 290.2643 | 290.2643 | 0 | 0
2025-07-11 21:00 | 32.9 | 74 | 100 | 26.8821 | 21.9707 | 65.6198 | 298.5108 | 298.5108 | 0 | 0
2025-07-11 22:00 | 32.5 | 75 | 70 | 26.7621 | 21.8893 | 65.7837 | 207.0147 | 207.0147 | 0 | 0
2025-07-11 23:00 | 31.75 | 79 | 70 | 26.5293 | 21.8966 | 67.1671 | 211.0267 | 211.0267 | 0 | 0
2025-07-12 | 30.75 | 86.5 | 70 | 26.2118 | 22.0373 | 69.968 | 222.7773 | 222.7773 | 0 | 0
2025-07-12 01:00 | 30 | 93 | 70 | 25.9711 | 22.1743 | 72.3572 | 233.2067 | 233.2067 | 0 | 0
2025-07-12 02:00 | 29.45 | 97 | 70 | 25.7955 | 22.2053 | 73.666 | 237.537 | 237.537 | 0 | 0
2025-07-12 03:00 | 29 | 99 | 70 | 25.653 | 22.1388 | 74.1093 | 236.6367 | 236.6367 | 0 | 0
2025-07-12 04:00 | 29.7 | 88.5 | 70 | 25.8865 | 21.7325 | 69.9069 | 213.51 | 213.51 | 0 | 0
2025-07-12 05:00 | 30.5 | 76.5 | 70 | 26.1557 | 21.1992 | 64.8177 | 184.1918 | 184.1918 | 0 | 0
2025-07-12 06:00 | 31.2 | 70.5 | 100 | 26.3837 | 21.019 | 62.379 | 246.0728 | 246.0728 | 0 | 0
2025-07-12 07:00 | 33 | 59.5 | 100 | 26.9572 | 20.7971 | 57.9187 | 218.846 | 218.846 | 0 | 0
2025-07-12 08:00 | 35.1 | 49.5 | 100 | 27.6112 | 20.6278 | 53.6178 | 193.6489 | 193.6489 | 0 | 0
2025-07-12 09:00 | 37.25 | 41 | 100 | 28.266 | 20.4691 | 49.6332 | 169.4983 | 169.4983 | 0 | 0
2025-07-12 10:00 | 39.3 | 33 | 100 | 28.8858 | 20.1809 | 45.3448 | 138.1824 | 138.1824 | 0 | 0
2025-07-12 11:00 | 41.05 | 27.5 | 100 | 29.4036 | 19.9776 | 42.1611 | 114.7983 | 114.7983 | 0 | 0
2025-07-12 12:00 | 42.25 | 25 | 100 | 29.745 | 19.9563 | 40.7183 | 106.6114 | 106.6114 | 0 | 0
2025-07-12 13:00 | 42.35 | 27 | 100 | 29.7494 | 20.2631 | 42.2484 | 125.7479 | 125.7479 | 0 | 0
2025-07-12 14:00 | 41.25 | 33 | 100 | 29.4038 | 20.7545 | 46.1968 | 164.0001 | 164.0001 | 0 | 0
2025-07-12 15:00 | 40.2 | 36 | 100 | 29.1025 | 20.815 | 47.8121 | 174.2145 | 174.2145 | 0 | 0
2025-07-12 16:00 | 39.65 | 36 | 100 | 28.9567 | 20.6463 | 47.5442 | 166.5118 | 166.5118 | 0 | 0
2025-07-12 17:00 | 38.8 | 36.5 | 100 | 28.7235 | 20.4459 | 47.4808 | 158.5971 | 158.5971 | 0 | 0
2025-07-12 18:00 | 37.9 | 39.5 | 100 | 28.456 | 20.5097 | 49.0088 | 168.2157 | 168.2157 | 0 | 0
2025-07-12 19:00 | 36.95 | 44 | 100 | 28.1647 | 20.6928 | 51.3538 | 186.0429 | 186.0429 | 0 | 0
2025-07-12 20:00 | 35.95 | 49 | 100 | 27.8568 | 20.87 | 53.8217 | 204.016 | 204.016 | 0 | 0
2025-07-12 21:00 | 35.6 | 50.5 | 100 | 27.7502 | 20.898 | 54.4972 | 208.0589 | 208.0589 | 0 | 0
2025-07-12 22:00 | 35.35 | 49 | 70 | 27.6856 | 20.6649 | 53.4639 | 136.0566 | 136.0566 | 0 | 0
2025-07-12 23:00 | 34.75 | 49.5 | 70 | 27.5096 | 20.5082 | 53.4146 | 131.6463 | 131.6463 | 0 | 0
2025-07-13 | 34.1 | 50.5 | 70 | 27.3148 | 20.3799 | 53.6244 | 128.8259 | 128.8259 | 0 | 0
2025-07-13 01:00 | 33.4 | 50.5 | 70 | 27.1062 | 20.1397 | 53.2494 | 121.2171 | 121.2171 | 0 | 0
2025-07-13 02:00 | 32.55 | 49.5 | 70 | 26.8512 | 19.762 | 52.2832 | 108.1733 | 108.1733 | 0 | 0
2025-07-13 03:00 | 31.8 | 48.5 | 70 | 26.6217 | 19.4237 | 51.4162 | 96.6142 | 96.6142 | 0 | 0
2025-07-13 04:00 | 32.1 | 47 | 70 | 26.7191 | 19.391 | 50.7513 | 93.719 | 93.719 | 0 | 0
2025-07-13 05:00 | 32.65 | 47 | 70 | 26.8891 | 19.5713 | 50.9816 | 99.1385 | 99.1385 | 0 | 0
2025-07-13 06:00 | 32.7 | 55 | 100 | 26.8809 | 20.2991 | 55.3019 | 188.0747 | 188.0747 | 0 | 0
2025-07-13 07:00 | 34 | 59 | 100 | 27.2538 | 21.1206 | 58.316 | 233.3719 | 233.3719 | 0 | 0
2025-07-13 08:00 | 36.7 | 45 | 100 | 28.0892 | 20.7165 | 51.8192 | 188.9241 | 188.9241 | 0 | 0
2025-07-13 09:00 | 39.6 | 28 | 100 | 29.0066 | 19.648 | 42.0459 | 102.174 | 102.174 | 0 | 0
2025-07-13 10:00 | 42.25 | 19.5 | 100 | 29.8033 | 19.1676 | 36.5991 | 56.6654 | 56.6654 | 0 | 0
2025-07-13 11:00 | 44.3 | 16 | 100 | 30.3853 | 19.0956 | 34.2079 | 40.9168 | 40.9168 | 0 | 0
2025-07-13 12:00 | 45.7 | 14 | 100 | 30.7735 | 19.0599 | 32.7427 | 31.3187 | 31.3187 | 0 | 0
2025-07-13 13:00 | 46.4 | 12.5 | 100 | 30.9746 | 18.9366 | 31.543 | 20.2401 | 20.2401 | 0 | 0
2025-07-13 14:00 | 45.8 | 16.5 | 100 | 30.7608 | 19.5067 | 34.8649 | 58.9142 | 58.9142 | 0 | 0
2025-07-13 15:00 | 43.8 | 26 | 100 | 30.1289 | 20.5126 | 42.0198 | 133.788 | 133.788 | 0 | 0
2025-07-13 16:00 | 41.25 | 35.5 | 100 | 29.3796 | 21.0741 | 47.9956 | 185.047 | 185.047 | 0 | 0
2025-07-13 17:00 | 39 | 44.5 | 100 | 28.7184 | 21.4258 | 52.8954 | 221.9368 | 221.9368 | 0 | 0
2025-07-13 18:00 | 37.35 | 51 | 100 | 28.2335 | 21.5574 | 55.974 | 241.068 | 241.068 | 0 | 0
2025-07-13 19:00 | 36.45 | 53.5 | 100 | 27.9732 | 21.4905 | 56.8739 | 242.2957 | 242.2957 | 0 | 0
2025-07-13 20:00 | 36 | 53.5 | 100 | 27.8482 | 21.3304 | 56.5539 | 234.4046 | 234.4046 | 0 | 0
2025-07-13 21:00 | 35.35 | 56.5 | 100 | 27.6512 | 21.3839 | 57.8641 | 242.2027 | 242.2027 | 0 | 0
2025-07-13 22:00 | 35 | 55 | 70 | 27.5584 | 21.1168 | 56.7479 | 158.6487 | 158.6487 | 0 | 0
2025-07-13 23:00 | 34.9 | 48 | 70 | 27.5596 | 20.4136 | 52.6397 | 126.7521 | 126.7521 | 0 | 0
2025-07-14 | 34.55 | 43 | 70 | 27.4771 | 19.8105 | 49.5898 | 101.1444 | 101.1444 | 0 | 0
2025-07-14 01:00 | 34.1 | 39.5 | 70 | 27.3558 | 19.3247 | 47.4199 | 81.6615 | 81.6615 | 0 | 0
2025-07-14 02:00 | 33.45 | 39.5 | 70 | 27.158 | 19.1253 | 47.2006 | 75.874 | 75.874 | 0 | 0
2025-07-14 03:00 | 32.75 | 41.5 | 70 | 26.9362 | 19.0983 | 48.0625 | 77.908 | 77.908 | 0 | 0
2025-07-14 04:00 | 32.45 | 41.5 | 70 | 26.843 | 19.005 | 47.9612 | 75.2056 | 75.2056 | 0 | 0
2025-07-14 05:00 | 32.25 | 39.5 | 70 | 26.786 | 18.76 | 46.8284 | 65.4247 | 65.4247 | 0 | 0
2025-07-14 06:00 | 32.85 | 36.5 | 100 | 26.9821 | 18.6583 | 45.3697 | 83.163 | 83.163 | 0 | 0
2025-07-14 07:00 | 35.4 | 31.5 | 100 | 27.7792 | 18.8876 | 43.1551 | 80.8056 | 80.8056 | 0 | 0
2025-07-14 08:00 | 38.6 | 28 | 100 | 28.7281 | 19.3727 | 41.7777 | 91.176 | 91.176 | 0 | 0
2025-07-14 09:00 | 41.2 | 23 | 100 | 29.486 | 19.4062 | 38.9706 | 77.8596 | 77.8596 | 0 | 0
2025-07-14 10:00 | 43.45 | 17.5 | 100 | 30.1443 | 19.1402 | 35.2807 | 48.6712 | 48.6712 | 0 | 0
2025-07-14 11:00 | 45.45 | 15 | 100 | 30.6951 | 19.175 | 33.5565 | 40.1027 | 40.1027 | 0 | 0
2025-07-14 12:00 | 46.4 | 14 | 100 | 30.9504 | 19.2012 | 32.8373 | 36.8768 | 36.8768 | 0 | 0
2025-07-14 13:00 | 46.05 | 16 | 100 | 30.831 | 19.4741 | 34.4946 | 55.8268 | 55.8268 | 0 | 0
2025-07-14 14:00 | 45.15 | 18.5 | 100 | 30.5682 | 19.6873 | 36.4099 | 74.1135 | 74.1135 | 0 | 0
2025-07-14 15:00 | 43.7 | 22 | 100 | 30.154 | 19.8853 | 38.8661 | 94.6026 | 94.6026 | 0 | 0
2025-07-14 16:00 | 41.9 | 25.5 | 100 | 29.648 | 19.9283 | 41.0041 | 107.4554 | 107.4554 | 0 | 0
2025-07-14 17:00 | 40.35 | 29.5 | 100 | 29.1982 | 20.0402 | 43.3635 | 123.5542 | 123.5542 | 0 | 0
2025-07-14 18:00 | 38.5 | 39 | 100 | 28.6239 | 20.6394 | 49.0002 | 173.3651 | 173.3651 | 0 | 0
2025-07-14 19:00 | 37.2 | 46 | 100 | 28.2223 | 20.9838 | 52.7611 | 204.0237 | 204.0237 | 0 | 0
2025-07-14 20:00 | 36.75 | 46 | 100 | 28.0974 | 20.8332 | 52.4947 | 196.8951 | 196.8951 | 0 | 0
2025-07-14 21:00 | 36.05 | 46 | 100 | 27.8999 | 20.5999 | 52.099 | 186.0008 | 186.0008 | 0 | 0
2025-07-14 22:00 | 35.1 | 49.5 | 70 | 27.611 | 20.626 | 53.6342 | 135.683 | 135.683 | 0 | 0
2025-07-14 23:00 | 34.45 | 53 | 70 | 27.4077 | 20.7329 | 55.2615 | 143.5971 | 143.5971 | 0 | 0
2025-07-15 | 34.55 | 52 | 70 | 27.4409 | 20.6738 | 54.7557 | 140.4632 | 140.4632 | 0 | 0
2025-07-15 01:00 | 34.55 | 48.5 | 70 | 27.455 | 20.3419 | 52.7585 | 125.3177 | 125.3177 | 0 | 0
2025-07-15 02:00 | 33.9 | 49 | 70 | 27.2608 | 20.1692 | 52.7002 | 120.4935 | 120.4935 | 0 | 0
2025-07-15 03:00 | 33.45 | 51.5 | 70 | 27.1177 | 20.2461 | 53.8484 | 126.0584 | 126.0584 | 0 | 0
2025-07-15 04:00 | 32.65 | 56 | 70 | 26.8626 | 20.3657 | 55.8376 | 135.2739 | 135.2739 | 0 | 0
2025-07-15 05:00 | 32.05 | 57 | 70 | 26.677 | 20.2378 | 56.0158 | 132.2967 | 132.2967 | 0 | 0
2025-07-15 06:00 | 33.15 | 48.5 | 100 | 27.0372 | 19.8713 | 52.0444 | 157.8249 | 157.8249 | 0 | 0
2025-07-15 07:00 | 35.6 | 38 | 100 | 27.8087 | 19.6323 | 47.0966 | 126.4969 | 126.4969 | 0 | 0
2025-07-15 08:00 | 38.75 | 29.5 | 100 | 28.7597 | 19.5949 | 42.823 | 104.5056 | 104.5056 | 0 | 0
2025-07-15 09:00 | 41.75 | 23 | 100 | 29.6337 | 19.5424 | 39.1097 | 83.5614 | 83.5614 | 0 | 0
2025-07-15 10:00 | 44 | 17.5 | 100 | 30.2881 | 19.2634 | 35.3755 | 53.5327 | 53.5327 | 0 | 0
2025-07-15 11:00 | 45.55 | 14.5 | 100 | 30.728 | 19.1086 | 33.1601 | 35.7083 | 35.7083 | 0 | 0
2025-07-15 12:00 | 46.55 | 13 | 100 | 31.0045 | 19.0508 | 32.0018 | 27.0707 | 27.0707 | 0 | 0
2025-07-15 13:00 | 45.4 | 19.5 | 100 | 30.6159 | 19.9092 | 37.2963 | 86.8741 | 86.8741 | 0 | 0
2025-07-15 14:00 | 43.45 | 27 | 100 | 30.0289 | 20.5588 | 42.6818 | 139.2212 | 139.2212 | 0 | 0
2025-07-15 15:00 | 43 | 26.5 | 100 | 29.9213 | 20.3634 | 42.1298 | 129.2106 | 129.2106 | 0 | 0
2025-07-15 16:00 | 42.1 | 26 | 100 | 29.6951 | 20.0504 | 41.4441 | 114.2352 | 114.2352 | 0 | 0
2025-07-15 17:00 | 40.65 | 27 | 100 | 29.3009 | 19.7949 | 41.7116 | 106.4142 | 106.4142 | 0 | 0
2025-07-15 18:00 | 39 | 33 | 100 | 28.8035 | 20.0868 | 45.2607 | 134.7544 | 134.7544 | 0 | 0
2025-07-15 19:00 | 37.6 | 38.5 | 100 | 28.3787 | 20.3007 | 48.2486 | 156.9987 | 156.9987 | 0 | 0
2025-07-15 20:00 | 37.25 | 36.5 | 100 | 28.2923 | 19.972 | 46.8275 | 137.889 | 137.889 | 0 | 0
2025-07-15 21:00 | 36.8 | 34.5 | 100 | 28.1752 | 19.6158 | 45.4045 | 117.9445 | 117.9445 | 0 | 0
2025-07-15 22:00 | 35.8 | 36.5 | 70 | 27.8744 | 19.5349 | 46.2751 | 83.3727 | 83.3727 | 0 | 0
2025-07-15 23:00 | 34.8 | 41 | 70 | 27.5594 | 19.6901 | 48.5516 | 94.7858 | 94.7858 | 0 | 0
2025-07-16 | 33.9 | 48 | 70 | 27.2645 | 20.0759 | 52.1364 | 116.2326 | 116.2326 | 0 | 0
2025-07-16 01:00 | 33.05 | 55.5 | 70 | 26.9847 | 20.4638 | 55.8074 | 137.8902 | 137.8902 | 0 | 0
2025-07-16 02:00 | 32.5 | 60.5 | 70 | 26.8041 | 20.6972 | 58.1447 | 151.223 | 151.223 | 0 | 0
2025-07-16 03:00 | 32.3 | 61.5 | 70 | 26.7409 | 20.708 | 58.5377 | 152.6428 | 152.6428 | 0 | 0
2025-07-16 04:00 | 33.15 | 46.5 | 70 | 27.0436 | 19.6878 | 50.9486 | 102.248 | 102.248 | 0 | 0
2025-07-16 05:00 | 33.75 | 33.5 | 70 | 27.2706 | 18.6259 | 43.9292 | 52.7476 | 52.7476 | 0 | 0
2025-07-16 06:00 | 34.7 | 32 | 100 | 27.5663 | 18.7431 | 43.2863 | 76.3744 | 76.3744 | 0 | 0
2025-07-16 07:00 | 37.15 | 26.5 | 100 | 28.3216 | 18.8033 | 40.4757 | 64.68 | 64.68 | 0 | 0
2025-07-16 08:00 | 39.35 | 23.5 | 100 | 28.9717 | 19.0032 | 38.9366 | 63.7218 | 63.7218 | 0 | 0
2025-07-16 09:00 | 41.5 | 21.5 | 100 | 29.5815 | 19.2703 | 37.952 | 67.7847 | 67.7847 | 0 | 0
2025-07-16 10:00 | 43.6 | 18.5 | 100 | 30.1715 | 19.3293 | 36.0895 | 59.6986 | 59.6986 | 0 | 0
2025-07-16 11:00 | 45.15 | 16 | 100 | 30.6041 | 19.2772 | 34.3442 | 48.1508 | 48.1508 | 0 | 0
2025-07-16 12:00 | 45.95 | 15 | 100 | 30.8216 | 19.2804 | 33.6314 | 44.2177 | 44.2177 | 0 | 0
2025-07-16 13:00 | 44.45 | 20.5 | 100 | 30.364 | 19.8408 | 37.8686 | 87.5336 | 87.5336 | 0 | 0
2025-07-16 14:00 | 41.95 | 28 | 100 | 29.6352 | 20.2876 | 42.8622 | 130.0575 | 130.0575 | 0 | 0
2025-07-16 15:00 | 40.3 | 31.5 | 100 | 29.1676 | 20.2814 | 44.7399 | 139.2898 | 139.2898 | 0 | 0
2025-07-16 16:00 | 38.85 | 36 | 100 | 28.7406 | 20.4 | 47.1869 | 155.6591 | 155.6591 | 0 | 0
2025-07-16 17:00 | 37.75 | 41.5 | 100 | 28.4016 | 20.6807 | 50.2293 | 180.6708 | 180.6708 | 0 | 0
2025-07-16 18:00 | 36.6 | 45.5 | 100 | 28.058 | 20.7312 | 52.1055 | 191.1875 | 191.1875 | 0 | 0
2025-07-16 19:00 | 35.4 | 49 | 100 | 27.6997 | 20.6793 | 53.519 | 195.4543 | 195.4543 | 0 | 0
2025-07-16 20:00 | 34.55 | 53 | 100 | 27.4369 | 20.768 | 55.3207 | 206.7651 | 206.7651 | 0 | 0
2025-07-16 21:00 | 33.75 | 56.5 | 100 | 27.1895 | 20.8042 | 56.7783 | 214.4131 | 214.4131 | 0 | 0
2025-07-16 22:00 | 32.9 | 58.5 | 70 | 26.9304 | 20.6731 | 57.3216 | 148.0501 | 148.0501 | 0 | 0
2025-07-16 23:00 | 32.1 | 61 | 70 | 26.6817 | 20.593 | 58.1341 | 148.2104 | 148.2104 | 0 | 0
2025-07-17 | 31.3 | 66.5 | 70 | 26.4234 | 20.7419 | 60.4346 | 158.9838 | 158.9838 | 0 | 0
2025-07-17 01:00 | 30.6 | 72 | 70 | 26.1956 | 20.8998 | 62.6847 | 169.7664 | 169.7664 | 0 | 0
2025-07-17 02:00 | 30.1 | 74.5 | 70 | 26.0352 | 20.8902 | 63.5289 | 171.8352 | 171.8352 | 0 | 0
2025-07-17 03:00 | 29.55 | 75.5 | 70 | 25.8606 | 20.7454 | 63.5886 | 167.8674 | 167.8674 | 0 | 0
2025-07-17 04:00 | 29.75 | 67 | 70 | 25.9378 | 20.1935 | 59.6425 | 141.4587 | 141.4587 | 0 | 0
2025-07-17 05:00 | 30.4 | 55.5 | 70 | 26.165 | 19.5326 | 54.365 | 108.3981 | 108.3981 | 0 | 0
2025-07-17 06:00 | 31.4 | 48.5 | 100 | 26.4963 | 19.2902 | 51.2608 | 132.4851 | 132.4851 | 0 | 0
2025-07-17 07:00 | 34.15 | 37 | 100 | 27.3802 | 19.0927 | 46.013 | 101.6998 | 101.6998 | 0 | 0
2025-07-17 08:00 | 38.1 | 25 | 100 | 28.6059 | 18.872 | 39.6943 | 63.0709 | 63.0709 | 0 | 0
2025-07-17 09:00 | 41.6 | 18 | 100 | 29.6428 | 18.7936 | 35.4051 | 37.6126 | 37.6126 | 0 | 0
2025-07-17 10:00 | 42.95 | 18 | 100 | 30.0064 | 19.1032 | 35.5901 | 49.1182 | 49.1182 | 0 | 0
2025-07-17 11:00 | 42 | 23.5 | 100 | 29.695 | 19.6785 | 39.5355 | 90.5169 | 90.5169 | 0 | 0
2025-07-17 12:00 | 41.15 | 27 | 100 | 29.4349 | 19.9358 | 41.8444 | 111.8096 | 111.8096 | 0 | 0
2025-07-17 13:00 | 41.45 | 25 | 100 | 29.5339 | 19.7432 | 40.4938 | 97.9705 | 97.9705 | 0 | 0
2025-07-17 14:00 | 41.5 | 22.5 | 100 | 29.5717 | 19.408 | 38.69 | 76.6876 | 76.6876 | 0 | 0
2025-07-17 15:00 | 41.05 | 22.5 | 100 | 29.4501 | 19.295 | 38.5941 | 72.2555 | 72.2555 | 0 | 0
2025-07-17 16:00 | 40.45 | 24 | 100 | 29.273 | 19.3463 | 39.5282 | 78.979 | 78.979 | 0 | 0
2025-07-17 17:00 | 39.55 | 26 | 100 | 29.0084 | 19.3734 | 40.6975 | 85.9794 | 85.9794 | 0 | 0
2025-07-17 18:00 | 38.15 | 31.5 | 100 | 28.5777 | 19.6641 | 43.9563 | 112.7272 | 112.7272 | 0 | 0
2025-07-17 19:00 | 36.55 | 39.5 | 100 | 28.0763 | 20.0832 | 48.3962 | 149.4097 | 149.4097 | 0 | 0
2025-07-17 20:00 | 35.55 | 43 | 100 | 27.7707 | 20.1309 | 50.0522 | 158.7847 | 158.7847 | 0 | 0
2025-07-17 21:00 | 34.9 | 43 | 100 | 27.5807 | 19.9221 | 49.7517 | 149.499 | 149.499 | 0 | 0
2025-07-17 22:00 | 33.9 | 46.5 | 70 | 27.27 | 19.9356 | 51.2886 | 109.8155 | 109.8155 | 0 | 0
2025-07-17 23:00 | 32.95 | 50.5 | 70 | 26.9702 | 19.9853 | 53.03 | 116.4891 | 116.4891 | 0 | 0
2025-07-18 | 32.4 | 52 | 70 | 26.798 | 19.9299 | 53.558 | 116.6173 | 116.6173 | 0 | 0
2025-07-18 01:00 | 32 | 56 | 70 | 26.6644 | 20.1358 | 55.4586 | 127.8381 | 127.8381 | 0 | 0
2025-07-18 02:00 | 31.55 | 55 | 70 | 26.5278 | 19.8928 | 54.694 | 119.0132 | 119.0132 | 0 | 0
2025-07-18 03:00 | 31.05 | 48.5 | 70 | 26.3857 | 19.1738 | 51.1238 | 89.3399 | 89.3399 | 0 | 0
2025-07-18 04:00 | 31.25 | 43.5 | 70 | 26.4602 | 18.8084 | 48.6287 | 72.3241 | 72.3241 | 0 | 0
2025-07-18 05:00 | 31.75 | 49 | 70 | 26.6048 | 19.4493 | 51.6679 | 98.1363 | 98.1363 | 0 | 0
2025-07-18 06:00 | 32.95 | 54 | 100 | 26.9594 | 20.2975 | 54.9215 | 186.5599 | 186.5599 | 0 | 0
2025-07-18 07:00 | 36 | 40 | 100 | 27.9156 | 19.9663 | 48.4474 | 145.0741 | 145.0741 | 0 | 0
2025-07-18 08:00 | 39.25 | 25.5 | 100 | 28.9286 | 19.2348 | 40.2661 | 78.5964 | 78.5964 | 0 | 0
2025-07-18 09:00 | 41.8 | 20.5 | 100 | 29.6722 | 19.2024 | 37.2703 | 61.6746 | 61.6746 | 0 | 0
2025-07-18 10:00 | 44.15 | 17 | 100 | 30.3334 | 19.2209 | 34.9922 | 49.7441 | 49.7441 | 0 | 0
2025-07-18 11:00 | 45.95 | 14 | 100 | 30.8371 | 19.1099 | 32.777 | 33.3153 | 33.3153 | 0 | 0
2025-07-18 12:00 | 46.15 | 15.5 | 100 | 30.8638 | 19.4124 | 34.0793 | 51.1763 | 51.1763 | 0 | 0
2025-07-18 13:00 | 44.25 | 23 | 100 | 30.2803 | 20.1806 | 39.8056 | 110.0114 | 110.0114 | 0 | 0
2025-07-18 14:00 | 42.3 | 31 | 100 | 29.6931 | 20.7966 | 45.2234 | 160.856 | 160.856 | 0 | 0
2025-07-18 15:00 | 41.65 | 36 | 100 | 29.4762 | 21.2599 | 48.5765 | 195.114 | 195.114 | 0 | 0
2025-07-18 16:00 | 41.45 | 39 | 100 | 29.3957 | 21.5767 | 50.6301 | 217.3318 | 217.3318 | 0 | 0
2025-07-18 17:00 | 40.4 | 43 | 100 | 29.0932 | 21.7192 | 52.7914 | 233.1733 | 233.1733 | 0 | 0
2025-07-18 18:00 | 38.9 | 47.5 | 100 | 28.6697 | 21.7246 | 54.8159 | 242.6506 | 242.6506 | 0 | 0
2025-07-18 19:00 | 38.4 | 48 | 100 | 28.5345 | 21.6071 | 54.7944 | 237.8068 | 237.8068 | 0 | 0
2025-07-18 20:00 | 38.15 | 46 | 100 | 28.4814 | 21.3053 | 53.3363 | 219.1874 | 219.1874 | 0 | 0
2025-07-18 21:00 | 37.5 | 44 | 100 | 28.3172 | 20.8721 | 51.6716 | 194.6104 | 194.6104 | 0 | 0
2025-07-18 22:00 | 36.85 | 42 | 70 | 28.1478 | 20.4459 | 50.0756 | 119.611 | 119.611 | 0 | 0
2025-07-18 23:00 | 36.05 | 44.5 | 70 | 27.9075 | 20.4465 | 51.1974 | 123.2287 | 123.2287 | 0 | 0
2025-07-19 | 35.05 | 49.5 | 70 | 27.5966 | 20.6084 | 53.609 | 135.1544 | 135.1544 | 0 | 0
2025-07-19 01:00 | 34.4 | 51 | 70 | 27.401 | 20.5279 | 54.0967 | 134.4493 | 134.4493 | 0 | 0
2025-07-19 02:00 | 33.9 | 49 | 70 | 27.2609 | 20.1692 | 52.6971 | 120.4688 | 120.4688 | 0 | 0
2025-07-19 03:00 | 33.25 | 47.5 | 70 | 27.0707 | 19.8123 | 51.5461 | 107.4116 | 107.4116 | 0 | 0
2025-07-19 04:00 | 32.8 | 56 | 70 | 26.9079 | 20.4193 | 55.9253 | 136.991 | 136.991 | 0 | 0
2025-07-19 05:00 | 32.6 | 64.5 | 70 | 26.8224 | 21.0714 | 60.3354 | 168.0572 | 168.0572 | 0 | 0
2025-07-19 06:00 | 33.4 | 58.5 | 100 | 27.0792 | 20.8548 | 57.6573 | 220.2054 | 220.2054 | 0 | 0
2025-07-19 07:00 | 35.85 | 42.5 | 100 | 27.86 | 20.1768 | 49.8908 | 159.7434 | 159.7434 | 0 | 0
2025-07-19 08:00 | 38.7 | 29 | 100 | 28.7492 | 19.5203 | 42.4747 | 100.0652 | 100.0652 | 0 | 0
2025-07-19 09:00 | 41.15 | 23.5 | 100 | 29.4678 | 19.4597 | 39.3272 | 81.7717 | 81.7717 | 0 | 0
2025-07-19 10:00 | 43.3 | 20 | 100 | 30.0752 | 19.4871 | 37.2013 | 71.3562 | 71.3562 | 0 | 0
2025-07-19 11:00 | 44.2 | 20 | 100 | 30.3072 | 19.703 | 37.4042 | 80.0664 | 80.0664 | 0 | 0
2025-07-19 12:00 | 43.7 | 23.5 | 100 | 30.1353 | 20.113 | 40.0349 | 108.9019 | 108.9019 | 0 | 0
2025-07-19 13:00 | 43.65 | 24 | 100 | 30.1164 | 20.1739 | 40.4144 | 113.1766 | 113.1766 | 0 | 0
2025-07-19 14:00 | 43.7 | 24 | 100 | 30.129 | 20.1856 | 40.4356 | 113.7988 | 113.7988 | 0 | 0
2025-07-19 15:00 | 42.9 | 25.5 | 100 | 29.9074 | 20.1927 | 41.3338 | 118.8622 | 118.8622 | 0 | 0
2025-07-19 16:00 | 41.45 | 31.5 | 100 | 29.47 | 20.6129 | 45.2312 | 154.2547 | 154.2547 | 0 | 0
2025-07-19 17:00 | 39.55 | 40 | 100 | 28.8979 | 21.0866 | 50.2344 | 196.5588 | 196.5588 | 0 | 0
2025-07-19 18:00 | 37.9 | 47 | 100 | 28.4071 | 21.3251 | 53.8409 | 222.5352 | 222.5352 | 0 | 0
2025-07-19 19:00 | 36.65 | 54.5 | 100 | 28.0223 | 21.6589 | 57.6539 | 252.7836 | 252.7836 | 0 | 0
2025-07-19 20:00 | 35.95 | 58 | 100 | 27.8112 | 21.7436 | 59.2282 | 262.9826 | 262.9826 | 0 | 0
2025-07-19 21:00 | 35.5 | 58.5 | 100 | 27.6837 | 21.6245 | 59.1753 | 257.8782 | 257.8782 | 0 | 0
2025-07-19 22:00 | 34.75 | 61.5 | 70 | 27.459 | 21.6214 | 60.3288 | 183.8209 | 183.8209 | 0 | 0
2025-07-19 23:00 | 33.7 | 72.5 | 70 | 27.1173 | 22.1678 | 65.5731 | 214.8156 | 214.8156 | 0 | 0
2025-07-20 | 32.85 | 83 | 70 | 26.8389 | 22.6636 | 70.3707 | 242.9392 | 242.9392 | 0 | 0
2025-07-20 01:00 | 32.35 | 86.5 | 70 | 26.6844 | 22.7197 | 71.6649 | 248.1325 | 248.1325 | 0 | 0
2025-07-20 02:00 | 31.8 | 88.5 | 70 | 26.519 | 22.6327 | 72.094 | 246.6227 | 246.6227 | 0 | 0
2025-07-20 03:00 | 31.25 | 89 | 70 | 26.3557 | 22.4321 | 71.7552 | 239.6082 | 239.6082 | 0 | 0
2025-07-20 04:00 | 31.25 | 84.5 | 70 | 26.3662 | 22.1022 | 69.5056 | 223.6509 | 223.6509 | 0 | 0
2025-07-20 05:00 | 31.4 | 78.5 | 70 | 26.4253 | 21.714 | 66.6281 | 204.3468 | 204.3468 | 0 | 0
2025-07-20 06:00 | 32.05 | 72.5 | 100 | 26.6354 | 21.5091 | 64.1206 | 273.492 | 273.492 | 0 | 0
2025-07-20 07:00 | 33.95 | 62.5 | 100 | 27.2257 | 21.4092 | 60.275 | 253.7099 | 253.7099 | 0 | 0
2025-07-20 08:00 | 36.4 | 50.5 | 100 | 27.9751 | 21.1722 | 55.0413 | 221.7176 | 221.7176 | 0 | 0
2025-07-20 09:00 | 38.3 | 41 | 100 | 28.5556 | 20.8018 | 50.2041 | 185.271 | 185.271 | 0 | 0
2025-07-20 10:00 | 39.35 | 38.5 | 100 | 28.8567 | 20.8481 | 49.106 | 181.9198 | 181.9198 | 0 | 0
2025-07-20 11:00 | 40.05 | 40.5 | 100 | 29.0247 | 21.3072 | 50.8594 | 208.0376 | 208.0376 | 0 | 0
2025-07-20 12:00 | 40.35 | 41.5 | 100 | 29.0933 | 21.5227 | 51.7372 | 220.6883 | 220.6883 | 0 | 0
2025-07-20 13:00 | 40.1 | 43 | 100 | 29.0161 | 21.6169 | 52.6177 | 228.5624 | 228.5624 | 0 | 0
2025-07-20 14:00 | 39.65 | 47 | 100 | 28.8672 | 21.9234 | 55.0398 | 252.001 | 252.001 | 0 | 0
2025-07-20 15:00 | 39.35 | 48.5 | 100 | 28.7781 | 21.9869 | 55.8339 | 258.1983 | 258.1983 | 0 | 0
2025-07-20 16:00 | 38.75 | 49.5 | 100 | 28.6152 | 21.8868 | 56.0539 | 255.1231 | 255.1231 | 0 | 0
2025-07-20 17:00 | 38.2 | 49 | 100 | 28.4739 | 21.6416 | 55.3346 | 241.9812 | 241.9812 | 0 | 0
2025-07-20 18:00 | 37.55 | 48.5 | 100 | 28.3026 | 21.3634 | 54.5747 | 227.4543 | 227.4543 | 0 | 0
2025-07-20 19:00 | 36.6 | 51.5 | 100 | 28.025 | 21.3409 | 55.7962 | 231.9342 | 231.9342 | 0 | 0
2025-07-20 20:00 | 35.8 | 55.5 | 100 | 27.7819 | 21.4487 | 57.6394 | 244.2544 | 244.2544 | 0 | 0
2025-07-20 21:00 | 35 | 60.5 | 100 | 27.5339 | 21.6236 | 59.9584 | 261.2105 | 261.2105 | 0 | 0
2025-07-20 22:00 | 34.3 | 64 | 70 | 27.3206 | 21.6733 | 61.3921 | 188.4701 | 188.4701 | 0 | 0
2025-07-20 23:00 | 33.65 | 67.5 | 70 | 27.1207 | 21.7261 | 62.8007 | 194.0614 | 194.0614 | 0 | 0
2025-07-21 | 32.85 | 75 | 70 | 26.8638 | 22.03 | 66.1436 | 212.372 | 212.372 | 0 | 0
2025-07-21 01:00 | 31.95 | 86 | 70 | 26.5694 | 22.5107 | 70.9869 | 239.9846 | 239.9846 | 0 | 0
2025-07-21 02:00 | 31.4 | 92 | 70 | 26.3928 | 22.7145 | 73.4232 | 252.6701 | 252.6701 | 0 | 0
2025-07-21 03:00 | 31.15 | 92.5 | 70 | 26.3179 | 22.6412 | 73.3889 | 250.3011 | 250.3011 | 0 | 0
2025-07-21 04:00 | 31.3 | 87 | 70 | 26.3753 | 22.3072 | 70.8039 | 233.2867 | 233.2867 | 0 | 0
2025-07-21 05:00 | 31.55 | 78 | 70 | 26.4717 | 21.7373 | 66.5026 | 204.6526 | 204.6526 | 0 | 0
2025-07-21 06:00 | 32.3 | 68 | 100 | 26.7226 | 21.2454 | 61.9688 | 253.9131 | 253.9131 | 0 | 0
2025-07-21 07:00 | 34.7 | 54.5 | 100 | 27.474 | 20.9597 | 56.2899 | 218.7147 | 218.7147 | 0 | 0
2025-07-21 08:00 | 38.55 | 37.5 | 100 | 28.648 | 20.4822 | 48.0433 | 162.8977 | 162.8977 | 0 | 0
2025-07-21 09:00 | 42.2 | 22 | 100 | 29.7637 | 19.5098 | 38.4905 | 79.3422 | 79.3422 | 0 | 0
2025-07-21 10:00 | 44.65 | 15.5 | 100 | 30.483 | 19.0799 | 33.8806 | 39.0991 | 39.0991 | 0 | 0
2025-07-21 11:00 | 46.4 | 13 | 100 | 30.9669 | 19.0176 | 31.9943 | 26.0696 | 26.0696 | 0 | 0
2025-07-21 12:00 | 47.5 | 11.5 | 100 | 31.2677 | 18.9594 | 30.7812 | 16.9308 | 16.9308 | 0 | 0
2025-07-21 13:00 | 47.45 | 12.5 | 100 | 31.2373 | 19.136 | 31.6681 | 28.177 | 28.177 | 0 | 0
2025-07-21 14:00 | 44.4 | 24 | 100 | 30.3041 | 20.3663 | 40.6764 | 121.7703 | 121.7703 | 0 | 0
2025-07-21 15:00 | 41.95 | 33 | 100 | 29.5827 | 20.9566 | 46.5609 | 173.9105 | 173.9105 | 0 | 0
2025-07-21 16:00 | 41.45 | 37 | 100 | 29.4152 | 21.3215 | 49.2109 | 200.8631 | 200.8631 | 0 | 0
2025-07-21 17:00 | 40.45 | 44 | 100 | 29.0964 | 21.851 | 53.5417 | 242.1667 | 242.1667 | 0 | 0
2025-07-21 18:00 | 39.4 | 48 | 100 | 28.7951 | 21.9501 | 55.5269 | 255.2095 | 255.2095 | 0 | 0
2025-07-21 19:00 | 38.25 | 51 | 100 | 28.4737 | 21.8726 | 56.6478 | 257.0598 | 257.0598 | 0 | 0
2025-07-21 20:00 | 37.6 | 51.5 | 100 | 28.2975 | 21.6951 | 56.4867 | 249.1164 | 249.1164 | 0 | 0
2025-07-21 21:00 | 37.2 | 49.5 | 100 | 28.2015 | 21.3482 | 54.9522 | 228.3459 | 228.3459 | 0 | 0
2025-07-21 22:00 | 36.8 | 48.5 | 70 | 28.0972 | 21.1075 | 54.0721 | 150.3848 | 150.3848 | 0 | 0
2025-07-21 23:00 | 36 | 54 | 70 | 27.8454 | 21.3768 | 56.8764 | 166.5472 | 166.5472 | 0 | 0
2025-07-22 | 34.9 | 60.5 | 70 | 27.5058 | 21.5869 | 59.8722 | 181.4816 | 181.4816 | 0 | 0
2025-07-22 01:00 | 34.05 | 62.5 | 70 | 27.2547 | 21.4469 | 60.3489 | 178.8775 | 178.8775 | 0 | 0
2025-07-22 02:00 | 33.45 | 63.5 | 70 | 27.0767 | 21.3075 | 60.4421 | 175.1581 | 175.1581 | 0 | 0
2025-07-22 03:00 | 33.1 | 62.5 | 70 | 26.9771 | 21.0899 | 59.636 | 166.6201 | 166.6201 | 0 | 0
2025-07-22 04:00 | 33.2 | 57.5 | 70 | 27.023 | 20.6934 | 56.9897 | 147.7475 | 147.7475 | 0 | 0
2025-07-22 05:00 | 32.75 | 61 | 70 | 26.8777 | 20.832 | 58.5796 | 156.2561 | 156.2561 | 0 | 0
2025-07-22 06:00 | 32.6 | 66.5 | 100 | 26.8165 | 21.2374 | 61.3969 | 251.1933 | 251.1933 | 0 | 0
2025-07-22 07:00 | 34.75 | 57.5 | 100 | 27.476 | 21.2573 | 58.0273 | 237.9255 | 237.9255 | 0 | 0
2025-07-22 08:00 | 38.5 | 39 | 100 | 28.624 | 20.6408 | 48.9897 | 173.242 | 173.242 | 0 | 0
2025-07-22 09:00 | 41.9 | 24 | 100 | 29.6634 | 19.721 | 39.8875 | 94.0311 | 94.0311 | 0 | 0
2025-07-22 10:00 | 44.15 | 18.5 | 100 | 30.314 | 19.4551 | 36.1997 | 64.7898 | 64.7898 | 0 | 0
2025-07-22 11:00 | 45.9 | 16 | 100 | 30.7936 | 19.4403 | 34.471 | 54.572 | 54.572 | 0 | 0
2025-07-22 12:00 | 47.05 | 14.5 | 100 | 31.1033 | 19.4244 | 33.369 | 47.7179 | 47.7179 | 0 | 0
2025-07-22 13:00 | 45.9 | 19 | 100 | 30.7468 | 19.9454 | 37.0063 | 86.5795 | 86.5795 | 0 | 0
2025-07-22 14:00 | 43.8 | 26.5 | 100 | 30.1224 | 20.5812 | 42.4308 | 138.782 | 138.782 | 0 | 0
2025-07-22 15:00 | 42.4 | 32 | 100 | 29.7072 | 20.9573 | 46.0317 | 171.2292 | 171.2292 | 0 | 0
2025-07-22 16:00 | 41.4 | 38 | 100 | 29.3928 | 21.4329 | 49.8954 | 208.3978 | 208.3978 | 0 | 0
2025-07-22 17:00 | 40.25 | 44 | 100 | 29.0459 | 21.7849 | 53.3962 | 238.7486 | 238.7486 | 0 | 0
2025-07-22 18:00 | 38.4 | 50.5 | 100 | 28.5167 | 21.8729 | 56.431 | 256.0605 | 256.0605 | 0 | 0
2025-07-22 19:00 | 37.05 | 55 | 100 | 28.1282 | 21.8542 | 58.2566 | 263.2909 | 263.2909 | 0 | 0
2025-07-22 20:00 | 36.25 | 57 | 100 | 27.8992 | 21.7587 | 58.8565 | 261.949 | 261.949 | 0 | 0
2025-07-22 21:00 | 35.6 | 57.5 | 100 | 27.7165 | 21.568 | 58.6577 | 253.2937 | 253.2937 | 0 | 0
2025-07-22 22:00 | 34.9 | 59.5 | 70 | 27.5101 | 21.4953 | 59.2939 | 177.1396 | 177.1396 | 0 | 0
2025-07-22 23:00 | 33.9 | 64.5 | 70 | 27.2039 | 21.565 | 61.3403 | 185.1345 | 185.1345 | 0 | 0
2025-07-23 | 32.8 | 73 | 70 | 26.8557 | 21.8488 | 65.0244 | 203.8445 | 203.8445 | 0 | 0
2025-07-23 01:00 | 32.25 | 81 | 70 | 26.6711 | 22.2566 | 68.7074 | 226.1185 | 226.1185 | 0 | 0
2025-07-23 02:00 | 32.15 | 82 | 70 | 26.639 | 22.2919 | 69.1277 | 228.3258 | 228.3258 | 0 | 0
2025-07-23 03:00 | 31.85 | 80.5 | 70 | 26.5547 | 22.0521 | 68.0623 | 218.2528 | 218.2528 | 0 | 0
2025-07-23 04:00 | 31.65 | 77 | 70 | 26.5041 | 21.7011 | 66.0872 | 202.4711 | 202.4711 | 0 | 0
2025-07-23 05:00 | 31.4 | 74.5 | 70 | 26.435 | 21.4072 | 64.5969 | 189.7769 | 189.7769 | 0 | 0
2025-07-23 06:00 | 31.6 | 72 | 100 | 26.5016 | 21.2915 | 63.4838 | 261.9017 | 261.9017 | 0 | 0
2025-07-23 07:00 | 33 | 65.5 | 100 | 26.938 | 21.3073 | 61.1779 | 253.1936 | 253.1936 | 0 | 0
2025-07-23 08:00 | 34.75 | 58.5 | 100 | 27.4717 | 21.3486 | 58.6081 | 244.1653 | 244.1653 | 0 | 0
2025-07-23 09:00 | 36.4 | 52 | 100 | 27.9671 | 21.3221 | 55.9465 | 231.654 | 231.654 | 0 | 0
2025-07-23 10:00 | 38.05 | 46.5 | 100 | 28.4509 | 21.3235 | 53.6087 | 221.3208 | 221.3208 | 0 | 0
2025-07-23 11:00 | 39.3 | 44.5 | 100 | 28.7969 | 21.5241 | 53.1069 | 227.0209 | 227.0209 | 0 | 0
2025-07-23 12:00 | 39.7 | 48 | 100 | 28.8719 | 22.0545 | 55.7447 | 260.394 | 260.394 | 0 | 0
2025-07-23 13:00 | 39.6 | 51.5 | 100 | 28.8177 | 22.4063 | 58.0329 | 285.1188 | 285.1188 | 0 | 0
2025-07-23 14:00 | 39.45 | 50.5 | 100 | 28.7878 | 22.2427 | 57.2479 | 274.9568 | 274.9568 | 0 | 0
2025-07-23 15:00 | 39.05 | 50 | 100 | 28.6892 | 22.0461 | 56.611 | 264.1307 | 264.1307 | 0 | 0
2025-07-23 16:00 | 37.8 | 54 | 100 | 28.3344 | 22.0224 | 58.2372 | 270.3513 | 270.3513 | 0 | 0
2025-07-23 17:00 | 36.4 | 58 | 100 | 27.9345 | 21.9085 | 59.6031 | 271.554 | 271.554 | 0 | 0
2025-07-23 18:00 | 35.3 | 60.5 | 100 | 27.618 | 21.735 | 60.2096 | 266.9812 | 266.9812 | 0 | 0
2025-07-23 19:00 | 34.25 | 64.5 | 100 | 27.3041 | 21.698 | 61.6458 | 271.4107 | 271.4107 | 0 | 0
2025-07-23 20:00 | 33.45 | 70 | 100 | 27.0541 | 21.8589 | 64.0039 | 287.7041 | 287.7041 | 0 | 0
2025-07-23 21:00 | 32.85 | 75.5 | 100 | 26.8622 | 22.0701 | 66.4152 | 306.2057 | 306.2057 | 0 | 0
2025-07-23 22:00 | 32.4 | 79 | 70 | 26.7205 | 22.1629 | 67.8289 | 221.0009 | 221.0009 | 0 | 0
2025-07-23 23:00 | 31.85 | 82 | 70 | 26.5506 | 22.1664 | 68.8431 | 223.8449 | 223.8449 | 0 | 0
2025-07-24 | 31.15 | 86.5 | 70 | 26.3315 | 22.2066 | 70.4167 | 229.2885 | 229.2885 | 0 | 0
2025-07-24 01:00 | 30.5 | 90 | 70 | 26.1284 | 22.1808 | 71.4764 | 231.3039 | 231.3039 | 0 | 0
2025-07-24 02:00 | 30 | 92 | 70 | 25.9724 | 22.1048 | 71.926 | 230.19 | 230.19 | 0 | 0
2025-07-24 03:00 | 29.6 | 94 | 70 | 25.8461 | 22.0682 | 72.4627 | 230.4845 | 230.4845 | 0 | 0
2025-07-24 04:00 | 29.55 | 93.5 | 70 | 25.8315 | 22.0122 | 72.1748 | 228.0486 | 228.0486 | 0 | 0
2025-07-24 05:00 | 29.5 | 92 | 70 | 25.8184 | 21.8883 | 71.4141 | 222.3225 | 222.3225 | 0 | 0
2025-07-24 06:00 | 29.8 | 89 | 100 | 25.9162 | 21.81 | 70.2872 | 310.0277 | 310.0277 | 0 | 0
2025-07-24 07:00 | 31.15 | 81.5 | 100 | 26.343 | 21.8369 | 67.915 | 302.1575 | 302.1575 | 0 | 0
2025-07-24 08:00 | 33 | 71.5 | 100 | 26.9186 | 21.8055 | 64.4153 | 287.075 | 287.075 | 0 | 0
2025-07-24 09:00 | 35 | 62 | 100 | 27.5272 | 21.7601 | 60.8265 | 270.5103 | 270.5103 | 0 | 0
2025-07-24 10:00 | 37.1 | 54.5 | 100 | 28.1444 | 21.8209 | 58.0012 | 260.9786 | 260.9786 | 0 | 0
2025-07-24 11:00 | 38.9 | 50 | 100 | 28.6505 | 21.9935 | 56.494 | 261.4307 | 261.4307 | 0 | 0
2025-07-24 12:00 | 39.6 | 50 | 100 | 28.8297 | 22.2399 | 57.0349 | 273.9582 | 273.9582 | 0 | 0
2025-07-24 13:00 | 38.5 | 54.5 | 100 | 28.5138 | 22.328 | 59.1266 | 286.884 | 286.884 | 0 | 0
2025-07-24 14:00 | 38.15 | 55.5 | 100 | 28.416 | 22.3034 | 59.485 | 287.4666 | 287.4666 | 0 | 0
2025-07-24 15:00 | 38.9 | 52 | 100 | 28.635 | 22.2076 | 57.8281 | 276.2892 | 276.2892 | 0 | 0
2025-07-24 16:00 | 38.4 | 52 | 100 | 28.5054 | 22.0284 | 57.4381 | 267.2432 | 267.2432 | 0 | 0
2025-07-24 17:00 | 37.65 | 53.5 | 100 | 28.2975 | 21.916 | 57.8188 | 264.2951 | 264.2951 | 0 | 0
2025-07-24 18:00 | 36.7 | 56.5 | 100 | 28.0242 | 21.8718 | 58.9424 | 267.345 | 267.345 | 0 | 0
2025-07-24 19:00 | 35.5 | 63 | 100 | 27.6618 | 22.0401 | 61.8394 | 286.5291 | 286.5291 | 0 | 0
2025-07-24 20:00 | 34.8 | 69.5 | 100 | 27.4384 | 22.3493 | 64.9545 | 312.3189 | 312.3189 | 0 | 0
2025-07-24 21:00 | 34.85 | 70 | 100 | 27.4501 | 22.4133 | 65.2824 | 316.3251 | 316.3251 | 0 | 0
2025-07-24 22:00 | 35.2 | 64.5 | 70 | 27.5717 | 22.0618 | 62.4465 | 202.9338 | 202.9338 | 0 | 0
2025-07-24 23:00 | 35.2 | 58 | 70 | 27.6013 | 21.4651 | 58.6837 | 174.6817 | 174.6817 | 0 | 0
2025-07-25 | 34.7 | 56 | 70 | 27.4674 | 21.0971 | 57.1775 | 159.7999 | 159.7999 | 0 | 0
2025-07-25 01:00 | 33.9 | 59.5 | 70 | 27.222 | 21.123 | 58.5985 | 164.7567 | 164.7567 | 0 | 0
2025-07-25 02:00 | 33.2 | 63 | 70 | 27.0046 | 21.1682 | 60.0154 | 170.1623 | 170.1623 | 0 | 0
2025-07-25 03:00 | 33.05 | 58.5 | 70 | 26.9748 | 20.7234 | 57.4722 | 150.2565 | 150.2565 | 0 | 0
2025-07-25 04:00 | 33.3 | 54 | 70 | 27.0642 | 20.4154 | 55.1745 | 134.944 | 134.944 | 0 | 0
2025-07-25 05:00 | 33.1 | 58.5 | 70 | 26.9898 | 20.7422 | 57.4988 | 150.8127 | 150.8127 | 0 | 0
2025-07-25 06:00 | 32.85 | 64.5 | 100 | 26.8965 | 21.1642 | 60.5518 | 245.0217 | 245.0217 | 0 | 0
2025-07-25 07:00 | 33.7 | 64 | 100 | 27.1476 | 21.444 | 60.9247 | 257.9673 | 257.9673 | 0 | 0
2025-07-25 08:00 | 35.85 | 56.5 | 100 | 27.7908 | 21.5623 | 58.2731 | 251.629 | 251.629 | 0 | 0
2025-07-25 09:00 | 38.8 | 45 | 100 | 28.6614 | 21.4111 | 53.1281 | 222.7633 | 222.7633 | 0 | 0
2025-07-25 10:00 | 41.8 | 34 | 100 | 29.5342 | 21.0425 | 47.2228 | 180.4912 | 180.4912 | 0 | 0
2025-07-25 11:00 | 44 | 28 | 100 | 30.1522 | 20.853 | 43.7052 | 155.688 | 155.688 | 0 | 0
2025-07-25 12:00 | 45.5 | 24 | 100 | 30.5724 | 20.6519 | 41.0791 | 134.527 | 134.527 | 0 | 0
2025-07-25 13:00 | 46.55 | 21 | 100 | 30.8713 | 20.431 | 38.9154 | 114.8786 | 114.8786 | 0 | 0
2025-07-25 14:00 | 47.3 | 18.5 | 100 | 31.0929 | 20.183 | 36.9645 | 95.2414 | 95.2414 | 0 | 0
2025-07-25 15:00 | 47.55 | 16 | 100 | 31.1981 | 19.7936 | 34.8132 | 69.3926 | 69.3926 | 0 | 0
2025-07-25 16:00 | 46.65 | 16 | 100 | 30.9797 | 19.5939 | 34.6387 | 61.5032 | 61.5032 | 0 | 0
2025-07-25 17:00 | 45.65 | 17 | 100 | 30.7159 | 19.5433 | 35.3008 | 63.4894 | 63.4894 | 0 | 0
2025-07-25 18:00 | 43.85 | 23 | 100 | 30.1795 | 20.0675 | 39.7227 | 106.1803 | 106.1803 | 0 | 0
2025-07-25 19:00 | 40.95 | 33.5 | 100 | 29.3207 | 20.7219 | 46.4573 | 164.6413 | 164.6413 | 0 | 0
2025-07-25 20:00 | 38.9 | 39.5 | 100 | 28.7284 | 20.8194 | 49.5577 | 183.1972 | 183.1972 | 0 | 0
2025-07-25 21:00 | 37.45 | 43.5 | 100 | 28.3061 | 20.7974 | 51.3593 | 190.6684 | 190.6684 | 0 | 0
2025-07-25 22:00 | 36.5 | 44.5 | 70 | 28.035 | 20.591 | 51.4625 | 128.196 | 128.196 | 0 | 0
2025-07-25 23:00 | 36.1 | 40 | 70 | 27.9443 | 19.9916 | 48.5331 | 102.8575 | 102.8575 | 0 | 0
2025-07-26 | 35.65 | 36.5 | 70 | 27.8303 | 19.484 | 46.2531 | 82.2945 | 82.2945 | 0 | 0
2025-07-26 01:00 | 35 | 36 | 70 | 27.64 | 19.2377 | 45.7423 | 74.3463 | 74.3463 | 0 | 0
2025-07-26 02:00 | 34.25 | 37 | 70 | 27.4105 | 19.1168 | 46.0835 | 72.3632 | 72.3632 | 0 | 0
2025-07-26 03:00 | 33.6 | 39.5 | 70 | 27.2039 | 19.167 | 47.2798 | 77.4359 | 77.4359 | 0 | 0
2025-07-26 04:00 | 33 | 46.5 | 70 | 26.9978 | 19.636 | 50.9041 | 100.9167 | 100.9167 | 0 | 0
2025-07-26 05:00 | 32.6 | 53.5 | 70 | 26.8547 | 20.1285 | 54.4854 | 124.8997 | 124.8997 | 0 | 0
2025-07-26 06:00 | 32.65 | 54.5 | 100 | 26.867 | 20.2342 | 55.0445 | 184.855 | 184.855 | 0 | 0
2025-07-26 07:00 | 33.8 | 57 | 100 | 27.2023 | 20.8661 | 57.1058 | 218.4217 | 218.4217 | 0 | 0
2025-07-26 08:00 | 36.9 | 49 | 100 | 28.1221 | 21.1938 | 54.4407 | 219.8533 | 219.8533 | 0 | 0
2025-07-26 09:00 | 40.15 | 33 | 100 | 29.1147 | 20.4263 | 45.7217 | 149.533 | 149.533 | 0 | 0
2025-07-26 10:00 | 42.25 | 25.5 | 100 | 29.7396 | 20.0221 | 41.1133 | 111.378 | 111.378 | 0 | 0
2025-07-26 11:00 | 44.05 | 21 | 100 | 30.256 | 19.8195 | 38.1723 | 88.5255 | 88.5255 | 0 | 0
2025-07-26 12:00 | 45.5 | 17.5 | 100 | 30.6706 | 19.6008 | 35.6633 | 67.0595 | 67.0595 | 0 | 0
2025-07-26 13:00 | 46.05 | 17 | 100 | 30.8153 | 19.6407 | 35.3567 | 66.7681 | 66.7681 | 0 | 0
2025-07-26 14:00 | 45.35 | 21 | 100 | 30.5812 | 20.1376 | 38.5361 | 101.9991 | 101.9991 | 0 | 0
2025-07-26 15:00 | 43.9 | 26.5 | 100 | 30.1472 | 20.6064 | 42.4781 | 140.096 | 140.096 | 0 | 0
2025-07-26 16:00 | 42.2 | 32 | 100 | 29.6567 | 20.8977 | 45.9417 | 168.5882 | 168.5882 | 0 | 0
2025-07-26 17:00 | 40.8 | 36 | 100 | 29.2587 | 20.9944 | 48.143 | 183.0546 | 183.0546 | 0 | 0
2025-07-26 18:00 | 39.6 | 38.5 | 100 | 28.9231 | 20.9253 | 49.2453 | 185.6635 | 185.6635 | 0 | 0
2025-07-26 19:00 | 38.4 | 41.5 | 100 | 28.5792 | 20.8887 | 50.5895 | 190.5189 | 190.5189 | 0 | 0
2025-07-26 20:00 | 37.9 | 41 | 100 | 28.4461 | 20.6725 | 49.9953 | 179.37 | 179.37 | 0 | 0
2025-07-26 21:00 | 37.7 | 39 | 100 | 28.4035 | 20.3874 | 48.6146 | 162.0112 | 162.0112 | 0 | 0
2025-07-26 22:00 | 36.95 | 40.5 | 70 | 28.1843 | 20.3155 | 49.2044 | 113.4159 | 113.4159 | 0 | 0
2025-07-26 23:00 | 35.95 | 44 | 70 | 27.8813 | 20.3611 | 50.8555 | 119.9385 | 119.9385 | 0 | 0
2025-07-27 | 35 | 49 | 70 | 27.5841 | 20.5416 | 53.3043 | 132.4976 | 132.4976 | 0 | 0
2025-07-27 01:00 | 34.1 | 54.5 | 70 | 27.2995 | 20.7464 | 55.9094 | 146.0468 | 146.0468 | 0 | 0
2025-07-27 02:00 | 33.35 | 59 | 70 | 27.0626 | 20.8793 | 57.9117 | 155.6759 | 155.6759 | 0 | 0
2025-07-27 03:00 | 32.6 | 63 | 70 | 26.8268 | 20.9453 | 59.5471 | 162.2719 | 162.2719 | 0 | 0
2025-07-27 04:00 | 31.65 | 65.5 | 70 | 26.5329 | 20.7936 | 60.1806 | 159.7953 | 159.7953 | 0 | 0
2025-07-27 05:00 | 31 | 63.5 | 70 | 26.3374 | 20.3893 | 58.7228 | 144.337 | 144.337 | 0 | 0
2025-07-27 06:00 | 31.85 | 52.5 | 100 | 26.6271 | 19.7838 | 53.5546 | 161.0794 | 161.0794 | 0 | 0
2025-07-27 07:00 | 34.75 | 35.5 | 100 | 27.5672 | 19.1175 | 45.3429 | 99.5936 | 99.5936 | 0 | 0
2025-07-27 08:00 | 38.25 | 25.5 | 100 | 28.6457 | 18.9697 | 40.0613 | 68.5013 | 68.5013 | 0 | 0
2025-07-27 09:00 | 40.5 | 24.5 | 100 | 29.2823 | 19.4264 | 39.8885 | 83.6362 | 83.6362 | 0 | 0
2025-07-27 10:00 | 42.2 | 23.5 | 100 | 29.7478 | 19.7268 | 39.6017 | 92.786 | 92.786 | 0 | 0
2025-07-27 11:00 | 44.1 | 20.5 | 100 | 30.2752 | 19.7551 | 37.7828 | 84.0618 | 84.0618 | 0 | 0
2025-07-27 12:00 | 45.6 | 17.5 | 100 | 30.6956 | 19.6252 | 35.6793 | 67.9109 | 67.9109 | 0 | 0
2025-07-27 13:00 | 45.85 | 18 | 100 | 30.7501 | 19.7652 | 36.1558 | 75.5532 | 75.5532 | 0 | 0
2025-07-27 14:00 | 44.1 | 23.5 | 100 | 30.236 | 20.2131 | 40.1745 | 113.4795 | 113.4795 | 0 | 0
2025-07-27 15:00 | 41.8 | 30 | 100 | 29.5756 | 20.5139 | 44.2865 | 145.8428 | 145.8428 | 0 | 0
2025-07-27 16:00 | 40.6 | 32 | 100 | 29.2428 | 20.4295 | 45.2262 | 147.3997 | 147.3997 | 0 | 0
2025-07-27 17:00 | 39.9 | 33.5 | 100 | 29.0437 | 20.4125 | 45.971 | 150.3909 | 150.3909 | 0 | 0
2025-07-27 18:00 | 39.1 | 37 | 100 | 28.801 | 20.5931 | 47.9776 | 166.8519 | 166.8519 | 0 | 0
2025-07-27 19:00 | 38.15 | 40 | 100 | 28.5213 | 20.6411 | 49.4785 | 175.7351 | 175.7351 | 0 | 0
2025-07-27 20:00 | 37.35 | 42 | 100 | 28.2877 | 20.6055 | 50.3418 | 178.3566 | 178.3566 | 0 | 0
2025-07-27 21:00 | 36.6 | 43.5 | 100 | 28.0689 | 20.5223 | 50.8828 | 177.6068 | 177.6068 | 0 | 0
2025-07-27 22:00 | 35.7 | 45.5 | 70 | 27.8022 | 20.432 | 51.6191 | 124.2129 | 124.2129 | 0 | 0
2025-07-27 23:00 | 34.65 | 56 | 70 | 27.4534 | 21.0818 | 57.1088 | 158.9265 | 158.9265 | 0 | 0
2025-07-28 | 33.35 | 73 | 70 | 27.0153 | 22.0694 | 65.5178 | 211.7099 | 211.7099 | 0 | 0
2025-07-28 01:00 | 32.5 | 80.5 | 70 | 26.7455 | 22.3224 | 68.6932 | 228.0335 | 228.0335 | 0 | 0
2025-07-28 02:00 | 32.05 | 82 | 70 | 26.6098 | 22.2498 | 69.0223 | 226.7579 | 226.7579 | 0 | 0
2025-07-28 03:00 | 31.5 | 80.5 | 70 | 26.4506 | 21.9068 | 67.7209 | 212.9737 | 212.9737 | 0 | 0
2025-07-28 04:00 | 31.3 | 71 | 70 | 26.4129 | 21.0963 | 62.7323 | 175.5753 | 175.5753 | 0 | 0
2025-07-28 05:00 | 31.25 | 61.5 | 70 | 26.4194 | 20.321 | 57.8662 | 139.9885 | 139.9885 | 0 | 0
2025-07-28 06:00 | 31.95 | 51 | 100 | 26.662 | 19.6889 | 52.8152 | 154.2778 | 154.2778 | 0 | 0
2025-07-28 07:00 | 35.05 | 34 | 100 | 27.6635 | 19.05 | 44.5528 | 93.4285 | 93.4285 | 0 | 0
2025-07-28 08:00 | 38.8 | 23 | 100 | 28.8198 | 18.7987 | 38.5088 | 54.5631 | 54.5631 | 0 | 0
2025-07-28 09:00 | 41.3 | 21 | 100 | 29.5321 | 19.1489 | 37.5556 | 61.5698 | 61.5698 | 0 | 0
2025-07-28 10:00 | 43.4 | 20 | 100 | 30.1012 | 19.5104 | 37.2242 | 72.3311 | 72.3311 | 0 | 0
2025-07-28 11:00 | 45.35 | 17.5 | 100 | 30.633 | 19.5707 | 35.621 | 65.534 | 65.534 | 0 | 0
2025-07-28 12:00 | 46.85 | 15 | 100 | 31.0455 | 19.4725 | 33.771 | 51.6353 | 51.6353 | 0 | 0
2025-07-28 13:00 | 47.1 | 14 | 100 | 31.1243 | 19.344 | 32.9399 | 42.5043 | 42.5043 | 0 | 0
2025-07-28 14:00 | 44.2 | 24 | 100 | 30.2545 | 20.3157 | 40.5988 | 119.3846 | 119.3846 | 0 | 0
2025-07-28 15:00 | 40.7 | 37.5 | 100 | 29.2193 | 21.1512 | 49.1385 | 193.7614 | 193.7614 | 0 | 0
2025-07-28 16:00 | 39.25 | 42 | 100 | 28.8031 | 21.223 | 51.3996 | 207.2167 | 207.2167 | 0 | 0
2025-07-28 17:00 | 38.65 | 44 | 100 | 28.629 | 21.2514 | 52.3622 | 212.7755 | 212.7755 | 0 | 0
2025-07-28 18:00 | 38.85 | 40 | 100 | 28.7115 | 20.8647 | 49.8396 | 185.9644 | 185.9644 | 0 | 0
2025-07-28 19:00 | 38.8 | 34.5 | 100 | 28.7378 | 20.208 | 46.1703 | 143.5675 | 143.5675 | 0 | 0
2025-07-28 20:00 | 37.5 | 40.5 | 100 | 28.3386 | 20.4913 | 49.4643 | 169.8321 | 169.8321 | 0 | 0
2025-07-28 21:00 | 36.1 | 51 | 100 | 27.8887 | 21.1187 | 55.1364 | 219.8777 | 219.8777 | 0 | 0
2025-07-28 22:00 | 35.25 | 57.5 | 70 | 27.6182 | 21.4401 | 58.3899 | 172.8154 | 172.8154 | 0 | 0
2025-07-28 23:00 | 34.6 | 62.5 | 70 | 27.4124 | 21.6555 | 60.7654 | 185.9963 | 185.9963 | 0 | 0
2025-07-29 | 34.2 | 65 | 70 | 27.2883 | 21.7245 | 61.8529 | 191.1561 | 191.1561 | 0 | 0
2025-07-29 01:00 | 33.85 | 64.5 | 70 | 27.1896 | 21.546 | 61.2954 | 184.431 | 184.431 | 0 | 0
2025-07-29 02:00 | 33.2 | 64 | 70 | 27.0018 | 21.256 | 60.5196 | 173.8789 | 173.8789 | 0 | 0
2025-07-29 03:00 | 32.45 | 64 | 70 | 26.7789 | 20.9729 | 59.9656 | 164.227 | 164.227 | 0 | 0
2025-07-29 04:00 | 32.05 | 60.5 | 70 | 26.6678 | 20.5323 | 57.8482 | 145.7494 | 145.7494 | 0 | 0
2025-07-29 05:00 | 31.75 | 58 | 70 | 26.5823 | 20.2149 | 56.3569 | 132.6355 | 132.6355 | 0 | 0
2025-07-29 06:00 | 32.1 | 55 | 100 | 26.6978 | 20.0859 | 54.9833 | 178.6404 | 178.6404 | 0 | 0
2025-07-29 07:00 | 34.35 | 44 | 100 | 27.4137 | 19.8437 | 50.0756 | 147.9404 | 147.9404 | 0 | 0
2025-07-29 08:00 | 38.1 | 29.5 | 100 | 28.5767 | 19.4158 | 42.6249 | 96.9865 | 96.9865 | 0 | 0
2025-07-29 09:00 | 41.1 | 20 | 100 | 29.4869 | 18.9626 | 36.7898 | 50.8988 | 50.8988 | 0 | 0
2025-07-29 10:00 | 43.2 | 17 | 100 | 30.0843 | 19.0056 | 34.8598 | 41.7844 | 41.7844 | 0 | 0
2025-07-29 11:00 | 45.3 | 15 | 100 | 30.6569 | 19.142 | 33.5394 | 38.9377 | 38.9377 | 0 | 0
2025-07-29 12:00 | 46.85 | 13 | 100 | 31.0795 | 19.1141 | 32.0271 | 29.2077 | 29.2077 | 0 | 0
2025-07-29 13:00 | 47.15 | 13.5 | 100 | 31.1453 | 19.2656 | 32.5017 | 37.1523 | 37.1523 | 0 | 0
2025-07-29 14:00 | 43.7 | 25.5 | 100 | 30.1102 | 20.4101 | 41.5999 | 127.9623 | 127.9623 | 0 | 0
2025-07-29 15:00 | 40.1 | 38 | 100 | 29.0591 | 21.0255 | 49.1543 | 188.8769 | 188.8769 | 0 | 0
2025-07-29 16:00 | 39.05 | 43 | 100 | 28.7427 | 21.2722 | 51.9396 | 211.5729 | 211.5729 | 0 | 0
2025-07-29 17:00 | 37.8 | 48 | 100 | 28.3738 | 21.3993 | 54.3973 | 227.8107 | 227.8107 | 0 | 0
2025-07-29 18:00 | 36.45 | 55.5 | 100 | 27.9623 | 21.6863 | 58.0953 | 255.642 | 255.642 | 0 | 0
2025-07-29 19:00 | 35.5 | 61 | 100 | 27.6721 | 21.8589 | 60.622 | 273.4641 | 273.4641 | 0 | 0
2025-07-29 20:00 | 34.9 | 61.5 | 100 | 27.5017 | 21.6789 | 60.4295 | 265.2289 | 265.2289 | 0 | 0
2025-07-29 21:00 | 34.25 | 62 | 100 | 27.3144 | 21.479 | 60.2047 | 256.0904 | 256.0904 | 0 | 0
2025-07-29 22:00 | 33.65 | 62 | 70 | 27.1406 | 21.2542 | 59.7517 | 171.5134 | 171.5134 | 0 | 0
2025-07-29 23:00 | 33 | 62.5 | 70 | 26.9476 | 21.0534 | 59.5518 | 165.261 | 165.261 | 0 | 0
2025-07-30 | 32.25 | 63.5 | 70 | 26.7203 | 20.8566 | 59.5533 | 159.7164 | 159.7164 | 0 | 0
2025-07-30 01:00 | 31.45 | 64 | 70 | 26.4754 | 20.5978 | 59.2662 | 151.6469 | 151.6469 | 0 | 0
2025-07-30 02:00 | 30.7 | 64 | 70 | 26.2429 | 20.3176 | 58.778 | 142.4826 | 142.4826 | 0 | 0
2025-07-30 03:00 | 30.15 | 62.5 | 70 | 26.0726 | 19.9973 | 57.6998 | 130.6023 | 130.6023 | 0 | 0
2025-07-30 04:00 | 30.8 | 56 | 70 | 26.2907 | 19.7121 | 54.8234 | 114.5958 | 114.5958 | 0 | 0
2025-07-30 05:00 | 31.35 | 52 | 70 | 26.4724 | 19.5699 | 53.0552 | 105.585 | 105.585 | 0 | 0
2025-07-30 06:00 | 31.5 | 52 | 100 | 26.5194 | 19.6214 | 53.1222 | 153.0357 | 153.0357 | 0 | 0
2025-07-30 07:00 | 33.25 | 48.5 | 100 | 27.0675 | 19.9048 | 52.0909 | 159.2899 | 159.2899 | 0 | 0
2025-07-30 08:00 | 35.75 | 46 | 100 | 27.8143 | 20.5003 | 51.9329 | 181.3658 | 181.3658 | 0 | 0
2025-07-30 09:00 | 38.25 | 42 | 100 | 28.5354 | 20.8995 | 50.8087 | 191.6575 | 191.6575 | 0 | 0
2025-07-30 10:00 | 40.45 | 32 | 100 | 29.2033 | 20.3905 | 45.139 | 145.1602 | 145.1602 | 0 | 0
2025-07-30 11:00 | 41.55 | 25.5 | 100 | 29.5556 | 19.8383 | 40.8878 | 103.4346 | 103.4346 | 0 | 0
2025-07-30 12:00 | 41.75 | 25.5 | 100 | 29.6085 | 19.8909 | 40.9513 | 105.6962 | 105.6962 | 0 | 0
2025-07-30 13:00 | 41.65 | 28.5 | 100 | 29.552 | 20.2724 | 43.1186 | 130.8055 | 130.8055 | 0 | 0
2025-07-30 14:00 | 41.1 | 34 | 100 | 29.3552 | 20.8346 | 46.8614 | 170.578 | 170.578 | 0 | 0
2025-07-30 15:00 | 40.2 | 39.5 | 100 | 29.0722 | 21.2361 | 50.2556 | 202.402 | 202.402 | 0 | 0
2025-07-30 16:00 | 39.3 | 43 | 100 | 28.8085 | 21.3532 | 52.104 | 215.6587 | 215.6587 | 0 | 0
2025-07-30 17:00 | 38.25 | 46 | 100 | 28.5079 | 21.3363 | 53.4204 | 221.0475 | 221.0475 | 0 | 0
2025-07-30 18:00 | 36.95 | 52 | 100 | 28.1184 | 21.5158 | 56.3356 | 241.2301 | 241.2301 | 0 | 0
2025-07-30 19:00 | 35.9 | 59 | 100 | 27.7924 | 21.8201 | 59.7817 | 268.4695 | 268.4695 | 0 | 0
2025-07-30 20:00 | 35.15 | 63 | 100 | 27.5651 | 21.9086 | 61.5104 | 279.3831 | 279.3831 | 0 | 0
2025-07-30 21:00 | 34.35 | 66.5 | 100 | 27.325 | 21.9125 | 62.8252 | 284.9748 | 284.9748 | 0 | 0
2025-07-30 22:00 | 33.45 | 71 | 70 | 27.051 | 21.9432 | 64.5246 | 205.2118 | 205.2118 | 0 | 0
2025-07-30 23:00 | 32.7 | 73 | 70 | 26.8264 | 21.8086 | 64.9353 | 202.4188 | 202.4188 | 0 | 0
2025-07-31 | 32.15 | 71.5 | 70 | 26.668 | 21.4695 | 63.6795 | 189.0251 | 189.0251 | 0 | 0
2025-07-31 01:00 | 31.65 | 71 | 70 | 26.5191 | 21.2328 | 63.0176 | 180.3536 | 180.3536 | 0 | 0
2025-07-31 02:00 | 31.2 | 72 | 70 | 26.38 | 21.1337 | 63.1722 | 177.9634 | 177.9634 | 0 | 0
2025-07-31 03:00 | 30.95 | 70.5 | 70 | 26.3066 | 20.92 | 62.2272 | 169.2225 | 169.2225 | 0 | 0
2025-07-31 04:00 | 31.25 | 65 | 70 | 26.4113 | 20.6013 | 59.6683 | 153.0632 | 153.0632 | 0 | 0
2025-07-31 05:00 | 31.45 | 59 | 70 | 26.4871 | 20.1877 | 56.7284 | 133.1781 | 133.1781 | 0 | 0
2025-07-31 06:00 | 32.2 | 51.5 | 100 | 26.7378 | 19.8153 | 53.2201 | 161.0411 | 161.0411 | 0 | 0
2025-07-31 07:00 | 34.45 | 41.5 | 100 | 27.4532 | 19.6271 | 48.7184 | 134.0537 | 134.0537 | 0 | 0
2025-07-31 08:00 | 36.45 | 36 | 100 | 28.0661 | 19.6734 | 46.2203 | 124.1403 | 124.1403 | 0 | 0
2025-07-31 09:00 | 37.9 | 33.5 | 100 | 28.4943 | 19.8235 | 45.1745 | 124.623 | 124.623 | 0 | 0
2025-07-31 10:00 | 39.45 | 31 | 100 | 28.9419 | 19.9727 | 44.0823 | 124.7742 | 124.7742 | 0 | 0
2025-07-31 11:00 | 41.55 | 26.5 | 100 | 29.5457 | 19.9705 | 41.6353 | 112.3784 | 112.3784 | 0 | 0
2025-07-31 12:00 | 43.75 | 21 | 100 | 30.1794 | 19.7424 | 38.1057 | 85.6231 | 85.6231 | 0 | 0
2025-07-31 13:00 | 44.65 | 19 | 100 | 30.4351 | 19.6454 | 36.7258 | 74.7209 | 74.7209 | 0 | 0
2025-07-31 14:00 | 44.65 | 20.5 | 100 | 30.4144 | 19.883 | 37.943 | 89.8467 | 89.8467 | 0 | 0
2025-07-31 15:00 | 44.2 | 26.5 | 100 | 30.2211 | 20.6869 | 42.6047 | 143.8435 | 143.8435 | 0 | 0
2025-07-31 16:00 | 42.95 | 30 | 100 | 29.8676 | 20.8403 | 44.7947 | 160.8131 | 160.8131 | 0 | 0
2025-07-31 17:00 | 41.65 | 30.5 | 100 | 29.5316 | 20.5358 | 44.6025 | 148.4158 | 148.4158 | 0 | 0
2025-07-31 18:00 | 39.9 | 36.5 | 100 | 29.0187 | 20.7771 | 48.0445 | 174.3979 | 174.3979 | 0 | 0
2025-07-31 19:00 | 38 | 41 | 100 | 28.4734 | 20.7024 | 50.0633 | 181.0292 | 181.0292 | 0 | 0
2025-07-31 20:00 | 37.4 | 40 | 100 | 28.3136 | 20.4016 | 49.1222 | 165.1031 | 165.1031 | 0 | 0
2025-07-31 21:00 | 37 | 38.5 | 100 | 28.2098 | 20.1126 | 47.9957 | 148.8982 | 148.8982 | 0 | 0
2025-07-31 22:00 | 36.3 | 37 | 70 | 28.0174 | 19.7347 | 46.7853 | 90.4269 | 90.4269 | 0 | 0
2025-07-31 23:00 | 35.35 | 39 | 70 | 27.7305 | 19.6549 | 47.6236 | 91.0956 | 91.0956 | 0 | 0
2025-08-01 | 33.85 | 51 | 70 | 27.2386 | 20.3353 | 53.8138 | 128.5542 | 128.5542 | 0 | 0
2025-08-01 01:00 | 33.5 | 66 | 70 | 27.0825 | 21.5402 | 61.8608 | 186.0068 | 186.0068 | 0 | 0
2025-08-01 02:00 | 33.8 | 70 | 70 | 27.1548 | 21.9972 | 64.3053 | 206.2726 | 206.2726 | 0 | 0
2025-08-01 03:00 | 33.45 | 59 | 70 | 27.092 | 20.9151 | 57.9901 | 156.981 | 156.981 | 0 | 0
2025-08-01 04:00 | 32.55 | 58.5 | 70 | 26.8249 | 20.5437 | 57.1309 | 144.1187 | 144.1187 | 0 | 0
2025-08-01 05:00 | 31.8 | 68 | 70 | 26.5721 | 21.0518 | 61.5915 | 171.1811 | 171.1811 | 0 | 0
2025-08-01 06:00 | 32.35 | 67 | 100 | 26.7403 | 21.1821 | 61.4841 | 249.405 | 249.405 | 0 | 0
2025-08-01 07:00 | 34.25 | 58.5 | 100 | 27.3278 | 21.1641 | 58.2558 | 235.2943 | 235.2943 | 0 | 0
2025-08-01 08:00 | 37.4 | 46.5 | 100 | 28.2743 | 21.1032 | 53.2023 | 210.788 | 210.788 | 0 | 0
2025-08-01 09:00 | 41 | 33.5 | 100 | 29.334 | 20.7408 | 46.4551 | 165.0113 | 165.0113 | 0 | 0
2025-08-01 10:00 | 43.85 | 23.5 | 100 | 30.1732 | 20.1504 | 40.0862 | 110.6073 | 110.6073 | 0 | 0
2025-08-01 11:00 | 45.4 | 20.5 | 100 | 30.601 | 20.0722 | 38.1239 | 97.2002 | 97.2002 | 0 | 0
2025-08-01 12:00 | 46.15 | 20 | 100 | 30.7919 | 20.1729 | 37.9163 | 99.6613 | 99.6613 | 0 | 0
2025-08-01 13:00 | 46.75 | 19 | 100 | 30.953 | 20.1477 | 37.2272 | 94.9653 | 94.9653 | 0 | 0
2025-08-01 14:00 | 47 | 16.5 | 100 | 31.0564 | 19.7692 | 35.1152 | 69.773 | 69.773 | 0 | 0
2025-08-01 15:00 | 47.4 | 13 | 100 | 31.216 | 19.2193 | 32.1042 | 33.5329 | 33.5329 | 0 | 0
2025-08-01 16:00 | 46.75 | 14 | 100 | 31.0379 | 19.2679 | 32.9 | 39.8532 | 39.8532 | 0 | 0
2025-08-01 17:00 | 44.55 | 21.5 | 100 | 30.3756 | 20.0203 | 38.7091 | 98.6264 | 98.6264 | 0 | 0
2025-08-01 18:00 | 42.1 | 31.5 | 100 | 29.6368 | 20.8029 | 45.515 | 162.7469 | 162.7469 | 0 | 0
2025-08-01 19:00 | 39.25 | 44.5 | 100 | 28.7839 | 21.5077 | 53.0689 | 226.1425 | 226.1425 | 0 | 0
2025-08-01 20:00 | 36.8 | 54.5 | 100 | 28.0634 | 21.714 | 57.7534 | 255.3384 | 255.3384 | 0 | 0
2025-08-01 21:00 | 35.5 | 57 | 100 | 27.6908 | 21.484 | 58.2878 | 248.2895 | 248.2895 | 0 | 0
2025-08-01 22:00 | 35.4 | 52.5 | 70 | 27.6835 | 21.0186 | 55.5806 | 152.5549 | 152.5549 | 0 | 0
2025-08-01 23:00 | 35.35 | 48.5 | 70 | 27.6875 | 20.6123 | 53.2039 | 134.0741 | 134.0741 | 0 | 0
2025-08-02 | 34.7 | 49.5 | 70 | 27.4948 | 20.4876 | 53.4196 | 131.3535 | 131.3535 | 0 | 0
2025-08-02 01:00 | 33.75 | 52.5 | 70 | 27.2036 | 20.4403 | 54.5765 | 133.5969 | 133.5969 | 0 | 0
2025-08-02 02:00 | 32.7 | 56.5 | 70 | 26.8762 | 20.4267 | 56.1388 | 137.8609 | 137.8609 | 0 | 0
2025-08-02 03:00 | 31.95 | 58 | 70 | 26.6438 | 20.2864 | 56.479 | 134.979 | 134.979 | 0 | 0
2025-08-02 04:00 | 31.4 | 65 | 70 | 26.4577 | 20.6594 | 59.7408 | 154.715 | 154.715 | 0 | 0
2025-08-02 05:00 | 30.95 | 73.5 | 70 | 26.3003 | 21.1517 | 63.702 | 179.8007 | 179.8007 | 0 | 0
2025-08-02 06:00 | 31.6 | 70.5 | 100 | 26.5055 | 21.1749 | 62.6957 | 253.7673 | 253.7673 | 0 | 0
2025-08-02 07:00 | 33.8 | 60 | 100 | 27.1916 | 21.1346 | 58.7491 | 235.9301 | 235.9301 | 0 | 0
2025-08-02 08:00 | 37 | 45.5 | 100 | 28.17 | 20.8667 | 52.3146 | 197.2041 | 197.2041 | 0 | 0
2025-08-02 09:00 | 40.2 | 32 | 100 | 29.1367 | 20.3192 | 45.0282 | 141.8434 | 141.8434 | 0 | 0
2025-08-02 10:00 | 42.7 | 24 | 100 | 29.873 | 19.9314 | 40.1036 | 102.496 | 102.496 | 0 | 0
2025-08-02 11:00 | 44.65 | 19.5 | 100 | 30.4281 | 19.7354 | 37.0985 | 79.3342 | 79.3342 | 0 | 0
2025-08-02 12:00 | 45.95 | 17 | 100 | 30.7904 | 19.6249 | 35.3154 | 65.5822 | 65.5822 | 0 | 0
2025-08-02 13:00 | 46.1 | 18.5 | 100 | 30.8037 | 19.9127 | 36.6202 | 83.0321 | 83.0321 | 0 | 0
2025-08-02 14:00 | 45 | 23.5 | 100 | 30.4589 | 20.4502 | 40.4586 | 123.3424 | 123.3424 | 0 | 0
2025-08-02 15:00 | 43.5 | 28 | 100 | 30.0291 | 20.7189 | 43.4679 | 149.0714 | 149.0714 | 0 | 0
2025-08-02 16:00 | 41.8 | 35.5 | 100 | 29.5191 | 21.2417 | 48.2962 | 193.0656 | 193.0656 | 0 | 0
2025-08-02 17:00 | 40.15 | 44 | 100 | 29.0207 | 21.7524 | 53.3183 | 236.9791 | 236.9791 | 0 | 0
2025-08-02 18:00 | 38.75 | 50 | 100 | 28.6122 | 21.9439 | 56.3519 | 258.4528 | 258.4528 | 0 | 0
2025-08-02 19:00 | 37.95 | 53.5 | 100 | 28.3781 | 22.0283 | 57.9989 | 269.1696 | 269.1696 | 0 | 0
2025-08-02 20:00 | 38.25 | 48.5 | 100 | 28.4912 | 21.609 | 55.0131 | 238.8597 | 238.8597 | 0 | 0
2025-08-02 21:00 | 37.85 | 44.5 | 100 | 28.41 | 21.0422 | 52.189 | 203.5897 | 203.5897 | 0 | 0
2025-08-02 22:00 | 36.45 | 48 | 70 | 28.0026 | 20.9381 | 53.537 | 143.9363 | 143.9363 | 0 | 0
2025-08-02 23:00 | 35.25 | 51.5 | 70 | 27.6453 | 20.8707 | 54.8914 | 146.2805 | 146.2805 | 0 | 0
2025-08-03 | 34.3 | 55 | 70 | 27.3561 | 20.8644 | 56.3026 | 150.4006 | 150.4006 | 0 | 0
2025-08-03 01:00 | 33.7 | 60.5 | 70 | 27.1605 | 21.1408 | 58.9637 | 166.0249 | 166.0249 | 0 | 0
2025-08-03 02:00 | 33.25 | 65 | 70 | 27.0133 | 21.3608 | 61.0861 | 178.4266 | 178.4266 | 0 | 0
2025-08-03 03:00 | 32.75 | 65 | 70 | 26.8657 | 21.1709 | 60.7031 | 171.8756 | 171.8756 | 0 | 0
2025-08-03 04:00 | 32.75 | 56.5 | 70 | 26.8914 | 20.4458 | 56.1539 | 138.3271 | 138.3271 | 0 | 0
2025-08-03 05:00 | 32.95 | 49.5 | 70 | 26.9733 | 19.8956 | 52.4841 | 112.4085 | 112.4085 | 0 | 0
2025-08-03 06:00 | 34.1 | 39.5 | 100 | 27.3558 | 19.3254 | 47.4163 | 116.6193 | 116.6193 | 0 | 0
2025-08-03 07:00 | 36.35 | 27.5 | 100 | 28.081 | 18.7071 | 40.941 | 63.625 | 63.625 | 0 | 0
2025-08-03 08:00 | 38.7 | 24.5 | 100 | 28.7807 | 18.9653 | 39.478 | 65.1535 | 65.1535 | 0 | 0
2025-08-03 09:00 | 41.15 | 22 | 100 | 29.4819 | 19.2553 | 38.2379 | 68.696 | 68.696 | 0 | 0
2025-08-03 10:00 | 43.25 | 20 | 100 | 30.0621 | 19.4775 | 37.1813 | 70.7567 | 70.7567 | 0 | 0
2025-08-03 11:00 | 43.6 | 24.5 | 100 | 30.0976 | 20.239 | 40.7692 | 117.1239 | 117.1239 | 0 | 0
2025-08-03 12:00 | 41.95 | 35.5 | 100 | 29.557 | 21.2897 | 48.3642 | 195.0823 | 195.0823 | 0 | 0
2025-08-03 13:00 | 41.25 | 39 | 100 | 29.3456 | 21.5139 | 50.5014 | 214.1582 | 214.1582 | 0 | 0
2025-08-03 14:00 | 41.4 | 36 | 100 | 29.413 | 21.1836 | 48.4357 | 191.4138 | 191.4138 | 0 | 0
2025-08-03 15:00 | 40.95 | 34 | 100 | 29.3165 | 20.7914 | 46.7779 | 168.3762 | 168.3762 | 0 | 0
2025-08-03 16:00 | 40.45 | 34.5 | 100 | 29.1813 | 20.7041 | 46.8939 | 165.633 | 165.633 | 0 | 0
2025-08-03 17:00 | 39.9 | 35.5 | 100 | 29.0273 | 20.6608 | 47.3273 | 166.1021 | 166.1021 | 0 | 0
2025-08-03 18:00 | 39.4 | 36 | 100 | 28.8897 | 20.5687 | 47.4322 | 163.1208 | 163.1208 | 0 | 0
2025-08-03 19:00 | 39.1 | 37 | 100 | 28.8012 | 20.5957 | 47.959 | 166.6318 | 166.6318 | 0 | 0
2025-08-03 20:00 | 38.75 | 38 | 100 | 28.6991 | 20.6048 | 48.4503 | 169.2557 | 169.2557 | 0 | 0
2025-08-03 21:00 | 37.75 | 43 | 100 | 28.3923 | 20.8473 | 51.1681 | 191.2253 | 191.2253 | 0 | 0
2025-08-03 22:00 | 36.55 | 47.5 | 70 | 28.0334 | 20.9221 | 53.2837 | 142.6344 | 142.6344 | 0 | 0
2025-08-03 23:00 | 35.85 | 48.5 | 70 | 27.8307 | 20.7843 | 53.4762 | 139.4917 | 139.4917 | 0 | 0
2025-08-04 | 35 | 51.5 | 70 | 27.5735 | 20.7842 | 54.7321 | 143.3633 | 143.3633 | 0 | 0
2025-08-04 01:00 | 34.1 | 55 | 70 | 27.2978 | 20.7943 | 56.1643 | 147.9575 | 147.9575 | 0 | 0
2025-08-04 02:00 | 33.6 | 58 | 70 | 27.1401 | 20.8847 | 57.5029 | 154.4275 | 154.4275 | 0 | 0
2025-08-04 03:00 | 32.85 | 59 | 70 | 26.9139 | 20.699 | 57.5502 | 149.379 | 149.379 | 0 | 0
2025-08-04 04:00 | 31.9 | 62.5 | 70 | 26.6169 | 20.6446 | 58.7739 | 151.4132 | 151.4132 | 0 | 0
2025-08-04 05:00 | 31.25 | 68 | 70 | 26.4047 | 20.8424 | 61.1438 | 163.7267 | 163.7267 | 0 | 0
2025-08-04 06:00 | 32 | 60.5 | 100 | 26.6527 | 20.516 | 57.7914 | 207.0891 | 207.0891 | 0 | 0
2025-08-04 07:00 | 34.25 | 46.5 | 100 | 27.3744 | 20.0537 | 51.4346 | 161.778 | 161.778 | 0 | 0
2025-08-04 08:00 | 36.8 | 35.5 | 100 | 28.1698 | 19.7312 | 45.9963 | 124.6131 | 124.6131 | 0 | 0
2025-08-04 09:00 | 39.1 | 28 | 100 | 28.8682 | 19.512 | 41.8995 | 96.5332 | 96.5332 | 0 | 0
2025-08-04 10:00 | 40.9 | 24.5 | 100 | 29.391 | 19.538 | 39.9597 | 87.4617 | 87.4617 | 0 | 0
2025-08-04 11:00 | 42.4 | 22 | 100 | 29.8165 | 19.57 | 38.5009 | 80.8791 | 80.8791 | 0 | 0
2025-08-04 12:00 | 43.65 | 20 | 100 | 30.166 | 19.577 | 37.2568 | 74.4443 | 74.4443 | 0 | 0
2025-08-04 13:00 | 44.25 | 19 | 100 | 30.333 | 19.5632 | 36.5994 | 70.4158 | 70.4158 | 0 | 0
2025-08-04 14:00 | 43.95 | 21 | 100 | 30.2305 | 19.801 | 38.1225 | 87.1992 | 87.1992 | 0 | 0
2025-08-04 15:00 | 42.7 | 26 | 100 | 29.8506 | 20.2173 | 41.6181 | 120.7937 | 120.7937 | 0 | 0
2025-08-04 16:00 | 40.75 | 32 | 100 | 29.2827 | 20.4793 | 45.2592 | 148.9793 | 148.9793 | 0 | 0
2025-08-04 17:00 | 39.2 | 39 | 100 | 28.8131 | 20.8631 | 49.3398 | 183.2963 | 183.2963 | 0 | 0
2025-08-04 18:00 | 38.1 | 47.5 | 100 | 28.458 | 21.4509 | 54.2608 | 229.0689 | 229.0689 | 0 | 0
2025-08-04 19:00 | 37.3 | 52.5 | 100 | 28.2111 | 21.6943 | 56.8657 | 250.4307 | 250.4307 | 0 | 0
2025-08-04 20:00 | 37.05 | 52 | 100 | 28.1463 | 21.5549 | 56.3699 | 242.5665 | 242.5665 | 0 | 0
2025-08-04 21:00 | 36.55 | 51.5 | 100 | 28.0119 | 21.3282 | 55.7115 | 230.517 | 230.517 | 0 | 0
2025-08-04 22:00 | 35.45 | 54.5 | 70 | 27.6889 | 21.2313 | 56.7541 | 161.8202 | 161.8202 | 0 | 0
2025-08-04 23:00 | 34.4 | 57.5 | 70 | 27.3756 | 21.1311 | 57.7608 | 162.0609 | 162.0609 | 0 | 0
2025-08-05 | 33.65 | 58.5 | 70 | 27.1531 | 20.9473 | 57.8087 | 157.0642 | 157.0642 | 0 | 0
2025-08-05 01:00 | 32.95 | 60.5 | 70 | 26.9392 | 20.8645 | 58.4252 | 156.5744 | 156.5744 | 0 | 0
2025-08-05 02:00 | 32.95 | 59.5 | 70 | 26.9423 | 20.7786 | 57.8843 | 152.5745 | 152.5745 | 0 | 0
2025-08-05 03:00 | 34.45 | 46 | 70 | 27.4356 | 20.0716 | 51.253 | 113.1885 | 113.1885 | 0 | 0
2025-08-05 04:00 | 35.4 | 35.5 | 70 | 27.7612 | 19.3137 | 45.5218 | 75.0533 | 75.0533 | 0 | 0
2025-08-05 05:00 | 34.7 | 38 | 70 | 27.542 | 19.3617 | 46.7517 | 80.286 | 80.286 | 0 | 0
2025-08-05 06:00 | 34.4 | 40 | 100 | 27.4442 | 19.4705 | 47.7914 | 123.4271 | 123.4271 | 0 | 0
2025-08-05 07:00 | 35.2 | 38.5 | 100 | 27.6887 | 19.5668 | 47.2133 | 124.2326 | 124.2326 | 0 | 0
2025-08-05 08:00 | 36.65 | 35.5 | 100 | 28.1266 | 19.6877 | 45.9343 | 122.6233 | 122.6233 | 0 | 0
2025-08-05 09:00 | 38.45 | 32 | 100 | 28.6586 | 19.817 | 44.3464 | 119.6597 | 119.6597 | 0 | 0
2025-08-05 10:00 | 40.3 | 28 | 100 | 29.1978 | 19.8414 | 42.2578 | 110.1305 | 110.1305 | 0 | 0
2025-08-05 11:00 | 41.9 | 25 | 100 | 29.6532 | 19.8679 | 40.5992 | 102.5731 | 102.5731 | 0 | 0
2025-08-05 12:00 | 43.05 | 23 | 100 | 29.9751 | 19.8791 | 39.4295 | 96.8361 | 96.8361 | 0 | 0
2025-08-05 13:00 | 43.15 | 24.5 | 100 | 29.9832 | 20.1231 | 40.6141 | 111.9618 | 111.9618 | 0 | 0
2025-08-05 14:00 | 42.35 | 28 | 100 | 29.7386 | 20.4039 | 42.9888 | 134.6112 | 134.6112 | 0 | 0
2025-08-05 15:00 | 41.55 | 30 | 100 | 29.5111 | 20.4501 | 44.1511 | 142.2676 | 142.2676 | 0 | 0
2025-08-05 16:00 | 40.65 | 32.5 | 100 | 29.2518 | 20.5145 | 45.5652 | 151.7549 | 151.7549 | 0 | 0
2025-08-05 17:00 | 39.25 | 36.5 | 100 | 28.8456 | 20.5853 | 47.6848 | 164.7545 | 164.7545 | 0 | 0
2025-08-05 18:00 | 37.55 | 43 | 100 | 28.3373 | 20.7824 | 51.0556 | 188.1581 | 188.1581 | 0 | 0
2025-08-05 19:00 | 36.3 | 50 | 100 | 27.9502 | 21.0899 | 54.6445 | 216.3954 | 216.3954 | 0 | 0
2025-08-05 20:00 | 35.8 | 52.5 | 100 | 27.7972 | 21.1622 | 55.8155 | 224.3941 | 224.3941 | 0 | 0
2025-08-05 21:00 | 35.8 | 47.5 | 100 | 27.8215 | 20.6692 | 52.8372 | 191.7771 | 191.7771 | 0 | 0
2025-08-05 22:00 | 35.6 | 42.5 | 70 | 27.7877 | 20.0992 | 49.7577 | 109.1878 | 109.1878 | 0 | 0
2025-08-05 23:00 | 34.95 | 42.5 | 70 | 27.5976 | 19.8906 | 49.4675 | 102.7832 | 102.7832 | 0 | 0
2025-08-06 | 34.3 | 43.5 | 70 | 27.4008 | 19.7802 | 49.7617 | 100.8356 | 100.8356 | 0 | 0
2025-08-06 01:00 | 33.65 | 45 | 70 | 27.2002 | 19.7132 | 50.3247 | 100.8585 | 100.8585 | 0 | 0
2025-08-06 02:00 | 33 | 46.5 | 70 | 26.9979 | 19.6407 | 50.8674 | 100.6313 | 100.6313 | 0 | 0
2025-08-06 03:00 | 32.6 | 47.5 | 70 | 26.8723 | 19.6001 | 51.2304 | 100.6607 | 100.6607 | 0 | 0
2025-08-06 04:00 | 32.75 | 49.5 | 70 | 26.9124 | 19.8297 | 52.3732 | 110.2106 | 110.2106 | 0 | 0
2025-08-06 05:00 | 33.05 | 46.5 | 70 | 27.0132 | 19.6576 | 50.8825 | 101.0775 | 101.0775 | 0 | 0
2025-08-06 06:00 | 33.8 | 37.5 | 100 | 27.2719 | 19.0407 | 46.1721 | 100.3284 | 100.3284 | 0 | 0
2025-08-06 07:00 | 35.4 | 32.5 | 100 | 27.7747 | 18.998 | 43.7323 | 87.2532 | 87.2532 | 0 | 0
2025-08-06 08:00 | 37.2 | 31.5 | 100 | 28.3073 | 19.3997 | 43.6252 | 101.0951 | 101.0951 | 0 | 0
2025-08-06 09:00 | 39.05 | 29.5 | 100 | 28.8432 | 19.6835 | 42.8922 | 107.697 | 107.697 | 0 | 0
2025-08-06 10:00 | 40.85 | 26.5 | 100 | 29.3593 | 19.7922 | 41.3742 | 103.9206 | 103.9206 | 0 | 0
2025-08-06 11:00 | 42.35 | 23.5 | 100 | 29.7872 | 19.7719 | 39.6167 | 94.0446 | 94.0446 | 0 | 0
2025-08-06 12:00 | 43.5 | 21.5 | 100 | 30.1089 | 19.7673 | 38.3968 | 87.4204 | 87.4204 | 0 | 0
2025-08-06 13:00 | 44 | 21.5 | 100 | 30.2368 | 19.8906 | 38.5312 | 92.5808 | 92.5808 | 0 | 0
2025-08-06 14:00 | 43.4 | 25 | 100 | 30.0409 | 20.2601 | 41.0917 | 119.5889 | 119.5889 | 0 | 0
2025-08-06 15:00 | 42 | 29.5 | 100 | 29.6326 | 20.5093 | 43.9726 | 143.6577 | 143.6577 | 0 | 0
2025-08-06 16:00 | 40.9 | 30 | 100 | 29.3406 | 20.2641 | 43.9008 | 134.2071 | 134.2071 | 0 | 0
2025-08-06 17:00 | 39.65 | 32.5 | 100 | 28.9847 | 20.2205 | 45.1535 | 138.8361 | 138.8361 | 0 | 0
2025-08-06 18:00 | 37.9 | 41.5 | 100 | 28.4431 | 20.7316 | 50.2909 | 182.6958 | 182.6958 | 0 | 0
2025-08-06 19:00 | 36.6 | 48.5 | 100 | 28.0419 | 21.0413 | 53.9242 | 211.3099 | 211.3099 | 0 | 0
2025-08-06 20:00 | 36.15 | 49 | 100 | 27.9132 | 20.9383 | 53.9477 | 207.3045 | 207.3045 | 0 | 0
2025-08-06 21:00 | 36.3 | 44.5 | 100 | 27.9788 | 20.5311 | 51.3086 | 179.5734 | 179.5734 | 0 | 0
2025-08-06 22:00 | 36.05 | 41 | 70 | 27.9251 | 20.0873 | 49.0676 | 106.6929 | 106.6929 | 0 | 0
2025-08-06 23:00 | 35.3 | 41.5 | 70 | 27.7048 | 19.9007 | 49.0363 | 101.699 | 101.699 | 0 | 0
2025-08-07 | 34.45 | 43 | 70 | 27.4474 | 19.7794 | 49.542 | 100.1307 | 100.1307 | 0 | 0
2025-08-07 01:00 | 33.8 | 45 | 70 | 27.2454 | 19.7622 | 50.3913 | 102.3516 | 102.3516 | 0 | 0
2025-08-07 02:00 | 33.55 | 45.5 | 70 | 27.1682 | 19.728 | 50.5585 | 101.9657 | 101.9657 | 0 | 0
2025-08-07 03:00 | 33.25 | 47 | 70 | 27.0724 | 19.7694 | 51.2497 | 105.1772 | 105.1772 | 0 | 0
2025-08-07 04:00 | 33.1 | 50 | 70 | 27.0173 | 19.9927 | 52.8177 | 115.9264 | 115.9264 | 0 | 0
2025-08-07 05:00 | 33.2 | 54 | 70 | 27.0347 | 20.3867 | 55.0519 | 133.3153 | 133.3153 | 0 | 0
2025-08-07 06:00 | 34.05 | 50.5 | 100 | 27.3001 | 20.3633 | 53.5896 | 183.1725 | 183.1725 | 0 | 0
2025-08-07 07:00 | 35.85 | 36.5 | 100 | 27.8891 | 19.5549 | 46.2615 | 119.3735 | 119.3735 | 0 | 0
2025-08-07 08:00 | 37.7 | 28 | 100 | 28.4719 | 19.1329 | 41.5285 | 81.1349 | 81.1349 | 0 | 0
2025-08-07 09:00 | 39.5 | 26 | 100 | 28.9945 | 19.3687 | 40.6478 | 84.99 | 84.99 | 0 | 0
2025-08-07 10:00 | 41.15 | 24.5 | 100 | 29.4584 | 19.6037 | 40.0224 | 90.0758 | 90.0758 | 0 | 0
2025-08-07 11:00 | 42.6 | 23 | 100 | 29.8581 | 19.7645 | 39.3049 | 92.0776 | 92.0776 | 0 | 0
2025-08-07 12:00 | 43.65 | 21 | 100 | 30.1536 | 19.7296 | 38.0417 | 84.1092 | 84.1092 | 0 | 0
2025-08-07 13:00 | 43.7 | 22 | 100 | 30.1541 | 19.8922 | 38.8418 | 94.2876 | 94.2876 | 0 | 0
2025-08-07 14:00 | 42.75 | 25.5 | 100 | 29.8691 | 20.1601 | 41.254 | 116.7721 | 116.7721 | 0 | 0
2025-08-07 15:00 | 41.35 | 28.5 | 100 | 29.4735 | 20.1927 | 42.9905 | 126.9566 | 126.9566 | 0 | 0
2025-08-07 16:00 | 39.85 | 33 | 100 | 29.0346 | 20.3413 | 45.5762 | 145.3816 | 145.3816 | 0 | 0
2025-08-07 17:00 | 38.55 | 39 | 100 | 28.6377 | 20.6581 | 49.0031 | 173.825 | 173.825 | 0 | 0
2025-08-07 18:00 | 37.75 | 41.5 | 100 | 28.4019 | 20.6838 | 50.2073 | 180.4162 | 180.4162 | 0 | 0
2025-08-07 19:00 | 37.3 | 40.5 | 100 | 28.283 | 20.4307 | 49.3443 | 166.6976 | 166.6976 | 0 | 0
2025-08-07 20:00 | 37 | 38.5 | 100 | 28.21 | 20.1195 | 47.9521 | 148.3895 | 148.3895 | 0 | 0
2025-08-07 21:00 | 36.9 | 39 | 100 | 28.1789 | 20.142 | 48.2196 | 150.5171 | 150.5171 | 0 | 0
2025-08-07 22:00 | 36.2 | 49 | 70 | 27.9273 | 20.9558 | 53.974 | 145.6479 | 145.6479 | 0 | 0
2025-08-07 23:00 | 35 | 58.5 | 70 | 27.5433 | 21.4425 | 58.7633 | 173.8605 | 173.8605 | 0 | 0
2025-08-08 | 34.15 | 61 | 70 | 27.2897 | 21.354 | 59.5524 | 173.6723 | 173.6723 | 0 | 0
2025-08-08 01:00 | 33.6 | 62 | 70 | 27.1262 | 21.2363 | 59.6987 | 170.753 | 170.753 | 0 | 0
2025-08-08 02:00 | 33.2 | 61.5 | 70 | 27.0102 | 21.0435 | 59.1355 | 163.6522 | 163.6522 | 0 | 0
2025-08-08 03:00 | 32.8 | 61 | 70 | 26.8929 | 20.8523 | 58.5851 | 156.6579 | 156.6579 | 0 | 0
2025-08-08 04:00 | 32.35 | 64 | 70 | 26.7492 | 20.9369 | 59.8628 | 162.7241 | 162.7241 | 0 | 0
2025-08-08 05:00 | 32.1 | 66.5 | 70 | 26.6671 | 21.0481 | 60.9885 | 169.071 | 169.071 | 0 | 0
2025-08-08 06:00 | 33.25 | 58.5 | 100 | 27.035 | 20.8027 | 57.5261 | 217.264 | 217.264 | 0 | 0
2025-08-08 07:00 | 35.55 | 41 | 100 | 27.7802 | 19.9319 | 48.83 | 145.2639 | 145.2639 | 0 | 0
2025-08-08 08:00 | 37.45 | 30.5 | 100 | 28.385 | 19.3567 | 43.0582 | 96.6734 | 96.6734 | 0 | 0
2025-08-08 09:00 | 39.2 | 28.5 | 100 | 28.8923 | 19.6026 | 42.259 | 101.5123 | 101.5123 | 0 | 0
2025-08-08 10:00 | 40.95 | 25.5 | 100 | 29.3954 | 19.6872 | 40.6826 | 96.4518 | 96.4518 | 0 | 0
2025-08-08 11:00 | 42.35 | 23 | 100 | 29.7926 | 19.7023 | 39.2342 | 89.41 | 89.41 | 0 | 0
2025-08-08 12:00 | 43.3 | 21.5 | 100 | 30.0573 | 19.7203 | 38.3382 | 85.288 | 85.288 | 0 | 0
2025-08-08 13:00 | 43 | 24 | 100 | 29.9506 | 20.0122 | 40.1807 | 105.607 | 105.607 | 0 | 0
2025-08-08 14:00 | 41.85 | 28 | 100 | 29.6094 | 20.2664 | 42.7971 | 128.5004 | 128.5004 | 0 | 0
2025-08-08 15:00 | 40.85 | 30.5 | 100 | 29.3228 | 20.3165 | 44.2254 | 137.6296 | 137.6296 | 0 | 0
2025-08-08 16:00 | 39.7 | 33.5 | 100 | 28.9903 | 20.3603 | 45.8458 | 147.2768 | 147.2768 | 0 | 0
2025-08-08 17:00 | 38.3 | 38.5 | 100 | 28.5729 | 20.5242 | 48.5446 | 166.4359 | 166.4359 | 0 | 0
2025-08-08 18:00 | 37.05 | 44.5 | 100 | 28.1898 | 20.7795 | 51.7092 | 190.9177 | 190.9177 | 0 | 0
2025-08-08 19:00 | 36.7 | 44.5 | 100 | 28.0919 | 20.6644 | 51.5117 | 185.5057 | 185.5057 | 0 | 0
2025-08-08 20:00 | 36.85 | 41 | 100 | 28.1536 | 20.3441 | 49.4229 | 163.5608 | 163.5608 | 0 | 0
2025-08-08 21:00 | 36.65 | 41.5 | 100 | 28.0942 | 20.3337 | 49.6324 | 164.1063 | 164.1063 | 0 | 0
2025-08-08 22:00 | 36.15 | 48 | 70 | 27.9186 | 20.8401 | 53.3222 | 140.2907 | 140.2907 | 0 | 0
2025-08-08 23:00 | 35.3 | 55 | 70 | 27.6442 | 21.2259 | 56.9314 | 162.1238 | 162.1238 | 0 | 0
2025-08-09 | 34.65 | 58.5 | 70 | 27.4436 | 21.3147 | 58.4934 | 169.3392 | 169.3392 | 0 | 0
2025-08-09 01:00 | 34.55 | 59.5 | 70 | 27.4108 | 21.3686 | 58.9915 | 172.3618 | 172.3618 | 0 | 0
2025-08-09 02:00 | 34.65 | 55.5 | 70 | 27.4559 | 21.0387 | 56.7845 | 156.4774 | 156.4774 | 0 | 0
2025-08-09 03:00 | 34.15 | 54 | 70 | 27.3165 | 20.7225 | 55.6071 | 144.1139 | 144.1139 | 0 | 0
2025-08-09 04:00 | 33.2 | 59.5 | 70 | 27.017 | 20.8725 | 58.0252 | 155.4256 | 155.4256 | 0 | 0
2025-08-09 05:00 | 32.55 | 63 | 70 | 26.8123 | 20.9305 | 59.4511 | 161.1878 | 161.1878 | 0 | 0
2025-08-09 06:00 | 32.95 | 60 | 100 | 26.941 | 20.8245 | 58.1179 | 220.4246 | 220.4246 | 0 | 0
2025-08-09 07:00 | 35.05 | 44.5 | 100 | 27.6186 | 20.1264 | 50.6404 | 160.6155 | 160.6155 | 0 | 0
2025-08-09 08:00 | 37.05 | 31.5 | 100 | 28.2641 | 19.363 | 43.5526 | 99.014 | 99.014 | 0 | 0
2025-08-09 09:00 | 38.4 | 30 | 100 | 28.6581 | 19.5683 | 42.9953 | 103.6578 | 103.6578 | 0 | 0
2025-08-09 10:00 | 40 | 27.5 | 100 | 29.1204 | 19.6991 | 41.7958 | 102.3442 | 102.3442 | 0 | 0
2025-08-09 11:00 | 41.45 | 25 | 100 | 29.534 | 19.7542 | 40.4476 | 97.3893 | 97.3893 | 0 | 0
2025-08-09 12:00 | 42.45 | 23.5 | 100 | 29.8134 | 19.8033 | 39.6225 | 94.8279 | 94.8279 | 0 | 0
2025-08-09 13:00 | 42.7 | 24 | 100 | 29.8731 | 19.9379 | 40.0751 | 102.1323 | 102.1323 | 0 | 0
2025-08-09 14:00 | 42.15 | 25.5 | 100 | 29.7136 | 20.0055 | 41.0364 | 109.6815 | 109.6815 | 0 | 0
2025-08-09 15:00 | 41.1 | 27.5 | 100 | 29.417 | 19.9957 | 42.1594 | 115.1525 | 115.1525 | 0 | 0
2025-08-09 16:00 | 39.95 | 29.5 | 100 | 29.0903 | 19.9369 | 43.1809 | 118.2257 | 118.2257 | 0 | 0
2025-08-09 17:00 | 38.6 | 33 | 100 | 28.6934 | 19.9787 | 45.0595 | 129.1072 | 129.1072 | 0 | 0
2025-08-09 18:00 | 37 | 40 | 100 | 28.2016 | 20.2842 | 48.8721 | 158.7226 | 158.7226 | 0 | 0
2025-08-09 19:00 | 35.9 | 46 | 100 | 27.8575 | 20.5545 | 51.9781 | 183.255 | 183.255 | 0 | 0
2025-08-09 20:00 | 35.8 | 45 | 100 | 27.8338 | 20.4209 | 51.3223 | 175.0907 | 175.0907 | 0 | 0
2025-08-09 21:00 | 35.75 | 41.5 | 100 | 27.8361 | 20.0482 | 49.2041 | 151.2125 | 151.2125 | 0 | 0
2025-08-09 22:00 | 35.3 | 40.5 | 70 | 27.7094 | 19.804 | 48.4176 | 96.9087 | 96.9087 | 0 | 0
2025-08-09 23:00 | 34.85 | 40 | 70 | 27.5786 | 19.6122 | 47.947 | 90.4354 | 90.4354 | 0 | 0
2025-08-10 | 34.25 | 42.5 | 70 | 27.3897 | 19.6708 | 49.1455 | 95.8004 | 95.8004 | 0 | 0
2025-08-10 01:00 | 33.65 | 46.5 | 70 | 27.1951 | 19.8576 | 51.1333 | 106.9661 | 106.9661 | 0 | 0
2025-08-10 02:00 | 32.9 | 54.5 | 70 | 26.943 | 20.3274 | 55.1279 | 131.7681 | 131.7681 | 0 | 0
2025-08-10 03:00 | 32.25 | 61 | 70 | 26.7275 | 20.6513 | 58.1916 | 149.7269 | 149.7269 | 0 | 0
2025-08-10 04:00 | 32.1 | 59 | 70 | 26.6873 | 20.4289 | 57.0457 | 140.2174 | 140.2174 | 0 | 0
2025-08-10 05:00 | 32.1 | 58 | 70 | 26.69 | 20.3442 | 56.5217 | 136.3669 | 136.3669 | 0 | 0
2025-08-10 06:00 | 33.2 | 48 | 100 | 27.0541 | 19.8475 | 51.7478 | 155.1111 | 155.1111 | 0 | 0
2025-08-10 07:00 | 35.2 | 34.5 | 100 | 27.7061 | 19.1549 | 44.8426 | 97.9197 | 97.9197 | 0 | 0
2025-08-10 08:00 | 36.95 | 31 | 100 | 28.238 | 19.2756 | 43.2194 | 94.4006 | 94.4006 | 0 | 0
2025-08-10 09:00 | 38.75 | 28.5 | 100 | 28.7668 | 19.4819 | 42.1156 | 96.2706 | 96.2706 | 0 | 0
2025-08-10 10:00 | 40.55 | 26 | 100 | 29.2828 | 19.6502 | 40.9137 | 96.1587 | 96.1587 | 0 | 0
2025-08-10 11:00 | 42 | 24 | 100 | 29.6899 | 19.7572 | 39.8752 | 94.5939 | 94.5939 | 0 | 0
2025-08-10 12:00 | 43.05 | 22 | 100 | 29.9867 | 19.7346 | 38.6511 | 87.3381 | 87.3381 | 0 | 0
2025-08-10 13:00 | 43.3 | 22 | 100 | 30.0514 | 19.7964 | 38.7198 | 89.9551 | 89.9551 | 0 | 0
2025-08-10 14:00 | 42.55 | 24 | 100 | 29.8341 | 19.8963 | 40.0432 | 100.6593 | 100.6593 | 0 | 0
2025-08-10 15:00 | 41.35 | 27 | 100 | 29.488 | 19.9942 | 41.891 | 113.8812 | 113.8812 | 0 | 0
2025-08-10 16:00 | 40.15 | 28.5 | 100 | 29.1529 | 19.8629 | 42.5646 | 112.5729 | 112.5729 | 0 | 0
2025-08-10 17:00 | 39 | 30 | 100 | 28.8257 | 19.7299 | 43.2152 | 111.0523 | 111.0523 | 0 | 0
2025-08-10 18:00 | 37.75 | 36.5 | 100 | 28.4334 | 20.1285 | 47.0033 | 144.1705 | 144.1705 | 0 | 0
2025-08-10 19:00 | 36.65 | 42 | 100 | 28.0915 | 20.3858 | 49.9485 | 167.6378 | 167.6378 | 0 | 0
2025-08-10 20:00 | 36.2 | 42.5 | 100 | 27.9607 | 20.2937 | 50.0302 | 164.4683 | 164.4683 | 0 | 0
2025-08-10 21:00 | 35.95 | 42 | 100 | 27.8914 | 20.1616 | 49.6071 | 157.4979 | 157.4979 | 0 | 0
2025-08-10 22:00 | 35.45 | 42 | 70 | 27.7465 | 20.0023 | 49.3785 | 105.2941 | 105.2941 | 0 | 0
2025-08-10 23:00 | 35 | 41 | 70 | 27.6188 | 19.7579 | 48.6002 | 96.4222 | 96.4222 | 0 | 0
2025-08-11 | 34.45 | 40.5 | 70 | 27.4573 | 19.5358 | 48.0952 | 89.0461 | 89.0461 | 0 | 0
2025-08-11 01:00 | 33.95 | 41 | 70 | 27.305 | 19.4282 | 48.1912 | 86.5938 | 86.5938 | 0 | 0
2025-08-11 02:00 | 33.6 | 44.5 | 70 | 27.1868 | 19.6519 | 50.011 | 98.1513 | 98.1513 | 0 | 0
2025-08-11 03:00 | 33.4 | 51.5 | 70 | 27.1029 | 20.2329 | 53.7837 | 125.2203 | 125.2203 | 0 | 0
2025-08-11 04:00 | 33.9 | 44 | 70 | 27.2791 | 19.7023 | 49.8513 | 98.9049 | 98.9049 | 0 | 0
2025-08-11 05:00 | 34.05 | 34 | 70 | 27.3608 | 18.7691 | 44.245 | 56.9766 | 56.9766 | 0 | 0
2025-08-11 06:00 | 34 | 35 | 100 | 27.3419 | 18.8554 | 44.7957 | 87.0089 | 87.0089 | 0 | 0
2025-08-11 07:00 | 34.9 | 34.5 | 100 | 27.6164 | 19.068 | 44.7525 | 94.3324 | 94.3324 | 0 | 0
2025-08-11 08:00 | 36.2 | 34 | 100 | 28.0038 | 19.3942 | 44.8436 | 106.4879 | 106.4879 | 0 | 0
2025-08-11 09:00 | 37.75 | 32.5 | 100 | 28.4584 | 19.6761 | 44.4134 | 114.6391 | 114.6391 | 0 | 0
2025-08-11 10:00 | 39.45 | 29 | 100 | 28.9576 | 19.737 | 42.6596 | 108.1578 | 108.1578 | 0 | 0
2025-08-11 11:00 | 41 | 26 | 100 | 29.4042 | 19.7702 | 41.0426 | 101.108 | 101.108 | 0 | 0
2025-08-11 12:00 | 42.15 | 24 | 100 | 29.7294 | 19.7954 | 39.9174 | 96.2039 | 96.2039 | 0 | 0
2025-08-11 13:00 | 42.35 | 25 | 100 | 29.7711 | 19.9881 | 40.7269 | 107.4413 | 107.4413 | 0 | 0
2025-08-11 14:00 | 41.55 | 28 | 100 | 29.531 | 20.1857 | 42.6779 | 124.7729 | 124.7729 | 0 | 0
2025-08-11 15:00 | 40.55 | 30.5 | 100 | 29.2433 | 20.2334 | 44.0986 | 133.7529 | 133.7529 | 0 | 0
2025-08-11 16:00 | 39.3 | 34 | 100 | 28.8783 | 20.3039 | 46.0066 | 145.8292 | 145.8292 | 0 | 0
2025-08-11 17:00 | 37.8 | 40 | 100 | 28.4253 | 20.5365 | 49.2589 | 170.1557 | 170.1557 | 0 | 0
2025-08-11 18:00 | 36.55 | 45.5 | 100 | 28.0443 | 20.7187 | 52.0413 | 190.0028 | 190.0028 | 0 | 0
2025-08-11 19:00 | 35.5 | 49 | 100 | 27.7287 | 20.7174 | 53.5432 | 196.666 | 196.666 | 0 | 0
2025-08-11 20:00 | 34.9 | 51 | 100 | 27.547 | 20.7047 | 54.3538 | 199.7165 | 199.7165 | 0 | 0
2025-08-11 21:00 | 34.7 | 50 | 100 | 27.4931 | 20.5407 | 53.6576 | 190.2179 | 190.2179 | 0 | 0
2025-08-11 22:00 | 34.3 | 48 | 70 | 27.3836 | 20.215 | 52.298 | 120.1324 | 120.1324 | 0 | 0
2025-08-11 23:00 | 33.7 | 46.5 | 70 | 27.2101 | 19.8738 | 51.1624 | 107.5209 | 107.5209 | 0 | 0
2025-08-12 | 33 | 46.5 | 70 | 26.9979 | 19.643 | 50.849 | 100.4886 | 100.4886 | 0 | 0
2025-08-12 01:00 | 32.25 | 47.5 | 70 | 26.7643 | 19.4862 | 51.0649 | 97.0602 | 97.0602 | 0 | 0
2025-08-12 02:00 | 31.65 | 48.5 | 70 | 26.5748 | 19.376 | 51.337 | 95.0019 | 95.0019 | 0 | 0
2025-08-12 03:00 | 31.25 | 49 | 70 | 26.4479 | 19.2866 | 51.4278 | 92.9337 | 92.9337 | 0 | 0
2025-08-12 04:00 | 31.2 | 48.5 | 70 | 26.4332 | 19.2276 | 51.1475 | 90.531 | 90.531 | 0 | 0
2025-08-12 05:00 | 31.25 | 47.5 | 70 | 26.4513 | 19.1594 | 50.6495 | 87.209 | 87.209 | 0 | 0
2025-08-12 06:00 | 32.05 | 44 | 100 | 26.7114 | 19.1113 | 49.1181 | 116.0399 | 116.0399 | 0 | 0
2025-08-12 07:00 | 34.3 | 36 | 100 | 27.4295 | 19.044 | 45.4483 | 96.8026 | 96.8026 | 0 | 0
2025-08-12 08:00 | 36.5 | 30 | 100 | 28.1122 | 19.0381 | 42.4774 | 82.2697 | 82.2697 | 0 | 0
2025-08-12 09:00 | 38.3 | 27.5 | 100 | 28.6466 | 19.2386 | 41.3339 | 83.6369 | 83.6369 | 0 | 0
2025-08-12 10:00 | 40.15 | 25 | 100 | 29.1821 | 19.4138 | 40.1057 | 83.5456 | 83.5456 | 0 | 0
2025-08-12 11:00 | 41.65 | 22.5 | 100 | 29.6119 | 19.4571 | 38.6812 | 77.6432 | 77.6432 | 0 | 0
2025-08-12 12:00 | 42.55 | 21 | 100 | 29.8669 | 19.4635 | 37.7722 | 73.0724 | 73.0724 | 0 | 0
2025-08-12 13:00 | 42.5 | 22 | 100 | 29.8429 | 19.5963 | 38.5192 | 81.8132 | 81.8132 | 0 | 0
2025-08-12 14:00 | 41.95 | 22.5 | 100 | 29.692 | 19.5295 | 38.7648 | 80.8352 | 80.8352 | 0 | 0
2025-08-12 15:00 | 41.15 | 23.5 | 100 | 29.4678 | 19.4648 | 39.3071 | 81.519 | 81.519 | 0 | 0
2025-08-12 16:00 | 39.7 | 28 | 100 | 29.0341 | 19.6755 | 42.0784 | 103.3396 | 103.3396 | 0 | 0
2025-08-12 17:00 | 38 | 35 | 100 | 28.5129 | 20.0332 | 46.1416 | 136.4904 | 136.4904 | 0 | 0
2025-08-12 18:00 | 36.35 | 44.5 | 100 | 27.9931 | 20.5486 | 51.3278 | 180.2444 | 180.2444 | 0 | 0
2025-08-12 19:00 | 35 | 55 | 100 | 27.5586 | 21.1175 | 56.7365 | 226.5156 | 226.5156 | 0 | 0
2025-08-12 20:00 | 34.2 | 63 | 100 | 27.2965 | 21.5507 | 60.7005 | 260.8434 | 260.8434 | 0 | 0
2025-08-12 21:00 | 33.7 | 67 | 100 | 27.1377 | 21.7058 | 62.5125 | 274.7314 | 274.7314 | 0 | 0
2025-08-12 22:00 | 33.15 | 69 | 70 | 26.9712 | 21.6603 | 63.1423 | 192.7886 | 192.7886 | 0 | 0
2025-08-12 23:00 | 32.4 | 70.5 | 70 | 26.7457 | 21.4896 | 63.3179 | 188.3287 | 188.3287 | 0 | 0
2025-08-13 | 31.75 | 71.5 | 70 | 26.5485 | 21.3138 | 63.3068 | 183.2171 | 183.2171 | 0 | 0
2025-08-13 01:00 | 31.2 | 72 | 70 | 26.3804 | 21.1358 | 63.1241 | 177.6127 | 177.6127 | 0 | 0
2025-08-13 02:00 | 30.8 | 72 | 70 | 26.2576 | 20.9792 | 62.814 | 172.256 | 172.256 | 0 | 0
2025-08-13 03:00 | 30.5 | 71.5 | 70 | 26.1657 | 20.8234 | 62.3385 | 166.5045 | 166.5045 | 0 | 0
2025-08-13 04:00 | 30.8 | 66.5 | 70 | 26.269 | 20.5532 | 60.0686 | 152.5338 | 152.5338 | 0 | 0
2025-08-13 05:00 | 31.1 | 60.5 | 70 | 26.3752 | 20.1874 | 57.2374 | 134.3078 | 134.3078 | 0 | 0
2025-08-13 06:00 | 31.45 | 55.5 | 100 | 26.4956 | 19.9016 | 54.8759 | 170.8968 | 170.8968 | 0 | 0
2025-08-13 07:00 | 33.35 | 47.5 | 100 | 27.1011 | 19.8492 | 51.5629 | 154.5752 | 154.5752 | 0 | 0
2025-08-13 08:00 | 36.2 | 38.5 | 100 | 27.981 | 19.8728 | 47.607 | 137.4745 | 137.4745 | 0 | 0
2025-08-13 09:00 | 38.95 | 30.5 | 100 | 28.8082 | 19.7775 | 43.5302 | 114.3032 | 114.3032 | 0 | 0
2025-08-13 10:00 | 40.3 | 29 | 100 | 29.1892 | 19.9688 | 42.9612 | 118.4132 | 118.4132 | 0 | 0
2025-08-13 11:00 | 40.35 | 31.5 | 100 | 29.1812 | 20.3025 | 44.7275 | 139.5309 | 139.5309 | 0 | 0
2025-08-13 12:00 | 40.2 | 34 | 100 | 29.1198 | 20.571 | 46.4084 | 157.9217 | 157.9217 | 0 | 0
2025-08-13 13:00 | 40.05 | 36 | 100 | 29.0631 | 20.7707 | 47.7268 | 171.9692 | 171.9692 | 0 | 0
2025-08-13 14:00 | 39.7 | 37.5 | 100 | 28.9581 | 20.843 | 48.5843 | 178.9124 | 178.9124 | 0 | 0
2025-08-13 15:00 | 39 | 40 | 100 | 28.752 | 20.915 | 49.9025 | 187.9834 | 187.9834 | 0 | 0
2025-08-13 16:00 | 38.1 | 40.5 | 100 | 28.5045 | 20.684 | 49.7571 | 178.4423 | 178.4423 | 0 | 0
2025-08-13 17:00 | 37.05 | 41.5 | 100 | 28.2069 | 20.4572 | 49.8608 | 170.2675 | 170.2675 | 0 | 0
2025-08-13 18:00 | 36 | 47 | 100 | 27.8808 | 20.6849 | 52.6672 | 191.7957 | 191.7957 | 0 | 0
2025-08-13 19:00 | 35.1 | 54.5 | 100 | 27.5891 | 21.1045 | 56.534 | 225.3223 | 225.3223 | 0 | 0
2025-08-13 20:00 | 34.3 | 60 | 100 | 27.3367 | 21.3199 | 59.1122 | 244.9566 | 244.9566 | 0 | 0
2025-08-13 21:00 | 33.5 | 63.5 | 100 | 27.0916 | 21.3282 | 60.4548 | 250.8847 | 250.8847 | 0 | 0
2025-08-13 22:00 | 32.75 | 66 | 70 | 26.8627 | 21.2549 | 61.2324 | 175.7587 | 175.7587 | 0 | 0
2025-08-13 23:00 | 32.05 | 68 | 70 | 26.6478 | 21.15 | 61.7505 | 174.2415 | 174.2415 | 0 | 0
2025-08-14 | 31.4 | 69 | 70 | 26.4483 | 20.9783 | 61.774 | 169.4323 | 169.4323 | 0 | 0
2025-08-14 01:00 | 30.75 | 68.5 | 70 | 26.2493 | 20.6893 | 61.0493 | 159.2075 | 159.2075 | 0 | 0
2025-08-14 02:00 | 30.15 | 67.5 | 70 | 26.0636 | 20.3828 | 60.1442 | 148.1076 | 148.1076 | 0 | 0
2025-08-14 03:00 | 29.65 | 65.5 | 70 | 25.9084 | 20.0432 | 58.8553 | 135.089 | 135.089 | 0 | 0
2025-08-14 04:00 | 29.9 | 61 | 70 | 25.9957 | 19.7897 | 56.8187 | 122.42 | 122.42 | 0 | 0
2025-08-14 05:00 | 30.15 | 58.5 | 70 | 26.0798 | 19.684 | 55.7255 | 116.4086 | 116.4086 | 0 | 0
2025-08-14 06:00 | 30.5 | 56 | 100 | 26.1958 | 19.608 | 54.6607 | 158.9375 | 158.9375 | 0 | 0
2025-08-14 07:00 | 32.55 | 48 | 100 | 26.8555 | 19.6269 | 51.4867 | 146.055 | 146.055 | 0 | 0
2025-08-14 08:00 | 35.5 | 39.5 | 100 | 27.7724 | 19.7582 | 47.941 | 134.9778 | 134.9778 | 0 | 0
2025-08-14 09:00 | 37.8 | 35 | 100 | 28.4568 | 19.9713 | 46.0735 | 134.0254 | 134.0254 | 0 | 0
2025-08-14 10:00 | 39.15 | 34 | 100 | 28.8373 | 20.2561 | 45.962 | 144.0775 | 144.0775 | 0 | 0
2025-08-14 11:00 | 40.05 | 34 | 100 | 29.0798 | 20.5239 | 46.353 | 156.048 | 156.048 | 0 | 0
2025-08-14 12:00 | 40.4 | 34 | 100 | 29.1725 | 20.628 | 46.5157 | 160.8186 | 160.8186 | 0 | 0
2025-08-14 13:00 | 40.45 | 34.5 | 100 | 29.1813 | 20.7046 | 46.8928 | 165.6198 | 165.6198 | 0 | 0
2025-08-14 14:00 | 40.25 | 36.5 | 100 | 29.1113 | 20.8899 | 48.1932 | 179.0462 | 179.0462 | 0 | 0
2025-08-14 15:00 | 39.6 | 38 | 100 | 28.9272 | 20.8678 | 48.894 | 181.628 | 181.628 | 0 | 0
2025-08-14 16:00 | 38.95 | 37.5 | 100 | 28.7568 | 20.6061 | 48.2336 | 168.5019 | 168.5019 | 0 | 0
2025-08-14 17:00 | 38.15 | 40.5 | 100 | 28.518 | 20.6974 | 49.7992 | 179.3648 | 179.3648 | 0 | 0
2025-08-14 18:00 | 37.1 | 47 | 100 | 28.1888 | 21.0544 | 53.3284 | 209.4057 | 209.4057 | 0 | 0
2025-08-14 19:00 | 36.05 | 54.5 | 100 | 27.8569 | 21.4437 | 57.206 | 242.0068 | 242.0068 | 0 | 0
2025-08-14 20:00 | 35.1 | 62.5 | 100 | 27.5535 | 21.8452 | 61.1723 | 275.2479 | 275.2479 | 0 | 0
2025-08-14 21:00 | 34.8 | 63.5 | 100 | 27.4648 | 21.821 | 61.4975 | 275.6029 | 275.6029 | 0 | 0
2025-08-14 22:00 | 34.85 | 58 | 70 | 27.5024 | 21.3398 | 58.3896 | 169.983 | 169.983 | 0 | 0
2025-08-14 23:00 | 34.3 | 55.5 | 70 | 27.3541 | 20.9099 | 56.5894 | 152.5582 | 152.5582 | 0 | 0
2025-08-15 | 33.5 | 57 | 70 | 27.1138 | 20.7579 | 56.9072 | 149.2768 | 149.2768 | 0 | 0
2025-08-15 01:00 | 33.2 | 54 | 70 | 27.0345 | 20.384 | 55.0816 | 133.5427 | 133.5427 | 0 | 0
2025-08-15 02:00 | 33.2 | 46.5 | 70 | 27.0587 | 19.7036 | 50.9787 | 102.8111 | 102.8111 | 0 | 0
2025-08-15 03:00 | 32.75 | 52.5 | 70 | 26.9033 | 20.094 | 54.0149 | 122.4492 | 122.4492 | 0 | 0
2025-08-15 04:00 | 32.45 | 64.5 | 70 | 26.7776 | 21.0151 | 60.223 | 166.1126 | 166.1126 | 0 | 0
2025-08-15 05:00 | 32.5 | 67.5 | 70 | 26.7838 | 21.2826 | 61.8436 | 178.3444 | 178.3444 | 0 | 0
2025-08-15 06:00 | 32.55 | 67.5 | 100 | 26.7988 | 21.3014 | 61.8794 | 255.6934 | 255.6934 | 0 | 0
2025-08-15 07:00 | 33.4 | 63.5 | 100 | 27.0623 | 21.2902 | 60.3814 | 249.0548 | 249.0548 | 0 | 0
2025-08-15 08:00 | 35.4 | 54.5 | 100 | 27.6745 | 21.2123 | 56.7352 | 230.4737 | 230.4737 | 0 | 0
2025-08-15 09:00 | 38.1 | 43.5 | 100 | 28.4846 | 21.0167 | 51.6888 | 200.2333 | 200.2333 | 0 | 0
2025-08-15 10:00 | 40.45 | 35.5 | 100 | 29.1725 | 20.8297 | 47.5851 | 173.6622 | 173.6622 | 0 | 0
2025-08-15 11:00 | 41.7 | 32.5 | 100 | 29.5246 | 20.8219 | 46.0467 | 165.8451 | 165.8451 | 0 | 0
2025-08-15 12:00 | 42.15 | 31.5 | 100 | 29.6497 | 20.8202 | 45.5239 | 163.2396 | 163.2396 | 0 | 0
2025-08-15 13:00 | 42.45 | 30.5 | 100 | 29.7366 | 20.771 | 44.9198 | 158.422 | 158.422 | 0 | 0
2025-08-15 14:00 | 42.55 | 30 | 100 | 29.7674 | 20.731 | 44.5929 | 155.3084 | 155.3084 | 0 | 0
2025-08-15 15:00 | 42.3 | 29.5 | 100 | 29.7093 | 20.5903 | 44.1149 | 147.6822 | 147.6822 | 0 | 0
2025-08-15 16:00 | 42 | 27 | 100 | 29.6586 | 20.1628 | 42.1461 | 121.8877 | 121.8877 | 0 | 0
2025-08-15 17:00 | 40.85 | 28.5 | 100 | 29.341 | 20.0492 | 42.8349 | 121.246 | 121.246 | 0 | 0
2025-08-15 18:00 | 38.5 | 36.5 | 100 | 28.6412 | 20.3514 | 47.3635 | 154.708 | 154.708 | 0 | 0
2025-08-15 19:00 | 36.25 | 44 | 100 | 27.967 | 20.46 | 51.0056 | 175.7632 | 175.7632 | 0 | 0
2025-08-15 20:00 | 34.5 | 51.5 | 100 | 27.4283 | 20.6088 | 54.4451 | 196.8151 | 196.8151 | 0 | 0
2025-08-15 21:00 | 33.45 | 55.5 | 100 | 27.1041 | 20.6064 | 56.0505 | 203.6168 | 203.6168 | 0 | 0
2025-08-15 22:00 | 33.15 | 54 | 70 | 27.0195 | 20.3663 | 55.052 | 132.9706 | 132.9706 | 0 | 0
2025-08-15 23:00 | 32.8 | 54 | 70 | 26.914 | 20.2434 | 54.853 | 129.0317 | 129.0317 | 0 | 0
2025-08-16 | 32.05 | 58 | 70 | 26.6744 | 20.3224 | 56.5422 | 136.1664 | 136.1664 | 0 | 0
2025-08-16 01:00 | 31.1 | 65 | 70 | 26.3651 | 20.5463 | 59.5438 | 151.0262 | 151.0262 | 0 | 0
2025-08-16 02:00 | 30.2 | 72 | 70 | 26.071 | 20.7426 | 62.3906 | 164.5286 | 164.5286 | 0 | 0
2025-08-16 03:00 | 29.65 | 75 | 70 | 25.893 | 20.7489 | 63.429 | 167.5405 | 167.5405 | 0 | 0
2025-08-16 04:00 | 29.75 | 74.5 | 70 | 25.9254 | 20.7519 | 63.2612 | 167.1505 | 167.1505 | 0 | 0
2025-08-16 05:00 | 30.05 | 72.5 | 70 | 26.0231 | 20.7223 | 62.5153 | 164.2348 | 164.2348 | 0 | 0
2025-08-16 06:00 | 30.5 | 68.5 | 100 | 26.1715 | 20.5931 | 60.8728 | 222.8792 | 222.8792 | 0 | 0
2025-08-16 07:00 | 31.95 | 64 | 100 | 26.6282 | 20.7856 | 59.5955 | 225.4072 | 225.4072 | 0 | 0
2025-08-16 08:00 | 34.65 | 55.5 | 100 | 27.4557 | 21.0376 | 56.803 | 223.7426 | 223.7426 | 0 | 0
2025-08-16 09:00 | 38 | 41 | 100 | 28.4738 | 20.7084 | 50.0213 | 180.5421 | 180.5421 | 0 | 0
2025-08-16 10:00 | 40.8 | 30 | 100 | 29.3141 | 20.2359 | 43.862 | 132.9605 | 132.9605 | 0 | 0
2025-08-16 11:00 | 42.65 | 25 | 100 | 29.8489 | 20.0608 | 40.8496 | 111.1547 | 111.1547 | 0 | 0
2025-08-16 12:00 | 44 | 21.5 | 100 | 30.2368 | 19.8869 | 38.5428 | 92.7316 | 92.7316 | 0 | 0
2025-08-16 13:00 | 45 | 18.5 | 100 | 30.5304 | 19.6531 | 36.3757 | 72.685 | 72.685 | 0 | 0
2025-08-16 14:00 | 45.65 | 16.5 | 100 | 30.7233 | 19.4679 | 34.8536 | 57.8171 | 57.8171 | 0 | 0
2025-08-16 15:00 | 45.65 | 16 | 100 | 30.7309 | 19.3821 | 34.4391 | 52.5778 | 52.5778 | 0 | 0
2025-08-16 16:00 | 42.4 | 31 | 100 | 29.7183 | 20.8236 | 45.279 | 162.303 | 162.303 | 0 | 0
2025-08-16 17:00 | 38.65 | 48 | 100 | 28.6003 | 21.6916 | 54.9784 | 242.1747 | 242.1747 | 0 | 0
2025-08-16 18:00 | 37.55 | 51.5 | 100 | 28.2842 | 21.6785 | 56.4429 | 248.1562 | 248.1562 | 0 | 0
2025-08-16 19:00 | 37.15 | 52 | 100 | 28.1731 | 21.5879 | 56.4668 | 244.5956 | 244.5956 | 0 | 0
2025-08-16 20:00 | 37.1 | 48 | 100 | 28.183 | 21.1595 | 53.9454 | 216.2508 | 216.2508 | 0 | 0
2025-08-16 21:00 | 37.25 | 42.5 | 100 | 28.257 | 20.6282 | 50.595 | 180.2918 | 180.2918 | 0 | 0
2025-08-16 22:00 | 36.8 | 43 | 70 | 28.1281 | 20.536 | 50.6695 | 123.9354 | 123.9354 | 0 | 0
2025-08-16 23:00 | 35.5 | 49 | 70 | 27.7284 | 20.7135 | 53.5752 | 137.9172 | 137.9172 | 0 | 0
2025-08-17 | 34.7 | 50.5 | 70 | 27.4907 | 20.5839 | 53.9849 | 135.6461 | 135.6461 | 0 | 0
2025-08-17 01:00 | 34.3 | 46 | 70 | 27.391 | 20.0192 | 51.2035 | 111.8259 | 111.8259 | 0 | 0
2025-08-17 02:00 | 33.75 | 41 | 70 | 27.2444 | 19.3616 | 48.1467 | 84.983 | 84.983 | 0 | 0
2025-08-17 03:00 | 32.95 | 45.5 | 70 | 26.9857 | 19.5312 | 50.3127 | 96.1359 | 96.1359 | 0 | 0
2025-08-17 04:00 | 32.65 | 49.5 | 70 | 26.8818 | 19.7943 | 52.3411 | 109.2911 | 109.2911 | 0 | 0
2025-08-17 05:00 | 32.25 | 52 | 70 | 26.752 | 19.879 | 53.4805 | 114.9982 | 114.9982 | 0 | 0
2025-08-17 06:00 | 32.1 | 56 | 100 | 26.6951 | 20.1717 | 55.5088 | 184.1725 | 184.1725 | 0 | 0
2025-08-17 07:00 | 33.95 | 50.5 | 100 | 27.2703 | 20.3273 | 53.5505 | 181.7807 | 181.7807 | 0 | 0
2025-08-17 08:00 | 37.05 | 38 | 100 | 28.227 | 20.0789 | 47.6678 | 145.6303 | 145.6303 | 0 | 0
2025-08-17 09:00 | 39.9 | 27.5 | 100 | 29.093 | 19.663 | 41.806 | 101.7096 | 101.7096 | 0 | 0
2025-08-17 10:00 | 41.9 | 23.5 | 100 | 29.6685 | 19.6537 | 39.5094 | 89.4707 | 89.4707 | 0 | 0
2025-08-17 11:00 | 43.3 | 21 | 100 | 30.0633 | 19.6397 | 37.9708 | 80.7995 | 80.7995 | 0 | 0
2025-08-17 12:00 | 44.15 | 19.5 | 100 | 30.301 | 19.6139 | 36.9923 | 74.6213 | 74.6213 | 0 | 0
2025-08-17 13:00 | 44.15 | 21 | 100 | 30.2814 | 19.8457 | 38.1897 | 89.4284 | 89.4284 | 0 | 0
2025-08-17 14:00 | 42.95 | 24.5 | 100 | 29.9319 | 20.0641 | 40.5768 | 110.0651 | 110.0651 | 0 | 0
2025-08-17 15:00 | 41.4 | 28.5 | 100 | 29.4865 | 20.2021 | 43.0279 | 127.7978 | 127.7978 | 0 | 0
2025-08-17 16:00 | 39.85 | 33 | 100 | 29.0345 | 20.3378 | 45.596 | 145.6204 | 145.6204 | 0 | 0
2025-08-17 17:00 | 38.25 | 39 | 100 | 28.5555 | 20.5607 | 48.8753 | 169.7698 | 169.7698 | 0 | 0
2025-08-17 18:00 | 36.65 | 46.5 | 100 | 28.0666 | 20.8511 | 52.7486 | 198.7821 | 198.7821 | 0 | 0
2025-08-17 19:00 | 35.45 | 52.5 | 100 | 27.6978 | 21.0365 | 55.6087 | 218.7286 | 218.7286 | 0 | 0
2025-08-17 20:00 | 35 | 55 | 100 | 27.5583 | 21.1155 | 56.7629 | 226.8052 | 226.8052 | 0 | 0
2025-08-17 21:00 | 34.6 | 56.5 | 100 | 27.4371 | 21.1109 | 57.3476 | 229.1028 | 229.1028 | 0 | 0
2025-08-17 22:00 | 34 | 59.5 | 70 | 27.2517 | 21.164 | 58.6172 | 165.6116 | 165.6116 | 0 | 0
2025-08-17 23:00 | 33.4 | 61 | 70 | 27.0708 | 21.0743 | 59.0154 | 164.2253 | 164.2253 | 0 | 0
2025-08-18 | 32.9 | 61 | 70 | 26.9227 | 20.8885 | 58.6641 | 157.9743 | 157.9743 | 0 | 0
2025-08-18 01:00 | 32.4 | 60.5 | 70 | 26.774 | 20.6618 | 58.0623 | 149.8824 | 149.8824 | 0 | 0
2025-08-18 02:00 | 31.75 | 60.5 | 70 | 26.5761 | 20.4235 | 57.6461 | 142.0673 | 142.0673 | 0 | 0
2025-08-18 03:00 | 31.15 | 62 | 70 | 26.3874 | 20.326 | 58.0402 | 140.5072 | 140.5072 | 0 | 0
2025-08-18 04:00 | 31.2 | 58.5 | 70 | 26.4108 | 20.0599 | 56.2896 | 128.1506 | 128.1506 | 0 | 0
2025-08-18 05:00 | 31.6 | 52.5 | 70 | 26.5495 | 19.6998 | 53.4138 | 109.9642 | 109.9642 | 0 | 0
2025-08-18 06:00 | 32.9 | 44 | 100 | 26.9749 | 19.3782 | 49.4647 | 127.7585 | 127.7585 | 0 | 0
2025-08-18 07:00 | 35.3 | 34 | 100 | 27.7382 | 19.1261 | 44.6042 | 96.1374 | 96.1374 | 0 | 0
2025-08-18 08:00 | 37.65 | 29 | 100 | 28.4515 | 19.2338 | 42.1702 | 88.1224 | 88.1224 | 0 | 0
2025-08-18 09:00 | 39.8 | 25.5 | 100 | 29.0816 | 19.3804 | 40.3919 | 84.2831 | 84.2831 | 0 | 0
2025-08-18 10:00 | 41.55 | 23.5 | 100 | 29.5753 | 19.5659 | 39.4104 | 85.7059 | 85.7059 | 0 | 0
2025-08-18 11:00 | 42.9 | 22 | 100 | 29.9476 | 19.6923 | 38.6312 | 86.0409 | 86.0409 | 0 | 0
2025-08-18 12:00 | 43.6 | 21 | 100 | 30.1408 | 19.7152 | 38.036 | 83.6947 | 83.6947 | 0 | 0
2025-08-18 13:00 | 43.4 | 23 | 100 | 30.0651 | 19.965 | 39.5431 | 100.7401 | 100.7401 | 0 | 0
2025-08-18 14:00 | 42.35 | 27.5 | 100 | 29.744 | 20.3321 | 42.6263 | 130.2782 | 130.2782 | 0 | 0
2025-08-18 15:00 | 40.8 | 31.5 | 100 | 29.3003 | 20.4283 | 44.933 | 145.5565 | 145.5565 | 0 | 0
2025-08-18 16:00 | 39.5 | 34.5 | 100 | 28.9283 | 20.4193 | 46.4596 | 152.737 | 152.737 | 0 | 0
2025-08-18 17:00 | 38.4 | 38 | 100 | 28.6035 | 20.495 | 48.2871 | 164.3798 | 164.3798 | 0 | 0
2025-08-18 18:00 | 37.35 | 41.5 | 100 | 28.2908 | 20.5532 | 50.0148 | 174.6833 | 174.6833 | 0 | 0
2025-08-18 19:00 | 36.75 | 43 | 100 | 28.114 | 20.5199 | 50.6399 | 176.2638 | 176.2638 | 0 | 0
2025-08-18 20:00 | 36.25 | 43.5 | 100 | 27.9697 | 20.4102 | 50.6854 | 172.2056 | 172.2056 | 0 | 0
2025-08-18 21:00 | 35.55 | 45 | 100 | 27.7615 | 20.3344 | 51.2249 | 171.7032 | 171.7032 | 0 | 0
2025-08-18 22:00 | 34.75 | 48 | 70 | 27.5158 | 20.3635 | 52.5591 | 125.1357 | 125.1357 | 0 | 0
2025-08-18 23:00 | 34.05 | 51.5 | 70 | 27.2963 | 20.4553 | 54.1635 | 132.5529 | 132.5529 | 0 | 0
2025-08-19 | 33.6 | 53 | 70 | 27.1575 | 20.4365 | 54.7403 | 133.7788 | 133.7788 | 0 | 0
2025-08-19 01:00 | 33.15 | 54 | 70 | 27.0196 | 20.3682 | 55.0303 | 132.8047 | 132.8047 | 0 | 0
2025-08-19 02:00 | 32.8 | 55.5 | 70 | 26.9095 | 20.3771 | 55.6407 | 134.8763 | 134.8763 | 0 | 0
2025-08-19 03:00 | 32.75 | 56 | 70 | 26.8929 | 20.4031 | 55.8786 | 136.2858 | 136.2858 | 0 | 0
2025-08-19 04:00 | 33.5 | 51 | 70 | 27.1345 | 20.2198 | 53.5794 | 124.3796 | 124.3796 | 0 | 0
2025-08-19 05:00 | 33.95 | 47 | 70 | 27.2832 | 20.0005 | 51.5801 | 112.3534 | 112.3534 | 0 | 0
2025-08-19 06:00 | 34 | 47.5 | 100 | 27.2963 | 20.0653 | 51.8817 | 164.2431 | 164.2431 | 0 | 0
2025-08-19 07:00 | 35.15 | 45 | 100 | 27.6455 | 20.2042 | 51.0131 | 165.6454 | 165.6454 | 0 | 0
2025-08-19 08:00 | 36.85 | 40.5 | 100 | 28.1563 | 20.289 | 49.1218 | 160.192 | 160.192 | 0 | 0
2025-08-19 09:00 | 38.55 | 36 | 100 | 28.6587 | 20.3148 | 47.022 | 151.2137 | 151.2137 | 0 | 0
2025-08-19 10:00 | 40.15 | 32 | 100 | 29.1234 | 20.3068 | 44.9974 | 141.0745 | 141.0745 | 0 | 0
2025-08-19 11:00 | 41.55 | 28.5 | 100 | 29.526 | 20.2499 | 43.0559 | 129.2758 | 129.2758 | 0 | 0
2025-08-19 12:00 | 42.5 | 26 | 100 | 29.7991 | 20.1643 | 41.5482 | 118.4599 | 118.4599 | 0 | 0
2025-08-19 13:00 | 42.35 | 27.5 | 100 | 29.744 | 20.3325 | 42.6245 | 130.2561 | 130.2561 | 0 | 0
2025-08-19 14:00 | 41.25 | 33 | 100 | 29.4038 | 20.7539 | 46.2012 | 164.053 | 164.053 | 0 | 0
2025-08-19 15:00 | 39.9 | 39 | 100 | 28.9984 | 21.0827 | 49.7286 | 193.7747 | 193.7747 | 0 | 0
2025-08-19 16:00 | 38.05 | 47.5 | 100 | 28.4444 | 21.4324 | 54.2392 | 228.3662 | 228.3662 | 0 | 0
2025-08-19 17:00 | 36.2 | 56.5 | 100 | 27.8882 | 21.6925 | 58.5079 | 257.6619 | 257.6619 | 0 | 0
2025-08-19 18:00 | 34.9 | 63.5 | 100 | 27.493 | 21.859 | 61.5789 | 277.5151 | 277.5151 | 0 | 0
2025-08-19 19:00 | 34.05 | 68.5 | 100 | 27.2321 | 21.969 | 63.6703 | 290.6983 | 290.6983 | 0 | 0
2025-08-19 20:00 | 33.7 | 70.5 | 100 | 27.1248 | 22.0011 | 64.4602 | 295.2172 | 295.2172 | 0 | 0
2025-08-19 21:00 | 33.6 | 70.5 | 100 | 27.0962 | 21.9615 | 64.3663 | 293.1422 | 293.1422 | 0 | 0
2025-08-19 22:00 | 33.45 | 69.5 | 70 | 27.0564 | 21.8188 | 63.688 | 199.0753 | 199.0753 | 0 | 0
2025-08-19 23:00 | 33.05 | 68.5 | 70 | 26.9433 | 21.5782 | 62.8105 | 189.5964 | 189.5964 | 0 | 0
2025-08-20 | 32.5 | 69.5 | 70 | 26.7781 | 21.4465 | 62.8937 | 186.0081 | 186.0081 | 0 | 0
2025-08-20 01:00 | 31.95 | 71.5 | 70 | 26.6084 | 21.3912 | 63.4926 | 186.117 | 186.117 | 0 | 0
2025-08-20 02:00 | 31.5 | 71 | 70 | 26.4739 | 21.1747 | 62.8767 | 178.1693 | 178.1693 | 0 | 0
2025-08-20 03:00 | 31.35 | 68.5 | 70 | 26.4341 | 20.9197 | 61.4896 | 166.9942 | 166.9942 | 0 | 0
2025-08-20 04:00 | 31.95 | 63 | 70 | 26.6307 | 20.7027 | 59.086 | 154.0674 | 154.0674 | 0 | 0
2025-08-20 05:00 | 32.4 | 59 | 70 | 26.7782 | 20.534 | 57.2794 | 144.1232 | 144.1232 | 0 | 0
2025-08-20 06:00 | 33.05 | 57 | 100 | 26.9799 | 20.5962 | 56.6129 | 205.5345 | 205.5345 | 0 | 0
2025-08-20 07:00 | 34.3 | 54 | 100 | 27.3601 | 20.773 | 55.7319 | 208.7191 | 208.7191 | 0 | 0
2025-08-20 08:00 | 36.15 | 46.5 | 100 | 27.9259 | 20.6849 | 52.4496 | 190.803 | 190.803 | 0 | 0
2025-08-20 09:00 | 38.5 | 37 | 100 | 28.6379 | 20.4121 | 47.6731 | 158.2361 | 158.2361 | 0 | 0
2025-08-20 10:00 | 40.4 | 32.5 | 100 | 29.1857 | 20.4396 | 45.4652 | 148.5667 | 148.5667 | 0 | 0
2025-08-20 11:00 | 42.05 | 29 | 100 | 29.6507 | 20.4544 | 43.629 | 139.9597 | 139.9597 | 0 | 0
2025-08-20 12:00 | 43.25 | 26 | 100 | 29.9908 | 20.3623 | 41.824 | 127.3666 | 127.3666 | 0 | 0
2025-08-20 13:00 | 43.8 | 24.5 | 100 | 30.1479 | 20.2871 | 40.856 | 119.6421 | 119.6421 | 0 | 0
2025-08-20 14:00 | 43.8 | 23.5 | 100 | 30.1606 | 20.1361 | 40.0762 | 110.1299 | 110.1299 | 0 | 0
2025-08-20 15:00 | 42.7 | 29.5 | 100 | 29.8108 | 20.7031 | 44.2894 | 152.8488 | 152.8488 | 0 | 0
2025-08-20 16:00 | 40.7 | 37.5 | 100 | 29.2192 | 21.1509 | 49.1403 | 193.7832 | 193.7832 | 0 | 0
2025-08-20 17:00 | 39.1 | 41 | 100 | 28.771 | 21.0594 | 50.6444 | 197.3108 | 197.3108 | 0 | 0
2025-08-20 18:00 | 38 | 44.5 | 100 | 28.4506 | 21.0905 | 52.2931 | 206.1243 | 206.1243 | 0 | 0
2025-08-20 19:00 | 37.5 | 46 | 100 | 28.3048 | 21.085 | 52.9419 | 208.8081 | 208.8081 | 0 | 0
2025-08-20 20:00 | 37.4 | 45 | 100 | 28.2836 | 20.9455 | 52.2457 | 200.1168 | 200.1168 | 0 | 0
2025-08-20 21:00 | 36.65 | 44 | 100 | 28.0804 | 20.5927 | 51.2015 | 181.6053 | 181.6053 | 0 | 0
2025-08-20 22:00 | 35.15 | 47 | 70 | 27.6366 | 20.3999 | 52.1988 | 125.0461 | 125.0461 | 0 | 0
2025-08-20 23:00 | 33.9 | 51 | 70 | 27.2537 | 20.3563 | 53.8065 | 128.8345 | 128.8345 | 0 | 0
2025-08-21 | 33.3 | 52.5 | 70 | 27.0694 | 20.2856 | 54.3054 | 128.44 | 128.44 | 0 | 0
2025-08-21 01:00 | 33.25 | 51 | 70 | 27.0593 | 20.1326 | 53.4586 | 121.7583 | 121.7583 | 0 | 0
2025-08-21 02:00 | 33.45 | 48 | 70 | 27.1295 | 19.9261 | 51.9089 | 111.4852 | 111.4852 | 0 | 0
2025-08-21 03:00 | 33.1 | 48 | 70 | 27.0236 | 19.8098 | 51.74 | 107.8535 | 107.8535 | 0 | 0
2025-08-21 04:00 | 32.7 | 49 | 70 | 26.8986 | 19.7672 | 52.0888 | 107.7491 | 107.7491 | 0 | 0
2025-08-21 05:00 | 32.5 | 49 | 70 | 26.8373 | 19.7015 | 51.9865 | 105.6205 | 105.6205 | 0 | 0
2025-08-21 06:00 | 32.4 | 49.5 | 100 | 26.8051 | 19.7128 | 52.2003 | 152.1815 | 152.1815 | 0 | 0
2025-08-21 07:00 | 33.35 | 48.5 | 100 | 27.0978 | 19.942 | 52.1066 | 160.4145 | 160.4145 | 0 | 0
2025-08-21 08:00 | 35.2 | 44 | 100 | 27.6645 | 20.1231 | 50.4398 | 159.8121 | 159.8121 | 0 | 0
2025-08-21 09:00 | 37.1 | 38 | 100 | 28.2413 | 20.0982 | 47.6673 | 146.0514 | 146.0514 | 0 | 0
2025-08-21 10:00 | 38.8 | 32 | 100 | 28.7559 | 19.9167 | 44.4743 | 124.0084 | 124.0084 | 0 | 0
2025-08-21 11:00 | 40.2 | 27.5 | 100 | 29.1749 | 19.7476 | 41.8831 | 104.9401 | 104.9401 | 0 | 0
2025-08-21 12:00 | 41.35 | 25 | 100 | 29.5073 | 19.7214 | 40.4484 | 96.669 | 96.669 | 0 | 0
2025-08-21 13:00 | 42.2 | 23 | 100 | 29.7531 | 19.66 | 39.2123 | 88.0676 | 88.0676 | 0 | 0
2025-08-21 14:00 | 42.4 | 23 | 100 | 29.8057 | 19.7096 | 39.2695 | 90.2137 | 90.2137 | 0 | 0
2025-08-21 15:00 | 42.05 | 25 | 100 | 29.6926 | 19.9016 | 40.6659 | 104.503 | 104.503 | 0 | 0
2025-08-21 16:00 | 39.85 | 34 | 100 | 29.0264 | 20.4641 | 46.2664 | 153.3957 | 153.3957 | 0 | 0
2025-08-21 17:00 | 37.15 | 45 | 100 | 28.2146 | 20.8639 | 52.0915 | 196.1001 | 196.1001 | 0 | 0
2025-08-21 18:00 | 35.7 | 53.5 | 100 | 27.7641 | 21.2237 | 56.3469 | 229.2086 | 229.2086 | 0 | 0
2025-08-21 19:00 | 34.75 | 60.5 | 100 | 27.4636 | 21.5331 | 59.7247 | 256.1371 | 256.1371 | 0 | 0
2025-08-21 20:00 | 34.4 | 61.5 | 100 | 27.3597 | 21.4924 | 60.0179 | 255.657 | 255.657 | 0 | 0
2025-08-21 21:00 | 34.2 | 62 | 100 | 27.3004 | 21.4623 | 60.14 | 254.8798 | 254.8798 | 0 | 0
2025-08-21 22:00 | 33.9 | 64.5 | 70 | 27.2045 | 21.5681 | 61.2948 | 184.7962 | 184.7962 | 0 | 0
2025-08-21 23:00 | 33.4 | 66.5 | 70 | 27.0525 | 21.5475 | 61.9911 | 186.2163 | 186.2163 | 0 | 0
2025-08-22 | 32.9 | 67 | 70 | 26.9042 | 21.3967 | 61.8626 | 181.5088 | 181.5088 | 0 | 0
2025-08-22 01:00 | 32.5 | 66.5 | 70 | 26.787 | 21.2013 | 61.2879 | 174.2804 | 174.2804 | 0 | 0
2025-08-22 02:00 | 32.15 | 66 | 70 | 26.6835 | 21.0265 | 60.7644 | 167.814 | 167.814 | 0 | 0
2025-08-22 03:00 | 31.85 | 66 | 70 | 26.5928 | 20.9119 | 60.5448 | 163.9486 | 163.9486 | 0 | 0
2025-08-22 04:00 | 32.15 | 58.5 | 70 | 26.7038 | 20.4035 | 56.828 | 138.9834 | 138.9834 | 0 | 0
2025-08-22 05:00 | 32.3 | 52 | 70 | 26.7675 | 19.8989 | 53.4754 | 115.301 | 115.301 | 0 | 0
2025-08-22 06:00 | 32.15 | 53.5 | 100 | 26.7173 | 19.9778 | 54.1891 | 170.7615 | 170.7615 | 0 | 0
2025-08-22 07:00 | 33.05 | 51.5 | 100 | 26.9976 | 20.1131 | 53.5895 | 173.3572 | 173.3572 | 0 | 0
2025-08-22 08:00 | 34.75 | 46 | 100 | 27.5242 | 20.1728 | 51.3798 | 165.9024 | 165.9024 | 0 | 0
2025-08-22 09:00 | 36.7 | 40 | 100 | 28.1166 | 20.1906 | 48.7295 | 154.4567 | 154.4567 | 0 | 0
2025-08-22 10:00 | 38.6 | 34.5 | 100 | 28.683 | 20.1556 | 46.0463 | 140.4484 | 140.4484 | 0 | 0
2025-08-22 11:00 | 40.05 | 30.5 | 100 | 29.1092 | 20.0904 | 43.9124 | 127.5877 | 127.5877 | 0 | 0
2025-08-22 12:00 | 40.4 | 30 | 100 | 29.2075 | 20.1254 | 43.6975 | 127.8555 | 127.8555 | 0 | 0
2025-08-22 13:00 | 39.85 | 32.5 | 100 | 29.0387 | 20.281 | 45.2237 | 141.278 | 141.278 | 0 | 0
2025-08-22 14:00 | 39.15 | 36.5 | 100 | 28.8186 | 20.5547 | 47.6347 | 163.3309 | 163.3309 | 0 | 0
2025-08-22 15:00 | 38.3 | 43 | 100 | 28.5423 | 21.028 | 51.4773 | 199.6478 | 199.6478 | 0 | 0
2025-08-22 16:00 | 37.4 | 48 | 100 | 28.2655 | 21.2639 | 54.1203 | 220.9964 | 220.9964 | 0 | 0
2025-08-22 17:00 | 36.45 | 52.5 | 100 | 27.9786 | 21.3919 | 56.2638 | 235.614 | 235.614 | 0 | 0
2025-08-22 18:00 | 35.5 | 59 | 100 | 27.6817 | 21.6734 | 59.4419 | 260.7537 | 260.7537 | 0 | 0
2025-08-22 19:00 | 34.9 | 63.5 | 100 | 27.4932 | 21.8604 | 61.5642 | 277.3599 | 277.3599 | 0 | 0
2025-08-22 20:00 | 34.45 | 66 | 100 | 27.3558 | 21.9094 | 62.6016 | 283.6695 | 283.6695 | 0 | 0
2025-08-22 21:00 | 34 | 68 | 100 | 27.2201 | 21.9077 | 63.3292 | 286.564 | 286.564 | 0 | 0
2025-08-22 22:00 | 33.5 | 70 | 70 | 27.0693 | 21.8814 | 63.9923 | 201.6912 | 201.6912 | 0 | 0
2025-08-22 23:00 | 32.8 | 73 | 70 | 26.8561 | 21.8502 | 64.9901 | 203.5963 | 203.5963 | 0 | 0
2025-08-23 | 32.1 | 76 | 70 | 26.6412 | 21.8072 | 65.9394 | 204.9847 | 204.9847 | 0 | 0
2025-08-23 01:00 | 31.5 | 78 | 70 | 26.457 | 21.7176 | 66.426 | 203.7019 | 203.7019 | 0 | 0
2025-08-23 02:00 | 30.95 | 80 | 70 | 26.2863 | 21.6432 | 66.9355 | 202.9037 | 202.9037 | 0 | 0
2025-08-23 03:00 | 30.65 | 81 | 70 | 26.1928 | 21.5938 | 67.1599 | 202.0555 | 202.0555 | 0 | 0
2025-08-23 04:00 | 30.9 | 77 | 70 | 26.2776 | 21.3979 | 65.3981 | 191.535 | 191.535 | 0 | 0
2025-08-23 05:00 | 31.2 | 71 | 70 | 26.3825 | 21.0577 | 62.6309 | 174.0646 | 174.0646 | 0 | 0
2025-08-23 06:00 | 31.55 | 66.5 | 100 | 26.5001 | 20.8374 | 60.5983 | 231.5237 | 231.5237 | 0 | 0
2025-08-23 07:00 | 33 | 58 | 100 | 26.962 | 20.6672 | 57.1047 | 210.2312 | 210.2312 | 0 | 0
2025-08-23 08:00 | 35.4 | 46.5 | 100 | 27.7113 | 20.4355 | 52.024 | 179.0768 | 179.0768 | 0 | 0
2025-08-23 09:00 | 37.85 | 36 | 100 | 28.4645 | 20.102 | 46.727 | 141.8874 | 141.8874 | 0 | 0
2025-08-23 10:00 | 39.6 | 30 | 100 | 28.9909 | 19.8981 | 43.4179 | 118.2188 | 118.2188 | 0 | 0
2025-08-23 11:00 | 40.35 | 29 | 100 | 29.2027 | 19.9814 | 42.9863 | 119.1048 | 119.1048 | 0 | 0
2025-08-23 12:00 | 40.55 | 29 | 100 | 29.2564 | 20.0365 | 43.0594 | 121.5375 | 121.5375 | 0 | 0
2025-08-23 13:00 | 40.3 | 31 | 100 | 29.172 | 20.2214 | 44.3744 | 135.0045 | 135.0045 | 0 | 0
2025-08-23 14:00 | 39.65 | 34.5 | 100 | 28.9687 | 20.4641 | 46.5238 | 154.7247 | 154.7247 | 0 | 0
2025-08-23 15:00 | 38.95 | 38 | 100 | 28.7532 | 20.6664 | 48.5552 | 172.1766 | 172.1766 | 0 | 0
2025-08-23 16:00 | 37.9 | 41.5 | 100 | 28.443 | 20.7301 | 50.3038 | 182.8449 | 182.8449 | 0 | 0
2025-08-23 17:00 | 36.4 | 48 | 100 | 27.9885 | 20.9204 | 53.5123 | 204.8806 | 204.8806 | 0 | 0
2025-08-23 18:00 | 35 | 55.5 | 100 | 27.5561 | 21.1617 | 57.0542 | 229.9523 | 229.9523 | 0 | 0
2025-08-23 19:00 | 34.1 | 60.5 | 100 | 27.2769 | 21.2897 | 59.2536 | 244.4031 | 244.4031 | 0 | 0
2025-08-23 20:00 | 33.55 | 65 | 100 | 27.101 | 21.4754 | 61.3197 | 260.5496 | 260.5496 | 0 | 0
2025-08-23 21:00 | 33.1 | 68.5 | 100 | 26.9579 | 21.5979 | 62.8527 | 271.8358 | 271.8358 | 0 | 0
2025-08-23 22:00 | 32.55 | 72 | 70 | 26.7856 | 21.6686 | 64.2522 | 196.2861 | 196.2861 | 0 | 0
2025-08-23 23:00 | 31.9 | 75 | 70 | 26.5843 | 21.6472 | 65.2541 | 198.4578 | 198.4578 | 0 | 0
2025-08-24 | 31.4 | 77 | 70 | 26.4293 | 21.6006 | 65.8379 | 198.6844 | 198.6844 | 0 | 0
2025-08-24 01:00 | 30.95 | 77.5 | 70 | 26.2917 | 21.4557 | 65.6966 | 194.068 | 194.068 | 0 | 0
2025-08-24 02:00 | 30.55 | 76.5 | 70 | 26.1711 | 21.2191 | 64.8628 | 184.9136 | 184.9136 | 0 | 0
2025-08-24 03:00 | 30.35 | 75 | 70 | 26.1122 | 21.0268 | 63.9632 | 176.9115 | 176.9115 | 0 | 0
2025-08-24 04:00 | 30.85 | 71 | 70 | 26.275 | 20.9209 | 62.3716 | 169.4767 | 169.4767 | 0 | 0
2025-08-24 05:00 | 31.35 | 68.5 | 70 | 26.4341 | 20.9199 | 61.4847 | 166.9579 | 166.9579 | 0 | 0
2025-08-24 06:00 | 31.55 | 68.5 | 100 | 26.4952 | 20.9966 | 61.6295 | 242.1996 | 242.1996 | 0 | 0
2025-08-24 07:00 | 32.65 | 66 | 100 | 26.833 | 21.2168 | 61.1515 | 249.1618 | 249.1618 | 0 | 0
2025-08-24 08:00 | 34.35 | 60.5 | 100 | 27.3493 | 21.3837 | 59.4205 | 248.764 | 248.764 | 0 | 0
2025-08-24 09:00 | 36.15 | 52.5 | 100 | 27.8954 | 21.2865 | 56.0469 | 230.3272 | 230.3272 | 0 | 0
2025-08-24 10:00 | 37.95 | 43.5 | 100 | 28.444 | 20.9687 | 51.5895 | 197.7606 | 197.7606 | 0 | 0
2025-08-24 11:00 | 39.1 | 37.5 | 100 | 28.7976 | 20.6575 | 48.2756 | 170.2551 | 170.2551 | 0 | 0
2025-08-24 12:00 | 39.45 | 36 | 100 | 28.9033 | 20.5877 | 47.4368 | 163.5866 | 163.5866 | 0 | 0
2025-08-24 13:00 | 39.35 | 37.5 | 100 | 28.8648 | 20.7343 | 48.4039 | 173.8614 | 173.8614 | 0 | 0
2025-08-24 14:00 | 38.9 | 40 | 100 | 28.7252 | 20.8832 | 49.8461 | 186.4686 | 186.4686 | 0 | 0
2025-08-24 15:00 | 38.4 | 41 | 100 | 28.583 | 20.8363 | 50.2381 | 186.5336 | 186.5336 | 0 | 0
2025-08-24 16:00 | 37.5 | 44 | 100 | 28.3173 | 20.8728 | 51.6651 | 194.5361 | 194.5361 | 0 | 0
2025-08-24 17:00 | 36.2 | 51 | 100 | 27.9169 | 21.1543 | 55.1901 | 221.4271 | 221.4271 | 0 | 0
2025-08-24 18:00 | 34.95 | 59 | 100 | 27.5268 | 21.4694 | 59.0235 | 250.662 | 250.662 | 0 | 0
2025-08-24 19:00 | 34.05 | 65 | 100 | 27.2456 | 21.6675 | 61.7112 | 269.9916 | 269.9916 | 0 | 0
2025-08-24 20:00 | 33.5 | 68 | 100 | 27.0762 | 21.7125 | 62.9055 | 276.7181 | 276.7181 | 0 | 0
2025-08-24 21:00 | 32.8 | 70 | 100 | 26.8654 | 21.6051 | 63.3941 | 274.226 | 274.226 | 0 | 0
2025-08-24 22:00 | 32.05 | 71 | 70 | 26.6399 | 21.3911 | 63.2997 | 185.4936 | 185.4936 | 0 | 0
2025-08-24 23:00 | 31.3 | 72 | 70 | 26.4108 | 21.1754 | 63.2091 | 179.0062 | 179.0062 | 0 | 0
2025-08-25 | 30.45 | 74 | 70 | 26.1452 | 20.9922 | 63.5383 | 174.6777 | 174.6777 | 0 | 0
2025-08-25 01:00 | 29.6 | 74.5 | 70 | 25.8781 | 20.6933 | 63.1326 | 165.0434 | 165.0434 | 0 | 0
2025-08-25 02:00 | 28.8 | 73 | 70 | 25.6248 | 20.272 | 61.8515 | 149.659 | 149.659 | 0 | 0
2025-08-25 03:00 | 28.65 | 68.5 | 70 | 25.5819 | 19.8907 | 59.6554 | 133.0608 | 133.0608 | 0 | 0
2025-08-25 04:00 | 29.8 | 60.5 | 70 | 25.9646 | 19.7161 | 56.5078 | 119.4491 | 119.4491 | 0 | 0
2025-08-25 05:00 | 30.55 | 55 | 70 | 26.2137 | 19.5452 | 54.1776 | 108.112 | 108.112 | 0 | 0
2025-08-25 06:00 | 31 | 51 | 100 | 26.3645 | 19.3694 | 52.363 | 140.0967 | 140.0967 | 0 | 0
2025-08-25 07:00 | 32.8 | 43.5 | 100 | 26.9457 | 19.3011 | 49.1509 | 123.4491 | 123.4491 | 0 | 0
2025-08-25 08:00 | 35.15 | 35 | 100 | 27.6891 | 19.1882 | 45.1453 | 100.8647 | 100.8647 | 0 | 0
2025-08-25 09:00 | 37.55 | 27 | 100 | 28.4348 | 18.9719 | 40.861 | 72.2617 | 72.2617 | 0 | 0
2025-08-25 10:00 | 39.95 | 20 | 100 | 29.1677 | 18.6921 | 36.6136 | 40.5636 | 40.5636 | 0 | 0
2025-08-25 11:00 | 41.65 | 16 | 100 | 29.6761 | 18.5144 | 33.9332 | 19.9817 | 19.9817 | 0 | 0
2025-08-25 12:00 | 42.05 | 16.5 | 100 | 29.7806 | 18.6748 | 34.3419 | 27.6815 | 27.6815 | 0 | 0
2025-08-25 13:00 | 41.5 | 19.5 | 100 | 29.6009 | 18.9865 | 36.489 | 50.0858 | 50.0858 | 0 | 0
2025-08-25 14:00 | 40.85 | 23 | 100 | 29.3911 | 19.3154 | 38.898 | 74.4213 | 74.4213 | 0 | 0
2025-08-25 15:00 | 40.25 | 26 | 100 | 29.2012 | 19.5611 | 40.8719 | 93.3987 | 93.3987 | 0 | 0
2025-08-25 16:00 | 39.75 | 24.5 | 100 | 29.0758 | 19.2343 | 39.7062 | 75.8199 | 75.8199 | 0 | 0
2025-08-25 17:00 | 38.6 | 26.5 | 100 | 28.7385 | 19.1868 | 40.7885 | 79.6762 | 79.6762 | 0 | 0
2025-08-25 18:00 | 36.55 | 39.5 | 100 | 28.0763 | 20.0856 | 48.3832 | 149.2593 | 149.2593 | 0 | 0
2025-08-25 19:00 | 35 | 51 | 100 | 27.5757 | 20.7368 | 54.4368 | 201.5964 | 201.5964 | 0 | 0
2025-08-25 20:00 | 33.9 | 55 | 100 | 27.2391 | 20.7231 | 56.0345 | 207.9701 | 207.9701 | 0 | 0
2025-08-25 21:00 | 32.7 | 55.5 | 100 | 26.8793 | 20.3418 | 55.5793 | 191.0163 | 191.0163 | 0 | 0
2025-08-25 22:00 | 31.65 | 53.5 | 70 | 26.5626 | 19.8024 | 53.9527 | 114.2762 | 114.2762 | 0 | 0
2025-08-25 23:00 | 30.8 | 49.5 | 70 | 26.3042 | 19.1774 | 51.5193 | 90.5148 | 90.5148 | 0 | 0
2025-08-26 | 30.05 | 45 | 70 | 26.0715 | 18.5591 | 49.0051 | 67.0884 | 67.0884 | 0 | 0
2025-08-26 01:00 | 29.3 | 42.5 | 70 | 25.8298 | 18.1193 | 47.5835 | 51.7991 | 51.7991 | 0 | 0
2025-08-26 02:00 | 28.5 | 41.5 | 70 | 25.5649 | 17.795 | 46.9402 | 41.9027 | 41.9027 | 0 | 0
2025-08-26 03:00 | 27.95 | 39.5 | 70 | 25.3817 | 17.4732 | 45.9181 | 31.0283 | 31.0283 | 0 | 0
2025-08-26 04:00 | 28.4 | 39 | 70 | 25.5342 | 17.5662 | 45.7471 | 32.7306 | 32.7306 | 0 | 0
2025-08-26 05:00 | 28.9 | 40 | 70 | 25.7005 | 17.7952 | 46.2976 | 39.9176 | 39.9176 | 0 | 0
2025-08-26 06:00 | 29.5 | 37 | 100 | 25.9041 | 17.7256 | 44.9405 | 48.5281 | 48.5281 | 0 | 0
2025-08-26 07:00 | 31.65 | 30.5 | 100 | 26.6182 | 17.755 | 41.9203 | 35.5644 | 35.5644 | 0 | 0
2025-08-26 08:00 | 34.55 | 25 | 100 | 27.5482 | 17.9665 | 39.1738 | 29.3299 | 29.3299 | 0 | 0
2025-08-26 09:00 | 37.35 | 21 | 100 | 28.4119 | 18.2009 | 36.9927 | 26.012 | 26.012 | 0 | 0
2025-08-26 10:00 | 39.7 | 18 | 100 | 29.1129 | 18.3649 | 35.1989 | 21.8859 | 21.8859 | 0 | 0
2025-08-26 11:00 | 41.4 | 15.5 | 100 | 29.6118 | 18.3878 | 33.5459 | 13.5661 | 13.5661 | 0 | 0
2025-08-26 12:00 | 42.6 | 13.5 | 100 | 29.9622 | 18.3366 | 32.1189 | 3.8536 | 3.8536 | 0 | 0
2025-08-26 13:00 | 43.2 | 14 | 100 | 30.1192 | 18.5372 | 32.5352 | 12.892 | 12.892 | 0 | 0
2025-08-26 14:00 | 43.2 | 14.5 | 100 | 30.1135 | 18.6149 | 32.9263 | 17.771 | 17.771 | 0 | 0
2025-08-26 15:00 | 42.65 | 14 | 100 | 29.9706 | 18.4207 | 32.5118 | 9.0611 | 9.0611 | 0 | 0
2025-08-26 16:00 | 41.85 | 15 | 100 | 29.7412 | 18.4053 | 33.2197 | 12.5726 | 12.5726 | 0 | 0
2025-08-26 17:00 | 40.6 | 19 | 100 | 29.3579 | 18.704 | 36.0071 | 37.9287 | 37.9287 | 0 | 0
2025-08-26 18:00 | 38.5 | 27.5 | 100 | 28.7033 | 19.2833 | 41.423 | 86.2692 | 86.2692 | 0 | 0
2025-08-26 19:00 | 36.65 | 35 | 100 | 28.1293 | 19.629 | 45.6457 | 119.3792 | 119.3792 | 0 | 0
2025-08-26 20:00 | 35.6 | 36.5 | 100 | 27.8157 | 19.4779 | 46.1871 | 116.3698 | 116.3698 | 0 | 0
2025-08-26 21:00 | 35 | 35 | 100 | 27.6442 | 19.1435 | 45.1053 | 99.1242 | 99.1242 | 0 | 0
2025-08-26 22:00 | 34.5 | 34.5 | 70 | 27.4958 | 18.9456 | 44.6723 | 63.0025 | 63.0025 | 0 | 0
2025-08-26 23:00 | 33.45 | 47.5 | 70 | 27.1313 | 19.8813 | 51.6196 | 109.3033 | 109.3033 | 0 | 0
2025-08-27 | 32.3 | 64 | 70 | 26.7341 | 20.9175 | 59.8361 | 162.1569 | 162.1569 | 0 | 0
2025-08-27 01:00 | 31.45 | 68.5 | 70 | 26.4647 | 20.9583 | 61.5515 | 168.2077 | 168.2077 | 0 | 0
2025-08-27 02:00 | 30.7 | 70.5 | 70 | 26.2297 | 20.8238 | 62.0035 | 165.6682 | 165.6682 | 0 | 0
2025-08-27 03:00 | 30.05 | 74 | 70 | 26.0205 | 20.8342 | 63.235 | 169.3479 | 169.3479 | 0 | 0
2025-08-27 04:00 | 29.95 | 75.5 | 70 | 25.9866 | 20.9051 | 63.8851 | 173.164 | 173.164 | 0 | 0
2025-08-27 05:00 | 30 | 75.5 | 70 | 26.0022 | 20.925 | 63.9234 | 173.835 | 173.835 | 0 | 0
2025-08-27 06:00 | 30.15 | 75.5 | 100 | 26.0491 | 20.9853 | 64.0377 | 251.2071 | 251.2071 | 0 | 0
2025-08-27 07:00 | 31.75 | 70.5 | 100 | 26.551 | 21.234 | 62.7985 | 256.4866 | 256.4866 | 0 | 0
2025-08-27 08:00 | 34.65 | 59.5 | 100 | 27.4394 | 21.4053 | 59.0727 | 248.1256 | 248.1256 | 0 | 0
2025-08-27 09:00 | 38.05 | 44 | 100 | 28.468 | 21.0571 | 51.9662 | 202.8982 | 202.8982 | 0 | 0
2025-08-27 10:00 | 40.95 | 29.5 | 100 | 29.3585 | 20.2152 | 43.5498 | 130.4528 | 130.4528 | 0 | 0
2025-08-27 11:00 | 42.8 | 21.5 | 100 | 29.9272 | 19.594 | 38.2251 | 80.3762 | 80.3762 | 0 | 0
2025-08-27 12:00 | 44.05 | 17.5 | 100 | 30.301 | 19.2778 | 35.3734 | 53.8313 | 53.8313 | 0 | 0
2025-08-27 13:00 | 45 | 15 | 100 | 30.58 | 19.0788 | 33.4993 | 36.5195 | 36.5195 | 0 | 0
2025-08-27 14:00 | 45.15 | 16 | 100 | 30.6042 | 19.2774 | 34.3449 | 48.1596 | 48.1596 | 0 | 0
2025-08-27 15:00 | 44.05 | 20.5 | 100 | 30.2624 | 19.7451 | 37.7639 | 83.4783 | 83.4783 | 0 | 0
2025-08-27 16:00 | 41.85 | 31.5 | 100 | 29.5732 | 20.7337 | 45.3854 | 159.2345 | 159.2345 | 0 | 0
2025-08-27 17:00 | 39.9 | 41.5 | 100 | 28.9777 | 21.3791 | 51.4341 | 213.3054 | 213.3054 | 0 | 0
2025-08-27 18:00 | 39.05 | 42.5 | 100 | 28.7467 | 21.2172 | 51.5948 | 207.6622 | 207.6622 | 0 | 0
2025-08-27 19:00 | 38.6 | 40.5 | 100 | 28.6407 | 20.8448 | 50.0144 | 185.7564 | 185.7564 | 0 | 0
2025-08-27 20:00 | 37.4 | 43 | 100 | 28.2958 | 20.7335 | 50.9706 | 185.8485 | 185.8485 | 0 | 0
2025-08-27 21:00 | 35.7 | 49.5 | 100 | 27.7833 | 20.8336 | 53.9685 | 203.2373 | 203.2373 | 0 | 0
2025-08-27 22:00 | 34.25 | 55.5 | 70 | 27.3399 | 20.8949 | 56.5286 | 151.7458 | 151.7458 | 0 | 0
2025-08-27 23:00 | 33.25 | 60.5 | 70 | 27.0283 | 20.9759 | 58.6257 | 160.2427 | 160.2427 | 0 | 0
2025-08-28 | 32.75 | 62 | 70 | 26.8749 | 20.9188 | 59.0895 | 160.0093 | 160.0093 | 0 | 0
2025-08-28 01:00 | 32.35 | 60 | 70 | 26.7604 | 20.6014 | 57.7605 | 147.2967 | 147.2967 | 0 | 0
2025-08-28 02:00 | 31.85 | 55.5 | 70 | 26.6195 | 20.0413 | 55.1007 | 124.1327 | 124.1327 | 0 | 0
2025-08-28 03:00 | 31.25 | 49.5 | 70 | 26.4467 | 19.3265 | 51.7042 | 94.9695 | 94.9695 | 0 | 0
2025-08-28 04:00 | 32.7 | 40 | 70 | 26.9251 | 18.9453 | 47.2201 | 71.2407 | 71.2407 | 0 | 0
2025-08-28 05:00 | 33.8 | 34 | 70 | 27.2842 | 18.6938 | 44.2012 | 55.1314 | 55.1314 | 0 | 0
2025-08-28 06:00 | 33.2 | 35 | 100 | 27.0956 | 18.6202 | 44.6098 | 77.9973 | 77.9973 | 0 | 0
2025-08-28 07:00 | 33.7 | 41.5 | 100 | 27.2275 | 19.3995 | 48.3718 | 123.3779 | 123.3779 | 0 | 0
2025-08-28 08:00 | 35.4 | 45.5 | 100 | 27.716 | 20.3384 | 51.4192 | 172.4331 | 172.4331 | 0 | 0
2025-08-28 09:00 | 38.05 | 39 | 100 | 28.5009 | 20.505 | 48.7336 | 166.4011 | 166.4011 | 0 | 0
2025-08-28 10:00 | 40.6 | 30.5 | 100 | 29.2566 | 20.2483 | 44.1156 | 134.3491 | 134.3491 | 0 | 0
2025-08-28 11:00 | 42.6 | 24 | 100 | 29.8471 | 19.9092 | 40.057 | 101.191 | 101.191 | 0 | 0
2025-08-28 12:00 | 44.1 | 19.5 | 100 | 30.2881 | 19.6081 | 36.9598 | 73.8618 | 73.8618 | 0 | 0
2025-08-28 13:00 | 44.75 | 18 | 100 | 30.4741 | 19.5205 | 35.8956 | 65.0006 | 65.0006 | 0 | 0
2025-08-28 14:00 | 43.6 | 24 | 100 | 30.1038 | 20.1657 | 40.3781 | 112.3599 | 112.3599 | 0 | 0
2025-08-28 15:00 | 41.5 | 32.5 | 100 | 29.4733 | 20.7636 | 45.9486 | 163.0895 | 163.0895 | 0 | 0
2025-08-28 16:00 | 40.05 | 35.5 | 100 | 29.0673 | 20.7087 | 47.387 | 168.0389 | 168.0389 | 0 | 0
2025-08-28 17:00 | 39.1 | 37 | 100 | 28.8013 | 20.598 | 47.9489 | 166.5129 | 166.5129 | 0 | 0
2025-08-28 18:00 | 38.1 | 41 | 100 | 28.5013 | 20.7411 | 50.0727 | 182.0079 | 182.0079 | 0 | 0
2025-08-28 19:00 | 37.05 | 45 | 100 | 28.1869 | 20.8313 | 52.0291 | 194.4848 | 194.4848 | 0 | 0
2025-08-28 20:00 | 36.25 | 46 | 100 | 27.9569 | 20.669 | 52.1885 | 188.8486 | 188.8486 | 0 | 0
2025-08-28 21:00 | 35.45 | 46 | 100 | 27.7281 | 20.4027 | 51.7525 | 176.5656 | 176.5656 | 0 | 0
2025-08-28 22:00 | 34.65 | 45.5 | 70 | 27.4967 | 20.0896 | 51.0573 | 113.0128 | 113.0128 | 0 | 0
2025-08-28 23:00 | 34 | 45 | 70 | 27.3055 | 19.8283 | 50.4724 | 104.2821 | 104.2821 | 0 | 0
2025-08-29 | 33.3 | 47 | 70 | 27.0876 | 19.786 | 51.2706 | 105.6686 | 105.6686 | 0 | 0
2025-08-29 01:00 | 32.45 | 51.5 | 70 | 26.8148 | 19.9049 | 53.3004 | 115.0484 | 115.0484 | 0 | 0
2025-08-29 02:00 | 31.7 | 55.5 | 70 | 26.5732 | 19.9889 | 55.0144 | 122.428 | 122.428 | 0 | 0
2025-08-29 03:00 | 30.9 | 57.5 | 70 | 26.3192 | 19.8722 | 55.6052 | 120.9921 | 120.9921 | 0 | 0
2025-08-29 04:00 | 30.5 | 55 | 70 | 26.1978 | 19.5289 | 54.1432 | 107.5028 | 107.5028 | 0 | 0
2025-08-29 05:00 | 30.4 | 51 | 70 | 26.1735 | 19.1693 | 52.0974 | 91.9496 | 91.9496 | 0 | 0
2025-08-29 06:00 | 30.65 | 48.5 | 100 | 26.2584 | 19.0458 | 50.9376 | 121.7578 | 121.7578 | 0 | 0
2025-08-29 07:00 | 32.5 | 43.5 | 100 | 26.8529 | 19.2076 | 49.0244 | 119.2757 | 119.2757 | 0 | 0
2025-08-29 08:00 | 35.95 | 34.5 | 100 | 27.9281 | 19.3724 | 45.0845 | 107.0662 | 107.0662 | 0 | 0
2025-08-29 09:00 | 39 | 28 | 100 | 28.8403 | 19.4858 | 41.8666 | 95.359 | 95.359 | 0 | 0
2025-08-29 10:00 | 40.85 | 25 | 100 | 29.3729 | 19.5922 | 40.3016 | 91.1619 | 91.1619 | 0 | 0
2025-08-29 11:00 | 42.4 | 21.5 | 100 | 29.8219 | 19.4965 | 38.1266 | 76.33 | 76.33 | 0 | 0
2025-08-29 12:00 | 43.5 | 19 | 100 | 30.1393 | 19.3867 | 36.448 | 63.4395 | 63.4395 | 0 | 0
2025-08-29 13:00 | 43.35 | 21 | 100 | 30.0762 | 19.6546 | 37.9744 | 81.1881 | 81.1881 | 0 | 0
2025-08-29 14:00 | 42.4 | 24 | 100 | 29.7949 | 19.8531 | 40.0165 | 99.2501 | 99.2501 | 0 | 0
2025-08-29 15:00 | 41.2 | 27 | 100 | 29.4482 | 19.9498 | 41.858 | 112.3519 | 112.3519 | 0 | 0
2025-08-29 16:00 | 39.7 | 33 | 100 | 28.9942 | 20.2973 | 45.5152 | 143.4455 | 143.4455 | 0 | 0
2025-08-29 17:00 | 37.8 | 44.5 | 100 | 28.3965 | 21.0266 | 52.1539 | 202.7396 | 202.7396 | 0 | 0
2025-08-29 18:00 | 35.7 | 57.5 | 100 | 27.7447 | 21.606 | 58.7133 | 254.8987 | 254.8987 | 0 | 0
2025-08-29 19:00 | 34.5 | 64.5 | 100 | 27.376 | 21.7961 | 61.8005 | 275.6877 | 275.6877 | 0 | 0
2025-08-29 20:00 | 34.1 | 66 | 100 | 27.2562 | 21.7742 | 62.3026 | 276.7849 | 276.7849 | 0 | 0
2025-08-29 21:00 | 33.9 | 61.5 | 100 | 27.2155 | 21.3054 | 59.6389 | 246.4268 | 246.4268 | 0 | 0
2025-08-29 22:00 | 33.55 | 58 | 70 | 27.1254 | 20.8672 | 57.458 | 153.7331 | 153.7331 | 0 | 0
2025-08-29 23:00 | 32.7 | 60.5 | 70 | 26.8645 | 20.7733 | 58.2466 | 153.4301 | 153.4301 | 0 | 0
2025-08-30 | 31.7 | 66.5 | 70 | 26.5459 | 20.8953 | 60.6986 | 163.9316 | 163.9316 | 0 | 0
2025-08-30 01:00 | 31.15 | 74 | 70 | 26.3606 | 21.2706 | 64.0944 | 184.191 | 184.191 | 0 | 0
2025-08-30 02:00 | 30.85 | 84 | 70 | 26.2475 | 21.8978 | 68.8185 | 215.4687 | 215.4687 | 0 | 0
2025-08-30 03:00 | 30.45 | 93 | 70 | 26.108 | 22.3705 | 72.8203 | 240.3209 | 240.3209 | 0 | 0
2025-08-30 04:00 | 30.2 | 86.5 | 70 | 26.0444 | 21.804 | 69.4117 | 214.2494 | 214.2494 | 0 | 0
2025-08-30 05:00 | 29.8 | 75.5 | 70 | 25.9396 | 20.8465 | 63.7497 | 171.0029 | 171.0029 | 0 | 0
2025-08-30 06:00 | 30.05 | 69.5 | 100 | 26.0287 | 20.4984 | 61.0208 | 219.411 | 219.411 | 0 | 0
2025-08-30 07:00 | 32.2 | 57 | 100 | 26.7232 | 20.2949 | 56.0603 | 190.9893 | 190.9893 | 0 | 0
2025-08-30 08:00 | 35.9 | 38.5 | 100 | 27.8941 | 19.7821 | 47.4751 | 133.3461 | 133.3461 | 0 | 0
2025-08-30 09:00 | 39.65 | 23 | 100 | 29.0596 | 19.0204 | 38.6239 | 62.2552 | 62.2552 | 0 | 0
2025-08-30 10:00 | 41.85 | 18.5 | 100 | 29.7057 | 18.9306 | 35.7829 | 43.9252 | 43.9252 | 0 | 0
2025-08-30 11:00 | 43.15 | 18.5 | 100 | 30.0534 | 19.2316 | 35.9862 | 55.3448 | 55.3448 | 0 | 0
2025-08-30 12:00 | 44.25 | 17.5 | 100 | 30.3526 | 19.328 | 35.3922 | 55.3846 | 55.3846 | 0 | 0
2025-08-30 13:00 | 43.6 | 22.5 | 100 | 30.1223 | 19.9446 | 39.1967 | 97.9229 | 97.9229 | 0 | 0
2025-08-30 14:00 | 41.3 | 32.5 | 100 | 29.4218 | 20.7069 | 45.8445 | 160.2591 | 160.2591 | 0 | 0
2025-08-30 15:00 | 39.45 | 41 | 100 | 28.8642 | 21.1774 | 50.8104 | 202.256 | 202.256 | 0 | 0
2025-08-30 16:00 | 38.05 | 49.5 | 100 | 28.4316 | 21.6479 | 55.4983 | 242.4013 | 242.4013 | 0 | 0
2025-08-30 17:00 | 36.7 | 58.5 | 100 | 28.0144 | 22.0726 | 60.0876 | 279.8246 | 279.8246 | 0 | 0
2025-08-30 18:00 | 35.7 | 64.5 | 100 | 27.711 | 22.259 | 62.8179 | 299.1035 | 299.1035 | 0 | 0
2025-08-30 19:00 | 35 | 67 | 100 | 27.5062 | 22.2121 | 63.6389 | 300.5185 | 300.5185 | 0 | 0
2025-08-30 20:00 | 34.35 | 69.5 | 100 | 27.3138 | 22.1745 | 64.463 | 302.2994 | 302.2994 | 0 | 0
2025-08-30 21:00 | 33.85 | 69.5 | 100 | 27.1719 | 21.9779 | 64.0113 | 292.1341 | 292.1341 | 0 | 0
2025-08-30 22:00 | 33.45 | 67 | 70 | 27.0654 | 21.6099 | 62.3013 | 188.8768 | 188.8768 | 0 | 0
2025-08-30 23:00 | 33 | 65.5 | 70 | 26.9384 | 21.3099 | 61.1352 | 176.9184 | 176.9184 | 0 | 0
2025-08-31 | 32.4 | 67.5 | 70 | 26.7543 | 21.2452 | 61.7386 | 176.8168 | 176.8168 | 0 | 0
2025-08-31 01:00 | 31.6 | 74.5 | 70 | 26.4958 | 21.4889 | 64.7202 | 192.2414 | 192.2414 | 0 | 0
2025-08-31 02:00 | 31.05 | 81 | 70 | 26.3145 | 21.7595 | 67.5135 | 207.8351 | 207.8351 | 0 | 0
2025-08-31 03:00 | 30.7 | 83.5 | 70 | 26.203 | 21.7981 | 68.4249 | 211.4391 | 211.4391 | 0 | 0
2025-08-31 04:00 | 30.45 | 72.5 | 70 | 26.1482 | 20.8801 | 62.7892 | 169.3315 | 169.3315 | 0 | 0
2025-08-31 05:00 | 30.15 | 56.5 | 70 | 26.0835 | 19.5284 | 54.7093 | 109.0792 | 109.0792 | 0 | 0
2025-08-31 06:00 | 30.25 | 52.5 | 100 | 26.1227 | 19.242 | 52.7729 | 136.8518 | 136.8518 | 0 | 0
2025-08-31 07:00 | 32 | 50 | 100 | 26.6802 | 19.6232 | 52.27 | 148.9953 | 148.9953 | 0 | 0
2025-08-31 08:00 | 35.45 | 37 | 100 | 27.7692 | 19.4888 | 46.4086 | 117.5116 | 117.5116 | 0 | 0
2025-08-31 09:00 | 38.55 | 25.5 | 100 | 28.7311 | 19.0577 | 40.0849 | 71.074 | 71.074 | 0 | 0
2025-08-31 10:00 | 40.6 | 23 | 100 | 29.3227 | 19.2605 | 38.8142 | 71.5592 | 71.5592 | 0 | 0
2025-08-31 11:00 | 42.3 | 21 | 100 | 29.8007 | 19.4017 | 37.7223 | 70.6976 | 70.6976 | 0 | 0
2025-08-31 12:00 | 43.7 | 18.5 | 100 | 30.1974 | 19.359 | 36.0867 | 60.3264 | 60.3264 | 0 | 0
2025-08-31 13:00 | 44.75 | 16.5 | 100 | 30.4947 | 19.2775 | 34.6734 | 49.6849 | 49.6849 | 0 | 0
2025-08-31 14:00 | 44.75 | 17 | 100 | 30.4879 | 19.3574 | 35.0849 | 54.8533 | 54.8533 | 0 | 0
2025-08-31 15:00 | 43.15 | 22.5 | 100 | 30.0067 | 19.8278 | 39.0838 | 93.3463 | 93.3463 | 0 | 0
2025-08-31 16:00 | 40.5 | 32.5 | 100 | 29.2122 | 20.4705 | 45.5015 | 149.7979 | 149.7979 | 0 | 0
2025-08-31 17:00 | 38.2 | 41.5 | 100 | 28.5253 | 20.829 | 50.4485 | 187.1409 | 187.1409 | 0 | 0
2025-08-31 18:00 | 36.8 | 47 | 100 | 28.1059 | 20.956 | 53.1222 | 204.3149 | 204.3149 | 0 | 0
2025-08-31 19:00 | 36.1 | 48.5 | 100 | 27.9017 | 20.8711 | 53.6133 | 203.1515 | 203.1515 | 0 | 0
2025-08-31 20:00 | 35.7 | 45.5 | 100 | 27.8024 | 20.4351 | 51.5915 | 177.1347 | 177.1347 | 0 | 0
2025-08-31 21:00 | 34.95 | 43 | 100 | 27.5955 | 19.9409 | 49.7546 | 149.9836 | 149.9836 | 0 | 0
2025-08-31 22:00 | 34.1 | 44 | 70 | 27.3391 | 19.7647 | 49.9552 | 101.0064 | 101.0064 | 0 | 0
2025-08-31 23:00 | 33.1 | 49 | 70 | 27.0205 | 19.9022 | 52.2758 | 111.8688 | 111.8688 | 0 | 0
2025-09-01 | 31.8 | 63.5 | 70 | 26.5839 | 20.6892 | 59.2276 | 153.9809 | 153.9809 | 0 | 0
2025-09-01 01:00 | 30.85 | 80.5 | 70 | 26.2548 | 21.6394 | 67.0938 | 203.2177 | 203.2177 | 0 | 0
2025-09-01 02:00 | 30.3 | 88.5 | 70 | 26.0711 | 21.9887 | 70.4938 | 222.7037 | 222.7037 | 0 | 0
2025-09-01 03:00 | 29.85 | 89 | 70 | 25.9321 | 21.8311 | 70.2875 | 217.4459 | 217.4459 | 0 | 0
2025-09-01 04:00 | 29.25 | 82 | 70 | 25.7559 | 21.0899 | 66.4177 | 185.3169 | 185.3169 | 0 | 0
2025-09-01 05:00 | 28.65 | 73 | 70 | 25.5763 | 20.2136 | 61.7503 | 147.7599 | 147.7599 | 0 | 0
2025-09-01 06:00 | 29.1 | 62.5 | 100 | 25.7359 | 19.6157 | 57.0896 | 169.1133 | 169.1133 | 0 | 0
2025-09-01 07:00 | 31.6 | 46.5 | 100 | 26.5639 | 19.1835 | 50.2913 | 124.1999 | 124.1999 | 0 | 0
2025-09-01 08:00 | 35.45 | 33.5 | 100 | 27.785 | 19.1171 | 44.3507 | 94.5914 | 94.5914 | 0 | 0
2025-09-01 09:00 | 38.95 | 26 | 100 | 28.8407 | 19.2198 | 40.53 | 79.3745 | 79.3745 | 0 | 0
2025-09-01 10:00 | 41.45 | 20 | 100 | 29.5824 | 19.0464 | 36.8434 | 54.025 | 54.025 | 0 | 0
2025-09-01 11:00 | 43.25 | 15.5 | 100 | 30.1151 | 18.7833 | 33.7038 | 27.7723 | 27.7723 | 0 | 0
2025-09-01 12:00 | 43.05 | 19.5 | 100 | 30.0156 | 19.3527 | 36.7623 | 64.2285 | 64.2285 | 0 | 0
2025-09-01 13:00 | 41 | 29.5 | 100 | 29.3716 | 20.2251 | 43.5886 | 131.3134 | 131.3134 | 0 | 0
2025-09-01 14:00 | 39.3 | 38 | 100 | 28.8474 | 20.7752 | 48.7328 | 177.2115 | 177.2115 | 0 | 0
2025-09-01 15:00 | 38.1 | 45.5 | 100 | 28.4712 | 21.2332 | 52.9904 | 214.8541 | 214.8541 | 0 | 0
2025-09-01 16:00 | 37 | 50 | 100 | 28.1439 | 21.3315 | 55.1206 | 228.3131 | 228.3131 | 0 | 0
2025-09-01 17:00 | 35.55 | 57 | 100 | 27.7049 | 21.5025 | 58.32 | 249.138 | 249.138 | 0 | 0
2025-09-01 18:00 | 33.95 | 69 | 100 | 27.2017 | 21.9725 | 63.8595 | 291.6135 | 291.6135 | 0 | 0
2025-09-01 19:00 | 33 | 77.5 | 100 | 26.8998 | 22.2927 | 67.5868 | 320.0455 | 320.0455 | 0 | 0
2025-09-01 20:00 | 32.45 | 82 | 100 | 26.7269 | 22.4181 | 69.4067 | 332.5246 | 332.5246 | 0 | 0
2025-09-01 21:00 | 31.9 | 86 | 100 | 26.5553 | 22.4897 | 70.8994 | 341.3623 | 341.3623 | 0 | 0
2025-09-01 22:00 | 31.2 | 90 | 70 | 26.3389 | 22.4828 | 72.1717 | 242.1384 | 242.1384 | 0 | 0
2025-09-01 23:00 | 30.45 | 94 | 70 | 26.1058 | 22.44 | 73.3252 | 243.8574 | 243.8574 | 0 | 0
2025-09-02 | 29.8 | 97 | 70 | 25.9029 | 22.36 | 74.0529 | 243.29 | 243.29 | 0 | 0
2025-09-02 01:00 | 29.3 | 98.5 | 70 | 25.7467 | 22.2388 | 74.2116 | 239.9959 | 239.9959 | 0 | 0
2025-09-02 02:00 | 28.85 | 99 | 70 | 25.6061 | 22.0723 | 73.9554 | 234.2469 | 234.2469 | 0 | 0
2025-09-02 03:00 | 28.45 | 99 | 70 | 25.4804 | 21.8948 | 73.5293 | 227.7676 | 227.7676 | 0 | 0
2025-09-02 04:00 | 28.75 | 96 | 70 | 25.5788 | 21.831 | 72.4697 | 223.1237 | 223.1237 | 0 | 0
2025-09-02 05:00 | 29.1 | 92.5 | 70 | 25.6934 | 21.7495 | 71.2024 | 217.4024 | 217.4024 | 0 | 0
2025-09-02 06:00 | 29.25 | 90.5 | 100 | 25.7433 | 21.6782 | 70.4122 | 304.5741 | 304.5741 | 0 | 0
2025-09-02 07:00 | 30.45 | 84.5 | 100 | 26.1247 | 21.7658 | 68.6925 | 301.8047 | 301.8047 | 0 | 0
2025-09-02 08:00 | 32.55 | 76.5 | 100 | 26.7724 | 22.0294 | 66.616 | 304.9111 | 304.9111 | 0 | 0
2025-09-02 09:00 | 34.75 | 67.5 | 100 | 27.4341 | 22.1579 | 63.7131 | 298.6481 | 298.6481 | 0 | 0
2025-09-02 10:00 | 36.75 | 57 | 100 | 28.0361 | 21.9442 | 59.2235 | 270.9107 | 270.9107 | 0 | 0
2025-09-02 11:00 | 38.55 | 47.5 | 100 | 28.5779 | 21.6053 | 54.5642 | 236.6144 | 236.6144 | 0 | 0
2025-09-02 12:00 | 39.65 | 43 | 100 | 28.9004 | 21.4715 | 52.3001 | 220.9819 | 220.9819 | 0 | 0
2025-09-02 13:00 | 39.25 | 45.5 | 100 | 28.7763 | 21.6216 | 53.727 | 233.5774 | 233.5774 | 0 | 0
2025-09-02 14:00 | 38.55 | 46 | 100 | 28.5882 | 21.4398 | 53.5997 | 225.7973 | 225.7973 | 0 | 0
2025-09-02 15:00 | 38 | 46.5 | 100 | 28.4375 | 21.3076 | 53.5714 | 220.4436 | 220.4436 | 0 | 0
2025-09-02 16:00 | 37.1 | 48.5 | 100 | 28.1801 | 21.2112 | 54.2569 | 219.7041 | 219.7041 | 0 | 0
2025-09-02 17:00 | 35.8 | 53.5 | 100 | 27.792 | 21.2578 | 56.4298 | 231.0941 | 231.0941 | 0 | 0
2025-09-02 18:00 | 34.25 | 64.5 | 100 | 27.3046 | 21.6995 | 61.6084 | 271.0142 | 271.0142 | 0 | 0
2025-09-02 19:00 | 33.45 | 71 | 100 | 27.0512 | 21.9439 | 64.507 | 292.9768 | 292.9768 | 0 | 0
2025-09-02 20:00 | 33.25 | 72.5 | 100 | 26.9885 | 21.9885 | 65.1322 | 297.3157 | 297.3157 | 0 | 0
2025-09-02 21:00 | 33 | 75 | 100 | 26.908 | 22.0924 | 66.2389 | 306.0629 | 306.0629 | 0 | 0
2025-09-02 22:00 | 32.45 | 79.5 | 70 | 26.7344 | 22.2241 | 68.0893 | 223.2843 | 223.2843 | 0 | 0
2025-09-02 23:00 | 31.7 | 84.5 | 70 | 26.5005 | 22.2922 | 69.9185 | 230.3076 | 230.3076 | 0 | 0
2025-09-03 | 30.9 | 88.5 | 70 | 26.2527 | 22.2453 | 71.1029 | 232.0564 | 232.0564 | 0 | 0
2025-09-03 01:00 | 30.05 | 92 | 70 | 25.9882 | 22.1263 | 71.9267 | 230.6265 | 230.6265 | 0 | 0
2025-09-03 02:00 | 29.35 | 95 | 70 | 25.7677 | 22.0265 | 72.6189 | 229.3995 | 229.3995 | 0 | 0
2025-09-03 03:00 | 28.9 | 95.5 | 70 | 25.6266 | 21.8633 | 72.3837 | 223.8436 | 223.8436 | 0 | 0
2025-09-03 04:00 | 28.65 | 93 | 70 | 25.5512 | 21.5886 | 70.9816 | 211.9795 | 211.9795 | 0 | 0
2025-09-03 05:00 | 28.45 | 90.5 | 70 | 25.4907 | 21.3364 | 69.6457 | 201.0261 | 201.0261 | 0 | 0
2025-09-03 06:00 | 28.8 | 86 | 100 | 25.6078 | 21.1805 | 67.8896 | 274.0483 | 274.0483 | 0 | 0
2025-09-03 07:00 | 30.7 | 72.5 | 100 | 26.2257 | 20.9774 | 62.9836 | 246.6949 | 246.6949 | 0 | 0
2025-09-03 08:00 | 34.1 | 50.5 | 100 | 27.3149 | 20.3809 | 53.6168 | 183.9535 | 183.9535 | 0 | 0
2025-09-03 09:00 | 37.55 | 29.5 | 100 | 28.4197 | 19.2661 | 42.4577 | 90.6128 | 90.6128 | 0 | 0
2025-09-03 10:00 | 39.8 | 19.5 | 100 | 29.1294 | 18.5893 | 36.2475 | 35.1187 | 35.1187 | 0 | 0
2025-09-03 11:00 | 41.1 | 17.5 | 100 | 29.5099 | 18.6108 | 34.9759 | 28.9446 | 28.9446 | 0 | 0
2025-09-03 12:00 | 42 | 16.5 | 100 | 29.767 | 18.665 | 34.3348 | 27.2555 | 27.2555 | 0 | 0
2025-09-03 13:00 | 42.45 | 16 | 100 | 29.8945 | 18.6871 | 34.0073 | 26.2446 | 26.2446 | 0 | 0
2025-09-03 14:00 | 42.1 | 16 | 100 | 29.7995 | 18.6095 | 33.9795 | 23.5713 | 23.5713 | 0 | 0
2025-09-03 15:00 | 40.6 | 23 | 100 | 29.3228 | 19.2529 | 38.8428 | 71.918 | 71.918 | 0 | 0
2025-09-03 16:00 | 39 | 32.5 | 100 | 28.8074 | 20.0312 | 44.9015 | 130.594 | 130.594 | 0 | 0
2025-09-03 17:00 | 37.55 | 40 | 100 | 28.3557 | 20.4545 | 49.1567 | 166.8042 | 166.8042 | 0 | 0
2025-09-03 18:00 | 36.15 | 47.5 | 100 | 27.9208 | 20.7867 | 53.0459 | 197.3777 | 197.3777 | 0 | 0
2025-09-03 19:00 | 35.55 | 50.5 | 100 | 27.7359 | 20.8799 | 54.4715 | 207.2971 | 207.2971 | 0 | 0
2025-09-03 20:00 | 35.35 | 51 | 100 | 27.6765 | 20.86 | 54.6363 | 207.1603 | 207.1603 | 0 | 0
2025-09-03 21:00 | 34.85 | 53 | 100 | 27.524 | 20.8763 | 55.4838 | 211.48 | 211.48 | 0 | 0
2025-09-03 22:00 | 33.85 | 56 | 70 | 27.2209 | 20.7971 | 56.5467 | 149.062 | 149.062 | 0 | 0
2025-09-03 23:00 | 32.9 | 57.5 | 70 | 26.9336 | 20.5876 | 56.7691 | 143.9555 | 143.9555 | 0 | 0
2025-09-04 | 32.1 | 60 | 70 | 26.6845 | 20.5105 | 57.597 | 144.2694 | 144.2694 | 0 | 0
2025-09-04 01:00 | 31.3 | 63.5 | 70 | 26.4305 | 20.5026 | 58.8925 | 147.8077 | 147.8077 | 0 | 0
2025-09-04 02:00 | 30.55 | 67.5 | 70 | 26.1891 | 20.5358 | 60.4024 | 153.0241 | 153.0241 | 0 | 0
2025-09-04 03:00 | 29.95 | 70.5 | 70 | 25.9953 | 20.5343 | 61.4584 | 155.93 | 155.93 | 0 | 0
2025-09-04 04:00 | 29.65 | 70.5 | 70 | 25.9004 | 20.4188 | 61.2486 | 152.0967 | 152.0967 | 0 | 0
2025-09-04 05:00 | 29.4 | 71 | 70 | 25.8201 | 20.3588 | 61.312 | 150.5886 | 150.5886 | 0 | 0
2025-09-04 06:00 | 29.9 | 64.5 | 100 | 25.9898 | 20.0614 | 58.4963 | 192.0276 | 192.0276 | 0 | 0
2025-09-04 07:00 | 32 | 51.5 | 100 | 26.6763 | 19.7529 | 53.0632 | 157.3787 | 157.3787 | 0 | 0
2025-09-04 08:00 | 34.65 | 43.5 | 100 | 27.5049 | 19.8958 | 49.8936 | 148.7285 | 148.7285 | 0 | 0
2025-09-04 09:00 | 37.15 | 37.5 | 100 | 28.2584 | 20.0586 | 47.3714 | 143.1489 | 143.1489 | 0 | 0
2025-09-04 10:00 | 39.45 | 31 | 100 | 28.9422 | 19.9828 | 44.0305 | 124.1446 | 124.1446 | 0 | 0
2025-09-04 11:00 | 41.65 | 24 | 100 | 29.5971 | 19.6648 | 39.7896 | 90.9925 | 90.9925 | 0 | 0
2025-09-04 12:00 | 43.6 | 17.5 | 100 | 30.1836 | 19.1793 | 35.2893 | 49.7717 | 49.7717 | 0 | 0
2025-09-04 13:00 | 44.35 | 15 | 100 | 30.4114 | 18.9432 | 33.4135 | 31.2717 | 31.2717 | 0 | 0
2025-09-04 14:00 | 43.85 | 16 | 100 | 30.2678 | 18.9953 | 34.1546 | 37.3138 | 37.3138 | 0 | 0
2025-09-04 15:00 | 42.75 | 20 | 100 | 29.9309 | 19.3585 | 37.0761 | 65.9864 | 65.9864 | 0 | 0
2025-09-04 16:00 | 41.8 | 23 | 100 | 29.647 | 19.5591 | 39.1083 | 83.9003 | 83.9003 | 0 | 0
2025-09-04 17:00 | 41.65 | 21.5 | 100 | 29.6219 | 19.31 | 37.9718 | 69.0944 | 69.0944 | 0 | 0
2025-09-04 18:00 | 40.15 | 26 | 100 | 29.1738 | 19.5386 | 40.8262 | 92.0837 | 92.0837 | 0 | 0
2025-09-04 19:00 | 37.15 | 39 | 100 | 28.2497 | 20.222 | 48.3208 | 153.8537 | 153.8537 | 0 | 0
2025-09-04 20:00 | 35 | 48.5 | 100 | 27.5867 | 20.4984 | 52.9627 | 185.5443 | 185.5443 | 0 | 0
2025-09-04 21:00 | 33.75 | 52.5 | 100 | 27.204 | 20.4453 | 54.526 | 190.2955 | 190.2955 | 0 | 0
2025-09-04 22:00 | 33 | 55 | 70 | 26.9715 | 20.4065 | 55.4629 | 134.966 | 134.966 | 0 | 0
2025-09-04 23:00 | 32.4 | 57 | 70 | 26.7841 | 20.3662 | 56.1811 | 136.0182 | 136.0182 | 0 | 0
2025-09-05 | 31.9 | 58.5 | 70 | 26.6274 | 20.3136 | 56.6719 | 136.0243 | 136.0243 | 0 | 0
2025-09-05 01:00 | 31.6 | 58 | 70 | 26.5362 | 20.1641 | 56.2359 | 130.6565 | 130.6565 | 0 | 0
2025-09-05 02:00 | 31.55 | 54.5 | 70 | 26.5292 | 19.8538 | 54.3988 | 116.8398 | 116.8398 | 0 | 0
2025-09-05 03:00 | 32.1 | 46.5 | 70 | 26.7204 | 19.3491 | 50.4674 | 91.604 | 91.604 | 0 | 0
2025-09-05 04:00 | 33.05 | 41 | 70 | 27.0304 | 19.15 | 47.8579 | 78.29 | 78.29 | 0 | 0
2025-09-05 05:00 | 33.3 | 41 | 70 | 27.1072 | 19.2282 | 47.94 | 80.5158 | 80.5158 | 0 | 0
2025-09-05 06:00 | 33.3 | 41 | 100 | 27.1072 | 19.2288 | 47.9357 | 114.9737 | 114.9737 | 0 | 0
2025-09-05 07:00 | 34.4 | 38.5 | 100 | 27.4501 | 19.3255 | 46.9054 | 113.6984 | 113.6984 | 0 | 0
2025-09-05 08:00 | 36.3 | 34 | 100 | 28.033 | 19.4243 | 44.8695 | 107.6273 | 107.6273 | 0 | 0
2025-09-05 09:00 | 38.3 | 29.5 | 100 | 28.6333 | 19.4813 | 42.6352 | 98.6904 | 98.6904 | 0 | 0
2025-09-05 10:00 | 40.2 | 25.5 | 100 | 29.1917 | 19.4941 | 40.4587 | 88.1001 | 88.1001 | 0 | 0
2025-09-05 11:00 | 41.85 | 22.5 | 100 | 29.6654 | 19.5092 | 38.72 | 79.5558 | 79.5558 | 0 | 0
2025-09-05 12:00 | 42.95 | 20 | 100 | 29.9835 | 19.4146 | 37.089 | 67.5181 | 67.5181 | 0 | 0
2025-09-05 13:00 | 43.2 | 20.5 | 100 | 30.0431 | 19.5485 | 37.5319 | 74.6958 | 74.6958 | 0 | 0
2025-09-05 14:00 | 42.35 | 26 | 100 | 29.7604 | 20.1289 | 41.4766 | 116.4667 | 116.4667 | 0 | 0
2025-09-05 15:00 | 40.85 | 30.5 | 100 | 29.3229 | 20.3196 | 44.2139 | 137.488 | 137.488 | 0 | 0
2025-09-05 16:00 | 39.3 | 34 | 100 | 28.8783 | 20.3048 | 46.0036 | 145.7939 | 145.7939 | 0 | 0
2025-09-05 17:00 | 38 | 39.5 | 100 | 28.4838 | 20.5451 | 49.0311 | 169.3348 | 169.3348 | 0 | 0
2025-09-05 18:00 | 36.95 | 43 | 100 | 28.1706 | 20.5898 | 50.7087 | 178.8367 | 178.8367 | 0 | 0
2025-09-05 19:00 | 36.3 | 45.5 | 100 | 27.9739 | 20.6373 | 51.8902 | 186.0075 | 186.0075 | 0 | 0
2025-09-05 20:00 | 36.05 | 47 | 100 | 27.8954 | 20.7071 | 52.6513 | 192.0786 | 192.0786 | 0 | 0
2025-09-05 21:00 | 35.75 | 46.5 | 100 | 27.8123 | 20.5563 | 52.1823 | 184.0957 | 184.0957 | 0 | 0
2025-09-05 22:00 | 35.3 | 46.5 | 70 | 27.6826 | 20.4057 | 51.941 | 124.0511 | 124.0511 | 0 | 0
2025-09-05 23:00 | 34.75 | 47.5 | 70 | 27.5181 | 20.3191 | 52.2345 | 122.6531 | 122.6531 | 0 | 0
2025-09-06 | 33.9 | 49.5 | 70 | 27.2594 | 20.222 | 52.9251 | 122.1785 | 122.1785 | 0 | 0
2025-09-06 01:00 | 32.8 | 53 | 70 | 26.9173 | 20.1608 | 54.2595 | 124.6069 | 124.6069 | 0 | 0
2025-09-06 02:00 | 32 | 56.5 | 70 | 26.6633 | 20.182 | 55.6741 | 129.4142 | 129.4142 | 0 | 0
2025-09-06 03:00 | 31.3 | 59 | 70 | 26.441 | 20.14 | 56.5641 | 130.8701 | 130.8701 | 0 | 0
2025-09-06 04:00 | 31 | 57.5 | 70 | 26.3506 | 19.9102 | 55.6288 | 121.8805 | 121.8805 | 0 | 0
2025-09-06 05:00 | 30.55 | 56.5 | 70 | 26.2109 | 19.6706 | 54.8844 | 113.2255 | 113.2255 | 0 | 0
2025-09-06 06:00 | 30.35 | 56 | 100 | 26.1483 | 19.5607 | 54.5307 | 156.0342 | 156.0342 | 0 | 0
2025-09-06 07:00 | 32.35 | 45.5 | 100 | 26.8009 | 19.3441 | 50.0095 | 128.3702 | 128.3702 | 0 | 0
2025-09-06 08:00 | 35.25 | 34 | 100 | 27.7232 | 19.1202 | 44.5443 | 95.0205 | 95.0205 | 0 | 0
2025-09-06 09:00 | 37.65 | 29 | 100 | 28.4514 | 19.2432 | 42.127 | 87.6034 | 87.6034 | 0 | 0
2025-09-06 10:00 | 39.75 | 25 | 100 | 29.0717 | 19.3121 | 39.9969 | 79.2206 | 79.2206 | 0 | 0
2025-09-06 11:00 | 41.35 | 22 | 100 | 29.5359 | 19.3151 | 38.2385 | 70.1266 | 70.1266 | 0 | 0
2025-09-06 12:00 | 42.2 | 21 | 100 | 29.7741 | 19.381 | 37.6859 | 69.5351 | 69.5351 | 0 | 0
2025-09-06 13:00 | 42.25 | 21 | 100 | 29.7874 | 19.3919 | 37.7026 | 70.0961 | 70.0961 | 0 | 0
2025-09-06 14:00 | 41.7 | 21.5 | 100 | 29.6352 | 19.3277 | 37.9626 | 69.33 | 69.33 | 0 | 0
2025-09-06 15:00 | 41.2 | 22 | 100 | 29.4954 | 19.2739 | 38.2248 | 68.8855 | 68.8855 | 0 | 0
2025-09-06 16:00 | 40.45 | 24.5 | 100 | 29.2686 | 19.4229 | 39.838 | 82.6367 | 82.6367 | 0 | 0
2025-09-06 17:00 | 38.5 | 34 | 100 | 28.6588 | 20.0683 | 45.6736 | 135.332 | 135.332 | 0 | 0
2025-09-06 18:00 | 36 | 50.5 | 100 | 27.8637 | 21.0387 | 54.7297 | 214.4503 | 214.4503 | 0 | 0
2025-09-06 19:00 | 34.35 | 65 | 100 | 27.3318 | 21.7847 | 61.9285 | 275.4687 | 275.4687 | 0 | 0
2025-09-06 20:00 | 33.5 | 73 | 100 | 27.0593 | 22.1312 | 65.6002 | 304.9687 | 304.9687 | 0 | 0
2025-09-06 21:00 | 32.75 | 79.5 | 100 | 26.822 | 22.3492 | 68.3578 | 325.1851 | 325.1851 | 0 | 0
2025-09-06 22:00 | 32.2 | 83 | 70 | 26.6518 | 22.3907 | 69.6309 | 232.3521 | 232.3521 | 0 | 0
2025-09-06 23:00 | 31.7 | 82 | 70 | 26.5072 | 22.1044 | 68.6177 | 221.0173 | 221.0173 | 0 | 0
2025-09-07 | 31.35 | 80.5 | 70 | 26.4063 | 21.8465 | 67.5225 | 210.3395 | 210.3395 | 0 | 0
2025-09-07 01:00 | 30.7 | 82 | 70 | 26.2063 | 21.6885 | 67.6667 | 206.0616 | 206.0616 | 0 | 0
2025-09-07 02:00 | 29.65 | 85.5 | 70 | 25.8762 | 21.5019 | 68.3968 | 202.5099 | 202.5099 | 0 | 0
2025-09-07 03:00 | 29 | 86.5 | 70 | 25.6707 | 21.2989 | 68.2785 | 196.2224 | 196.2224 | 0 | 0
2025-09-07 04:00 | 29 | 84.5 | 70 | 25.6734 | 21.1608 | 67.3472 | 189.7323 | 189.7323 | 0 | 0
2025-09-07 05:00 | 29.15 | 82 | 70 | 25.7245 | 21.0491 | 66.3059 | 183.7045 | 183.7045 | 0 | 0
2025-09-07 06:00 | 29.6 | 76 | 100 | 25.8759 | 20.8032 | 63.8231 | 242.739 | 242.739 | 0 | 0
2025-09-07 07:00 | 31.6 | 63 | 100 | 26.5241 | 20.576 | 58.8048 | 213.4341 | 213.4341 | 0 | 0
2025-09-07 08:00 | 34.45 | 50 | 100 | 27.42 | 20.4557 | 53.5075 | 186.1663 | 186.1663 | 0 | 0
2025-09-07 09:00 | 37.15 | 40.5 | 100 | 28.2411 | 20.3872 | 49.2428 | 164.2133 | 164.2133 | 0 | 0
2025-09-07 10:00 | 39.45 | 31.5 | 100 | 28.9384 | 20.0465 | 44.3621 | 127.9967 | 127.9967 | 0 | 0
2025-09-07 11:00 | 40.7 | 25.5 | 100 | 29.3279 | 19.6225 | 40.6066 | 93.6546 | 93.6546 | 0 | 0
2025-09-07 12:00 | 40.85 | 25 | 100 | 29.3729 | 19.5943 | 40.2956 | 91.0865 | 91.0865 | 0 | 0
2025-09-07 13:00 | 40.55 | 26.5 | 100 | 29.2784 | 19.713 | 41.2796 | 100.5026 | 100.5026 | 0 | 0
2025-09-07 14:00 | 40 | 29.5 | 100 | 29.1039 | 19.9492 | 43.2042 | 118.8979 | 118.8979 | 0 | 0
2025-09-07 15:00 | 39 | 36 | 100 | 28.7817 | 20.4517 | 47.2218 | 157.3155 | 157.3155 | 0 | 0
2025-09-07 16:00 | 37.8 | 42 | 100 | 28.4126 | 20.7565 | 50.5427 | 184.6362 | 184.6362 | 0 | 0
2025-09-07 17:00 | 36.55 | 47.5 | 100 | 28.0335 | 20.9242 | 53.2682 | 203.5891 | 203.5891 | 0 | 0
2025-09-07 18:00 | 35.35 | 53.5 | 100 | 27.6651 | 21.1007 | 56.0977 | 223.058 | 223.058 | 0 | 0
2025-09-07 19:00 | 34.55 | 57 | 100 | 27.421 | 21.1407 | 57.5721 | 231.0072 | 231.0072 | 0 | 0
2025-09-07 20:00 | 33.95 | 61.5 | 100 | 27.2301 | 21.3243 | 59.6686 | 247.2617 | 247.2617 | 0 | 0
2025-09-07 21:00 | 33.15 | 69 | 100 | 26.9712 | 21.6609 | 63.1399 | 275.387 | 275.387 | 0 | 0
2025-09-07 22:00 | 32.35 | 73 | 70 | 26.7238 | 21.67 | 64.5858 | 197.1541 | 197.1541 | 0 | 0
2025-09-07 23:00 | 31.7 | 74 | 70 | 26.5271 | 21.4901 | 64.5482 | 191.7901 | 191.7901 | 0 | 0
2025-09-08 | 31 | 77 | 70 | 26.3082 | 21.4387 | 65.469 | 192.8423 | 192.8423 | 0 | 0
2025-09-08 01:00 | 30.4 | 81 | 70 | 26.1163 | 21.4913 | 66.9221 | 198.3249 | 198.3249 | 0 | 0
2025-09-08 02:00 | 29.95 | 85 | 70 | 25.9701 | 21.592 | 68.4531 | 205.4137 | 205.4137 | 0 | 0
2025-09-08 03:00 | 29.45 | 87.5 | 70 | 25.8105 | 21.5572 | 69.1786 | 206.3011 | 206.3011 | 0 | 0
2025-09-08 04:00 | 29.3 | 87.5 | 70 | 25.7635 | 21.4936 | 69.0397 | 204.0636 | 204.0636 | 0 | 0
2025-09-08 05:00 | 29.2 | 88.5 | 70 | 25.7307 | 21.5199 | 69.4153 | 205.8343 | 205.8343 | 0 | 0
2025-09-08 06:00 | 29.4 | 88 | 100 | 25.7941 | 21.5705 | 69.3666 | 295.9872 | 295.9872 | 0 | 0
2025-09-08 07:00 | 31.05 | 80 | 100 | 26.3168 | 21.6847 | 67.012 | 291.8006 | 291.8006 | 0 | 0
2025-09-08 08:00 | 33.3 | 69.5 | 100 | 27.0132 | 21.7608 | 63.5382 | 281.1923 | 281.1923 | 0 | 0
2025-09-08 09:00 | 35.15 | 61.5 | 100 | 27.5725 | 21.7747 | 60.6001 | 269.6356 | 269.6356 | 0 | 0
2025-09-08 10:00 | 36.8 | 55 | 100 | 28.0612 | 21.767 | 58.0244 | 258.3057 | 258.3057 | 0 | 0
2025-09-08 11:00 | 38.3 | 49.5 | 100 | 28.4981 | 21.7357 | 55.672 | 246.6738 | 246.6738 | 0 | 0
2025-09-08 12:00 | 39.4 | 46 | 100 | 28.8119 | 21.7311 | 54.1419 | 239.6133 | 239.6133 | 0 | 0
2025-09-08 13:00 | 39.65 | 46.5 | 100 | 28.8723 | 21.8722 | 54.6573 | 247.6892 | 247.6892 | 0 | 0
2025-09-08 14:00 | 39.3 | 47.5 | 100 | 28.774 | 21.8637 | 55.0856 | 249.3382 | 249.3382 | 0 | 0
2025-09-08 15:00 | 38.65 | 48 | 100 | 28.6007 | 21.6938 | 54.9605 | 241.9742 | 241.9742 | 0 | 0
2025-09-08 16:00 | 37.55 | 51.5 | 100 | 28.2845 | 21.6799 | 56.4252 | 247.9603 | 247.9603 | 0 | 0
2025-09-08 17:00 | 35.8 | 61.5 | 100 | 27.7529 | 22.0189 | 61.1541 | 282.2622 | 282.2622 | 0 | 0
2025-09-08 18:00 | 33.95 | 74.5 | 100 | 27.1813 | 22.436 | 66.8822 | 323.3433 | 323.3433 | 0 | 0
2025-09-08 19:00 | 33 | 81 | 100 | 26.8888 | 22.5708 | 69.4365 | 339.174 | 339.174 | 0 | 0
2025-09-08 20:00 | 32.6 | 83 | 100 | 26.7676 | 22.5585 | 70.0695 | 341.0748 | 341.0748 | 0 | 0
2025-09-08 21:00 | 32.2 | 84.5 | 100 | 26.6473 | 22.5043 | 70.4266 | 340.0705 | 340.0705 | 0 | 0
2025-09-08 22:00 | 31.75 | 86.5 | 70 | 26.5102 | 22.463 | 70.9782 | 238.2759 | 238.2759 | 0 | 0
2025-09-08 23:00 | 31.15 | 89.5 | 70 | 26.3254 | 22.4251 | 71.8528 | 239.464 | 239.464 | 0 | 0
2025-09-09 | 30.5 | 92.5 | 70 | 26.1241 | 22.3572 | 72.6341 | 239.4429 | 239.4429 | 0 | 0
2025-09-09 01:00 | 29.9 | 95.5 | 70 | 25.9363 | 22.3017 | 73.4306 | 239.8331 | 239.8331 | 0 | 0
2025-09-09 02:00 | 29.4 | 98 | 70 | 25.7786 | 22.2495 | 74.0656 | 239.8685 | 239.8685 | 0 | 0
2025-09-09 03:00 | 28.9 | 99.5 | 70 | 25.6212 | 22.1268 | 74.2156 | 236.4837 | 236.4837 | 0 | 0
2025-09-09 04:00 | 29 | 100 | 70 | 25.6517 | 22.2039 | 74.553 | 239.6971 | 239.6971 | 0 | 0
2025-09-09 05:00 | 29.3 | 100 | 70 | 25.7447 | 22.3378 | 74.8826 | 244.6371 | 244.6371 | 0 | 0
2025-09-09 06:00 | 29.45 | 96 | 100 | 25.7973 | 22.1379 | 73.1725 | 334.4503 | 334.4503 | 0 | 0
2025-09-09 07:00 | 31.05 | 79.5 | 100 | 26.318 | 21.6471 | 66.7535 | 289.1665 | 289.1665 | 0 | 0
2025-09-09 08:00 | 34.2 | 59.5 | 100 | 27.3101 | 21.2402 | 58.7288 | 239.8305 | 239.8305 | 0 | 0
2025-09-09 09:00 | 37.8 | 43.5 | 100 | 28.4032 | 20.9217 | 51.4887 | 195.2705 | 195.2705 | 0 | 0
2025-09-09 10:00 | 40.75 | 31.5 | 100 | 29.2874 | 20.4198 | 44.8797 | 144.5163 | 144.5163 | 0 | 0
2025-09-09 11:00 | 42.7 | 26 | 100 | 29.8507 | 20.2226 | 41.5964 | 120.5189 | 120.5189 | 0 | 0
2025-09-09 12:00 | 44 | 23 | 100 | 30.2176 | 20.1228 | 39.703 | 106.9632 | 106.9632 | 0 | 0
2025-09-09 13:00 | 44.8 | 20.5 | 100 | 30.452 | 19.9343 | 37.9321 | 90.703 | 90.703 | 0 | 0
2025-09-09 14:00 | 45.05 | 18.5 | 100 | 30.543 | 19.6712 | 36.3644 | 72.8593 | 72.8593 | 0 | 0
2025-09-09 15:00 | 44.85 | 17.5 | 100 | 30.5065 | 19.4616 | 35.5094 | 60.8305 | 60.8305 | 0 | 0
2025-09-09 16:00 | 42.5 | 31.5 | 100 | 29.7384 | 20.9267 | 45.6679 | 167.6895 | 167.6895 | 0 | 0
2025-09-09 17:00 | 39 | 52 | 100 | 28.6625 | 22.25 | 57.8337 | 277.3086 | 277.3086 | 0 | 0
2025-09-09 18:00 | 36.95 | 60.5 | 100 | 28.0701 | 22.3605 | 61.5192 | 297.8847 | 297.8847 | 0 | 0
2025-09-09 19:00 | 36.1 | 60 | 100 | 27.8432 | 21.9928 | 60.4922 | 278.178 | 278.178 | 0 | 0
2025-09-09 20:00 | 35.7 | 53.5 | 100 | 27.7643 | 21.2255 | 56.325 | 228.9671 | 228.9671 | 0 | 0
2025-09-09 21:00 | 34.65 | 52 | 100 | 27.4703 | 20.7128 | 54.7749 | 201.8394 | 201.8394 | 0 | 0
2025-09-09 22:00 | 33.05 | 56.5 | 70 | 26.9818 | 20.5557 | 56.3053 | 141.5834 | 141.5834 | 0 | 0
2025-09-09 23:00 | 31.85 | 59 | 70 | 26.6107 | 20.3374 | 56.9026 | 137.3526 | 137.3526 | 0 | 0
2025-09-10 | 31.15 | 58.5 | 70 | 26.3953 | 20.044 | 56.2383 | 127.4078 | 127.4078 | 0 | 0
2025-09-10 01:00 | 30.55 | 59 | 70 | 26.2059 | 19.8689 | 56.1571 | 122.4408 | 122.4408 | 0 | 0
2025-09-10 02:00 | 29.95 | 62.5 | 70 | 26.0092 | 19.9268 | 57.5448 | 127.9872 | 127.9872 | 0 | 0
2025-09-10 03:00 | 29.3 | 66.5 | 70 | 25.7948 | 19.9894 | 59.0854 | 134.0438 | 134.0438 | 0 | 0
2025-09-10 04:00 | 29.45 | 61 | 70 | 25.8514 | 19.6308 | 56.535 | 117.042 | 117.042 | 0 | 0
2025-09-10 05:00 | 30.15 | 51.5 | 70 | 26.0924 | 19.1278 | 52.2276 | 91.1439 | 91.1439 | 0 | 0
2025-09-10 06:00 | 30.65 | 48.5 | 100 | 26.2584 | 19.0476 | 50.9232 | 121.6023 | 121.6023 | 0 | 0
2025-09-10 07:00 | 31.85 | 45 | 100 | 26.6462 | 19.1371 | 49.5667 | 118.9095 | 118.9095 | 0 | 0
2025-09-10 08:00 | 33.9 | 39 | 100 | 27.2971 | 19.2223 | 47.0202 | 110.4716 | 110.4716 | 0 | 0
2025-09-10 09:00 | 36.3 | 32.5 | 100 | 28.0407 | 19.2601 | 43.9562 | 97.3384 | 97.3384 | 0 | 0
2025-09-10 10:00 | 38.75 | 26 | 100 | 28.7843 | 19.1739 | 40.4516 | 76.8928 | 76.8928 | 0 | 0
2025-09-10 11:00 | 40.65 | 21 | 100 | 29.3539 | 19.0023 | 37.3994 | 54.9906 | 54.9906 | 0 | 0
2025-09-10 12:00 | 41.8 | 18.5 | 100 | 29.6921 | 18.9203 | 35.7725 | 43.4506 | 43.4506 | 0 | 0
2025-09-10 13:00 | 42.05 | 19 | 100 | 29.7547 | 19.0498 | 36.1847 | 50.2127 | 50.2127 | 0 | 0
2025-09-10 14:00 | 40.95 | 25 | 100 | 29.3999 | 19.6187 | 40.3287 | 92.2364 | 92.2364 | 0 | 0
2025-09-10 15:00 | 39 | 34 | 100 | 28.7965 | 20.2147 | 45.8835 | 141.9178 | 141.9178 | 0 | 0
2025-09-10 16:00 | 37.4 | 41.5 | 100 | 28.305 | 20.5735 | 50.0114 | 175.0826 | 175.0826 | 0 | 0
2025-09-10 17:00 | 35.95 | 49.5 | 100 | 27.8544 | 20.9209 | 54.1109 | 207.1868 | 207.1868 | 0 | 0
2025-09-10 18:00 | 34.95 | 54 | 100 | 27.5486 | 21.0061 | 56.122 | 219.3738 | 219.3738 | 0 | 0
2025-09-10 19:00 | 34.7 | 51.5 | 100 | 27.4869 | 20.6824 | 54.523 | 199.6033 | 199.6033 | 0 | 0
2025-09-10 20:00 | 34.25 | 47.5 | 100 | 27.3707 | 20.1504 | 51.9892 | 167.7912 | 167.7912 | 0 | 0
2025-09-10 21:00 | 33.7 | 45.5 | 100 | 27.2136 | 19.7797 | 50.6013 | 147.5368 | 147.5368 | 0 | 0
2025-09-10 22:00 | 33.2 | 47 | 70 | 27.0573 | 19.755 | 51.207 | 104.516 | 104.516 | 0 | 0
2025-09-10 23:00 | 32.5 | 54.5 | 70 | 26.8216 | 20.1865 | 54.91 | 127.332 | 127.332 | 0 | 0
2025-09-11 | 31.65 | 61 | 70 | 26.5443 | 20.4296 | 57.8182 | 142.5846 | 142.5846 | 0 | 0
2025-09-11 01:00 | 30.75 | 64.5 | 70 | 26.2577 | 20.3781 | 59.0257 | 144.638 | 144.638 | 0 | 0
2025-09-11 02:00 | 30.1 | 67.5 | 70 | 26.0479 | 20.3657 | 60.0839 | 147.2876 | 147.2876 | 0 | 0
2025-09-11 03:00 | 29.8 | 63.5 | 70 | 25.9597 | 19.9483 | 57.9448 | 129.7234 | 129.7234 | 0 | 0
2025-09-11 04:00 | 30.3 | 53 | 70 | 26.1378 | 19.2996 | 53.0428 | 98.1041 | 98.1041 | 0 | 0
2025-09-11 05:00 | 30.8 | 45 | 70 | 26.3134 | 18.7999 | 49.2153 | 73.6416 | 73.6416 | 0 | 0
2025-09-11 06:00 | 31 | 42 | 100 | 26.3837 | 18.6055 | 47.7431 | 91.6258 | 91.6258 | 0 | 0
2025-09-11 07:00 | 32.3 | 40 | 100 | 26.8003 | 18.8271 | 47.0709 | 96.504 | 96.504 | 0 | 0
2025-09-11 08:00 | 34.5 | 36.5 | 100 | 27.488 | 19.154 | 45.7942 | 102.3645 | 102.3645 | 0 | 0
2025-09-11 09:00 | 36.8 | 31.5 | 100 | 28.1917 | 19.2907 | 43.4866 | 96.1962 | 96.1962 | 0 | 0
2025-09-11 10:00 | 38.8 | 27 | 100 | 28.7914 | 19.3114 | 41.1306 | 85.2021 | 85.2021 | 0 | 0
2025-09-11 11:00 | 40.45 | 23.5 | 100 | 29.2772 | 19.2908 | 39.129 | 74.1986 | 74.1986 | 0 | 0
2025-09-11 12:00 | 41.55 | 21.5 | 100 | 29.5948 | 19.2902 | 37.9326 | 67.89 | 67.89 | 0 | 0
2025-09-11 13:00 | 41.75 | 23 | 100 | 29.6337 | 19.55 | 39.0811 | 83.1978 | 83.1978 | 0 | 0
2025-09-11 14:00 | 41.15 | 27.5 | 100 | 29.4302 | 20.0075 | 42.1817 | 115.8046 | 115.8046 | 0 | 0
2025-09-11 15:00 | 39.95 | 32.5 | 100 | 29.0657 | 20.3115 | 45.2567 | 142.4731 | 142.4731 | 0 | 0
2025-09-11 16:00 | 38.5 | 36.5 | 100 | 28.6415 | 20.3581 | 47.3247 | 154.2487 | 154.2487 | 0 | 0
2025-09-11 17:00 | 37.3 | 40 | 100 | 28.286 | 20.3782 | 49.0187 | 163.0316 | 163.0316 | 0 | 0
2025-09-11 18:00 | 36.15 | 47 | 100 | 27.9236 | 20.7383 | 52.7269 | 193.8559 | 193.8559 | 0 | 0
2025-09-11 19:00 | 35.15 | 54 | 100 | 27.6059 | 21.0775 | 56.2499 | 222.7362 | 222.7362 | 0 | 0
2025-09-11 20:00 | 34.85 | 54.5 | 100 | 27.5178 | 21.018 | 56.337 | 220.7049 | 220.7049 | 0 | 0
2025-09-11 21:00 | 34.2 | 56 | 100 | 27.3235 | 20.9239 | 56.7601 | 218.7573 | 218.7573 | 0 | 0
2025-09-11 22:00 | 32.95 | 61.5 | 70 | 26.9362 | 20.9519 | 58.9403 | 160.3763 | 160.3763 | 0 | 0
2025-09-11 23:00 | 32.4 | 63.5 | 70 | 26.7657 | 20.9149 | 59.6227 | 161.336 | 161.336 | 0 | 0
2025-09-12 | 32.2 | 63.5 | 70 | 26.7054 | 20.8401 | 59.4842 | 158.8336 | 158.8336 | 0 | 0
2025-09-12 01:00 | 31.65 | 65 | 70 | 26.5344 | 20.756 | 59.8819 | 157.6178 | 157.6178 | 0 | 0
2025-09-12 02:00 | 31.3 | 65.5 | 70 | 26.426 | 20.6636 | 59.8942 | 155.0668 | 155.0668 | 0 | 0
2025-09-12 03:00 | 31.25 | 66 | 70 | 26.4094 | 20.6851 | 60.1106 | 156.2541 | 156.2541 | 0 | 0
2025-09-12 04:00 | 31.75 | 58.5 | 70 | 26.5813 | 20.26 | 56.5788 | 134.2533 | 134.2533 | 0 | 0
2025-09-12 05:00 | 32 | 51 | 70 | 26.6776 | 19.711 | 52.7911 | 108.1506 | 108.1506 | 0 | 0
2025-09-12 06:00 | 31.85 | 55 | 100 | 26.621 | 20.0022 | 54.8044 | 174.2086 | 174.2086 | 0 | 0
2025-09-12 07:00 | 32.55 | 57 | 100 | 26.8297 | 20.4216 | 56.2528 | 196.599 | 196.599 | 0 | 0
2025-09-12 08:00 | 33.9 | 52 | 100 | 27.2504 | 20.4537 | 54.3139 | 189.4925 | 189.4925 | 0 | 0
2025-09-12 09:00 | 35.4 | 44 | 100 | 27.7229 | 20.1908 | 50.5129 | 162.4593 | 162.4593 | 0 | 0
2025-09-12 10:00 | 36.8 | 38 | 100 | 28.1561 | 20.0088 | 47.5171 | 141.7288 | 141.7288 | 0 | 0
2025-09-12 11:00 | 38.15 | 34 | 100 | 28.5615 | 19.967 | 45.523 | 130.6701 | 130.6701 | 0 | 0
2025-09-12 12:00 | 39.45 | 30 | 100 | 28.9499 | 19.8616 | 43.341 | 116.1104 | 116.1104 | 0 | 0
2025-09-12 13:00 | 40.5 | 27 | 100 | 29.2605 | 19.7679 | 41.6085 | 104.0064 | 104.0064 | 0 | 0
2025-09-12 14:00 | 40.5 | 28.5 | 100 | 29.2475 | 19.9625 | 42.6681 | 116.5226 | 116.5226 | 0 | 0
2025-09-12 15:00 | 39.35 | 34.5 | 100 | 28.888 | 20.3799 | 46.3607 | 150.333 | 150.333 | 0 | 0
2025-09-12 16:00 | 37.55 | 44 | 100 | 28.3314 | 20.8934 | 51.6648 | 194.9803 | 194.9803 | 0 | 0
2025-09-12 17:00 | 36.3 | 50.5 | 100 | 27.9478 | 21.1424 | 54.9252 | 219.4758 | 219.4758 | 0 | 0
2025-09-12 18:00 | 35.85 | 53 | 100 | 27.809 | 21.231 | 56.1263 | 228.2701 | 228.2701 | 0 | 0
2025-09-12 19:00 | 35.25 | 54 | 100 | 27.6345 | 21.1139 | 56.309 | 224.3638 | 224.3638 | 0 | 0
2025-09-12 20:00 | 34.2 | 55.5 | 100 | 27.3255 | 20.8789 | 56.4719 | 215.6636 | 215.6636 | 0 | 0
2025-09-12 21:00 | 33.05 | 60.5 | 100 | 26.9693 | 20.9045 | 58.4561 | 225.0383 | 225.0383 | 0 | 0
2025-09-12 22:00 | 32.3 | 63.5 | 70 | 26.7358 | 20.8788 | 59.5339 | 159.9391 | 159.9391 | 0 | 0
2025-09-12 23:00 | 31.9 | 63 | 70 | 26.6159 | 20.6878 | 58.9988 | 153.0498 | 153.0498 | 0 | 0
2025-09-13 | 31.4 | 63 | 70 | 26.4627 | 20.5016 | 58.6677 | 146.9156 | 146.9156 | 0 | 0
2025-09-13 01:00 | 30.8 | 65 | 70 | 26.2723 | 20.4375 | 59.2882 | 146.9051 | 146.9051 | 0 | 0
2025-09-13 02:00 | 30.2 | 68.5 | 70 | 26.0777 | 20.4808 | 60.6207 | 151.8894 | 151.8894 | 0 | 0
2025-09-13 03:00 | 29.6 | 73 | 70 | 25.8807 | 20.5848 | 62.3772 | 159.6946 | 159.6946 | 0 | 0
2025-09-13 04:00 | 29.75 | 73 | 70 | 25.9282 | 20.6435 | 62.4844 | 161.6394 | 161.6394 | 0 | 0
2025-09-13 05:00 | 30.1 | 71 | 70 | 26.0418 | 20.6313 | 61.7657 | 159.2826 | 159.2826 | 0 | 0
2025-09-13 06:00 | 30.35 | 70 | 100 | 26.122 | 20.6534 | 61.4501 | 227.1105 | 227.1105 | 0 | 0
2025-09-13 07:00 | 31.65 | 63 | 100 | 26.5396 | 20.5957 | 58.817 | 214.0884 | 214.0884 | 0 | 0
2025-09-13 08:00 | 33.45 | 53.5 | 100 | 27.1114 | 20.4343 | 54.8757 | 191.0538 | 191.0538 | 0 | 0
2025-09-13 09:00 | 34.95 | 48 | 100 | 27.5745 | 20.437 | 52.6119 | 181.2311 | 181.2311 | 0 | 0
2025-09-13 10:00 | 36.45 | 43.5 | 100 | 28.027 | 20.4827 | 50.7306 | 174.5194 | 174.5194 | 0 | 0
2025-09-13 11:00 | 37.8 | 39.5 | 100 | 28.4287 | 20.4855 | 48.91 | 166.202 | 166.202 | 0 | 0
2025-09-13 12:00 | 38.95 | 36.5 | 100 | 28.7647 | 20.4996 | 47.504 | 160.1197 | 160.1197 | 0 | 0
2025-09-13 13:00 | 40.1 | 33.5 | 100 | 29.0977 | 20.4836 | 45.9923 | 152.2511 | 152.2511 | 0 | 0
2025-09-13 14:00 | 40.65 | 32 | 100 | 29.2566 | 20.4559 | 45.1851 | 147.2921 | 147.2921 | 0 | 0
2025-09-13 15:00 | 40.15 | 33 | 100 | 29.1151 | 20.4349 | 45.6753 | 148.972 | 148.972 | 0 | 0
2025-09-13 16:00 | 39.2 | 35.5 | 100 | 28.8399 | 20.455 | 46.9635 | 156.0264 | 156.0264 | 0 | 0
2025-09-13 17:00 | 37.75 | 39 | 100 | 28.4178 | 20.4114 | 48.5834 | 162.076 | 162.076 | 0 | 0
2025-09-13 18:00 | 35.9 | 44 | 100 | 27.8673 | 20.3527 | 50.7715 | 169.9316 | 169.9316 | 0 | 0
2025-09-13 19:00 | 33.95 | 51.5 | 100 | 27.267 | 20.4246 | 54.0686 | 187.3472 | 187.3472 | 0 | 0
2025-09-13 20:00 | 32.3 | 58.5 | 100 | 26.7497 | 20.4601 | 56.8929 | 200.7737 | 200.7737 | 0 | 0
2025-09-13 21:00 | 31.3 | 63 | 100 | 26.4319 | 20.4653 | 58.5929 | 208.0352 | 208.0352 | 0 | 0
2025-09-13 22:00 | 30.7 | 65.5 | 70 | 26.2402 | 20.4394 | 59.4625 | 147.4023 | 147.4023 | 0 | 0
2025-09-13 23:00 | 30.3 | 66.5 | 70 | 26.1129 | 20.3666 | 59.6957 | 146.0354 | 146.0354 | 0 | 0
2025-09-14 | 29.9 | 67.5 | 70 | 25.9848 | 20.2916 | 59.923 | 144.5975 | 144.5975 | 0 | 0
2025-09-14 01:00 | 29.45 | 69 | 70 | 25.8392 | 20.2327 | 60.3505 | 144.1633 | 144.1633 | 0 | 0
2025-09-14 02:00 | 29.1 | 70.5 | 70 | 25.7249 | 20.2092 | 60.8313 | 144.8361 | 144.8361 | 0 | 0
2025-09-14 03:00 | 28.9 | 72 | 70 | 25.6585 | 20.2411 | 61.4018 | 147.2827 | 147.2827 | 0 | 0
2025-09-14 04:00 | 28.85 | 71.5 | 70 | 25.6431 | 20.1857 | 61.132 | 144.9915 | 144.9915 | 0 | 0
2025-09-14 05:00 | 28.8 | 70.5 | 70 | 25.6282 | 20.0945 | 60.6279 | 141.0546 | 141.0546 | 0 | 0
2025-09-14 06:00 | 28.9 | 70.5 | 100 | 25.6605 | 20.133 | 60.6877 | 203.2245 | 203.2245 | 0 | 0
2025-09-14 07:00 | 29.95 | 67 | 100 | 26.0016 | 20.2738 | 59.6919 | 204.7558 | 204.7558 | 0 | 0
2025-09-14 08:00 | 31.9 | 58 | 100 | 26.6289 | 20.2755 | 56.3635 | 191.0742 | 191.0742 | 0 | 0
2025-09-14 09:00 | 33.85 | 49 | 100 | 27.2465 | 20.1619 | 52.5852 | 170.3795 | 170.3795 | 0 | 0
2025-09-14 10:00 | 35.45 | 44 | 100 | 27.7376 | 20.2102 | 50.5166 | 162.9549 | 162.9549 | 0 | 0
2025-09-14 11:00 | 36.85 | 40.5 | 100 | 28.1567 | 20.2961 | 49.0734 | 159.6316 | 159.6316 | 0 | 0
2025-09-14 12:00 | 38.15 | 37.5 | 100 | 28.5386 | 20.371 | 47.7819 | 156.4472 | 156.4472 | 0 | 0
2025-09-14 13:00 | 38.95 | 35 | 100 | 28.7757 | 20.3238 | 46.5 | 148.5858 | 148.5858 | 0 | 0
2025-09-14 14:00 | 38.85 | 35 | 100 | 28.7483 | 20.2932 | 46.4616 | 147.3069 | 147.3069 | 0 | 0
2025-09-14 15:00 | 38 | 39.5 | 100 | 28.484 | 20.5475 | 49.0153 | 169.1499 | 169.1499 | 0 | 0
2025-09-14 16:00 | 36.9 | 46 | 100 | 28.1398 | 20.8905 | 52.5243 | 198.6001 | 198.6001 | 0 | 0
2025-09-14 17:00 | 36.05 | 49 | 100 | 27.8854 | 20.9082 | 53.8457 | 205.2225 | 205.2225 | 0 | 0
2025-09-14 18:00 | 35.65 | 45.5 | 100 | 27.7883 | 20.4238 | 51.5273 | 175.949 | 175.949 | 0 | 0
2025-09-14 19:00 | 34.95 | 43 | 100 | 27.5957 | 19.9464 | 49.7137 | 149.5191 | 149.5191 | 0 | 0
2025-09-14 20:00 | 33.7 | 45.5 | 100 | 27.2137 | 19.7836 | 50.5736 | 147.2269 | 147.2269 | 0 | 0
2025-09-14 21:00 | 32.6 | 49 | 100 | 26.8682 | 19.7405 | 51.9829 | 151.805 | 151.805 | 0 | 0
2025-09-14 22:00 | 31.75 | 52.5 | 70 | 26.5963 | 19.7574 | 53.4262 | 111.0918 | 111.0918 | 0 | 0
2025-09-14 23:00 | 31.05 | 55.5 | 70 | 26.3707 | 19.7662 | 54.6184 | 114.8775 | 114.8775 | 0 | 0
2025-09-15 | 30.35 | 58.5 | 70 | 26.1436 | 19.7613 | 55.7603 | 118.1048 | 118.1048 | 0 | 0
2025-09-15 01:00 | 29.7 | 60.5 | 70 | 25.9327 | 19.6845 | 56.3976 | 117.9082 | 117.9082 | 0 | 0
2025-09-15 02:00 | 29.15 | 61.5 | 70 | 25.7537 | 19.5626 | 56.5871 | 115.1749 | 115.1749 | 0 | 0
2025-09-15 03:00 | 28.7 | 62.5 | 70 | 25.6058 | 19.4742 | 56.823 | 113.4794 | 113.4794 | 0 | 0
2025-09-15 04:00 | 29.6 | 58.5 | 70 | 25.9037 | 19.4946 | 55.3762 | 109.8643 | 109.8643 | 0 | 0
2025-09-15 05:00 | 30.6 | 52 | 70 | 26.2356 | 19.3233 | 52.6386 | 97.2723 | 97.2723 | 0 | 0
2025-09-15 06:00 | 30.35 | 52 | 100 | 26.1557 | 19.2392 | 52.5277 | 135.3036 | 135.3036 | 0 | 0
2025-09-15 07:00 | 30.7 | 53 | 100 | 26.2654 | 19.4403 | 53.178 | 145.5689 | 145.5689 | 0 | 0
2025-09-15 08:00 | 32 | 49.5 | 100 | 26.6816 | 19.585 | 51.9623 | 145.7252 | 145.7252 | 0 | 0
2025-09-15 09:00 | 33.6 | 44.5 | 100 | 27.187 | 19.6589 | 49.9576 | 139.6179 | 139.6179 | 0 | 0
2025-09-15 10:00 | 35.1 | 40 | 100 | 27.6528 | 19.6959 | 48.0079 | 132.1006 | 132.1006 | 0 | 0
2025-09-15 11:00 | 36.45 | 36.5 | 100 | 28.0637 | 19.7428 | 46.4375 | 126.5408 | 126.5408 | 0 | 0
2025-09-15 12:00 | 37.6 | 34 | 100 | 28.4068 | 19.8068 | 45.3074 | 123.5836 | 123.5836 | 0 | 0
2025-09-15 13:00 | 38.2 | 33 | 100 | 28.582 | 19.866 | 44.8878 | 123.806 | 123.806 | 0 | 0
2025-09-15 14:00 | 37.35 | 38.5 | 100 | 28.3091 | 20.2329 | 48.0714 | 152.786 | 152.786 | 0 | 0
2025-09-15 15:00 | 36.05 | 44.5 | 100 | 27.9079 | 20.4535 | 51.1418 | 175.4076 | 175.4076 | 0 | 0
2025-09-15 16:00 | 35.25 | 48.5 | 100 | 27.6593 | 20.5859 | 53.0833 | 189.243 | 189.243 | 0 | 0
2025-09-15 17:00 | 34.15 | 54 | 100 | 27.3166 | 20.7248 | 55.5877 | 205.6633 | 205.6633 | 0 | 0
2025-09-15 18:00 | 33.4 | 58 | 100 | 27.0814 | 20.8153 | 57.3267 | 216.6798 | 216.6798 | 0 | 0
2025-09-15 19:00 | 33.05 | 62 | 100 | 26.9646 | 21.0335 | 59.2571 | 233.4949 | 233.4949 | 0 | 0
2025-09-15 20:00 | 32.65 | 65.5 | 100 | 26.835 | 21.1782 | 60.8332 | 245.8213 | 245.8213 | 0 | 0
2025-09-15 21:00 | 32.3 | 69 | 100 | 26.7206 | 21.3302 | 62.4065 | 258.4595 | 258.4595 | 0 | 0
2025-09-15 22:00 | 31.85 | 73 | 70 | 26.5752 | 21.4732 | 64.1182 | 189.8606 | 189.8606 | 0 | 0
2025-09-15 23:00 | 31.4 | 76 | 70 | 26.4323 | 21.5258 | 65.2699 | 194.607 | 194.607 | 0 | 0
2025-09-16 | 30.95 | 78 | 70 | 26.2912 | 21.4951 | 65.8864 | 195.4203 | 195.4203 | 0 | 0
2025-09-16 01:00 | 30.45 | 80 | 70 | 26.1339 | 21.4395 | 66.44 | 195.3126 | 195.3126 | 0 | 0
2025-09-16 02:00 | 29.95 | 81.5 | 70 | 25.9765 | 21.3424 | 66.7326 | 193.2931 | 193.2931 | 0 | 0
2025-09-16 03:00 | 29.55 | 82.5 | 70 | 25.8499 | 21.2492 | 66.8625 | 190.9106 | 190.9106 | 0 | 0
2025-09-16 04:00 | 29.55 | 82.5 | 70 | 25.8499 | 21.2491 | 66.8617 | 190.9046 | 190.9046 | 0 | 0
2025-09-16 05:00 | 29.65 | 82 | 70 | 25.8821 | 21.2553 | 66.7078 | 190.6487 | 190.6487 | 0 | 0
2025-09-16 06:00 | 29.95 | 80 | 100 | 25.9791 | 21.2347 | 66.0024 | 268.7684 | 268.7684 | 0 | 0
2025-09-16 07:00 | 31.25 | 74 | 100 | 26.3914 | 21.3116 | 64.1286 | 264.6028 | 264.6028 | 0 | 0
2025-09-16 08:00 | 33 | 66.5 | 100 | 26.9357 | 21.3952 | 61.6327 | 257.9613 | 257.9613 | 0 | 0
2025-09-16 09:00 | 34.75 | 57.5 | 100 | 27.4769 | 21.2632 | 57.9562 | 237.1516 | 237.1516 | 0 | 0
2025-09-16 10:00 | 36.55 | 47.5 | 100 | 28.034 | 20.9285 | 53.2281 | 203.1359 | 203.1359 | 0 | 0
2025-09-16 11:00 | 38.1 | 40.5 | 100 | 28.505 | 20.692 | 49.7036 | 177.8189 | 177.8189 | 0 | 0
2025-09-16 12:00 | 39.05 | 38.5 | 100 | 28.7771 | 20.7636 | 48.8856 | 176.7966 | 176.7966 | 0 | 0
2025-09-16 13:00 | 38.9 | 42 | 100 | 28.7111 | 21.1168 | 51.1341 | 201.0993 | 201.0993 | 0 | 0
2025-09-16 14:00 | 38.2 | 43.5 | 100 | 28.5122 | 21.0543 | 51.712 | 201.3871 | 201.3871 | 0 | 0
2025-09-16 15:00 | 37.35 | 45.5 | 100 | 28.2673 | 20.9876 | 52.4889 | 202.3629 | 202.3629 | 0 | 0
2025-09-16 16:00 | 36.05 | 52.5 | 100 | 27.8677 | 21.253 | 55.9571 | 228.3695 | 228.3695 | 0 | 0
2025-09-16 17:00 | 34.5 | 63 | 100 | 27.3826 | 21.6651 | 60.9208 | 266.3238 | 266.3238 | 0 | 0
2025-09-16 18:00 | 33.2 | 73.5 | 100 | 26.9712 | 22.0515 | 65.5907 | 301.5489 | 301.5489 | 0 | 0
2025-09-16 19:00 | 32.7 | 77.5 | 100 | 26.8136 | 22.1705 | 67.2487 | 313.1572 | 313.1572 | 0 | 0
2025-09-16 20:00 | 32.5 | 78.5 | 100 | 26.7524 | 22.1672 | 67.5783 | 314.2873 | 314.2873 | 0 | 0
2025-09-16 21:00 | 32.15 | 80.5 | 100 | 26.6442 | 22.1776 | 68.2761 | 317.4565 | 317.4565 | 0 | 0
2025-09-16 22:00 | 31.8 | 83 | 70 | 26.5344 | 22.2223 | 69.2151 | 226.1085 | 226.1085 | 0 | 0
2025-09-16 23:00 | 31.3 | 86 | 70 | 26.3786 | 22.2345 | 70.2299 | 229.2201 | 229.2201 | 0 | 0
2025-09-17 | 30.7 | 89 | 70 | 26.1919 | 22.1959 | 71.1029 | 230.374 | 230.374 | 0 | 0
2025-09-17 01:00 | 30.1 | 91.5 | 70 | 26.0049 | 22.1131 | 71.697 | 229.4498 | 229.4498 | 0 | 0
2025-09-17 02:00 | 29.55 | 94.5 | 70 | 25.8307 | 22.0803 | 72.551 | 230.6687 | 230.6687 | 0 | 0
2025-09-17 03:00 | 29.05 | 96.5 | 70 | 25.6725 | 21.9951 | 72.9588 | 229.1334 | 229.1334 | 0 | 0
2025-09-17 04:00 | 29.25 | 95.5 | 70 | 25.7363 | 22.0161 | 72.7016 | 229.1025 | 229.1025 | 0 | 0
2025-09-17 05:00 | 29.45 | 95 | 70 | 25.7991 | 22.0704 | 72.6749 | 230.6612 | 230.6612 | 0 | 0
2025-09-17 06:00 | 29.45 | 94.5 | 100 | 25.7999 | 22.0361 | 72.4363 | 327.1476 | 327.1476 | 0 | 0
2025-09-17 07:00 | 30.75 | 87 | 100 | 26.2114 | 22.0734 | 70.1566 | 320.1625 | 320.1625 | 0 | 0
2025-09-17 08:00 | 32.9 | 73 | 100 | 26.886 | 21.8916 | 65.0274 | 292.353 | 292.353 | 0 | 0
2025-09-17 09:00 | 35.1 | 58.5 | 100 | 27.5723 | 21.4837 | 58.7864 | 249.6318 | 249.6318 | 0 | 0
2025-09-17 10:00 | 37.15 | 47 | 100 | 28.2036 | 21.0804 | 53.2814 | 209.3331 | 209.3331 | 0 | 0
2025-09-17 11:00 | 38.7 | 39.5 | 100 | 28.6754 | 20.7704 | 49.3594 | 179.169 | 179.169 | 0 | 0
2025-09-17 12:00 | 39.5 | 37.5 | 100 | 28.9053 | 20.787 | 48.4401 | 175.5409 | 175.5409 | 0 | 0
2025-09-17 13:00 | 39.5 | 37.5 | 100 | 28.9053 | 20.7868 | 48.4457 | 175.6067 | 175.6067 | 0 | 0
2025-09-17 14:00 | 38.9 | 35.5 | 100 | 28.7583 | 20.3655 | 46.825 | 151.907 | 151.907 | 0 | 0
2025-09-17 15:00 | 37.65 | 40 | 100 | 28.3838 | 20.4907 | 49.1722 | 167.8495 | 167.8495 | 0 | 0
2025-09-17 16:00 | 36.25 | 51 | 100 | 27.9313 | 21.1757 | 55.1866 | 221.864 | 221.864 | 0 | 0
2025-09-17 17:00 | 34.95 | 60 | 100 | 27.5229 | 21.5639 | 59.5639 | 256.4633 | 256.4633 | 0 | 0
2025-09-17 18:00 | 33.6 | 69.5 | 100 | 27.1003 | 21.8792 | 63.7812 | 287.0036 | 287.0036 | 0 | 0
2025-09-17 19:00 | 32.75 | 77.5 | 100 | 26.8282 | 22.1911 | 67.2968 | 314.2218 | 314.2218 | 0 | 0
2025-09-17 20:00 | 32.3 | 81 | 100 | 26.6868 | 22.2788 | 68.6858 | 323.3953 | 323.3953 | 0 | 0
2025-09-17 21:00 | 31.7 | 84.5 | 100 | 26.5011 | 22.2932 | 69.8768 | 328.5934 | 328.5934 | 0 | 0
2025-09-17 22:00 | 31.05 | 88 | 70 | 26.2994 | 22.274 | 70.967 | 232.36 | 232.36 | 0 | 0
2025-09-17 23:00 | 30.4 | 90.5 | 70 | 26.0982 | 22.1728 | 71.5209 | 230.7747 | 230.7747 | 0 | 0
2025-09-18 | 29.7 | 93 | 70 | 25.8795 | 22.0436 | 71.9955 | 228.0985 | 228.0985 | 0 | 0
2025-09-18 01:00 | 29.05 | 95 | 70 | 25.6746 | 21.8952 | 72.2653 | 224.3342 | 224.3342 | 0 | 0
2025-09-18 02:00 | 28.45 | 96.5 | 70 | 25.4838 | 21.7318 | 72.3432 | 219.6159 | 219.6159 | 0 | 0
2025-09-18 03:00 | 28.1 | 96.5 | 70 | 25.3724 | 21.5789 | 71.9917 | 214.1211 | 214.1211 | 0 | 0
2025-09-18 04:00 | 28.1 | 96.5 | 70 | 25.3724 | 21.5786 | 71.99 | 214.1094 | 214.1094 | 0 | 0
2025-09-18 05:00 | 28 | 97 | 70 | 25.3399 | 21.567 | 72.1129 | 214.0694 | 214.0694 | 0 | 0
2025-09-18 06:00 | 28.1 | 95 | 100 | 25.374 | 21.4818 | 71.31 | 299.207 | 299.207 | 0 | 0
2025-09-18 07:00 | 29.75 | 85.5 | 100 | 25.9075 | 21.5445 | 68.4674 | 291.2017 | 291.2017 | 0 | 0
2025-09-18 08:00 | 32.4 | 70.5 | 100 | 26.7462 | 21.4912 | 63.2774 | 268.6172 | 268.6172 | 0 | 0
2025-09-18 09:00 | 34.95 | 55 | 100 | 27.5447 | 21.103 | 56.6618 | 225.2037 | 225.2037 | 0 | 0
2025-09-18 10:00 | 37.35 | 40.5 | 100 | 28.2973 | 20.4533 | 49.3238 | 166.8961 | 166.8961 | 0 | 0
2025-09-18 11:00 | 39.3 | 31.5 | 100 | 28.8974 | 20.0056 | 44.2955 | 126.0012 | 126.0012 | 0 | 0
2025-09-18 12:00 | 40.35 | 29 | 100 | 29.2028 | 19.9875 | 42.9549 | 118.719 | 118.719 | 0 | 0
2025-09-18 13:00 | 40.35 | 28.5 | 100 | 29.2071 | 19.9227 | 42.6097 | 114.6586 | 114.6586 | 0 | 0
2025-09-18 14:00 | 39.5 | 30 | 100 | 28.9636 | 19.8747 | 43.3634 | 116.774 | 116.774 | 0 | 0
2025-09-18 15:00 | 38.2 | 36.5 | 100 | 28.5588 | 20.2679 | 47.1811 | 150.0428 | 150.0428 | 0 | 0
2025-09-18 16:00 | 36.8 | 42 | 100 | 28.134 | 20.4357 | 50.0105 | 169.6806 | 169.6806 | 0 | 0
2025-09-18 17:00 | 35.1 | 47.5 | 100 | 27.6201 | 20.4361 | 52.427 | 180.6471 | 180.6471 | 0 | 0
2025-09-18 18:00 | 33.5 | 57 | 100 | 27.1143 | 20.7621 | 56.8528 | 212.6605 | 212.6605 | 0 | 0
2025-09-18 19:00 | 32.55 | 65.5 | 100 | 26.8051 | 21.1388 | 60.7742 | 244.1339 | 244.1339 | 0 | 0
2025-09-18 20:00 | 31.8 | 72 | 100 | 26.5626 | 21.3737 | 63.5767 | 265.0798 | 265.0798 | 0 | 0
2025-09-18 21:00 | 30.9 | 78 | 100 | 26.2758 | 21.4744 | 65.8518 | 278.2448 | 278.2448 | 0 | 0
2025-09-18 22:00 | 29.9 | 83.5 | 70 | 25.9574 | 21.465 | 67.6558 | 199.3865 | 199.3865 | 0 | 0
2025-09-18 23:00 | 29 | 86.5 | 70 | 25.6707 | 21.2994 | 68.2667 | 196.1395 | 196.1395 | 0 | 0
2025-09-19 | 28.25 | 87.5 | 70 | 25.4303 | 21.0525 | 68.0658 | 188.4016 | 188.4016 | 0 | 0
2025-09-19 01:00 | 27.5 | 90 | 70 | 25.1849 | 20.9009 | 68.5385 | 185.2446 | 185.2446 | 0 | 0
2025-09-19 02:00 | 26.75 | 93.5 | 70 | 24.9359 | 20.8055 | 69.4187 | 184.7382 | 184.7382 | 0 | 0
2025-09-19 03:00 | 26 | 95.5 | 70 | 24.685 | 20.6086 | 69.6235 | 179.5368 | 179.5368 | 0 | 0
2025-09-19 04:00 | 26.1 | 94 | 70 | 24.7192 | 20.5598 | 69.0746 | 176.7295 | 176.7295 | 0 | 0
2025-09-19 05:00 | 26.6 | 90 | 70 | 24.8884 | 20.5229 | 67.7803 | 172.3372 | 172.3372 | 0 | 0
2025-09-19 06:00 | 27.1 | 82.5 | 100 | 25.0596 | 20.2485 | 64.9033 | 224.2581 | 224.2581 | 0 | 0
2025-09-19 07:00 | 29.2 | 69 | 100 | 25.7592 | 20.1378 | 60.1861 | 201.5138 | 201.5138 | 0 | 0
2025-09-19 08:00 | 32.2 | 56 | 100 | 26.726 | 20.2125 | 55.5063 | 185.1479 | 185.1479 | 0 | 0
2025-09-19 09:00 | 34.6 | 47 | 100 | 27.4762 | 20.2227 | 51.8541 | 169.6453 | 169.6453 | 0 | 0
2025-09-19 10:00 | 36.35 | 41 | 100 | 28.0116 | 20.1895 | 49.1576 | 156.1016 | 156.1016 | 0 | 0
2025-09-19 11:00 | 37.45 | 38.5 | 100 | 28.3372 | 20.2651 | 48.1107 | 154.1018 | 154.1018 | 0 | 0
2025-09-19 12:00 | 37.9 | 39.5 | 100 | 28.4564 | 20.5158 | 48.9658 | 167.7137 | 167.7137 | 0 | 0
2025-09-19 13:00 | 38 | 42 | 100 | 28.4677 | 20.8242 | 50.6295 | 187.395 | 187.395 | 0 | 0
2025-09-19 14:00 | 38 | 41 | 100 | 28.4741 | 20.7129 | 49.9922 | 180.2042 | 180.2042 | 0 | 0
2025-09-19 15:00 | 37.55 | 39.5 | 100 | 28.359 | 20.4035 | 48.8115 | 162.8998 | 162.8998 | 0 | 0
2025-09-19 16:00 | 36.25 | 45.5 | 100 | 27.9597 | 20.6206 | 51.8652 | 185.2667 | 185.2667 | 0 | 0
2025-09-19 17:00 | 34.55 | 56.5 | 100 | 27.4231 | 21.096 | 57.2746 | 227.808 | 227.808 | 0 | 0
2025-09-19 18:00 | 33.2 | 65 | 100 | 26.9991 | 21.3447 | 61.0072 | 253.5287 | 253.5287 | 0 | 0
2025-09-19 19:00 | 32.55 | 69 | 100 | 26.7948 | 21.4269 | 62.629 | 263.5106 | 263.5106 | 0 | 0
2025-09-19 20:00 | 32.25 | 70 | 100 | 26.7027 | 21.3907 | 62.9079 | 263.1273 | 263.1273 | 0 | 0
2025-09-19 21:00 | 31.8 | 72 | 100 | 26.5626 | 21.3739 | 63.5779 | 265.0925 | 265.0925 | 0 | 0
2025-09-19 22:00 | 31.2 | 75.5 | 70 | 26.3727 | 21.4061 | 64.8619 | 190.0904 | 190.0904 | 0 | 0
2025-09-19 23:00 | 30.6 | 77.5 | 70 | 26.1849 | 21.3156 | 65.354 | 188.8092 | 188.8092 | 0 | 0
2025-09-20 | 30.1 | 77 | 70 | 26.031 | 21.077 | 64.6984 | 180.1285 | 180.1285 | 0 | 0
2025-09-20 01:00 | 29.8 | 76 | 70 | 25.9388 | 20.8834 | 63.9791 | 172.6248 | 172.6248 | 0 | 0
2025-09-20 02:00 | 29.55 | 75.5 | 70 | 25.8608 | 20.7476 | 63.5479 | 167.574 | 167.574 | 0 | 0
2025-09-20 03:00 | 29.1 | 75 | 70 | 25.7185 | 20.533 | 62.9755 | 159.939 | 159.939 | 0 | 0
2025-09-20 04:00 | 29 | 71.5 | 70 | 25.6913 | 20.2421 | 61.2564 | 147.0509 | 147.0509 | 0 | 0
2025-09-20 05:00 | 29.1 | 69 | 70 | 25.7269 | 20.099 | 60.139 | 139.9537 | 139.9537 | 0 | 0
2025-09-20 06:00 | 29.3 | 69.5 | 100 | 25.7905 | 20.2121 | 60.5 | 205.7973 | 205.7973 | 0 | 0
2025-09-20 07:00 | 30.4 | 68.5 | 100 | 26.1405 | 20.5575 | 60.7505 | 220.5133 | 220.5133 | 0 | 0
2025-09-20 08:00 | 32.35 | 64.5 | 100 | 26.7481 | 20.9811 | 60.0877 | 234.8089 | 234.8089 | 0 | 0
2025-09-20 09:00 | 35.05 | 53 | 100 | 27.5819 | 20.9497 | 55.5772 | 214.4525 | 214.4525 | 0 | 0
2025-09-20 10:00 | 37.5 | 39.5 | 100 | 28.3452 | 20.3907 | 48.7692 | 161.9759 | 161.9759 | 0 | 0
2025-09-20 11:00 | 39.15 | 30 | 100 | 28.8673 | 19.7779 | 43.236 | 112.4827 | 112.4827 | 0 | 0
2025-09-20 12:00 | 40.5 | 23.5 | 100 | 29.2909 | 19.3047 | 39.1373 | 74.6665 | 74.6665 | 0 | 0
2025-09-20 13:00 | 41.4 | 20 | 100 | 29.5687 | 19.0416 | 36.8099 | 53.249 | 53.249 | 0 | 0
2025-09-20 14:00 | 41.35 | 20 | 100 | 29.5551 | 19.0281 | 36.8066 | 52.8581 | 52.8581 | 0 | 0
2025-09-20 15:00 | 39.5 | 33 | 100 | 28.9403 | 20.2423 | 45.4105 | 140.5793 | 140.5793 | 0 | 0
2025-09-20 16:00 | 37.35 | 48 | 100 | 28.2522 | 21.2498 | 54.064 | 219.9001 | 219.9001 | 0 | 0
2025-09-20 17:00 | 36.3 | 55 | 100 | 27.9243 | 21.5867 | 57.6422 | 249.221 | 249.221 | 0 | 0
2025-09-20 18:00 | 36.25 | 53.5 | 100 | 27.9183 | 21.4221 | 56.6998 | 238.4381 | 238.4381 | 0 | 0
2025-09-20 19:00 | 35.55 | 50.5 | 100 | 27.7361 | 20.8828 | 54.4449 | 207.0009 | 207.0009 | 0 | 0
2025-09-20 20:00 | 33.8 | 55.5 | 100 | 27.2082 | 20.7361 | 56.2121 | 208.8569 | 208.8569 | 0 | 0
2025-09-20 21:00 | 32.65 | 60 | 100 | 26.8512 | 20.7142 | 57.9173 | 215.1886 | 215.1886 | 0 | 0
2025-09-20 22:00 | 31.9 | 62 | 70 | 26.6185 | 20.6056 | 58.4771 | 149.2386 | 149.2386 | 0 | 0
2025-09-20 23:00 | 31.3 | 62 | 70 | 26.4341 | 20.3842 | 58.0928 | 141.9937 | 141.9937 | 0 | 0
2025-09-21 | 30.65 | 63 | 70 | 26.2295 | 20.2242 | 58.1939 | 137.885 | 137.885 | 0 | 0
2025-09-21 01:00 | 30.1 | 63 | 70 | 26.056 | 20.0212 | 57.8616 | 131.3769 | 131.3769 | 0 | 0
2025-09-21 02:00 | 29.95 | 62 | 70 | 26.0101 | 19.889 | 57.2853 | 126.1247 | 126.1247 | 0 | 0
2025-09-21 03:00 | 30 | 61.5 | 70 | 26.0269 | 19.8689 | 57.0692 | 124.9481 | 124.9481 | 0 | 0
2025-09-21 04:00 | 29.95 | 61 | 70 | 26.0118 | 19.812 | 56.7952 | 122.6116 | 122.6116 | 0 | 0
2025-09-21 05:00 | 29.7 | 61.5 | 70 | 25.931 | 19.7601 | 56.8977 | 121.4878 | 121.4878 | 0 | 0
2025-09-21 06:00 | 29.5 | 61.5 | 100 | 25.8668 | 19.688 | 56.7849 | 170.2755 | 170.2755 | 0 | 0
2025-09-21 07:00 | 30.6 | 57.5 | 100 | 26.2248 | 19.7695 | 55.4023 | 167.6234 | 167.6234 | 0 | 0
2025-09-21 08:00 | 32.85 | 50 | 100 | 26.9416 | 19.9136 | 52.6438 | 161.2899 | 161.2899 | 0 | 0
2025-09-21 09:00 | 34.9 | 43 | 100 | 27.581 | 19.9312 | 49.6843 | 148.7334 | 148.7334 | 0 | 0
2025-09-21 10:00 | 36.7 | 37.5 | 100 | 28.1303 | 19.9257 | 47.1585 | 136.8202 | 136.8202 | 0 | 0
2025-09-21 11:00 | 38.55 | 32.5 | 100 | 28.6831 | 19.9096 | 44.6846 | 124.3646 | 124.3646 | 0 | 0
2025-09-21 12:00 | 40 | 29 | 100 | 29.1081 | 19.8918 | 42.8324 | 114.5237 | 114.5237 | 0 | 0
2025-09-21 13:00 | 40.4 | 29.5 | 100 | 29.2119 | 20.066 | 43.3235 | 123.448 | 123.448 | 0 | 0
2025-09-21 14:00 | 39.75 | 33 | 100 | 29.0079 | 20.3182 | 45.5021 | 143.6876 | 143.6876 | 0 | 0
2025-09-21 15:00 | 38.65 | 37 | 100 | 28.6793 | 20.4639 | 47.7081 | 159.906 | 159.906 | 0 | 0
2025-09-21 16:00 | 37.4 | 40.5 | 100 | 28.3111 | 20.4665 | 49.3673 | 167.8357 | 167.8357 | 0 | 0
2025-09-21 17:00 | 35.85 | 44.5 | 100 | 27.8505 | 20.3871 | 51.0476 | 172.5213 | 172.5213 | 0 | 0
2025-09-21 18:00 | 34.45 | 53 | 100 | 27.4082 | 20.7372 | 55.2144 | 204.6195 | 204.6195 | 0 | 0
2025-09-21 19:00 | 33.6 | 61.5 | 100 | 27.1283 | 21.1948 | 59.3911 | 240.6672 | 240.6672 | 0 | 0
2025-09-21 20:00 | 33.25 | 64.5 | 100 | 27.0155 | 21.3214 | 60.7639 | 251.4963 | 251.4963 | 0 | 0
2025-09-21 21:00 | 32.9 | 64 | 100 | 26.9138 | 21.1468 | 60.227 | 242.127 | 242.127 | 0 | 0
2025-09-21 22:00 | 32.35 | 60.5 | 70 | 26.7593 | 20.647 | 57.9797 | 148.9007 | 148.9007 | 0 | 0
2025-09-21 23:00 | 31.8 | 57.5 | 70 | 26.5993 | 20.196 | 56.0694 | 130.8778 | 130.8778 | 0 | 0
2025-09-22 | 31.1 | 59.5 | 70 | 26.3776 | 20.1093 | 56.6919 | 130.3374 | 130.3374 | 0 | 0
2025-09-22 01:00 | 30.35 | 67 | 70 | 26.1277 | 20.4237 | 59.9763 | 148.4292 | 148.4292 | 0 | 0
2025-09-22 02:00 | 29.7 | 72.5 | 70 | 25.9132 | 20.5875 | 62.2032 | 159.251 | 159.251 | 0 | 0
2025-09-22 03:00 | 29.05 | 72 | 70 | 25.7067 | 20.2983 | 61.5086 | 149.2178 | 149.2178 | 0 | 0
2025-09-22 04:00 | 28.9 | 68.5 | 70 | 25.6631 | 19.9877 | 59.7635 | 135.7506 | 135.7506 | 0 | 0
2025-09-22 05:00 | 28.95 | 67 | 70 | 25.6813 | 19.8967 | 59.0866 | 131.3618 | 131.3618 | 0 | 0
2025-09-22 06:00 | 29.2 | 67 | 100 | 25.762 | 19.9906 | 59.2344 | 191.8948 | 191.8948 | 0 | 0
2025-09-22 07:00 | 31 | 59.5 | 100 | 26.3464 | 20.0739 | 56.6226 | 184.4273 | 184.4273 | 0 | 0
2025-09-22 08:00 | 33.8 | 47 | 100 | 27.2386 | 19.9582 | 51.4502 | 157.6492 | 157.6492 | 0 | 0
2025-09-22 09:00 | 36.4 | 37.5 | 100 | 28.0441 | 19.8357 | 47.0291 | 132.7438 | 132.7438 | 0 | 0
2025-09-22 10:00 | 38.4 | 32 | 100 | 28.6447 | 19.8097 | 44.2906 | 118.5868 | 118.5868 | 0 | 0
2025-09-22 11:00 | 39.65 | 29 | 100 | 29.0126 | 19.7973 | 42.7041 | 110.2509 | 110.2509 | 0 | 0
2025-09-22 12:00 | 39.75 | 30.5 | 100 | 29.028 | 20.012 | 43.7691 | 123.4954 | 123.4954 | 0 | 0
2025-09-22 13:00 | 38.95 | 33.5 | 100 | 28.7866 | 20.1463 | 45.4983 | 137.048 | 137.048 | 0 | 0
2025-09-22 14:00 | 38.2 | 36.5 | 100 | 28.559 | 20.2712 | 47.1616 | 149.813 | 149.813 | 0 | 0
2025-09-22 15:00 | 37.4 | 40.5 | 100 | 28.3112 | 20.4684 | 49.3525 | 167.664 | 167.664 | 0 | 0
2025-09-22 16:00 | 36.35 | 45 | 100 | 27.9908 | 20.6046 | 51.5976 | 183.2243 | 183.2243 | 0 | 0
2025-09-22 17:00 | 34.9 | 53.5 | 100 | 27.5367 | 20.9443 | 55.77 | 215.0633 | 215.0633 | 0 | 0
2025-09-22 18:00 | 33.45 | 66 | 100 | 27.0691 | 21.5258 | 61.7285 | 263.7914 | 263.7914 | 0 | 0
2025-09-22 19:00 | 32.55 | 76 | 100 | 26.7745 | 21.9909 | 66.3011 | 301.6583 | 301.6583 | 0 | 0
2025-09-22 20:00 | 31.95 | 80.5 | 100 | 26.5855 | 22.0954 | 68.0685 | 313.0193 | 313.0193 | 0 | 0
2025-09-22 21:00 | 31.35 | 84 | 100 | 26.3984 | 22.1081 | 69.2574 | 318.1674 | 318.1674 | 0 | 0
2025-09-22 22:00 | 30.75 | 86.5 | 70 | 26.2125 | 22.0378 | 69.9046 | 222.3322 | 222.3322 | 0 | 0
2025-09-22 23:00 | 30.1 | 88 | 70 | 26.0114 | 21.8681 | 69.9925 | 217.4929 | 217.4929 | 0 | 0
2025-09-23 | 29.45 | 90 | 70 | 25.807 | 21.7298 | 70.3098 | 214.1964 | 214.1964 | 0 | 0
2025-09-23 01:00 | 28.9 | 93 | 70 | 25.6304 | 21.6966 | 71.1722 | 215.4615 | 215.4615 | 0 | 0
2025-09-23 02:00 | 28.4 | 96.5 | 70 | 25.468 | 21.71 | 72.2771 | 218.7207 | 218.7207 | 0 | 0
2025-09-23 03:00 | 28.05 | 99 | 70 | 25.3538 | 21.7168 | 73.0478 | 220.9105 | 220.9105 | 0 | 0
2025-09-23 04:00 | 28.2 | 95 | 70 | 25.4061 | 21.5253 | 71.3969 | 210.9161 | 210.9161 | 0 | 0
2025-09-23 05:00 | 28.15 | 93 | 70 | 25.3923 | 21.373 | 70.4429 | 203.9229 | 203.9229 | 0 | 0
2025-09-23 06:00 | 28.05 | 96 | 100 | 25.3571 | 21.5243 | 71.6928 | 302.3293 | 302.3293 | 0 | 0
2025-09-23 07:00 | 29.3 | 89 | 100 | 25.7618 | 21.5972 | 69.6838 | 297.9318 | 297.9318 | 0 | 0
2025-09-23 08:00 | 31.1 | 76 | 100 | 26.3414 | 21.4055 | 64.9932 | 271.7617 | 271.7617 | 0 | 0
2025-09-23 09:00 | 32.8 | 65 | 100 | 26.8814 | 21.1949 | 60.6587 | 245.5936 | 245.5936 | 0 | 0
2025-09-23 10:00 | 34.65 | 55 | 100 | 27.4586 | 20.9974 | 56.4443 | 219.8627 | 219.8627 | 0 | 0
2025-09-23 11:00 | 36.3 | 47 | 100 | 27.9665 | 20.7948 | 52.7637 | 195.6552 | 195.6552 | 0 | 0
2025-09-23 12:00 | 37.25 | 44.5 | 100 | 28.2459 | 20.8518 | 51.7731 | 193.4475 | 193.4475 | 0 | 0
2025-09-23 13:00 | 37.5 | 44.5 | 100 | 28.3149 | 20.9337 | 51.9232 | 197.4102 | 197.4102 | 0 | 0
2025-09-23 14:00 | 37.3 | 43 | 100 | 28.2685 | 20.7069 | 50.8735 | 183.8445 | 183.8445 | 0 | 0
2025-09-23 15:00 | 36.45 | 45.5 | 100 | 28.0164 | 20.6888 | 51.9606 | 188.1747 | 188.1747 | 0 | 0
2025-09-23 16:00 | 35.2 | 51.5 | 100 | 27.6315 | 20.8587 | 54.8055 | 207.5388 | 207.5388 | 0 | 0
2025-09-23 17:00 | 33.8 | 58 | 100 | 27.1993 | 20.9607 | 57.5941 | 223.6189 | 223.6189 | 0 | 0
2025-09-23 18:00 | 32.4 | 66.5 | 100 | 26.7574 | 21.1649 | 61.1835 | 246.798 | 246.798 | 0 | 0
2025-09-23 19:00 | 31.6 | 74.5 | 100 | 26.4962 | 21.4901 | 64.6851 | 274.267 | 274.267 | 0 | 0
2025-09-23 20:00 | 31.25 | 80 | 100 | 26.3776 | 21.7678 | 67.1569 | 295.5952 | 295.5952 | 0 | 0
2025-09-23 21:00 | 30.75 | 84 | 100 | 26.2176 | 21.8561 | 68.6764 | 305.1939 | 305.1939 | 0 | 0
2025-09-23 22:00 | 30.25 | 87 | 70 | 26.0592 | 21.861 | 69.6596 | 216.4142 | 216.4142 | 0 | 0
2025-09-23 23:00 | 29.8 | 89.5 | 70 | 25.9163 | 21.8455 | 70.4226 | 217.9673 | 217.9673 | 0 | 0
2025-09-24 | 29.15 | 93 | 70 | 25.7088 | 21.8048 | 71.4301 | 219.4139 | 219.4139 | 0 | 0
2025-09-24 01:00 | 28.6 | 95.5 | 70 | 25.5325 | 21.732 | 72.0353 | 218.8124 | 218.8124 | 0 | 0
2025-09-24 02:00 | 28.25 | 95.5 | 70 | 25.4214 | 21.5795 | 71.6891 | 213.3627 | 213.3627 | 0 | 0
2025-09-24 03:00 | 27.95 | 94.5 | 70 | 25.3264 | 21.3847 | 70.9496 | 205.6608 | 205.6608 | 0 | 0
2025-09-24 04:00 | 27.95 | 95.5 | 70 | 25.3254 | 21.4486 | 71.3948 | 208.7113 | 208.7113 | 0 | 0
2025-09-24 05:00 | 27.9 | 96.5 | 70 | 25.3083 | 21.4914 | 71.7888 | 210.9692 | 210.9692 | 0 | 0
2025-09-24 06:00 | 27.8 | 95 | 100 | 25.2776 | 21.3515 | 71.0209 | 292.6218 | 292.6218 | 0 | 0
2025-09-24 07:00 | 29.3 | 87 | 100 | 25.7646 | 21.4599 | 68.7625 | 288.7517 | 288.7517 | 0 | 0
2025-09-24 08:00 | 32.65 | 70.5 | 100 | 26.8202 | 21.589 | 63.4861 | 273.5391 | 273.5391 | 0 | 0
2025-09-24 09:00 | 35.5 | 55.5 | 100 | 27.6989 | 21.3481 | 57.3331 | 237.9432 | 237.9432 | 0 | 0
2025-09-24 10:00 | 36.75 | 47.5 | 100 | 28.0898 | 20.9961 | 53.3505 | 206.3659 | 206.3659 | 0 | 0
2025-09-24 11:00 | 37.4 | 42.5 | 100 | 28.2993 | 20.6856 | 50.6125 | 181.821 | 181.821 | 0 | 0
2025-09-24 12:00 | 37.95 | 36 | 100 | 28.4926 | 20.1371 | 46.7386 | 142.8601 | 142.8601 | 0 | 0
2025-09-24 13:00 | 37.75 | 33 | 100 | 28.4553 | 19.7326 | 44.7405 | 118.3815 | 118.3815 | 0 | 0
2025-09-24 14:00 | 36.8 | 35.5 | 100 | 28.1698 | 19.7336 | 45.9827 | 124.4534 | 124.4534 | 0 | 0
2025-09-24 15:00 | 35.75 | 38.5 | 100 | 27.8503 | 19.7362 | 47.4156 | 131.3564 | 131.3564 | 0 | 0
2025-09-24 16:00 | 34.45 | 44 | 100 | 27.4436 | 19.8802 | 50.0888 | 149.0037 | 149.0037 | 0 | 0
2025-09-24 17:00 | 33.1 | 51 | 100 | 27.0143 | 20.0853 | 53.3412 | 171.1972 | 171.1972 | 0 | 0
2025-09-24 18:00 | 32.2 | 55 | 100 | 26.7286 | 20.1249 | 55.0022 | 179.8423 | 179.8423 | 0 | 0
2025-09-24 19:00 | 31.65 | 56.5 | 100 | 26.5554 | 20.0575 | 55.4806 | 179.2637 | 179.2637 | 0 | 0
2025-09-24 20:00 | 31.2 | 58.5 | 100 | 26.4109 | 20.0625 | 56.2539 | 182.6893 | 182.6893 | 0 | 0
2025-09-24 21:00 | 30.75 | 61 | 100 | 26.2649 | 20.1018 | 57.2561 | 188.3652 | 188.3652 | 0 | 0
2025-09-24 22:00 | 30.2 | 63 | 70 | 26.0877 | 20.058 | 57.9239 | 132.5739 | 132.5739 | 0 | 0
2025-09-24 23:00 | 29.55 | 65.5 | 70 | 25.8766 | 20.0083 | 58.7521 | 133.5847 | 133.5847 | 0 | 0
2025-09-25 | 29 | 68.5 | 70 | 25.6954 | 20.0241 | 59.8457 | 137.1093 | 137.1093 | 0 | 0
2025-09-25 01:00 | 28.65 | 72 | 70 | 25.5777 | 20.1436 | 61.2608 | 144.3246 | 144.3246 | 0 | 0
2025-09-25 02:00 | 28.4 | 75 | 70 | 25.493 | 20.2576 | 62.4806 | 150.867 | 150.867 | 0 | 0
2025-09-25 03:00 | 28.2 | 76.5 | 70 | 25.4263 | 20.2842 | 63.0285 | 153.0741 | 153.0741 | 0 | 0
2025-09-25 04:00 | 28.2 | 72 | 70 | 25.4312 | 19.9701 | 60.966 | 138.7083 | 138.7083 | 0 | 0
2025-09-25 05:00 | 28.1 | 68 | 70 | 25.4027 | 19.6499 | 59.0688 | 124.6817 | 124.6817 | 0 | 0
2025-09-25 06:00 | 28.1 | 68 | 100 | 25.4027 | 19.6501 | 59.0636 | 178.0638 | 178.0638 | 0 | 0
2025-09-25 07:00 | 29.4 | 63.5 | 100 | 25.8315 | 19.803 | 57.6925 | 178.4404 | 178.4404 | 0 | 0
2025-09-25 08:00 | 31.35 | 59.5 | 100 | 26.4554 | 20.1994 | 56.8368 | 190.3147 | 190.3147 | 0 | 0
2025-09-25 09:00 | 32.9 | 57 | 100 | 26.9354 | 20.5475 | 56.4601 | 202.3679 | 202.3679 | 0 | 0
2025-09-25 10:00 | 34.3 | 51.5 | 100 | 27.3702 | 20.5459 | 54.2637 | 192.8804 | 192.8804 | 0 | 0
2025-09-25 11:00 | 35.8 | 43 | 100 | 27.8434 | 20.219 | 50.1185 | 161.7887 | 161.7887 | 0 | 0
2025-09-25 12:00 | 37.4 | 33.5 | 100 | 28.3529 | 19.6879 | 44.9389 | 117.7155 | 117.7155 | 0 | 0
2025-09-25 13:00 | 38.45 | 28 | 100 | 28.6857 | 19.3368 | 41.7136 | 89.2321 | 89.2321 | 0 | 0
2025-09-25 14:00 | 37.45 | 37.5 | 100 | 28.3431 | 20.1502 | 47.5032 | 147.2453 | 147.2453 | 0 | 0
2025-09-25 15:00 | 35.65 | 48.5 | 100 | 27.774 | 20.7194 | 53.3313 | 195.775 | 195.775 | 0 | 0
2025-09-25 16:00 | 34.7 | 51 | 100 | 27.489 | 20.6356 | 54.2306 | 196.4327 | 196.4327 | 0 | 0
2025-09-25 17:00 | 33.6 | 55.5 | 100 | 27.149 | 20.6639 | 56.0938 | 205.5796 | 205.5796 | 0 | 0
2025-09-25 18:00 | 32.7 | 60.5 | 100 | 26.8646 | 20.7749 | 58.2252 | 218.9556 | 218.9556 | 0 | 0
2025-09-25 19:00 | 32.25 | 64.5 | 100 | 26.7179 | 20.9424 | 60.0283 | 233.1217 | 233.1217 | 0 | 0
2025-09-25 20:00 | 31.75 | 68 | 100 | 26.5576 | 21.0369 | 61.477 | 242.7997 | 242.7997 | 0 | 0
2025-09-25 21:00 | 31.2 | 71.5 | 100 | 26.3818 | 21.0989 | 62.8375 | 250.7809 | 250.7809 | 0 | 0
2025-09-25 22:00 | 30.55 | 74.5 | 70 | 26.1755 | 21.0715 | 63.8224 | 177.4918 | 177.4918 | 0 | 0
2025-09-25 23:00 | 29.95 | 77 | 70 | 25.9843 | 21.0169 | 64.5642 | 177.9687 | 177.9687 | 0 | 0
2025-09-26 | 29.4 | 79.5 | 70 | 25.8073 | 20.9752 | 65.3164 | 178.8163 | 178.8163 | 0 | 0
2025-09-26 01:00 | 28.7 | 82.5 | 70 | 25.5806 | 20.8998 | 66.1492 | 178.8833 | 178.8833 | 0 | 0
2025-09-26 02:00 | 27.85 | 85.5 | 70 | 25.3031 | 20.7528 | 66.8192 | 176.4187 | 176.4187 | 0 | 0
2025-09-26 03:00 | 27.1 | 86.5 | 70 | 25.0565 | 20.5082 | 66.6574 | 168.9709 | 168.9709 | 0 | 0
2025-09-26 04:00 | 26.95 | 82.5 | 70 | 25.0098 | 20.1877 | 64.79 | 154.9567 | 154.9567 | 0 | 0
2025-09-26 05:00 | 26.85 | 80 | 70 | 24.9782 | 19.9851 | 63.6219 | 146.1462 | 146.1462 | 0 | 0
2025-09-26 06:00 | 26.9 | 80 | 100 | 24.9949 | 20.005 | 63.6502 | 209.6431 | 209.6431 | 0 | 0
2025-09-26 07:00 | 28.4 | 73.5 | 100 | 25.4949 | 20.1545 | 61.7501 | 208.2281 | 208.2281 | 0 | 0
2025-09-26 08:00 | 30.8 | 62 | 100 | 26.2787 | 20.2025 | 57.7542 | 194.031 | 194.031 | 0 | 0
2025-09-26 09:00 | 32.9 | 53 | 100 | 26.9478 | 20.1987 | 54.2804 | 179.2183 | 179.2183 | 0 | 0
2025-09-26 10:00 | 34.65 | 47.5 | 100 | 27.4889 | 20.2888 | 52.1543 | 173.3848 | 173.3848 | 0 | 0
2025-09-26 11:00 | 36.35 | 41.5 | 100 | 28.009 | 20.2428 | 49.4543 | 159.4055 | 159.4055 | 0 | 0
2025-09-26 12:00 | 37.8 | 36 | 100 | 28.4507 | 20.0936 | 46.6655 | 140.7429 | 140.7429 | 0 | 0
2025-09-26 13:00 | 38.15 | 37.5 | 100 | 28.5385 | 20.3692 | 47.7905 | 156.5487 | 156.5487 | 0 | 0
2025-09-26 14:00 | 37.3 | 44 | 100 | 28.2625 | 20.8126 | 51.5069 | 190.9341 | 190.9341 | 0 | 0
2025-09-26 15:00 | 36.15 | 48.5 | 100 | 27.9162 | 20.8923 | 53.6065 | 203.5415 | 203.5415 | 0 | 0
2025-09-26 16:00 | 35.1 | 53 | 100 | 27.5963 | 20.9672 | 55.612 | 215.3224 | 215.3224 | 0 | 0
2025-09-26 17:00 | 33.85 | 59 | 100 | 27.2104 | 21.0685 | 58.1782 | 230.3583 | 230.3583 | 0 | 0
2025-09-26 18:00 | 32.8 | 64.5 | 100 | 26.8827 | 21.1512 | 60.4145 | 243.0328 | 243.0328 | 0 | 0
2025-09-26 19:00 | 32.4 | 67 | 100 | 26.7561 | 21.2058 | 61.4339 | 249.4111 | 249.4111 | 0 | 0
2025-09-26 20:00 | 32.25 | 66.5 | 100 | 26.7126 | 21.1082 | 61.0523 | 243.8077 | 243.8077 | 0 | 0
2025-09-26 21:00 | 31.85 | 67 | 100 | 26.5906 | 20.9961 | 61.0127 | 239.0655 | 239.0655 | 0 | 0
2025-09-26 22:00 | 31.1 | 69 | 70 | 26.3568 | 20.8665 | 61.4806 | 164.9964 | 164.9964 | 0 | 0
2025-09-26 23:00 | 30.45 | 69.5 | 70 | 26.1543 | 20.6547 | 61.2609 | 158.3974 | 158.3974 | 0 | 0
2025-09-27 | 29.95 | 69 | 70 | 25.9982 | 20.4246 | 60.67 | 150.3054 | 150.3054 | 0 | 0
2025-09-27 01:00 | 29.45 | 69.5 | 70 | 25.8385 | 20.2707 | 60.5761 | 145.7594 | 145.7594 | 0 | 0
2025-09-27 02:00 | 28.85 | 72 | 70 | 25.6424 | 20.222 | 61.3589 | 146.5844 | 146.5844 | 0 | 0
2025-09-27 03:00 | 28.2 | 76 | 70 | 25.427 | 20.2503 | 62.7628 | 151.2188 | 151.2188 | 0 | 0
2025-09-27 04:00 | 28.4 | 74 | 70 | 25.4943 | 20.1893 | 61.9809 | 147.3714 | 147.3714 | 0 | 0
2025-09-27 05:00 | 28.65 | 69 | 70 | 25.5815 | 19.9303 | 59.8223 | 134.2206 | 134.2206 | 0 | 0
2025-09-27 06:00 | 28.75 | 64 | 100 | 25.6203 | 19.6042 | 57.5379 | 169.8563 | 169.8563 | 0 | 0
2025-09-27 07:00 | 30.5 | 55 | 100 | 26.198 | 19.5351 | 54.0761 | 152.858 | 152.858 | 0 | 0
2025-09-27 08:00 | 32.65 | 47.5 | 100 | 26.8879 | 19.6258 | 51.1761 | 143.6761 | 143.6761 | 0 | 0
2025-09-27 09:00 | 34.55 | 42 | 100 | 27.4814 | 19.7246 | 48.9305 | 137.2444 | 137.2444 | 0 | 0
2025-09-27 10:00 | 36.85 | 35.5 | 100 | 28.1843 | 19.7572 | 45.9509 | 124.5006 | 124.5006 | 0 | 0
2025-09-27 11:00 | 38.8 | 29.5 | 100 | 28.7737 | 19.6257 | 42.7586 | 104.1163 | 104.1163 | 0 | 0
2025-09-27 12:00 | 40.2 | 25.5 | 100 | 29.1917 | 19.4989 | 40.4384 | 87.8473 | 87.8473 | 0 | 0
2025-09-27 13:00 | 41 | 23 | 100 | 29.4317 | 19.3694 | 38.8701 | 75.1522 | 75.1522 | 0 | 0
2025-09-27 14:00 | 40.4 | 27.5 | 100 | 29.2292 | 19.8113 | 41.9044 | 106.7183 | 106.7183 | 0 | 0
2025-09-27 15:00 | 38.6 | 36.5 | 100 | 28.6693 | 20.3946 | 47.3312 | 155.1591 | 155.1591 | 0 | 0
2025-09-27 16:00 | 36.95 | 42.5 | 100 | 28.1737 | 20.5411 | 50.3665 | 175.003 | 175.003 | 0 | 0
2025-09-27 17:00 | 35.35 | 52 | 100 | 27.6725 | 20.9611 | 55.1725 | 212.9898 | 212.9898 | 0 | 0
2025-09-27 18:00 | 34.05 | 60.5 | 100 | 27.2633 | 21.2762 | 59.1404 | 242.6715 | 242.6715 | 0 | 0
2025-09-27 19:00 | 33.6 | 61 | 100 | 27.1303 | 21.1537 | 59.0853 | 237.4193 | 237.4193 | 0 | 0
2025-09-27 20:00 | 33.35 | 59 | 100 | 27.0635 | 20.8873 | 57.8094 | 221.288 | 221.288 | 0 | 0
2025-09-27 21:00 | 32.8 | 58.5 | 100 | 26.901 | 20.6437 | 57.1751 | 208.9012 | 208.9012 | 0 | 0
2025-09-27 22:00 | 32 | 59 | 70 | 26.657 | 20.3958 | 56.9394 | 138.7022 | 138.7022 | 0 | 0
2025-09-27 23:00 | 31.25 | 60 | 70 | 26.4233 | 20.2065 | 57.0041 | 133.7008 | 133.7008 | 0 | 0
2025-09-28 | 30.5 | 62.5 | 70 | 26.1835 | 20.1322 | 57.8148 | 134.0243 | 134.0243 | 0 | 0
2025-09-28 01:00 | 29.65 | 65.5 | 70 | 25.9087 | 20.0485 | 58.7696 | 134.4614 | 134.4614 | 0 | 0
2025-09-28 02:00 | 28.9 | 69.5 | 70 | 25.6619 | 20.0614 | 60.2064 | 138.8663 | 138.8663 | 0 | 0
2025-09-28 03:00 | 28.3 | 75.5 | 70 | 25.4601 | 20.2555 | 62.5917 | 150.8298 | 150.8298 | 0 | 0
2025-09-28 04:00 | 28.05 | 78.5 | 70 | 25.3755 | 20.3639 | 63.7815 | 157.076 | 157.076 | 0 | 0
2025-09-28 05:00 | 27.8 | 78 | 70 | 25.2942 | 20.2304 | 63.371 | 152.1947 | 152.1947 | 0 | 0
2025-09-28 06:00 | 27.95 | 67 | 100 | 25.3544 | 19.5263 | 58.4752 | 170.5265 | 170.5265 | 0 | 0
2025-09-28 07:00 | 29.7 | 50 | 100 | 25.9495 | 18.8631 | 51.2614 | 115.7336 | 115.7336 | 0 | 0
2025-09-28 08:00 | 32.05 | 45.5 | 100 | 26.7076 | 19.2522 | 49.8572 | 123.8793 | 123.8793 | 0 | 0
2025-09-28 09:00 | 34.3 | 44 | 100 | 27.3992 | 19.8393 | 49.9647 | 146.2327 | 146.2327 | 0 | 0
2025-09-28 10:00 | 36.55 | 37 | 100 | 28.09 | 19.8306 | 46.7628 | 131.0554 | 131.0554 | 0 | 0
2025-09-28 11:00 | 38.35 | 30 | 100 | 28.6441 | 19.561 | 42.9488 | 102.701 | 102.701 | 0 | 0
2025-09-28 12:00 | 39.25 | 28 | 100 | 28.9099 | 19.5638 | 41.8919 | 97.5968 | 97.5968 | 0 | 0
2025-09-28 13:00 | 39.15 | 29.5 | 100 | 28.871 | 19.7206 | 42.8785 | 108.3131 | 108.3131 | 0 | 0
2025-09-28 14:00 | 38.7 | 28.5 | 100 | 28.7527 | 19.4731 | 42.0795 | 95.4431 | 95.4431 | 0 | 0
2025-09-28 15:00 | 37.7 | 31.5 | 100 | 28.4504 | 19.5502 | 43.7387 | 106.496 | 106.496 | 0 | 0
2025-09-28 16:00 | 35.95 | 43 | 100 | 27.8868 | 20.2698 | 50.172 | 163.7474 | 163.7474 | 0 | 0
2025-09-28 17:00 | 34.15 | 57 | 100 | 27.3055 | 20.9992 | 57.2555 | 223.556 | 223.556 | 0 | 0
2025-09-28 18:00 | 32.9 | 66 | 100 | 26.9078 | 21.3153 | 61.2839 | 253.2265 | 253.2265 | 0 | 0
2025-09-28 19:00 | 32.2 | 68.5 | 100 | 26.6922 | 21.2518 | 62.0604 | 253.7659 | 253.7659 | 0 | 0
2025-09-28 20:00 | 31.4 | 71 | 100 | 26.4441 | 21.1392 | 62.7206 | 251.7978 | 251.7978 | 0 | 0
2025-09-28 21:00 | 30.5 | 74.5 | 100 | 26.1602 | 21.0518 | 63.7623 | 252.3773 | 252.3773 | 0 | 0
2025-09-28 22:00 | 29.8 | 77.5 | 70 | 25.9366 | 20.9935 | 64.6653 | 177.4722 | 177.4722 | 0 | 0
2025-09-28 23:00 | 29.25 | 82.5 | 70 | 25.7556 | 21.1258 | 66.5906 | 186.5207 | 186.5207 | 0 | 0
2025-09-29 | 28.5 | 88.5 | 70 | 25.5094 | 21.2249 | 68.7208 | 195.0532 | 195.0532 | 0 | 0
2025-09-29 01:00 | 27.45 | 92 | 70 | 25.167 | 21.0092 | 69.3566 | 190.4033 | 190.4033 | 0 | 0
2025-09-29 02:00 | 26.55 | 94.5 | 70 | 24.8691 | 20.7822 | 69.6523 | 184.564 | 184.564 | 0 | 0
2025-09-29 03:00 | 26.2 | 96.5 | 70 | 24.7515 | 20.7551 | 70.1981 | 185.1582 | 185.1582 | 0 | 0
2025-09-29 04:00 | 26.45 | 96.5 | 70 | 24.8347 | 20.8629 | 70.4192 | 188.8578 | 188.8578 | 0 | 0
2025-09-29 05:00 | 26.7 | 95.5 | 70 | 24.9182 | 20.9084 | 70.2123 | 189.6675 | 189.6675 | 0 | 0
2025-09-29 06:00 | 27.2 | 93.5 | 100 | 25.0841 | 20.9976 | 69.7919 | 273.1397 | 273.1397 | 0 | 0
2025-09-29 07:00 | 29.15 | 85 | 100 | 25.7204 | 21.2589 | 67.6809 | 276.1604 | 276.1604 | 0 | 0
2025-09-29 08:00 | 32.5 | 68.5 | 100 | 26.7817 | 21.368 | 62.3 | 259.5325 | 259.5325 | 0 | 0
2025-09-29 09:00 | 35.8 | 49 | 100 | 27.8147 | 20.8246 | 53.6797 | 201.0153 | 201.0153 | 0 | 0
2025-09-29 10:00 | 37.55 | 37.5 | 100 | 28.3714 | 20.1869 | 47.5118 | 148.1951 | 148.1951 | 0 | 0
2025-09-29 11:00 | 37.9 | 36.5 | 100 | 28.4756 | 20.1806 | 47.0255 | 145.6922 | 145.6922 | 0 | 0
2025-09-29 12:00 | 37.7 | 39 | 100 | 28.4041 | 20.3988 | 48.5417 | 161.16 | 161.16 | 0 | 0
2025-09-29 13:00 | 37.25 | 43 | 100 | 28.2546 | 20.6897 | 50.8513 | 183.1442 | 183.1442 | 0 | 0
2025-09-29 14:00 | 36.65 | 46.5 | 100 | 28.0672 | 20.858 | 52.6916 | 198.136 | 198.136 | 0 | 0
2025-09-29 15:00 | 35.8 | 50.5 | 100 | 27.8072 | 20.9696 | 54.5968 | 211.0696 | 211.0696 | 0 | 0
2025-09-29 16:00 | 34.7 | 56 | 100 | 27.4685 | 21.1047 | 57.0858 | 227.2832 | 227.2832 | 0 | 0
2025-09-29 17:00 | 33.3 | 65 | 100 | 27.0285 | 21.3832 | 61.0803 | 255.3624 | 255.3624 | 0 | 0
2025-09-29 18:00 | 32.1 | 72.5 | 100 | 26.6511 | 21.5317 | 64.0913 | 273.741 | 273.741 | 0 | 0
2025-09-29 19:00 | 31.4 | 75.5 | 100 | 26.4333 | 21.4863 | 65.034 | 275.5914 | 275.5914 | 0 | 0
2025-09-29 20:00 | 30.85 | 77.5 | 100 | 26.2616 | 21.4168 | 65.5642 | 274.7387 | 274.7387 | 0 | 0
2025-09-29 21:00 | 30.25 | 80 | 100 | 26.0721 | 21.3569 | 66.274 | 275.0104 | 275.0104 | 0 | 0
2025-09-29 22:00 | 29.55 | 83.5 | 70 | 25.8483 | 21.3199 | 67.3452 | 194.2998 | 194.2998 | 0 | 0
2025-09-29 23:00 | 28.85 | 87 | 70 | 25.6226 | 21.2705 | 68.3656 | 195.5613 | 195.5613 | 0 | 0
2025-09-30 | 28.15 | 90.5 | 70 | 25.3949 | 21.2091 | 69.3367 | 196.3133 | 196.3133 | 0 | 0
2025-09-30 01:00 | 27.4 | 93 | 70 | 25.1497 | 21.0515 | 69.7763 | 192.8378 | 192.8378 | 0 | 0
2025-09-30 02:00 | 26.8 | 94.5 | 70 | 24.9518 | 20.8895 | 69.8962 | 188.4106 | 188.4106 | 0 | 0
2025-09-30 03:00 | 26.45 | 95.5 | 70 | 24.8352 | 20.8014 | 70.0175 | 186.154 | 186.154 | 0 | 0
2025-09-30 04:00 | 26.35 | 94.5 | 70 | 24.8025 | 20.6969 | 69.5031 | 181.8067 | 181.8067 | 0 | 0
2025-09-30 05:00 | 26.2 | 94 | 70 | 24.7527 | 20.6022 | 69.1602 | 178.1817 | 178.1817 | 0 | 0
2025-09-30 06:00 | 26.3 | 93.5 | 100 | 24.7864 | 20.6141 | 69.03 | 254.5422 | 254.5422 | 0 | 0
2025-09-30 07:00 | 28.1 | 84.5 | 100 | 25.3852 | 20.7888 | 66.5768 | 252.6389 | 252.6389 | 0 | 0
2025-09-30 08:00 | 30.65 | 74 | 100 | 26.2074 | 21.0727 | 63.6576 | 253.0111 | 253.0111 | 0 | 0
2025-09-30 09:00 | 32.7 | 64.5 | 100 | 26.8528 | 21.1132 | 60.3492 | 241.2833 | 241.2833 | 0 | 0
2025-09-30 10:00 | 34.9 | 51.5 | 100 | 27.545 | 20.7539 | 54.6265 | 202.6723 | 202.6723 | 0 | 0
2025-09-30 11:00 | 37.25 | 39 | 100 | 28.278 | 20.2555 | 48.3525 | 155.0836 | 155.0836 | 0 | 0
2025-09-30 12:00 | 38.8 | 32.5 | 100 | 28.7523 | 19.978 | 44.8008 | 127.7748 | 127.7748 | 0 | 0
2025-09-30 13:00 | 39.05 | 30 | 100 | 28.8396 | 19.7453 | 43.2252 | 111.5667 | 111.5667 | 0 | 0
2025-09-30 14:00 | 38.35 | 29.5 | 100 | 28.6474 | 19.4883 | 42.6807 | 99.6342 | 99.6342 | 0 | 0
2025-09-30 15:00 | 37.3 | 36 | 100 | 28.3096 | 19.9366 | 46.5013 | 134.6145 | 134.6145 | 0 | 0
2025-09-30 16:00 | 35.85 | 46 | 100 | 27.8431 | 20.5361 | 51.9646 | 182.6432 | 182.6432 | 0 | 0
2025-09-30 17:00 | 33.95 | 58.5 | 100 | 27.2411 | 21.0577 | 58.0035 | 229.5254 | 229.5254 | 0 | 0
2025-09-30 18:00 | 32.7 | 68.5 | 100 | 26.8406 | 21.4434 | 62.5022 | 263.8236 | 263.8236 | 0 | 0
2025-09-30 19:00 | 32.05 | 73.5 | 100 | 26.6333 | 21.5911 | 64.5815 | 278.2546 | 278.2546 | 0 | 0
2025-09-30 20:00 | 31.25 | 79 | 100 | 26.3796 | 21.6922 | 66.6828 | 290.7554 | 290.7554 | 0 | 0
2025-09-30 21:00 | 30.4 | 84 | 100 | 26.1106 | 21.7088 | 68.3749 | 298.0049 | 298.0049 | 0 | 0
2025-09-30 22:00 | 29.6 | 88 | 70 | 25.8566 | 21.6558 | 69.5422 | 210.1109 | 210.1109 | 0 | 0
2025-09-30 23:00 | 29.05 | 90.5 | 70 | 25.6808 | 21.593 | 70.1931 | 209.9644 | 209.9644 | 0 | 0
2025-10-01 | 28.55 | 92.5 | 70 | 25.5202 | 21.5123 | 70.6392 | 208.7474 | 208.7474 | 0 | 0
2025-10-01 01:00 | 27.65 | 95.5 | 70 | 25.2286 | 21.3192 | 71.1313 | 204.2764 | 204.2764 | 0 | 0
2025-10-01 02:00 | 26.9 | 98 | 70 | 24.9822 | 21.1499 | 71.5158 | 200.2608 | 200.2608 | 0 | 0
2025-10-01 03:00 | 26.85 | 99.5 | 70 | 24.9647 | 21.2208 | 72.1172 | 203.8813 | 203.8813 | 0 | 0
2025-10-01 04:00 | 26.9 | 100 | 70 | 24.9808 | 21.2736 | 72.3818 | 206.1175 | 206.1175 | 0 | 0
2025-10-01 05:00 | 27.05 | 100 | 70 | 25.0298 | 21.3397 | 72.5254 | 208.4317 | 208.4317 | 0 | 0
2025-10-01 06:00 | 27.5 | 100 | 100 | 25.176 | 21.5382 | 72.9667 | 307.7912 | 307.7912 | 0 | 0
2025-10-01 07:00 | 27.95 | 98.5 | 100 | 25.3222 | 21.6412 | 72.7513 | 311.4223 | 311.4223 | 0 | 0
2025-10-01 08:00 | 28.95 | 93 | 100 | 25.646 | 21.7183 | 71.2485 | 309.1765 | 309.1765 | 0 | 0
2025-10-01 09:00 | 31.35 | 81 | 100 | 26.4051 | 21.8839 | 67.7758 | 303.0705 | 303.0705 | 0 | 0
2025-10-01 10:00 | 34.3 | 64.5 | 100 | 27.3195 | 21.7216 | 61.6082 | 271.54 | 271.54 | 0 | 0
2025-10-01 11:00 | 36.6 | 50.5 | 100 | 28.0313 | 21.247 | 55.1215 | 224.5059 | 224.5059 | 0 | 0
2025-10-01 12:00 | 37.8 | 44.5 | 100 | 28.3968 | 21.0294 | 52.1314 | 202.4826 | 202.4826 | 0 | 0
2025-10-01 13:00 | 37.6 | 46.5 | 100 | 28.3296 | 21.176 | 53.2835 | 213.5346 | 213.5346 | 0 | 0
2025-10-01 14:00 | 36.7 | 51 | 100 | 28.0561 | 21.3313 | 55.5055 | 229.6911 | 229.6911 | 0 | 0
2025-10-01 15:00 | 36.1 | 53.5 | 100 | 27.8763 | 21.3667 | 56.612 | 236.0153 | 236.0153 | 0 | 0
2025-10-01 16:00 | 35.4 | 56.5 | 100 | 27.6655 | 21.4028 | 57.8919 | 243.0028 | 243.0028 | 0 | 0
2025-10-01 17:00 | 34 | 63 | 100 | 27.2389 | 21.4744 | 60.5496 | 257.1457 | 257.1457 | 0 | 0
2025-10-01 18:00 | 32.6 | 69.5 | 100 | 26.8079 | 21.4863 | 62.9564 | 267.472 | 267.472 | 0 | 0
2025-10-01 19:00 | 31.8 | 73.5 | 100 | 26.5585 | 21.4908 | 64.373 | 273.3018 | 273.3018 | 0 | 0
2025-10-01 20:00 | 31.3 | 77.5 | 100 | 26.3982 | 21.5982 | 65.9749 | 284.0935 | 284.0935 | 0 | 0
2025-10-01 21:00 | 30.55 | 80.5 | 100 | 26.1634 | 21.5161 | 66.7983 | 283.8169 | 283.8169 | 0 | 0
2025-10-01 22:00 | 29.85 | 82 | 70 | 25.9443 | 21.3371 | 66.9059 | 193.6934 | 193.6934 | 0 | 0
2025-10-01 23:00 | 29.25 | 85 | 70 | 25.7517 | 21.2998 | 67.8022 | 195.0002 | 195.0002 | 0 | 0
2025-10-02 | 28.75 | 88 | 70 | 25.5894 | 21.2959 | 68.7509 | 197.3915 | 197.3915 | 0 | 0
2025-10-02 01:00 | 28.4 | 89.5 | 70 | 25.4761 | 21.2487 | 69.1222 | 196.9793 | 196.9793 | 0 | 0
2025-10-02 02:00 | 28 | 90.5 | 70 | 25.3466 | 21.1454 | 69.2134 | 194.1757 | 194.1757 | 0 | 0
2025-10-02 03:00 | 27.65 | 92 | 70 | 25.2319 | 21.0943 | 69.5687 | 193.5914 | 193.5914 | 0 | 0
2025-10-02 04:00 | 27.7 | 92 | 70 | 25.2481 | 21.1156 | 69.6121 | 194.3218 | 194.3218 | 0 | 0
2025-10-02 05:00 | 27.45 | 92.5 | 70 | 25.1664 | 21.0408 | 69.603 | 192.0897 | 192.0897 | 0 | 0
2025-10-02 06:00 | 26.9 | 95.5 | 100 | 24.984 | 20.9946 | 70.4117 | 275.4009 | 275.4009 | 0 | 0
2025-10-02 07:00 | 28.1 | 90.5 | 100 | 25.3788 | 21.1882 | 69.2846 | 279.3192 | 279.3192 | 0 | 0
2025-10-02 08:00 | 30.4 | 78 | 100 | 26.1224 | 21.272 | 65.4171 | 268.0638 | 268.0638 | 0 | 0
2025-10-02 09:00 | 32.3 | 67 | 100 | 26.7262 | 21.168 | 61.3615 | 247.5738 | 247.5738 | 0 | 0
2025-10-02 10:00 | 34.1 | 56.5 | 100 | 27.2927 | 20.9357 | 56.9482 | 219.7602 | 219.7602 | 0 | 0
2025-10-02 11:00 | 35.7 | 47 | 100 | 27.7957 | 20.591 | 52.4411 | 186.4683 | 186.4683 | 0 | 0
2025-10-02 12:00 | 36.6 | 43.5 | 100 | 28.0694 | 20.5311 | 50.8156 | 176.8375 | 176.8375 | 0 | 0
2025-10-02 13:00 | 36.9 | 41 | 100 | 28.1679 | 20.363 | 49.4283 | 164.0615 | 164.0615 | 0 | 0
2025-10-02 14:00 | 36.9 | 35.5 | 100 | 28.1985 | 19.7648 | 46.0117 | 125.635 | 125.635 | 0 | 0
2025-10-02 15:00 | 36.3 | 39 | 100 | 28.0074 | 19.96 | 47.9332 | 141.9955 | 141.9955 | 0 | 0
2025-10-02 16:00 | 35.1 | 46 | 100 | 27.6267 | 20.2899 | 51.5487 | 171.039 | 171.039 | 0 | 0
2025-10-02 17:00 | 33.5 | 53 | 100 | 27.1279 | 20.4045 | 54.6492 | 189.1343 | 189.1343 | 0 | 0
2025-10-02 18:00 | 32.2 | 63.5 | 100 | 26.7056 | 20.8411 | 59.4635 | 226.6841 | 226.6841 | 0 | 0
2025-10-02 19:00 | 31.55 | 70.5 | 100 | 26.4908 | 21.158 | 62.6 | 252.2183 | 252.2183 | 0 | 0
2025-10-02 20:00 | 31 | 75 | 100 | 26.3129 | 21.2889 | 64.4289 | 264.8541 | 264.8541 | 0 | 0
2025-10-02 21:00 | 30.4 | 77.5 | 100 | 26.1234 | 21.2351 | 65.1645 | 265.4993 | 265.4993 | 0 | 0
2025-10-02 22:00 | 29.75 | 80 | 70 | 25.9167 | 21.1538 | 65.8297 | 185.2863 | 185.2863 | 0 | 0
2025-10-02 23:00 | 29.15 | 83 | 70 | 25.7232 | 21.1194 | 66.7445 | 186.7691 | 186.7691 | 0 | 0
2025-10-03 | 28.65 | 85 | 70 | 25.5616 | 21.0506 | 67.2473 | 186.1029 | 186.1029 | 0 | 0
2025-10-03 01:00 | 28.3 | 86 | 70 | 25.4482 | 20.9729 | 67.4074 | 184.27 | 184.27 | 0 | 0
2025-10-03 02:00 | 28.1 | 86 | 70 | 25.3837 | 20.89 | 67.239 | 181.4191 | 181.4191 | 0 | 0
2025-10-03 03:00 | 27.9 | 87 | 70 | 25.3179 | 20.8733 | 67.5198 | 181.6635 | 181.6635 | 0 | 0
2025-10-03 04:00 | 27.5 | 89.5 | 70 | 25.1855 | 20.8693 | 68.2926 | 183.5582 | 183.5582 | 0 | 0
2025-10-03 05:00 | 26.8 | 93 | 70 | 24.9529 | 20.7956 | 69.2169 | 183.8023 | 183.8023 | 0 | 0
2025-10-03 06:00 | 26.2 | 96.5 | 100 | 24.7515 | 20.7546 | 70.1815 | 264.3488 | 264.3488 | 0 | 0
2025-10-03 07:00 | 27.25 | 92 | 100 | 25.1017 | 20.9239 | 69.159 | 267.5975 | 267.5975 | 0 | 0
2025-10-03 08:00 | 29.9 | 77 | 100 | 25.9689 | 20.9982 | 64.4852 | 252.8604 | 252.8604 | 0 | 0
2025-10-03 09:00 | 32.4 | 62.5 | 100 | 26.7691 | 20.8358 | 59.0304 | 224.2589 | 224.2589 | 0 | 0
2025-10-03 10:00 | 34.7 | 48.5 | 100 | 27.4997 | 20.4039 | 52.7355 | 180.1803 | 180.1803 | 0 | 0
2025-10-03 11:00 | 36.8 | 35 | 100 | 28.1727 | 19.6872 | 45.6227 | 120.3669 | 120.3669 | 0 | 0
2025-10-03 12:00 | 38.2 | 28 | 100 | 28.6148 | 19.2787 | 41.6023 | 85.9364 | 85.9364 | 0 | 0
2025-10-03 13:00 | 38.35 | 31 | 100 | 28.6374 | 19.6786 | 43.6112 | 110.3475 | 110.3475 | 0 | 0
2025-10-03 14:00 | 37.55 | 36 | 100 | 28.3805 | 20.0207 | 46.5489 | 137.2734 | 137.2734 | 0 | 0
2025-10-03 15:00 | 36.55 | 37 | 100 | 28.09 | 19.8279 | 46.7784 | 131.2371 | 131.2371 | 0 | 0
2025-10-03 16:00 | 35.05 | 45.5 | 100 | 27.6145 | 20.2283 | 51.1991 | 166.7305 | 166.7305 | 0 | 0
2025-10-03 17:00 | 33.15 | 60 | 100 | 27.0009 | 20.9 | 58.2245 | 223.6218 | 223.6218 | 0 | 0
2025-10-03 18:00 | 31.8 | 69.5 | 100 | 26.5692 | 21.1768 | 62.259 | 251.4456 | 251.4456 | 0 | 0
2025-10-03 19:00 | 31.1 | 73 | 100 | 26.3481 | 21.176 | 63.484 | 256.2989 | 256.2989 | 0 | 0
2025-10-03 20:00 | 30.4 | 77 | 100 | 26.1245 | 21.1983 | 64.8966 | 262.7748 | 262.7748 | 0 | 0
2025-10-03 21:00 | 29.6 | 80.5 | 100 | 25.869 | 21.1286 | 65.9188 | 263.8344 | 263.8344 | 0 | 0
2025-10-03 22:00 | 29 | 82 | 70 | 25.6772 | 20.9891 | 66.1259 | 181.1996 | 181.1996 | 0 | 0
2025-10-03 23:00 | 28.45 | 85 | 70 | 25.4977 | 20.9682 | 67.0546 | 183.0848 | 183.0848 | 0 | 0
2025-10-04 | 27.95 | 88.5 | 70 | 25.3327 | 20.9931 | 68.2152 | 186.8732 | 186.8732 | 0 | 0
2025-10-04 01:00 | 27.4 | 91.5 | 70 | 25.1512 | 20.9562 | 69.0707 | 188.0146 | 188.0146 | 0 | 0
2025-10-04 02:00 | 26.65 | 93.5 | 70 | 24.9029 | 20.7635 | 69.2868 | 182.9646 | 182.9646 | 0 | 0
2025-10-04 03:00 | 25.95 | 95 | 70 | 24.6685 | 20.5567 | 69.3232 | 177.0734 | 177.0734 | 0 | 0
2025-10-04 04:00 | 25.7 | 95.5 | 70 | 24.5841 | 20.4808 | 69.3186 | 174.8408 | 174.8408 | 0 | 0
2025-10-04 05:00 | 25.65 | 95 | 70 | 24.5674 | 20.4289 | 69.0649 | 172.7038 | 172.7038 | 0 | 0
2025-10-04 06:00 | 25.65 | 94.5 | 100 | 24.5676 | 20.3991 | 68.8521 | 244.6863 | 244.6863 | 0 | 0
2025-10-04 07:00 | 27.2 | 88 | 100 | 25.0885 | 20.6471 | 67.3432 | 249.279 | 249.279 | 0 | 0
2025-10-04 08:00 | 30 | 76.5 | 100 | 26.0011 | 21.0019 | 64.3099 | 252.2326 | 252.2326 | 0 | 0
2025-10-04 09:00 | 32.45 | 65 | 100 | 26.7771 | 21.0632 | 60.3774 | 238.9012 | 238.9012 | 0 | 0
2025-10-04 10:00 | 34.45 | 53 | 100 | 27.4087 | 20.7427 | 55.1579 | 203.9956 | 203.9956 | 0 | 0
2025-10-04 11:00 | 35.95 | 43.5 | 100 | 27.8845 | 20.3241 | 50.447 | 166.7837 | 166.7837 | 0 | 0
2025-10-04 12:00 | 36.65 | 39 | 100 | 28.108 | 20.075 | 48.0398 | 146.2663 | 146.2663 | 0 | 0
2025-10-04 13:00 | 36.75 | 37.5 | 100 | 28.1447 | 19.944 | 47.1598 | 137.2629 | 137.2629 | 0 | 0
2025-10-04 14:00 | 36.4 | 39.5 | 100 | 28.0338 | 20.0495 | 48.2475 | 146.3814 | 146.3814 | 0 | 0
2025-10-04 15:00 | 35.65 | 43 | 100 | 27.8002 | 20.1741 | 50.0201 | 159.3182 | 159.3182 | 0 | 0
2025-10-04 16:00 | 34.7 | 45.5 | 100 | 27.5118 | 20.1125 | 51.0275 | 161.5716 | 161.5716 | 0 | 0
2025-10-04 17:00 | 33.35 | 53 | 100 | 27.0833 | 20.3555 | 54.5324 | 186.3855 | 186.3855 | 0 | 0
2025-10-04 18:00 | 31.95 | 64 | 100 | 26.6287 | 20.7903 | 59.5217 | 224.622 | 224.622 | 0 | 0
2025-10-04 19:00 | 31.1 | 71.5 | 100 | 26.3514 | 21.0612 | 62.7303 | 248.5608 | 248.5608 | 0 | 0
2025-10-04 20:00 | 30.5 | 75.5 | 100 | 26.1583 | 21.1268 | 64.2438 | 257.28 | 257.28 | 0 | 0
2025-10-04 21:00 | 29.85 | 79 | 100 | 25.9498 | 21.123 | 65.4135 | 261.6602 | 261.6602 | 0 | 0
2025-10-04 22:00 | 29.2 | 83.5 | 70 | 25.7384 | 21.1754 | 67.0029 | 188.9894 | 188.9894 | 0 | 0
2025-10-04 23:00 | 28.7 | 87 | 70 | 25.5751 | 21.2074 | 68.195 | 193.1039 | 193.1039 | 0 | 0
2025-10-05 | 28.25 | 88.5 | 70 | 25.4294 | 21.1195 | 68.4836 | 191.282 | 191.282 | 0 | 0
2025-10-05 01:00 | 27.65 | 90 | 70 | 25.2339 | 20.9651 | 68.6324 | 187.172 | 187.172 | 0 | 0
2025-10-05 02:00 | 27.05 | 91.5 | 70 | 25.0364 | 20.8071 | 68.7741 | 182.965 | 182.965 | 0 | 0
2025-10-05 03:00 | 26.8 | 91.5 | 70 | 24.9539 | 20.7014 | 68.5615 | 179.3562 | 179.3562 | 0 | 0
2025-10-05 04:00 | 26.85 | 91 | 70 | 24.9708 | 20.6914 | 68.3882 | 178.612 | 178.612 | 0 | 0
2025-10-05 05:00 | 26.7 | 91.5 | 70 | 24.9208 | 20.6595 | 68.4767 | 177.9149 | 177.9149 | 0 | 0
2025-10-05 06:00 | 26.85 | 89.5 | 100 | 24.9718 | 20.5967 | 67.7326 | 248.7965 | 248.7965 | 0 | 0
2025-10-05 07:00 | 28.5 | 80.5 | 100 | 25.5191 | 20.6816 | 65.0296 | 242.0456 | 242.0456 | 0 | 0
2025-10-05 08:00 | 30.95 | 67.5 | 100 | 26.3139 | 20.6923 | 60.5992 | 224.9844 | 224.9844 | 0 | 0
2025-10-05 09:00 | 32.7 | 60 | 100 | 26.8665 | 20.7359 | 57.9079 | 215.6 | 215.6 | 0 | 0
2025-10-05 10:00 | 33.95 | 55.5 | 100 | 27.2527 | 20.7936 | 56.2636 | 210.9072 | 210.9072 | 0 | 0
2025-10-05 11:00 | 35.1 | 49 | 100 | 27.614 | 20.5872 | 53.2554 | 189.6782 | 189.6782 | 0 | 0
2025-10-05 12:00 | 35.8 | 43 | 100 | 27.8436 | 20.223 | 50.0872 | 161.4313 | 161.4313 | 0 | 0
2025-10-05 13:00 | 36 | 38 | 100 | 27.9257 | 19.7669 | 47.1742 | 130.8576 | 130.8576 | 0 | 0
2025-10-05 14:00 | 35.6 | 38 | 100 | 27.8089 | 19.6432 | 47.0259 | 125.6807 | 125.6807 | 0 | 0
2025-10-05 15:00 | 34.65 | 44.5 | 100 | 27.501 | 19.998 | 50.4361 | 154.6474 | 154.6474 | 0 | 0
2025-10-05 16:00 | 33.45 | 53.5 | 100 | 27.1114 | 20.4345 | 54.8733 | 191.0274 | 191.0274 | 0 | 0
2025-10-05 17:00 | 32.25 | 60 | 100 | 26.7304 | 20.5695 | 57.6393 | 208.095 | 208.095 | 0 | 0
2025-10-05 18:00 | 31.35 | 63.5 | 100 | 26.4462 | 20.5248 | 58.8678 | 211.4175 | 211.4175 | 0 | 0
2025-10-05 19:00 | 30.7 | 67 | 100 | 26.2372 | 20.5574 | 60.193 | 218.0808 | 218.0808 | 0 | 0
2025-10-05 20:00 | 30 | 71 | 100 | 26.0105 | 20.5939 | 61.669 | 225.4406 | 225.4406 | 0 | 0
2025-10-05 21:00 | 29.25 | 75 | 100 | 25.7666 | 20.5945 | 63.0429 | 230.8661 | 230.8661 | 0 | 0
2025-10-05 22:00 | 28.5 | 79 | 70 | 25.5208 | 20.578 | 64.3496 | 164.6987 | 164.6987 | 0 | 0
2025-10-05 23:00 | 27.7 | 82.5 | 70 | 25.2572 | 20.492 | 65.3285 | 164.8888 | 164.8888 | 0 | 0
2025-10-06 | 26.9 | 85.5 | 70 | 24.9911 | 20.3622 | 66.0385 | 163.0529 | 163.0529 | 0 | 0
2025-10-06 01:00 | 26.15 | 88.5 | 70 | 24.7388 | 20.2424 | 66.7516 | 161.5136 | 161.5136 | 0 | 0
2025-10-06 02:00 | 25.5 | 91 | 70 | 24.5179 | 20.1258 | 67.3022 | 159.6157 | 159.6157 | 0 | 0
2025-10-06 03:00 | 25.1 | 91.5 | 70 | 24.3811 | 19.9892 | 67.2058 | 155.5074 | 155.5074 | 0 | 0
2025-10-06 04:00 | 25.05 | 91.5 | 70 | 24.364 | 19.9682 | 67.1683 | 154.8247 | 154.8247 | 0 | 0
2025-10-06 05:00 | 24.85 | 93 | 70 | 24.295 | 19.973 | 67.626 | 156.1203 | 156.1203 | 0 | 0
2025-10-06 06:00 | 24.8 | 93 | 100 | 24.2777 | 19.952 | 67.5838 | 222.0048 | 222.0048 | 0 | 0
2025-10-06 07:00 | 26.45 | 83.5 | 100 | 24.8422 | 20.0507 | 64.8285 | 215.7687 | 215.7687 | 0 | 0
2025-10-06 08:00 | 29.75 | 65.5 | 100 | 25.9406 | 20.0862 | 58.8204 | 193.6885 | 193.6885 | 0 | 0
2025-10-06 09:00 | 33 | 52.5 | 100 | 26.9796 | 20.1908 | 54.0482 | 177.7352 | 177.7352 | 0 | 0
2025-10-06 10:00 | 35.65 | 43 | 100 | 27.8003 | 20.1757 | 50.0074 | 159.1725 | 159.1725 | 0 | 0
2025-10-06 11:00 | 38.1 | 29.5 | 100 | 28.5767 | 19.4305 | 42.5542 | 96.1346 | 96.1346 | 0 | 0
2025-10-06 12:00 | 39.7 | 20.5 | 100 | 29.093 | 18.7123 | 36.8781 | 41.8854 | 41.8854 | 0 | 0
2025-10-06 13:00 | 39.1 | 29 | 100 | 28.8608 | 19.6443 | 42.5323 | 103.887 | 103.887 | 0 | 0
2025-10-06 14:00 | 37 | 42.5 | 100 | 28.1877 | 20.5568 | 50.3946 | 175.7693 | 175.7693 | 0 | 0
2025-10-06 15:00 | 35.5 | 49 | 100 | 27.729 | 20.7213 | 53.5049 | 196.2376 | 196.2376 | 0 | 0
2025-10-06 16:00 | 34.35 | 57 | 100 | 27.3636 | 21.072 | 57.3905 | 227.0284 | 227.0284 | 0 | 0
2025-10-06 17:00 | 32.85 | 65 | 100 | 26.8961 | 21.2132 | 60.7065 | 246.6306 | 246.6306 | 0 | 0
2025-10-06 18:00 | 31.8 | 71 | 100 | 26.5654 | 21.296 | 63.0347 | 259.4748 | 259.4748 | 0 | 0
2025-10-06 19:00 | 31.25 | 75 | 100 | 26.3893 | 21.3896 | 64.6172 | 269.6128 | 269.6128 | 0 | 0
2025-10-06 20:00 | 30.75 | 77 | 100 | 26.2323 | 21.3396 | 65.1917 | 269.7914 | 269.7914 | 0 | 0
2025-10-06 21:00 | 30.2 | 78.5 | 100 | 26.0597 | 21.228 | 65.4632 | 266.2177 | 266.2177 | 0 | 0
2025-10-06 22:00 | 29.7 | 79.5 | 70 | 25.902 | 21.0973 | 65.5293 | 182.7578 | 182.7578 | 0 | 0
2025-10-06 23:00 | 29.05 | 82 | 70 | 25.693 | 21.009 | 66.173 | 181.9428 | 181.9428 | 0 | 0
2025-10-07 | 28.25 | 86 | 70 | 25.4322 | 20.9528 | 67.3457 | 183.4194 | 183.4194 | 0 | 0
2025-10-07 01:00 | 27.5 | 90 | 70 | 25.1851 | 20.9016 | 68.4994 | 184.9719 | 184.9719 | 0 | 0
2025-10-07 02:00 | 26.75 | 93.5 | 70 | 24.936 | 20.8059 | 69.3793 | 184.4651 | 184.4651 | 0 | 0
2025-10-07 03:00 | 26.1 | 95 | 70 | 24.7188 | 20.6209 | 69.4573 | 179.2942 | 179.2942 | 0 | 0
2025-10-07 04:00 | 25.45 | 94.5 | 70 | 24.4998 | 20.3147 | 68.7057 | 168.5494 | 168.5494 | 0 | 0
2025-10-07 05:00 | 24.8 | 94 | 70 | 24.2776 | 20.0105 | 67.9865 | 158.0678 | 158.0678 | 0 | 0
2025-10-07 06:00 | 24.75 | 90.5 | 100 | 24.2609 | 19.7849 | 66.5283 | 211.3985 | 211.3985 | 0 | 0
2025-10-07 07:00 | 26.7 | 76.5 | 100 | 24.9304 | 19.6978 | 61.9629 | 190.8254 | 190.8254 | 0 | 0
2025-10-07 08:00 | 30.2 | 57 | 100 | 26.0987 | 19.5918 | 54.9087 | 158.3757 | 158.3757 | 0 | 0
2025-10-07 09:00 | 33.75 | 38.5 | 100 | 27.2532 | 19.1356 | 46.6411 | 104.9679 | 104.9679 | 0 | 0
2025-10-07 10:00 | 36.6 | 25.5 | 100 | 28.165 | 18.5638 | 39.6648 | 51.0197 | 51.0197 | 0 | 0
2025-10-07 11:00 | 38.3 | 19.5 | 100 | 28.6989 | 18.2565 | 36.0387 | 21.8159 | 21.8159 | 0 | 0
2025-10-07 12:00 | 39.3 | 16 | 100 | 29.0129 | 18.0225 | 33.7528 | 1.792 | 1.792 | 0 | 0
2025-10-07 13:00 | 39.15 | 20 | 100 | 28.9406 | 18.5179 | 36.4631 | 32.9778 | 32.9778 | 0 | 0
2025-10-07 14:00 | 37.85 | 28 | 100 | 28.5149 | 19.1832 | 41.5203 | 82.2116 | 82.2116 | 0 | 0
2025-10-07 15:00 | 36.35 | 35.5 | 100 | 28.0399 | 19.606 | 45.7838 | 118.3301 | 118.3301 | 0 | 0
2025-10-07 16:00 | 34.75 | 44.5 | 100 | 27.5306 | 20.0316 | 50.4734 | 155.9842 | 155.9842 | 0 | 0
2025-10-07 17:00 | 33 | 56 | 100 | 26.9687 | 20.4981 | 55.9581 | 198.0562 | 198.0562 | 0 | 0
2025-10-07 18:00 | 31.8 | 64.5 | 100 | 26.5819 | 20.775 | 59.6723 | 224.5863 | 224.5863 | 0 | 0
2025-10-07 19:00 | 31.1 | 67 | 100 | 26.3613 | 20.7101 | 60.4567 | 225.1527 | 225.1527 | 0 | 0
2025-10-07 20:00 | 30.25 | 70.5 | 100 | 26.09 | 20.6543 | 61.5903 | 227.4222 | 227.4222 | 0 | 0
2025-10-07 21:00 | 29.2 | 76 | 100 | 25.7493 | 20.6467 | 63.4636 | 234.52 | 234.52 | 0 | 0
2025-10-07 22:00 | 28.25 | 80 | 70 | 25.4389 | 20.5463 | 64.6028 | 164.4103 | 164.4103 | 0 | 0
2025-10-07 23:00 | 27.35 | 83 | 70 | 25.1419 | 20.3837 | 65.2692 | 161.5636 | 161.5636 | 0 | 0
2025-10-08 | 26.55 | 85.5 | 70 | 24.8746 | 20.2187 | 65.7591 | 158.1953 | 158.1953 | 0 | 0
2025-10-08 01:00 | 25.9 | 87 | 70 | 24.6551 | 20.0471 | 65.9182 | 153.7627 | 153.7627 | 0 | 0
2025-10-08 02:00 | 25.05 | 89.5 | 70 | 24.3644 | 19.8489 | 66.3402 | 149.317 | 149.317 | 0 | 0
2025-10-08 03:00 | 24.4 | 91.5 | 70 | 24.1395 | 19.6989 | 66.683 | 145.9718 | 145.9718 | 0 | 0
2025-10-08 04:00 | 24.35 | 90.5 | 70 | 24.1222 | 19.6202 | 66.2465 | 142.663 | 142.663 | 0 | 0
2025-10-08 05:00 | 24.25 | 89 | 70 | 24.0875 | 19.4919 | 65.5776 | 137.396 | 137.396 | 0 | 0
2025-10-08 06:00 | 24.65 | 84.5 | 100 | 24.2271 | 19.3886 | 64.0248 | 186.4782 | 186.4782 | 0 | 0
2025-10-08 07:00 | 26.6 | 73.5 | 100 | 24.8986 | 19.4626 | 60.5893 | 176.2618 | 176.2618 | 0 | 0
2025-10-08 08:00 | 29.45 | 59 | 100 | 25.8546 | 19.4834 | 55.4998 | 156.6273 | 156.6273 | 0 | 0
2025-10-08 09:00 | 32.2 | 44.5 | 100 | 26.757 | 19.2126 | 49.3715 | 120.1297 | 120.1297 | 0 | 0
2025-10-08 10:00 | 34.45 | 35.5 | 100 | 27.4768 | 19.0478 | 45.1467 | 94.7664 | 94.7664 | 0 | 0
2025-10-08 11:00 | 36.45 | 29 | 100 | 28.1026 | 18.9217 | 41.8008 | 74.1595 | 74.1595 | 0 | 0
2025-10-08 12:00 | 37.8 | 24 | 100 | 28.5252 | 18.6923 | 38.9163 | 51.6934 | 51.6934 | 0 | 0
2025-10-08 13:00 | 37.65 | 28.5 | 100 | 28.4545 | 19.1885 | 41.7869 | 83.6834 | 83.6834 | 0 | 0
2025-10-08 14:00 | 36.75 | 34 | 100 | 28.1637 | 19.5602 | 44.9951 | 112.8543 | 112.8543 | 0 | 0
2025-10-08 15:00 | 35.85 | 36.5 | 100 | 27.8892 | 19.5631 | 46.2114 | 118.7923 | 118.7923 | 0 | 0
2025-10-08 16:00 | 34.35 | 46 | 100 | 27.4063 | 20.0465 | 51.139 | 159.4905 | 159.4905 | 0 | 0
2025-10-08 17:00 | 32.5 | 57.5 | 100 | 26.8134 | 20.4497 | 56.4548 | 198.2093 | 198.2093 | 0 | 0
2025-10-08 18:00 | 31.1 | 67 | 100 | 26.3613 | 20.7102 | 60.4571 | 225.157 | 225.157 | 0 | 0
2025-10-08 19:00 | 30.2 | 74 | 100 | 26.068 | 20.8968 | 63.2638 | 243.9013 | 243.9013 | 0 | 0
2025-10-08 20:00 | 29.4 | 78 | 100 | 25.8099 | 20.8697 | 64.5575 | 247.8181 | 247.8181 | 0 | 0
2025-10-08 21:00 | 28.75 | 79.5 | 100 | 25.6007 | 20.7136 | 64.7479 | 242.1649 | 242.1649 | 0 | 0
2025-10-08 22:00 | 28.3 | 78 | 70 | 25.4574 | 20.4298 | 63.7158 | 158.6521 | 158.6521 | 0 | 0
2025-10-08 23:00 | 27.85 | 76.5 | 70 | 25.3121 | 20.1482 | 62.7136 | 148.0466 | 148.0466 | 0 | 0
2025-10-09 | 27.15 | 80 | 70 | 25.0782 | 20.1055 | 63.7869 | 149.7368 | 149.7368 | 0 | 0
2025-10-09 01:00 | 26.35 | 85 | 70 | 24.8078 | 20.106 | 65.3842 | 153.9633 | 153.9633 | 0 | 0
2025-10-09 02:00 | 25.7 | 86 | 70 | 24.5877 | 19.9035 | 65.3414 | 148.1845 | 148.1845 | 0 | 0
2025-10-09 03:00 | 25.05 | 88 | 70 | 24.3648 | 19.7595 | 65.7101 | 145.121 | 145.121 | 0 | 0
2025-10-09 04:00 | 24.65 | 89.5 | 70 | 24.2265 | 19.6854 | 66.0364 | 143.8571 | 143.8571 | 0 | 0
2025-10-09 05:00 | 24.5 | 88.5 | 70 | 24.1746 | 19.5654 | 65.5273 | 139.2038 | 139.2038 | 0 | 0
2025-10-09 06:00 | 24.65 | 83.5 | 100 | 24.2273 | 19.3298 | 63.5979 | 182.4273 | 182.4273 | 0 | 0
2025-10-09 07:00 | 26.1 | 68.5 | 100 | 24.7315 | 18.9461 | 58.1386 | 146.7362 | 146.7362 | 0 | 0
2025-10-09 08:00 | 28.6 | 55 | 100 | 25.5822 | 18.8852 | 53.1941 | 124.3687 | 124.3687 | 0 | 0
2025-10-09 09:00 | 31.3 | 48.5 | 100 | 26.465 | 19.2718 | 51.0922 | 129.692 | 129.692 | 0 | 0
2025-10-09 10:00 | 33.85 | 40 | 100 | 27.2784 | 19.3149 | 47.4923 | 115.1397 | 115.1397 | 0 | 0
2025-10-09 11:00 | 35.8 | 31.5 | 100 | 27.8982 | 19.0217 | 43.1453 | 83.9906 | 83.9906 | 0 | 0
2025-10-09 12:00 | 37.15 | 26 | 100 | 28.3241 | 18.7686 | 40.0577 | 59.8271 | 59.8271 | 0 | 0
2025-10-09 13:00 | 37.95 | 22.5 | 100 | 28.578 | 18.551 | 37.9496 | 41.5832 | 41.5832 | 0 | 0
2025-10-09 14:00 | 37.9 | 24 | 100 | 28.5542 | 18.721 | 38.9199 | 52.4926 | 52.4926 | 0 | 0
2025-10-09 15:00 | 36.55 | 32.5 | 100 | 28.1137 | 19.3401 | 43.9823 | 99.706 | 99.706 | 0 | 0
2025-10-09 16:00 | 34.9 | 38.5 | 100 | 27.5998 | 19.4862 | 47.0313 | 119.5227 | 119.5227 | 0 | 0
2025-10-09 17:00 | 33.35 | 44.5 | 100 | 27.1112 | 19.5817 | 49.8274 | 135.8555 | 135.8555 | 0 | 0
2025-10-09 18:00 | 31.9 | 52.5 | 100 | 26.643 | 19.813 | 53.4614 | 160.5584 | 160.5584 | 0 | 0
2025-10-09 19:00 | 30.9 | 57.5 | 100 | 26.3195 | 19.8803 | 55.5107 | 171.8354 | 171.8354 | 0 | 0
2025-10-09 20:00 | 29.9 | 62 | 100 | 25.9944 | 19.8762 | 57.1887 | 178.6365 | 178.6365 | 0 | 0
2025-10-09 21:00 | 29 | 64 | 100 | 25.7017 | 19.698 | 57.6438 | 173.6173 | 173.6173 | 0 | 0
2025-10-09 22:00 | 28.25 | 64 | 70 | 25.4565 | 19.4235 | 57.2393 | 113.0073 | 113.0073 | 0 | 0
2025-10-09 23:00 | 27.55 | 67 | 70 | 25.2218 | 19.3792 | 58.2347 | 114.6079 | 114.6079 | 0 | 0
2025-10-10 | 26.9 | 72 | 70 | 25.0005 | 19.4774 | 60.0969 | 122.3911 | 122.3911 | 0 | 0
2025-10-10 01:00 | 26.45 | 74 | 70 | 24.8476 | 19.4377 | 60.7103 | 123.0092 | 123.0092 | 0 | 0
2025-10-10 02:00 | 26.1 | 75 | 70 | 24.7284 | 19.3687 | 60.9393 | 121.7611 | 121.7611 | 0 | 0
2025-10-10 03:00 | 25.5 | 78.5 | 70 | 24.522 | 19.3589 | 62.0661 | 124.5063 | 124.5063 | 0 | 0
2025-10-10 04:00 | 25.05 | 81.5 | 70 | 24.3662 | 19.3676 | 63.0366 | 127.2998 | 127.2998 | 0 | 0
2025-10-10 05:00 | 24.65 | 85 | 70 | 24.2271 | 19.419 | 64.2101 | 131.7601 | 131.7601 | 0 | 0
2025-10-10 06:00 | 24.55 | 87 | 100 | 24.1921 | 19.4972 | 64.9469 | 193.9871 | 193.9871 | 0 | 0
2025-10-10 07:00 | 26.05 | 79 | 100 | 24.7096 | 19.6061 | 62.5995 | 189.438 | 189.438 | 0 | 0
2025-10-10 08:00 | 29.15 | 61.5 | 100 | 25.7538 | 19.5668 | 56.5267 | 163.9033 | 163.9033 | 0 | 0
2025-10-10 09:00 | 32.45 | 44 | 100 | 26.8361 | 19.2496 | 49.1831 | 120.4699 | 120.4699 | 0 | 0
2025-10-10 10:00 | 34.75 | 33 | 100 | 27.5773 | 18.882 | 43.7673 | 82.0879 | 82.0879 | 0 | 0
2025-10-10 11:00 | 36.2 | 26.5 | 100 | 28.0411 | 18.5773 | 40.2 | 53.9577 | 53.9577 | 0 | 0
2025-10-10 12:00 | 37.2 | 22 | 100 | 28.3613 | 18.3063 | 37.5388 | 31.1775 | 31.1775 | 0 | 0
2025-10-10 13:00 | 37.7 | 19.5 | 100 | 28.5233 | 18.119 | 35.9862 | 16.8408 | 16.8408 | 0 | 0
2025-10-10 14:00 | 37.55 | 19.5 | 100 | 28.4791 | 18.0827 | 35.9807 | 15.6849 | 15.6849 | 0 | 0
2025-10-10 15:00 | 36.6 | 23.5 | 100 | 28.1755 | 18.3319 | 38.4251 | 36.8292 | 36.8292 | 0 | 0
2025-10-10 16:00 | 34.9 | 31.5 | 100 | 27.6287 | 18.7642 | 42.9521 | 74.3054 | 74.3054 | 0 | 0
2025-10-10 17:00 | 32.95 | 42.5 | 100 | 26.995 | 19.2671 | 48.5842 | 118.7257 | 118.7257 | 0 | 0
2025-10-10 18:00 | 31.65 | 53 | 100 | 26.5641 | 19.7684 | 53.61 | 159.6242 | 159.6242 | 0 | 0
2025-10-10 19:00 | 31 | 59 | 100 | 26.3476 | 20.0362 | 56.3369 | 181.4537 | 181.4537 | 0 | 0
2025-10-10 20:00 | 30.4 | 61.5 | 100 | 26.154 | 20.0183 | 57.2415 | 184.4942 | 184.4942 | 0 | 0
2025-10-10 21:00 | 29.75 | 63 | 100 | 25.9447 | 19.8969 | 57.6003 | 181.2445 | 181.2445 | 0 | 0
2025-10-10 22:00 | 29.25 | 65 | 70 | 25.7811 | 19.8635 | 58.2725 | 127.8834 | 127.8834 | 0 | 0
2025-10-10 23:00 | 28.55 | 68.5 | 70 | 25.5496 | 19.8582 | 59.5052 | 131.2125 | 131.2125 | 0 | 0
2025-10-11 | 27.45 | 74 | 70 | 25.1825 | 19.8226 | 61.332 | 135.2758 | 135.2758 | 0 | 0
2025-10-11 01:00 | 26.45 | 79.5 | 70 | 24.8445 | 19.7945 | 63.0994 | 139.2868 | 139.2868 | 0 | 0
2025-10-11 02:00 | 25.75 | 83 | 70 | 24.6058 | 19.7382 | 64.1244 | 140.4237 | 140.4237 | 0 | 0
2025-10-11 03:00 | 25.25 | 84.5 | 70 | 24.4344 | 19.6298 | 64.4148 | 138.179 | 138.179 | 0 | 0
2025-10-11 04:00 | 25.1 | 84 | 70 | 24.3829 | 19.539 | 64.1069 | 134.8619 | 134.8619 | 0 | 0
2025-10-11 05:00 | 25 | 83.5 | 70 | 24.3485 | 19.4686 | 63.8336 | 132.2 | 132.2 | 0 | 0
2025-10-11 06:00 | 25.05 | 82.5 | 100 | 24.366 | 19.4281 | 63.4499 | 185.7973 | 185.7973 | 0 | 0
2025-10-11 07:00 | 26.6 | 75.5 | 100 | 24.8974 | 19.5944 | 61.45 | 184.661 | 184.661 | 0 | 0
2025-10-11 08:00 | 29.15 | 65 | 100 | 25.7489 | 19.8274 | 58.202 | 180.8883 | 180.8883 | 0 | 0
2025-10-11 09:00 | 31.2 | 54.5 | 100 | 26.4201 | 19.7399 | 54.1385 | 160.6168 | 160.6168 | 0 | 0
2025-10-11 10:00 | 32.95 | 41.5 | 100 | 26.9981 | 19.1768 | 48.0204 | 112.6468 | 112.6468 | 0 | 0
2025-10-11 11:00 | 34.65 | 29.5 | 100 | 27.5609 | 18.4875 | 41.7224 | 58.53 | 58.53 | 0 | 0
2025-10-11 12:00 | 35.8 | 24 | 100 | 27.9333 | 18.1898 | 38.6348 | 33.0409 | 33.0409 | 0 | 0
2025-10-11 13:00 | 35.75 | 29 | 100 | 27.895 | 18.7308 | 41.652 | 66.779 | 66.779 | 0 | 0
2025-10-11 14:00 | 34.4 | 42 | 100 | 27.4367 | 19.6766 | 48.8694 | 135.2017 | 135.2017 | 0 | 0
2025-10-11 15:00 | 33.65 | 46.5 | 100 | 27.1953 | 19.864 | 51.0817 | 152.2337 | 152.2337 | 0 | 0
2025-10-11 16:00 | 33.05 | 49.5 | 100 | 27.0041 | 19.939 | 52.4463 | 161.1237 | 161.1237 | 0 | 0
2025-10-11 17:00 | 31.65 | 56.5 | 100 | 26.5556 | 20.0625 | 55.4287 | 178.7043 | 178.7043 | 0 | 0
2025-10-11 18:00 | 30.85 | 59.5 | 100 | 26.2996 | 20.0223 | 56.5098 | 181.6812 | 181.6812 | 0 | 0
2025-10-11 19:00 | 30.45 | 62 | 100 | 26.1688 | 20.0753 | 57.5238 | 187.9319 | 187.9319 | 0 | 0
2025-10-11 20:00 | 29.95 | 61.5 | 100 | 26.0111 | 19.8545 | 56.9855 | 177.092 | 177.092 | 0 | 0
2025-10-11 21:00 | 29.35 | 61 | 100 | 25.8192 | 19.5999 | 56.4143 | 164.8924 | 164.8924 | 0 | 0
2025-10-11 22:00 | 28.8 | 63 | 70 | 25.6379 | 19.5501 | 57.0724 | 115.9844 | 115.9844 | 0 | 0
2025-10-11 23:00 | 28.25 | 65 | 70 | 25.4554 | 19.4952 | 57.7116 | 116.3225 | 116.3225 | 0 | 0
2025-10-12 | 27.5 | 67.5 | 70 | 25.2046 | 19.3949 | 58.4465 | 115.695 | 115.695 | 0 | 0
2025-10-12 01:00 | 26.8 | 70.5 | 70 | 24.9679 | 19.3381 | 59.3974 | 116.8023 | 116.8023 | 0 | 0
2025-10-12 02:00 | 26.3 | 73.5 | 70 | 24.7971 | 19.3472 | 60.422 | 119.8484 | 119.8484 | 0 | 0
2025-10-12 03:00 | 25.95 | 75 | 70 | 24.6773 | 19.3104 | 60.8628 | 120.0375 | 120.0375 | 0 | 0
2025-10-12 04:00 | 25.85 | 75 | 70 | 24.6431 | 19.2723 | 60.8033 | 118.8293 | 118.8293 | 0 | 0
2025-10-12 05:00 | 25.75 | 75 | 70 | 24.6089 | 19.2341 | 60.7437 | 117.6218 | 117.6218 | 0 | 0
2025-10-12 06:00 | 25.9 | 73 | 100 | 24.6611 | 19.1633 | 59.974 | 162.304 | 162.304 | 0 | 0
2025-10-12 07:00 | 27.55 | 63 | 100 | 25.2252 | 19.0991 | 56.4306 | 145.8083 | 145.8083 | 0 | 0
2025-10-12 08:00 | 30.15 | 45 | 100 | 26.1039 | 18.6041 | 48.9275 | 95.9573 | 95.9573 | 0 | 0
2025-10-12 09:00 | 32.6 | 32 | 100 | 26.9166 | 18.1765 | 42.7585 | 52.6712 | 52.6712 | 0 | 0
2025-10-12 10:00 | 34.7 | 28.5 | 100 | 27.5801 | 18.3977 | 41.1421 | 52.4736 | 52.4736 | 0 | 0
2025-10-12 11:00 | 36.05 | 27 | 100 | 27.994 | 18.5921 | 40.4855 | 56.007 | 56.007 | 0 | 0
2025-10-12 12:00 | 36.9 | 24.5 | 100 | 28.259 | 18.5254 | 39.0842 | 46.7028 | 46.7028 | 0 | 0
2025-10-12 13:00 | 37.3 | 23 | 100 | 28.3852 | 18.4478 | 38.1969 | 39.5486 | 39.5486 | 0 | 0
2025-10-12 14:00 | 37.7 | 22.5 | 100 | 28.5053 | 18.4843 | 37.9335 | 39.5237 | 39.5237 | 0 | 0
2025-10-12 15:00 | 36.3 | 30.5 | 100 | 28.0508 | 19.0464 | 42.6943 | 83.0643 | 83.0643 | 0 | 0
2025-10-12 16:00 | 34.1 | 38 | 100 | 27.3614 | 19.1912 | 46.4782 | 106.3191 | 106.3191 | 0 | 0
2025-10-12 17:00 | 33.6 | 36.5 | 100 | 27.2141 | 18.8953 | 45.4812 | 90.9828 | 90.9828 | 0 | 0
2025-10-12 18:00 | 33.45 | 36 | 100 | 27.1696 | 18.8025 | 45.159 | 86.1454 | 86.1454 | 0 | 0
2025-10-12 19:00 | 32.75 | 41 | 100 | 26.9377 | 19.0662 | 47.6917 | 107.2717 | 107.2717 | 0 | 0
2025-10-12 20:00 | 31.75 | 51 | 100 | 26.6002 | 19.6333 | 52.6054 | 150.0452 | 150.0452 | 0 | 0
2025-10-12 21:00 | 31.35 | 53 | 100 | 26.4705 | 19.6665 | 53.4478 | 154.9082 | 154.9082 | 0 | 0
2025-10-12 22:00 | 31.1 | 54 | 70 | 26.3898 | 19.6638 | 53.8374 | 109.5237 | 109.5237 | 0 | 0
2025-10-12 23:00 | 30.9 | 54 | 70 | 26.3268 | 19.5947 | 53.7423 | 107.4137 | 107.4137 | 0 | 0
2025-10-13 | 30.8 | 46 | 70 | 26.3114 | 18.894 | 49.6492 | 76.805 | 76.805 | 0 | 0
2025-10-13 01:00 | 30.55 | 41.5 | 70 | 26.2398 | 18.4332 | 47.2999 | 57.9247 | 57.9247 | 0 | 0
2025-10-13 02:00 | 30 | 42 | 70 | 26.0603 | 18.3063 | 47.4105 | 55.1357 | 55.1357 | 0 | 0
2025-10-13 03:00 | 29.4 | 48 | 70 | 25.8547 | 18.6071 | 50.1726 | 71.1003 | 71.1003 | 0 | 0
2025-10-13 04:00 | 29.2 | 53 | 70 | 25.782 | 18.9346 | 52.5033 | 86.4224 | 86.4224 | 0 | 0
2025-10-13 05:00 | 29.25 | 49.5 | 70 | 25.8033 | 18.6777 | 50.8374 | 74.8406 | 74.8406 | 0 | 0
2025-10-13 06:00 | 29.45 | 44.5 | 100 | 25.8762 | 18.343 | 48.4784 | 84.6143 | 84.6143 | 0 | 0
2025-10-13 07:00 | 30.3 | 41.5 | 100 | 26.1588 | 18.3589 | 47.218 | 79.5571 | 79.5571 | 0 | 0
2025-10-13 08:00 | 32 | 36.5 | 100 | 26.7149 | 18.4288 | 45.0468 | 72.0832 | 72.0832 | 0 | 0
2025-10-13 09:00 | 33.45 | 33 | 100 | 27.1794 | 18.5138 | 43.4584 | 67.5691 | 67.5691 | 0 | 0
2025-10-13 10:00 | 34.35 | 32 | 100 | 27.4597 | 18.6674 | 43.0874 | 71.1583 | 71.1583 | 0 | 0
2025-10-13 11:00 | 35.25 | 29.5 | 100 | 27.7427 | 18.6544 | 41.8236 | 64.5998 | 64.5998 | 0 | 0
2025-10-13 12:00 | 36.05 | 27 | 100 | 27.994 | 18.5939 | 40.4784 | 55.9231 | 55.9231 | 0 | 0
2025-10-13 13:00 | 36.35 | 26 | 100 | 28.0882 | 18.5586 | 39.9222 | 51.9852 | 51.9852 | 0 | 0
2025-10-13 14:00 | 36.35 | 26 | 100 | 28.0883 | 18.5578 | 39.9263 | 52.0338 | 52.0338 | 0 | 0
2025-10-13 15:00 | 35.8 | 27 | 100 | 27.9193 | 18.525 | 40.4478 | 53.5836 | 53.5836 | 0 | 0
2025-10-13 16:00 | 34.9 | 29.5 | 100 | 27.6369 | 18.5544 | 41.7745 | 61.1761 | 61.1761 | 0 | 0
2025-10-13 17:00 | 33.65 | 38 | 100 | 27.2244 | 19.0573 | 46.3262 | 100.6392 | 100.6392 | 0 | 0
2025-10-13 18:00 | 32.25 | 48.5 | 100 | 26.7618 | 19.5841 | 51.5173 | 143.4355 | 143.4355 | 0 | 0
2025-10-13 19:00 | 31.4 | 54 | 100 | 26.4838 | 19.7673 | 53.9863 | 161.0509 | 161.0509 | 0 | 0
2025-10-13 20:00 | 30.6 | 58.5 | 100 | 26.223 | 19.8539 | 55.8476 | 172.2121 | 172.2121 | 0 | 0
2025-10-13 21:00 | 30.05 | 59 | 100 | 26.0474 | 19.6975 | 55.8004 | 165.9864 | 165.9864 | 0 | 0
2025-10-13 22:00 | 29.85 | 58 | 70 | 25.985 | 19.5484 | 55.21 | 110.4874 | 110.4874 | 0 | 0
2025-10-13 23:00 | 29.5 | 60.5 | 70 | 25.8684 | 19.6164 | 56.2446 | 115.3248 | 115.3248 | 0 | 0
2025-10-14 | 28.75 | 63 | 70 | 25.6216 | 19.5325 | 57.0399 | 115.3772 | 115.3772 | 0 | 0
2025-10-14 01:00 | 27.95 | 64 | 70 | 25.3574 | 19.3143 | 57.0893 | 109.6854 | 109.6854 | 0 | 0
2025-10-14 02:00 | 27.4 | 64 | 70 | 25.1742 | 19.1147 | 56.8167 | 103.6175 | 103.6175 | 0 | 0
2025-10-14 03:00 | 26.6 | 63 | 70 | 24.9049 | 18.7581 | 56.0068 | 91.9666 | 91.9666 | 0 | 0
2025-10-14 04:00 | 25.95 | 62.5 | 70 | 24.6827 | 18.4931 | 55.521 | 83.7364 | 83.7364 | 0 | 0
2025-10-14 05:00 | 25.75 | 63.5 | 70 | 24.6134 | 18.4891 | 55.8656 | 84.5691 | 84.5691 | 0 | 0
2025-10-14 06:00 | 25.55 | 64.5 | 100 | 24.5438 | 18.4835 | 56.2044 | 121.9226 | 121.9226 | 0 | 0
2025-10-14 07:00 | 27 | 60 | 100 | 25.0426 | 18.6932 | 54.8435 | 124.1924 | 124.1924 | 0 | 0
2025-10-14 08:00 | 29.8 | 54 | 100 | 25.9755 | 19.2174 | 53.2286 | 136.9748 | 136.9748 | 0 | 0
2025-10-14 09:00 | 32.1 | 51 | 100 | 26.7088 | 19.7533 | 52.7586 | 155.1193 | 155.1193 | 0 | 0
2025-10-14 10:00 | 33.95 | 43.5 | 100 | 27.2962 | 19.6817 | 49.5093 | 138.0132 | 138.0132 | 0 | 0
2025-10-14 11:00 | 35.35 | 34 | 100 | 27.7531 | 19.1576 | 44.5261 | 95.6531 | 95.6531 | 0 | 0
2025-10-14 12:00 | 35.4 | 33 | 100 | 27.7724 | 19.0658 | 43.9513 | 89.6648 | 89.6648 | 0 | 0
2025-10-14 13:00 | 34.75 | 38 | 100 | 27.5571 | 19.39 | 46.6883 | 114.4058 | 114.4058 | 0 | 0
2025-10-14 14:00 | 34.45 | 40.5 | 100 | 27.4574 | 19.5457 | 48.0249 | 126.4103 | 126.4103 | 0 | 0
2025-10-14 15:00 | 34.3 | 39 | 100 | 27.4181 | 19.3509 | 47.1155 | 115.0906 | 115.0906 | 0 | 0
2025-10-14 16:00 | 33.8 | 39.5 | 100 | 27.2649 | 19.2466 | 47.2269 | 111.808 | 111.808 | 0 | 0
2025-10-14 17:00 | 32.7 | 46 | 100 | 26.9077 | 19.507 | 50.3872 | 135.724 | 135.724 | 0 | 0
2025-10-14 18:00 | 31.75 | 53.5 | 100 | 26.594 | 19.8452 | 53.9214 | 163.9015 | 163.9015 | 0 | 0
2025-10-14 19:00 | 31.1 | 59.5 | 100 | 26.3778 | 20.1125 | 56.6504 | 185.7522 | 185.7522 | 0 | 0
2025-10-14 20:00 | 30.55 | 63.5 | 100 | 26.1974 | 20.2302 | 58.3285 | 197.2797 | 197.2797 | 0 | 0
2025-10-14 21:00 | 29.85 | 65 | 100 | 25.9734 | 20.086 | 58.6327 | 192.8572 | 192.8572 | 0 | 0
2025-10-14 22:00 | 29.3 | 66 | 70 | 25.7958 | 19.9563 | 58.7804 | 131.8672 | 131.8672 | 0 | 0
2025-10-14 23:00 | 28.85 | 69.5 | 70 | 25.6458 | 20.0437 | 60.1594 | 138.1426 | 138.1426 | 0 | 0
2025-10-15 | 28.2 | 74 | 70 | 25.4292 | 20.1127 | 61.8224 | 144.6664 | 144.6664 | 0 | 0
2025-10-15 01:00 | 27.65 | 77.5 | 70 | 25.2454 | 20.1373 | 63.0359 | 148.6575 | 148.6575 | 0 | 0
2025-10-15 02:00 | 27.2 | 80.5 | 70 | 25.0943 | 20.1585 | 64.0567 | 152.0015 | 152.0015 | 0 | 0
2025-10-15 03:00 | 26.75 | 80.5 | 70 | 24.9445 | 19.9781 | 63.7411 | 146.1305 | 146.1305 | 0 | 0
2025-10-15 04:00 | 26.5 | 79 | 70 | 24.8616 | 19.7818 | 62.9214 | 138.4872 | 138.4872 | 0 | 0
2025-10-15 05:00 | 26.3 | 79 | 70 | 24.7942 | 19.7038 | 62.7892 | 135.9483 | 135.9483 | 0 | 0
2025-10-15 06:00 | 26.05 | 79 | 100 | 24.7095 | 19.6049 | 62.6256 | 189.6979 | 189.6979 | 0 | 0
2025-10-15 07:00 | 27.3 | 74 | 100 | 25.1327 | 19.7644 | 61.2325 | 190.5568 | 190.5568 | 0 | 0
2025-10-15 08:00 | 29.75 | 66.5 | 100 | 25.9391 | 20.1626 | 59.2921 | 198.4879 | 198.4879 | 0 | 0
2025-10-15 09:00 | 31.6 | 63.5 | 100 | 26.5233 | 20.6206 | 58.997 | 215.418 | 215.418 | 0 | 0
2025-10-15 10:00 | 33.15 | 58.5 | 100 | 27.0059 | 20.7722 | 57.3852 | 214.7243 | 214.7243 | 0 | 0
2025-10-15 11:00 | 34.8 | 48.5 | 100 | 27.5289 | 20.4381 | 52.7895 | 181.7256 | 181.7256 | 0 | 0
2025-10-15 12:00 | 35.65 | 43 | 100 | 27.8003 | 20.1755 | 50.0066 | 159.1637 | 159.1637 | 0 | 0
2025-10-15 13:00 | 35.3 | 45 | 100 | 27.6896 | 20.2621 | 51.023 | 167.1297 | 167.1297 | 0 | 0
2025-10-15 14:00 | 34.85 | 45 | 100 | 27.558 | 20.1137 | 50.8058 | 160.552 | 160.552 | 0 | 0
2025-10-15 15:00 | 34.25 | 45 | 100 | 27.3804 | 19.9174 | 50.5245 | 151.8654 | 151.8654 | 0 | 0
2025-10-15 16:00 | 32.9 | 53 | 100 | 26.9478 | 20.199 | 54.2756 | 179.1655 | 179.1655 | 0 | 0
2025-10-15 17:00 | 31.45 | 65 | 100 | 26.4736 | 20.6837 | 59.6885 | 220.998 | 220.998 | 0 | 0
2025-10-15 18:00 | 30.55 | 72 | 100 | 26.1807 | 20.8838 | 62.5573 | 240.6447 | 240.6447 | 0 | 0
2025-10-15 19:00 | 30.05 | 75 | 100 | 26.0193 | 20.9111 | 63.6386 | 246.0043 | 246.0043 | 0 | 0
2025-10-15 20:00 | 29.45 | 79.5 | 100 | 25.8234 | 20.9966 | 65.3161 | 256.0243 | 256.0243 | 0 | 0
2025-10-15 21:00 | 28.7 | 84 | 100 | 25.579 | 21.0035 | 66.7978 | 261.9891 | 261.9891 | 0 | 0
2025-10-15 22:00 | 28.05 | 87 | 70 | 25.3666 | 20.9361 | 67.6159 | 183.5932 | 183.5932 | 0 | 0
2025-10-15 23:00 | 27.4 | 89.5 | 70 | 25.1529 | 20.8271 | 68.1792 | 181.9203 | 181.9203 | 0 | 0
2025-10-16 | 26.55 | 93 | 70 | 24.8701 | 20.6898 | 68.978 | 180.0018 | 180.0018 | 0 | 0
2025-10-16 01:00 | 25.8 | 96 | 70 | 24.6176 | 20.5535 | 69.6102 | 177.6737 | 177.6737 | 0 | 0
2025-10-16 02:00 | 25.2 | 97.5 | 70 | 24.4138 | 20.3849 | 69.726 | 173.1287 | 173.1287 | 0 | 0
2025-10-16 03:00 | 24.9 | 97.5 | 70 | 24.3113 | 20.2566 | 69.477 | 168.8108 | 168.8108 | 0 | 0
2025-10-16 04:00 | 25.15 | 93.5 | 70 | 24.3978 | 20.1283 | 68.0442 | 161.5133 | 161.5133 | 0 | 0
2025-10-16 05:00 | 25.5 | 83 | 70 | 24.5205 | 19.638 | 63.9524 | 137.1778 | 137.1778 | 0 | 0
2025-10-16 06:00 | 25.7 | 72.5 | 100 | 24.5927 | 19.0558 | 59.6592 | 156.9884 | 156.9884 | 0 | 0
2025-10-16 07:00 | 26.9 | 64 | 100 | 25.006 | 18.9346 | 56.5767 | 140.2307 | 140.2307 | 0 | 0
2025-10-16 08:00 | 29 | 55.5 | 100 | 25.7131 | 19.059 | 53.6105 | 132.7061 | 132.7061 | 0 | 0
2025-10-16 09:00 | 30.9 | 48.5 | 100 | 26.3382 | 19.1386 | 50.9434 | 124.2317 | 124.2317 | 0 | 0
2025-10-16 10:00 | 32.65 | 41.5 | 100 | 26.9053 | 19.0838 | 47.9153 | 108.7501 | 108.7501 | 0 | 0
2025-10-16 11:00 | 34.1 | 36 | 100 | 27.3687 | 18.9961 | 45.3272 | 93.6915 | 93.6915 | 0 | 0
2025-10-16 12:00 | 35.1 | 32.5 | 100 | 27.6848 | 18.9267 | 43.5803 | 82.9863 | 82.9863 | 0 | 0
2025-10-16 13:00 | 35.8 | 30 | 100 | 27.9052 | 18.8542 | 42.2642 | 74.086 | 74.086 | 0 | 0
2025-10-16 14:00 | 36 | 29 | 100 | 27.9695 | 18.7978 | 41.7074 | 69.4445 | 69.4445 | 0 | 0
2025-10-16 15:00 | 34.75 | 37.5 | 100 | 27.5591 | 19.3375 | 46.4096 | 111.3357 | 111.3357 | 0 | 0
2025-10-16 16:00 | 33 | 48.5 | 100 | 26.992 | 19.8323 | 51.8758 | 154.5338 | 154.5338 | 0 | 0
2025-10-16 17:00 | 31.95 | 53.5 | 100 | 26.6559 | 19.9146 | 54.0228 | 166.9783 | 166.9783 | 0 | 0
2025-10-16 18:00 | 31.35 | 57.5 | 100 | 26.4602 | 20.0394 | 55.769 | 179.1738 | 179.1738 | 0 | 0
2025-10-16 19:00 | 30.9 | 60 | 100 | 26.3143 | 20.0815 | 56.7781 | 184.9808 | 184.9808 | 0 | 0
2025-10-16 20:00 | 30.15 | 63 | 100 | 26.0721 | 20.0447 | 57.8253 | 187.8255 | 187.8255 | 0 | 0
2025-10-16 21:00 | 29.3 | 65 | 100 | 25.7973 | 19.883 | 58.2887 | 183.3932 | 183.3932 | 0 | 0
2025-10-16 22:00 | 28.85 | 65 | 70 | 25.6517 | 19.7166 | 58.0294 | 123.1206 | 123.1206 | 0 | 0
2025-10-16 23:00 | 28.45 | 66 | 70 | 25.52 | 19.6416 | 58.272 | 121.7792 | 121.7792 | 0 | 0
2025-10-17 | 27.8 | 68 | 70 | 25.3038 | 19.542 | 58.8243 | 120.6386 | 120.6386 | 0 | 0
2025-10-17 01:00 | 27.2 | 68 | 70 | 25.104 | 19.3188 | 58.4969 | 113.7194 | 113.7194 | 0 | 0
2025-10-17 02:00 | 26.65 | 67 | 70 | 24.9194 | 19.0476 | 57.7745 | 104.4908 | 104.4908 | 0 | 0
2025-10-17 03:00 | 26.05 | 69 | 70 | 24.7141 | 18.9596 | 58.3416 | 103.7098 | 103.7098 | 0 | 0
2025-10-17 04:00 | 25.85 | 71 | 70 | 24.6448 | 19.0157 | 59.0911 | 107.2309 | 107.2309 | 0 | 0
2025-10-17 05:00 | 25.85 | 69.5 | 70 | 24.6454 | 18.9188 | 58.4499 | 102.8815 | 102.8815 | 0 | 0
2025-10-17 06:00 | 25.95 | 60.5 | 100 | 24.6836 | 18.3607 | 54.6451 | 111.086 | 111.086 | 0 | 0
2025-10-17 07:00 | 27.3 | 47.5 | 100 | 25.1537 | 17.8979 | 49.3281 | 72.4125 | 72.4125 | 0 | 0
2025-10-17 08:00 | 29.45 | 39 | 100 | 25.8844 | 17.896 | 45.7883 | 56.8234 | 56.8234 | 0 | 0
2025-10-17 09:00 | 31.3 | 34.5 | 100 | 26.4961 | 18.0461 | 43.8491 | 53.1014 | 53.1014 | 0 | 0
2025-10-17 10:00 | 32.8 | 31.5 | 100 | 26.981 | 18.1867 | 42.5029 | 51.5969 | 51.5969 | 0 | 0
2025-10-17 11:00 | 34.05 | 29 | 100 | 27.3786 | 18.2774 | 41.3136 | 49.0325 | 49.0325 | 0 | 0
2025-10-17 12:00 | 34.95 | 27 | 100 | 27.6624 | 18.3052 | 40.2991 | 45.0797 | 45.0797 | 0 | 0
2025-10-17 13:00 | 35.6 | 25.5 | 100 | 27.866 | 18.3086 | 39.5052 | 41.3308 | 41.3308 | 0 | 0
2025-10-17 14:00 | 36 | 24.5 | 100 | 27.9911 | 18.2977 | 38.957 | 38.2554 | 38.2554 | 0 | 0
2025-10-17 15:00 | 34.9 | 30.5 | 100 | 27.6328 | 18.6608 | 42.3571 | 67.6738 | 67.6738 | 0 | 0
2025-10-17 16:00 | 32.95 | 40 | 100 | 27.0026 | 19.0358 | 47.208 | 103.8872 | 103.8872 | 0 | 0
2025-10-17 17:00 | 31.55 | 47 | 100 | 26.5472 | 19.223 | 50.4359 | 125.2113 | 125.2113 | 0 | 0
2025-10-17 18:00 | 30.7 | 53 | 100 | 26.2655 | 19.4441 | 53.1392 | 145.1524 | 145.1524 | 0 | 0
2025-10-17 19:00 | 30.2 | 56 | 100 | 26.1006 | 19.5145 | 54.3939 | 153.0613 | 153.0613 | 0 | 0
2025-10-17 20:00 | 29.55 | 58 | 100 | 25.8884 | 19.4434 | 55.0506 | 153.0799 | 153.0799 | 0 | 0
2025-10-17 21:00 | 28.85 | 60.5 | 100 | 25.6575 | 19.3848 | 55.8958 | 154.3248 | 154.3248 | 0 | 0
2025-10-17 22:00 | 28.25 | 62.5 | 70 | 25.4582 | 19.3163 | 56.529 | 108.0174 | 108.0174 | 0 | 0
2025-10-17 23:00 | 27.5 | 64.5 | 70 | 25.2073 | 19.1873 | 57.0696 | 106.1287 | 106.1287 | 0 | 0
2025-10-18 | 26.55 | 67.5 | 70 | 24.8853 | 19.0453 | 57.9296 | 104.7791 | 104.7791 | 0 | 0
2025-10-18 01:00 | 25.75 | 70 | 70 | 24.6109 | 18.9141 | 58.6106 | 103.1875 | 103.1875 | 0 | 0
2025-10-18 02:00 | 25.1 | 72.5 | 70 | 24.3856 | 18.831 | 59.3371 | 102.9519 | 102.9519 | 0 | 0
2025-10-18 03:00 | 24.6 | 72.5 | 70 | 24.2112 | 18.6436 | 59.0923 | 97.3417 | 97.3417 | 0 | 0
2025-10-18 04:00 | 24.45 | 70 | 70 | 24.1589 | 18.4347 | 58.0058 | 88.925 | 88.925 | 0 | 0
2025-10-18 05:00 | 24.35 | 69 | 70 | 24.1237 | 18.3367 | 57.5562 | 85.1526 | 85.1526 | 0 | 0
2025-10-18 06:00 | 24.7 | 63 | 100 | 24.2476 | 18.087 | 55.2387 | 103.4072 | 103.4072 | 0 | 0
2025-10-18 07:00 | 26.45 | 47.5 | 100 | 24.8624 | 17.6302 | 49.1376 | 62.1677 | 62.1677 | 0 | 0
2025-10-18 08:00 | 29 | 33.5 | 100 | 25.7422 | 17.3131 | 43.0638 | 24.6107 | 24.6107 | 0 | 0
2025-10-18 09:00 | 31.5 | 28.5 | 100 | 26.5741 | 17.5506 | 40.7418 | 21.6332 | 21.6332 | 0 | 0
2025-10-18 10:00 | 33.45 | 27 | 100 | 27.1989 | 17.9157 | 40.1023 | 30.752 | 30.752 | 0 | 0
2025-10-18 11:00 | 34.7 | 25.5 | 100 | 27.5919 | 18.0809 | 39.3845 | 32.8386 | 32.8386 | 0 | 0
2025-10-18 12:00 | 35.6 | 24 | 100 | 27.8728 | 18.1426 | 38.5997 | 31.082 | 31.082 | 0 | 0
2025-10-18 13:00 | 36.15 | 23 | 100 | 28.0434 | 18.1645 | 38.0562 | 29.1522 | 29.1522 | 0 | 0
2025-10-18 14:00 | 35.25 | 29.5 | 100 | 27.7428 | 18.6497 | 41.8438 | 64.8342 | 64.8342 | 0 | 0
2025-10-18 15:00 | 33.65 | 38.5 | 100 | 27.2227 | 19.1047 | 46.6102 | 103.7357 | 103.7357 | 0 | 0
2025-10-18 16:00 | 32.6 | 43 | 100 | 26.8854 | 19.2031 | 48.7241 | 116.9697 | 116.9697 | 0 | 0
2025-10-18 17:00 | 31.5 | 48.5 | 100 | 26.5279 | 19.334 | 51.2044 | 132.8333 | 132.8333 | 0 | 0
2025-10-18 18:00 | 30.65 | 54.5 | 100 | 26.2466 | 19.5478 | 53.8837 | 152.3861 | 152.3861 | 0 | 0
2025-10-18 19:00 | 30.1 | 59 | 100 | 26.0633 | 19.7144 | 55.8377 | 166.8953 | 166.8953 | 0 | 0
2025-10-18 20:00 | 29.35 | 63 | 100 | 25.8163 | 19.7511 | 57.3664 | 174.5717 | 174.5717 | 0 | 0
2025-10-18 21:00 | 28.6 | 65.5 | 100 | 25.5696 | 19.6604 | 58.1255 | 174.1363 | 174.1363 | 0 | 0
2025-10-18 22:00 | 28 | 65.5 | 70 | 25.3725 | 19.4395 | 57.7965 | 115.008 | 115.008 | 0 | 0
2025-10-18 23:00 | 27.35 | 66.5 | 70 | 25.1554 | 19.2706 | 57.9081 | 110.804 | 110.804 | 0 | 0
2025-10-19 | 26.6 | 69.5 | 70 | 24.901 | 19.1969 | 58.842 | 111.4232 | 111.4232 | 0 | 0
2025-10-19 01:00 | 25.85 | 72.5 | 70 | 24.6442 | 19.1121 | 59.7376 | 111.6136 | 111.6136 | 0 | 0
2025-10-19 02:00 | 25.3 | 75 | 70 | 24.4542 | 19.0627 | 60.4957 | 112.3298 | 112.3298 | 0 | 0
2025-10-19 03:00 | 24.8 | 74.5 | 70 | 24.2808 | 18.8415 | 60.0263 | 105.1686 | 105.1686 | 0 | 0
2025-10-19 04:00 | 24.5 | 72 | 70 | 24.1762 | 18.5746 | 58.8612 | 95.0127 | 95.0127 | 0 | 0
2025-10-19 05:00 | 24.2 | 71.5 | 70 | 24.0707 | 18.4331 | 58.5232 | 90.393 | 90.393 | 0 | 0
2025-10-19 06:00 | 24 | 71 | 100 | 24 | 18.3295 | 58.2317 | 124.1203 | 124.1203 | 0 | 0
2025-10-19 07:00 | 25.25 | 64.5 | 100 | 24.4397 | 18.3764 | 56.08 | 117.4535 | 117.4535 | 0 | 0
2025-10-19 08:00 | 28.05 | 54 | 100 | 25.4007 | 18.6224 | 52.5308 | 112.0488 | 112.0488 | 0 | 0
2025-10-19 09:00 | 30.8 | 47 | 100 | 26.3094 | 18.9797 | 50.1442 | 114.899 | 114.899 | 0 | 0
2025-10-19 10:00 | 32.65 | 42 | 100 | 26.9038 | 19.1298 | 48.1838 | 111.6327 | 111.6327 | 0 | 0
2025-10-19 11:00 | 33.8 | 38.5 | 100 | 27.2685 | 19.1526 | 46.6466 | 105.4722 | 105.4722 | 0 | 0
2025-10-19 12:00 | 34 | 42.5 | 100 | 27.3148 | 19.6003 | 48.9778 | 132.6994 | 132.6994 | 0 | 0
2025-10-19 13:00 | 33.65 | 46.5 | 100 | 27.1953 | 19.8653 | 51.0718 | 152.1231 | 152.1231 | 0 | 0
2025-10-19 14:00 | 33.2 | 46 | 100 | 27.0607 | 19.6707 | 50.5989 | 142.7516 | 142.7516 | 0 | 0
2025-10-19 15:00 | 32.5 | 51 | 100 | 26.8319 | 19.8859 | 52.983 | 161.4549 | 161.4549 | 0 | 0
2025-10-19 16:00 | 31.55 | 59 | 100 | 26.5187 | 20.2335 | 56.6645 | 190.5927 | 190.5927 | 0 | 0
2025-10-19 17:00 | 30.65 | 62.5 | 100 | 26.2307 | 20.1878 | 57.8987 | 193.9232 | 193.9232 | 0 | 0
2025-10-19 18:00 | 30.15 | 63.5 | 100 | 26.0712 | 20.0819 | 58.0891 | 190.5352 | 190.5352 | 0 | 0
2025-10-19 19:00 | 29.75 | 65 | 100 | 25.9415 | 20.0484 | 58.5759 | 191.1962 | 191.1962 | 0 | 0
2025-10-19 20:00 | 29.1 | 68 | 100 | 25.7285 | 20.0288 | 59.6081 | 194.5601 | 194.5601 | 0 | 0
2025-10-19 21:00 | 28.4 | 71.5 | 100 | 25.4972 | 20.0147 | 60.7976 | 198.7087 | 198.7087 | 0 | 0
2025-10-19 22:00 | 27.8 | 74 | 70 | 25.2981 | 19.958 | 61.5512 | 139.5871 | 139.5871 | 0 | 0
2025-10-19 23:00 | 27.2 | 76.5 | 70 | 25.0975 | 19.8933 | 62.2774 | 139.7796 | 139.7796 | 0 | 0
2025-10-20 | 26.5 | 79.5 | 70 | 24.8613 | 19.8146 | 63.128 | 139.8917 | 139.8917 | 0 | 0
2025-10-20 01:00 | 25.65 | 82.5 | 70 | 24.5719 | 19.6664 | 63.8463 | 137.7176 | 137.7176 | 0 | 0
2025-10-20 02:00 | 24.9 | 85.5 | 70 | 24.3136 | 19.5493 | 64.5962 | 136.4377 | 136.4377 | 0 | 0
2025-10-20 03:00 | 24.45 | 86 | 70 | 24.1574 | 19.3977 | 64.5054 | 132.028 | 132.028 | 0 | 0
2025-10-20 04:00 | 24.25 | 85.5 | 70 | 24.0876 | 19.2879 | 64.1769 | 128.1675 | 128.1675 | 0 | 0
2025-10-20 05:00 | 23.85 | 88.5 | 70 | 23.9473 | 19.3005 | 65.111 | 130.9028 | 130.9028 | 0 | 0
2025-10-20 06:00 | 23.65 | 91 | 100 | 23.877 | 19.3611 | 65.9552 | 192.4279 | 192.4279 | 0 | 0
2025-10-20 07:00 | 25.25 | 84 | 100 | 24.4345 | 19.5991 | 64.1961 | 195.3072 | 195.3072 | 0 | 0
2025-10-20 08:00 | 28.1 | 69 | 100 | 25.4018 | 19.7248 | 59.4553 | 181.9513 | 181.9513 | 0 | 0
2025-10-20 09:00 | 30.4 | 59.5 | 100 | 26.1578 | 19.862 | 56.2388 | 174.1636 | 174.1636 | 0 | 0
2025-10-20 10:00 | 32.35 | 51.5 | 100 | 26.7845 | 19.8809 | 53.1557 | 161.7993 | 161.7993 | 0 | 0
2025-10-20 11:00 | 34.2 | 38 | 100 | 27.3917 | 19.223 | 46.5007 | 107.4522 | 107.4522 | 0 | 0
2025-10-20 12:00 | 35.05 | 28.5 | 100 | 27.6866 | 18.4883 | 41.216 | 56.165 | 56.165 | 0 | 0
2025-10-20 13:00 | 35 | 27 | 100 | 27.6777 | 18.3139 | 40.328 | 45.8148 | 45.8148 | 0 | 0
2025-10-20 14:00 | 34.35 | 33.5 | 100 | 27.4541 | 18.8145 | 43.9813 | 81.0493 | 81.0493 | 0 | 0
2025-10-20 15:00 | 33.6 | 38 | 100 | 27.2091 | 19.0405 | 46.3222 | 100.1531 | 100.1531 | 0 | 0
2025-10-20 16:00 | 32.55 | 43.5 | 100 | 26.8685 | 19.2319 | 48.9822 | 119.2705 | 119.2705 | 0 | 0
2025-10-20 17:00 | 31.05 | 55 | 100 | 26.3719 | 19.7272 | 54.3383 | 161.1845 | 161.1845 | 0 | 0
2025-10-20 18:00 | 30.25 | 58.5 | 100 | 26.112 | 19.7278 | 55.6779 | 166.82 | 166.82 | 0 | 0
2025-10-20 19:00 | 29.7 | 56 | 100 | 25.94 | 19.3383 | 54.1766 | 145.6924 | 145.6924 | 0 | 0
2025-10-20 20:00 | 28.7 | 59 | 100 | 25.6103 | 19.218 | 55.1407 | 145.1114 | 145.1114 | 0 | 0
2025-10-20 21:00 | 28.15 | 62 | 100 | 25.4257 | 19.2426 | 56.2692 | 150.6401 | 150.6401 | 0 | 0
2025-10-20 22:00 | 27.85 | 62.5 | 70 | 25.3257 | 19.1709 | 56.3514 | 103.7729 | 103.7729 | 0 | 0
2025-10-20 23:00 | 27.3 | 64.5 | 70 | 25.1403 | 19.1136 | 56.9887 | 104.05 | 104.05 | 0 | 0
2025-10-21 | 26.85 | 65.5 | 70 | 24.9881 | 19.0187 | 57.2157 | 102.1852 | 102.1852 | 0 | 0
2025-10-21 01:00 | 26.2 | 67.5 | 70 | 24.7661 | 18.9159 | 57.7764 | 101.0262 | 101.0262 | 0 | 0
2025-10-21 02:00 | 25.5 | 70.5 | 70 | 24.5246 | 18.8524 | 58.7151 | 101.933 | 101.933 | 0 | 0
2025-10-21 03:00 | 24.8 | 77.5 | 70 | 24.2803 | 19.0259 | 61.2517 | 113.3394 | 113.3394 | 0 | 0
2025-10-21 04:00 | 24.35 | 83.5 | 70 | 24.1227 | 19.2106 | 63.4211 | 124.0172 | 124.0172 | 0 | 0
2025-10-21 05:00 | 24.05 | 85 | 70 | 24.0176 | 19.1792 | 63.8348 | 124.2235 | 124.2235 | 0 | 0
2025-10-21 06:00 | 23.85 | 86 | 100 | 23.9472 | 19.157 | 64.1022 | 177.555 | 177.555 | 0 | 0
2025-10-21 07:00 | 25.25 | 79.5 | 100 | 24.4357 | 19.3238 | 62.3163 | 177.331 | 177.331 | 0 | 0
2025-10-21 08:00 | 28.2 | 64 | 100 | 25.4401 | 19.4065 | 57.1986 | 160.4864 | 160.4864 | 0 | 0
2025-10-21 09:00 | 31.2 | 45.5 | 100 | 26.4399 | 18.9824 | 49.515 | 112.1394 | 112.1394 | 0 | 0
2025-10-21 10:00 | 33.7 | 29.5 | 100 | 27.2686 | 18.2328 | 41.5463 | 48.703 | 48.703 | 0 | 0
2025-10-21 11:00 | 35.4 | 20.5 | 100 | 27.8274 | 17.7024 | 36.4819 | 5.5351 | 5.5351 | 0 | 0
2025-10-21 12:00 | 36.25 | 18 | 100 | 28.0981 | 17.6077 | 34.9817 | 0 | 0 | 0 | 0
2025-10-21 13:00 | 35.95 | 23.5 | 100 | 27.9808 | 18.1731 | 38.3395 | 30.8415 | 30.8415 | 0 | 0
2025-10-21 14:00 | 34.8 | 32 | 100 | 27.5965 | 18.7902 | 43.2098 | 76.3259 | 76.3259 | 0 | 0
2025-10-21 15:00 | 33.6 | 39 | 100 | 27.2057 | 19.139 | 46.866 | 106.0685 | 106.0685 | 0 | 0
2025-10-21 16:00 | 32.25 | 45.5 | 100 | 26.7699 | 19.3178 | 49.9231 | 126.4802 | 126.4802 | 0 | 0
2025-10-21 17:00 | 30.9 | 54.5 | 100 | 26.3257 | 19.6356 | 53.9962 | 156.0916 | 156.0916 | 0 | 0
2025-10-21 18:00 | 30.2 | 61.5 | 100 | 26.0907 | 19.9464 | 57.1135 | 181.054 | 181.054 | 0 | 0
2025-10-21 19:00 | 29.7 | 63.5 | 100 | 25.928 | 19.9177 | 57.7946 | 182.6848 | 182.6848 | 0 | 0
2025-10-21 20:00 | 28.8 | 67.5 | 100 | 25.6323 | 19.8811 | 59.1617 | 186.7476 | 186.7476 | 0 | 0
2025-10-21 21:00 | 28 | 70.5 | 100 | 25.3674 | 19.7931 | 60.0618 | 186.8738 | 186.8738 | 0 | 0
2025-10-21 22:00 | 27.45 | 71.5 | 70 | 25.1847 | 19.6532 | 60.182 | 127.321 | 127.321 | 0 | 0
2025-10-21 23:00 | 26.9 | 73.5 | 70 | 24.9995 | 19.5779 | 60.7415 | 126.8135 | 126.8135 | 0 | 0
2025-10-22 | 26.25 | 77 | 70 | 24.7784 | 19.5561 | 61.8662 | 129.2636 | 129.2636 | 0 | 0
2025-10-22 01:00 | 25.65 | 80 | 70 | 24.5729 | 19.5118 | 62.7655 | 130.4393 | 130.4393 | 0 | 0
2025-10-22 02:00 | 25.15 | 81.5 | 70 | 24.4008 | 19.4077 | 63.0777 | 128.3998 | 128.3998 | 0 | 0
2025-10-22 03:00 | 24.6 | 84.5 | 70 | 24.2098 | 19.3696 | 63.9575 | 129.6607 | 129.6607 | 0 | 0
2025-10-22 04:00 | 24.25 | 86.5 | 70 | 24.0876 | 19.3468 | 64.5372 | 130.5348 | 130.5348 | 0 | 0
2025-10-22 05:00 | 23.95 | 85.5 | 70 | 23.9824 | 19.1685 | 63.9488 | 124.1242 | 124.1242 | 0 | 0
2025-10-22 06:00 | 23.7 | 82 | 100 | 23.8941 | 18.8671 | 62.4167 | 159.9717 | 159.9717 | 0 | 0
2025-10-22 07:00 | 25.05 | 71.5 | 100 | 24.3685 | 18.7508 | 58.8724 | 142.0497 | 142.0497 | 0 | 0
2025-10-22 08:00 | 28 | 58 | 100 | 25.38 | 18.9025 | 54.3205 | 129.5015 | 129.5015 | 0 | 0
2025-10-22 09:00 | 30.85 | 50 | 100 | 26.3193 | 19.2508 | 51.6542 | 131.1608 | 131.1608 | 0 | 0
2025-10-22 10:00 | 33.1 | 42.5 | 100 | 27.0412 | 19.3206 | 48.5905 | 120.1664 | 120.1664 | 0 | 0
2025-10-22 11:00 | 34.85 | 32.5 | 100 | 27.6095 | 18.8618 | 43.4829 | 79.7703 | 79.7703 | 0 | 0
2025-10-22 12:00 | 35.7 | 29.5 | 100 | 27.8777 | 18.7787 | 41.9077 | 69.235 | 69.235 | 0 | 0
2025-10-22 13:00 | 35.2 | 37.5 | 100 | 27.6932 | 19.4793 | 46.5299 | 116.6232 | 116.6232 | 0 | 0
2025-10-22 14:00 | 34.35 | 44.5 | 100 | 27.4123 | 19.9076 | 50.2433 | 149.7238 | 149.7238 | 0 | 0
2025-10-22 15:00 | 34.25 | 40 | 100 | 27.3994 | 19.4382 | 47.6391 | 120.364 | 120.364 | 0 | 0
2025-10-22 16:00 | 33.85 | 36 | 100 | 27.2924 | 18.9246 | 45.2426 | 90.5654 | 90.5654 | 0 | 0
2025-10-22 17:00 | 32.2 | 43.5 | 100 | 26.7597 | 19.1247 | 48.8247 | 114.2944 | 114.2944 | 0 | 0
2025-10-22 18:00 | 30.8 | 51 | 100 | 26.3013 | 19.3145 | 52.1635 | 135.9891 | 135.9891 | 0 | 0
2025-10-22 19:00 | 30.2 | 53 | 100 | 26.106 | 19.275 | 52.9005 | 137.6363 | 137.6363 | 0 | 0
2025-10-22 20:00 | 29.4 | 55 | 100 | 25.8444 | 19.1597 | 53.524 | 135.9199 | 135.9199 | 0 | 0
2025-10-22 21:00 | 28.3 | 56 | 100 | 25.4818 | 18.8577 | 53.5337 | 124.7104 | 124.7104 | 0 | 0
2025-10-22 22:00 | 27.45 | 57 | 70 | 25.1968 | 18.6385 | 53.6574 | 81.9972 | 81.9972 | 0 | 0
2025-10-22 23:00 | 26.85 | 60 | 70 | 24.9918 | 18.6424 | 54.7632 | 85.2625 | 85.2625 | 0 | 0
2025-10-23 | 26.5 | 65 | 70 | 24.8697 | 18.8597 | 56.8072 | 96.6977 | 96.6977 | 0 | 0
2025-10-23 01:00 | 26.3 | 70 | 70 | 24.7989 | 19.1195 | 58.8772 | 109.3108 | 109.3108 | 0 | 0
2025-10-23 02:00 | 26 | 73 | 70 | 24.6953 | 19.2025 | 60.0053 | 114.6169 | 114.6169 | 0 | 0
2025-10-23 03:00 | 25.6 | 71.5 | 70 | 24.5587 | 18.9552 | 59.1602 | 105.722 | 105.722 | 0 | 0
2025-10-23 04:00 | 25.4 | 70 | 70 | 24.4902 | 18.7851 | 58.4322 | 99.2347 | 99.2347 | 0 | 0
2025-10-23 05:00 | 25.15 | 72.5 | 70 | 24.4029 | 18.8503 | 59.3498 | 103.432 | 103.432 | 0 | 0
2025-10-23 06:00 | 24.65 | 75 | 100 | 24.2284 | 18.8164 | 60.1208 | 149.4099 | 149.4099 | 0 | 0
2025-10-23 07:00 | 25.45 | 72 | 100 | 24.5069 | 18.9316 | 59.2831 | 150.517 | 150.517 | 0 | 0
2025-10-23 08:00 | 27.95 | 64 | 100 | 25.3575 | 19.3165 | 57.0522 | 156.3127 | 156.3127 | 0 | 0
2025-10-23 09:00 | 30.7 | 55 | 100 | 26.2616 | 19.61 | 54.1165 | 155.2974 | 155.2974 | 0 | 0
2025-10-23 10:00 | 32.55 | 47 | 100 | 26.8587 | 19.5533 | 50.8172 | 138.8677 | 138.8677 | 0 | 0
2025-10-23 11:00 | 33.65 | 43 | 100 | 27.2074 | 19.54 | 49.0922 | 130.6952 | 130.6952 | 0 | 0
2025-10-23 12:00 | 34.15 | 42.5 | 100 | 27.36 | 19.6505 | 49.0207 | 134.5436 | 134.5436 | 0 | 0
2025-10-23 13:00 | 33.95 | 42.5 | 100 | 27.2998 | 19.5862 | 48.9442 | 131.868 | 131.868 | 0 | 0
2025-10-23 14:00 | 33.35 | 43 | 100 | 27.1161 | 19.4428 | 48.9888 | 126.7964 | 126.7964 | 0 | 0
2025-10-23 15:00 | 32.5 | 49 | 100 | 26.8376 | 19.712 | 51.891 | 149.8373 | 149.8373 | 0 | 0
2025-10-23 16:00 | 31.55 | 54.5 | 100 | 26.5295 | 19.8617 | 54.3187 | 166.0485 | 166.0485 | 0 | 0
2025-10-23 17:00 | 30.6 | 55.5 | 100 | 26.2288 | 19.6134 | 54.3462 | 156.6695 | 156.6695 | 0 | 0
2025-10-23 18:00 | 29.95 | 56.5 | 100 | 26.0196 | 19.4663 | 54.5228 | 151.8177 | 151.8177 | 0 | 0
2025-10-23 19:00 | 29.55 | 57 | 100 | 25.89 | 19.3657 | 54.5727 | 148.1954 | 148.1954 | 0 | 0
2025-10-23 20:00 | 28.75 | 60 | 100 | 25.6254 | 19.3115 | 55.6165 | 150.4431 | 150.4431 | 0 | 0
2025-10-23 21:00 | 27.65 | 63 | 100 | 25.2586 | 19.1361 | 56.4645 | 147.2192 | 147.2192 | 0 | 0
2025-10-23 22:00 | 26.8 | 65.5 | 70 | 24.9712 | 19.002 | 57.1698 | 101.4824 | 101.4824 | 0 | 0
2025-10-23 23:00 | 26.45 | 68 | 70 | 24.851 | 19.0422 | 58.0929 | 105.1216 | 105.1216 | 0 | 0
2025-10-24 | 26.35 | 67.5 | 70 | 24.8173 | 18.9721 | 57.8293 | 102.5445 | 102.5445 | 0 | 0
2025-10-24 01:00 | 26.2 | 66.5 | 70 | 24.7666 | 18.8506 | 57.329 | 97.97 | 97.97 | 0 | 0
2025-10-24 02:00 | 25.95 | 66 | 70 | 24.6812 | 18.7264 | 57.0025 | 93.8225 | 93.8225 | 0 | 0
2025-10-24 03:00 | 25.45 | 68.5 | 70 | 24.508 | 18.707 | 57.8353 | 95.6004 | 95.6004 | 0 | 0
2025-10-24 04:00 | 24.85 | 72 | 70 | 24.2987 | 18.7064 | 59.0072 | 98.7584 | 98.7584 | 0 | 0
2025-10-24 05:00 | 24.25 | 74.5 | 70 | 24.0882 | 18.6345 | 59.7327 | 98.7983 | 98.7983 | 0 | 0
2025-10-24 06:00 | 23.95 | 75.5 | 100 | 23.9823 | 18.5817 | 59.985 | 140.0731 | 140.0731 | 0 | 0
2025-10-24 07:00 | 25.1 | 70 | 100 | 24.3862 | 18.6742 | 58.2893 | 137.0279 | 137.0279 | 0 | 0
2025-10-24 08:00 | 27.85 | 58 | 100 | 25.33 | 18.8489 | 54.2728 | 127.4595 | 127.4595 | 0 | 0
2025-10-24 09:00 | 30.45 | 46 | 100 | 26.1991 | 18.7857 | 49.503 | 104.8207 | 104.8207 | 0 | 0
2025-10-24 10:00 | 32.15 | 37.5 | 100 | 26.7597 | 18.566 | 45.6066 | 79.42 | 79.42 | 0 | 0
2025-10-24 11:00 | 33.45 | 31 | 100 | 27.1859 | 18.316 | 42.3423 | 55.3508 | 55.3508 | 0 | 0
2025-10-24 12:00 | 34.05 | 28.5 | 100 | 27.3805 | 18.2252 | 41.034 | 45.9409 | 45.9409 | 0 | 0
2025-10-24 13:00 | 33.95 | 30 | 100 | 27.3443 | 18.3507 | 41.8769 | 54.4301 | 54.4301 | 0 | 0
2025-10-24 14:00 | 33.4 | 32.5 | 100 | 27.1655 | 18.4478 | 43.1856 | 64.1632 | 64.1632 | 0 | 0
2025-10-24 15:00 | 32.7 | 36 | 100 | 26.9367 | 18.5838 | 44.9594 | 77.3591 | 77.3591 | 0 | 0
2025-10-24 16:00 | 31.9 | 39 | 100 | 26.677 | 18.6239 | 46.3642 | 85.2769 | 85.2769 | 0 | 0
2025-10-24 17:00 | 31 | 40 | 100 | 26.3878 | 18.4411 | 46.6504 | 80.0864 | 80.0864 | 0 | 0
2025-10-24 18:00 | 30.3 | 41 | 100 | 26.1598 | 18.3151 | 46.9814 | 77.0899 | 77.0899 | 0 | 0
2025-10-24 19:00 | 29.65 | 43 | 100 | 25.9442 | 18.2822 | 47.8063 | 79.5756 | 79.5756 | 0 | 0
2025-10-24 20:00 | 28.95 | 46 | 100 | 25.7092 | 18.3053 | 49.0672 | 85.8545 | 85.8545 | 0 | 0
2025-10-24 21:00 | 28.25 | 50 | 100 | 25.4717 | 18.3894 | 50.7454 | 96.0567 | 96.0567 | 0 | 0
2025-10-24 22:00 | 27.75 | 53 | 70 | 25.3012 | 18.4481 | 51.9675 | 72.3357 | 72.3357 | 0 | 0
2025-10-24 23:00 | 27.35 | 54.5 | 70 | 25.1651 | 18.4229 | 52.5148 | 73.3079 | 73.3079 | 0 | 0
2025-10-25 | 26.7 | 56.5 | 70 | 24.9429 | 18.3445 | 53.1866 | 73.2732 | 73.2732 | 0 | 0
2025-10-25 01:00 | 25.6 | 60.5 | 70 | 24.5625 | 18.2379 | 54.5336 | 74.3946 | 74.3946 | 0 | 0
2025-10-25 02:00 | 24.35 | 64 | 70 | 24.1241 | 18.0253 | 55.5494 | 71.8076 | 71.8076 | 0 | 0
2025-10-25 03:00 | 23.5 | 64.5 | 70 | 23.8215 | 17.7567 | 55.4693 | 64.8003 | 64.8003 | 0 | 0
2025-10-25 04:00 | 23.3 | 63.5 | 70 | 23.7496 | 17.6265 | 55.0157 | 60.3011 | 60.3011 | 0 | 0
2025-10-25 05:00 | 23.2 | 64 | 70 | 23.7137 | 17.622 | 55.1817 | 60.6279 | 60.6279 | 0 | 0
2025-10-25 06:00 | 23.05 | 65 | 100 | 23.6598 | 17.6293 | 55.524 | 88.1709 | 88.1709 | 0 | 0
2025-10-25 07:00 | 24.6 | 59.5 | 100 | 24.2128 | 17.8286 | 53.7868 | 88.4555 | 88.4555 | 0 | 0
2025-10-25 08:00 | 27.75 | 49.5 | 100 | 25.3044 | 18.1889 | 50.3656 | 87.2571 | 87.2571 | 0 | 0
2025-10-25 09:00 | 30.15 | 45.5 | 100 | 26.1031 | 18.6458 | 49.173 | 98.5076 | 98.5076 | 0 | 0
2025-10-25 10:00 | 31.5 | 43.5 | 100 | 26.5396 | 18.9025 | 48.5942 | 105.2717 | 105.2717 | 0 | 0
2025-10-25 11:00 | 32.7 | 38 | 100 | 26.9309 | 18.7722 | 46.0452 | 89.081 | 89.081 | 0 | 0
2025-10-25 12:00 | 33.75 | 33.5 | 100 | 27.2704 | 18.6437 | 43.8321 | 74.2504 | 74.2504 | 0 | 0
2025-10-25 13:00 | 34.2 | 33 | 100 | 27.4102 | 18.7205 | 43.659 | 76.209 | 76.209 | 0 | 0
2025-10-25 14:00 | 33.35 | 40.5 | 100 | 27.1242 | 19.2036 | 47.6332 | 112.1387 | 112.1387 | 0 | 0
2025-10-25 15:00 | 31.9 | 47.5 | 100 | 26.6556 | 19.3784 | 50.8588 | 133.0681 | 133.0681 | 0 | 0
2025-10-25 16:00 | 31.2 | 47.5 | 100 | 26.4355 | 19.1486 | 50.5799 | 123.3506 | 123.3506 | 0 | 0
2025-10-25 17:00 | 30.45 | 49.5 | 100 | 26.1925 | 19.0702 | 51.3013 | 123.5599 | 123.5599 | 0 | 0
2025-10-25 18:00 | 29.8 | 54 | 100 | 25.9755 | 19.2147 | 53.2537 | 137.2409 | 137.2409 | 0 | 0
2025-10-25 19:00 | 29.45 | 58 | 100 | 25.856 | 19.4059 | 55.0276 | 151.8114 | 151.8114 | 0 | 0
2025-10-25 20:00 | 28.7 | 61.5 | 100 | 25.6072 | 19.4032 | 56.3155 | 156.9809 | 156.9809 | 0 | 0
2025-10-25 21:00 | 27.95 | 63 | 100 | 25.3584 | 19.2425 | 56.6332 | 152.1375 | 152.1375 | 0 | 0
2025-10-25 22:00 | 27.25 | 64 | 70 | 25.1239 | 19.0605 | 56.7456 | 101.9862 | 101.9862 | 0 | 0
2025-10-25 23:00 | 26.5 | 66.5 | 70 | 24.8688 | 18.9585 | 57.4899 | 101.3836 | 101.3836 | 0 | 0
2025-10-26 | 25.8 | 69 | 70 | 24.6284 | 18.8667 | 58.2288 | 100.9945 | 100.9945 | 0 | 0
2025-10-26 01:00 | 25.1 | 72 | 70 | 24.3857 | 18.7987 | 59.1477 | 101.6847 | 101.6847 | 0 | 0
2025-10-26 02:00 | 24.35 | 75.5 | 70 | 24.1233 | 18.7317 | 60.208 | 102.7561 | 102.7561 | 0 | 0
2025-10-26 03:00 | 23.7 | 78.5 | 70 | 23.8939 | 18.6623 | 61.0788 | 103.2168 | 103.2168 | 0 | 0
2025-10-26 04:00 | 23.1 | 81 | 70 | 23.6805 | 18.5753 | 61.7503 | 102.6637 | 102.6637 | 0 | 0
2025-10-26 05:00 | 22.55 | 83 | 70 | 23.4833 | 18.4745 | 62.2362 | 101.2366 | 101.2366 | 0 | 0
2025-10-26 06:00 | 22.4 | 83 | 100 | 23.4291 | 18.416 | 62.158 | 142.1166 | 142.1166 | 0 | 0
2025-10-26 07:00 | 24 | 75 | 100 | 24 | 18.5697 | 59.8304 | 139.1972 | 139.1972 | 0 | 0
2025-10-26 08:00 | 26.9 | 63.5 | 100 | 25.0063 | 18.9003 | 56.3525 | 138.02 | 138.02 | 0 | 0
2025-10-26 09:00 | 28.9 | 57 | 100 | 25.6784 | 19.1386 | 54.2784 | 138.46 | 138.46 | 0 | 0
2025-10-26 10:00 | 30.05 | 52.5 | 100 | 26.0586 | 19.1825 | 52.6046 | 133.0733 | 133.0733 | 0 | 0
2025-10-26 11:00 | 31.15 | 47.5 | 100 | 26.4197 | 19.135 | 50.5398 | 122.4376 | 122.4376 | 0 | 0
2025-10-26 12:00 | 31.9 | 44.5 | 100 | 26.6632 | 19.1164 | 49.2671 | 116.1836 | 116.1836 | 0 | 0
2025-10-26 13:00 | 31.85 | 44.5 | 100 | 26.6475 | 19.0995 | 49.2539 | 115.5722 | 115.5722 | 0 | 0
2025-10-26 14:00 | 31.35 | 45.5 | 100 | 26.4875 | 19.026 | 49.6 | 114.4798 | 114.4798 | 0 | 0
2025-10-26 15:00 | 31.25 | 46 | 100 | 26.4547 | 19.0368 | 49.8239 | 115.8813 | 115.8813 | 0 | 0
2025-10-26 16:00 | 30.75 | 48 | 100 | 26.2914 | 19.0444 | 50.6587 | 119.8018 | 119.8018 | 0 | 0
2025-10-26 17:00 | 29.7 | 52 | 100 | 25.9463 | 19.0229 | 52.2354 | 125.759 | 125.759 | 0 | 0
2025-10-26 18:00 | 29 | 55.5 | 100 | 25.7131 | 19.0574 | 53.6283 | 132.8924 | 132.8924 | 0 | 0
2025-10-26 19:00 | 28.35 | 59 | 100 | 25.495 | 19.0945 | 54.9826 | 139.8388 | 139.8388 | 0 | 0
2025-10-26 20:00 | 27.75 | 62 | 100 | 25.2929 | 19.0993 | 56.0798 | 144.4649 | 144.4649 | 0 | 0
2025-10-26 21:00 | 27.15 | 64 | 100 | 25.0903 | 19.0243 | 56.6955 | 144.1146 | 144.1146 | 0 | 0
2025-10-26 22:00 | 26.4 | 66.5 | 70 | 24.8348 | 18.9225 | 57.4396 | 100.2692 | 100.2692 | 0 | 0
2025-10-26 23:00 | 25.65 | 69 | 70 | 24.5768 | 18.8118 | 58.1555 | 99.3265 | 99.3265 | 0 | 0
2025-10-27 | 24.9 | 72 | 70 | 24.3161 | 18.7238 | 59.0501 | 99.445 | 99.445 | 0 | 0
2025-10-27 01:00 | 24.1 | 75 | 70 | 24.0353 | 18.6068 | 59.8845 | 98.6011 | 98.6011 | 0 | 0
2025-10-27 02:00 | 23.3 | 77.5 | 70 | 23.7515 | 18.4509 | 60.4919 | 96.1127 | 96.1127 | 0 | 0
2025-10-27 03:00 | 22.55 | 80.5 | 70 | 23.4826 | 18.3352 | 61.2901 | 95.1414 | 95.1414 | 0 | 0
2025-10-27 04:00 | 21.8 | 83.5 | 70 | 23.2112 | 18.2102 | 62.0567 | 93.8243 | 93.8243 | 0 | 0
2025-10-27 05:00 | 21.1 | 86.5 | 70 | 22.9554 | 18.0962 | 62.8179 | 92.7583 | 92.7583 | 0 | 0
2025-10-27 06:00 | 20.9 | 87.5 | 100 | 22.882 | 18.0699 | 63.0768 | 132.4136 | 132.4136 | 0 | 0
2025-10-27 07:00 | 22.35 | 80.5 | 100 | 23.4103 | 18.2587 | 61.1788 | 132.5323 | 132.5323 | 0 | 0
2025-10-27 08:00 | 25.35 | 66.5 | 100 | 24.4739 | 18.5419 | 56.9518 | 126.9473 | 126.9473 | 0 | 0
2025-10-27 09:00 | 28.25 | 54 | 100 | 25.4674 | 18.6911 | 52.5982 | 114.7676 | 114.7676 | 0 | 0
2025-10-27 10:00 | 30.25 | 46 | 100 | 26.1345 | 18.7197 | 49.451 | 102.3588 | 102.3588 | 0 | 0
2025-10-27 11:00 | 31.55 | 41.5 | 100 | 26.5601 | 18.7424 | 47.569 | 94.8787 | 94.8787 | 0 | 0
2025-10-27 12:00 | 32.4 | 39.5 | 100 | 26.8329 | 18.8213 | 46.7682 | 94.1465 | 94.1465 | 0 | 0
2025-10-27 13:00 | 32.5 | 41.5 | 100 | 26.8586 | 19.0349 | 47.878 | 106.9699 | 106.9699 | 0 | 0
2025-10-27 14:00 | 31.95 | 46 | 100 | 26.675 | 19.2645 | 50.077 | 125.2576 | 125.2576 | 0 | 0
2025-10-27 15:00 | 31.35 | 49.5 | 100 | 26.4784 | 19.3705 | 51.6561 | 136.1165 | 136.1165 | 0 | 0
2025-10-27 16:00 | 30.8 | 52.5 | 100 | 26.2982 | 19.4358 | 52.9445 | 144.1357 | 144.1357 | 0 | 0
2025-10-27 17:00 | 29.85 | 57.5 | 100 | 25.9858 | 19.5083 | 54.9756 | 155.4378 | 155.4378 | 0 | 0
2025-10-27 18:00 | 29.05 | 61.5 | 100 | 25.7213 | 19.5296 | 56.49 | 162.4718 | 162.4718 | 0 | 0
2025-10-27 19:00 | 28.65 | 64 | 100 | 25.5878 | 19.5701 | 57.4491 | 167.8704 | 167.8704 | 0 | 0
2025-10-27 20:00 | 28.1 | 68 | 100 | 25.4029 | 19.6544 | 58.9876 | 177.2827 | 177.2827 | 0 | 0
2025-10-27 21:00 | 27.6 | 69.5 | 100 | 25.2362 | 19.572 | 59.3802 | 175.6357 | 175.6357 | 0 | 0
2025-10-27 22:00 | 27.15 | 69.5 | 70 | 25.0862 | 19.4029 | 59.1285 | 117.6895 | 117.6895 | 0 | 0
2025-10-27 23:00 | 26.7 | 70.5 | 70 | 24.9342 | 19.3017 | 59.3238 | 115.5078 | 115.5078 | 0 | 0
2025-10-28 | 26.1 | 72.5 | 70 | 24.7296 | 19.2071 | 59.8628 | 114.4472 | 114.4472 | 0 | 0
2025-10-28 01:00 | 25.35 | 75.5 | 70 | 24.4713 | 19.1129 | 60.7211 | 114.2457 | 114.2457 | 0 | 0
2025-10-28 02:00 | 24.55 | 79.5 | 70 | 24.1929 | 19.0504 | 61.922 | 115.7506 | 115.7506 | 0 | 0
2025-10-28 03:00 | 23.85 | 83 | 70 | 23.9472 | 18.983 | 62.9249 | 116.5675 | 116.5675 | 0 | 0
2025-10-28 04:00 | 23.5 | 84.5 | 70 | 23.8234 | 18.9315 | 63.3125 | 116.1714 | 116.1714 | 0 | 0
2025-10-28 05:00 | 23.25 | 85.5 | 70 | 23.7347 | 18.8894 | 63.5556 | 115.6478 | 115.6478 | 0 | 0
2025-10-28 06:00 | 23.25 | 85 | 100 | 23.7346 | 18.8615 | 63.358 | 163.3753 | 163.3753 | 0 | 0
2025-10-28 07:00 | 24.7 | 78 | 100 | 24.2454 | 19.0179 | 61.3854 | 162.0165 | 162.0165 | 0 | 0
2025-10-28 08:00 | 27.45 | 66.5 | 100 | 25.1889 | 19.3083 | 57.9458 | 159.759 | 159.759 | 0 | 0
2025-10-28 09:00 | 29.95 | 57.5 | 100 | 26.018 | 19.5455 | 55.0043 | 156.7629 | 156.7629 | 0 | 0
2025-10-28 10:00 | 31.9 | 49.5 | 100 | 26.6506 | 19.5564 | 51.8748 | 143.8062 | 143.8062 | 0 | 0
2025-10-28 11:00 | 33.2 | 44 | 100 | 27.0671 | 19.4882 | 49.481 | 130.7087 | 130.7087 | 0 | 0
2025-10-28 12:00 | 33.6 | 44 | 100 | 27.1888 | 19.6156 | 49.6513 | 136.2941 | 136.2941 | 0 | 0
2025-10-28 13:00 | 33.15 | 48 | 100 | 27.0392 | 19.8379 | 51.6628 | 153.6953 | 153.6953 | 0 | 0
2025-10-28 14:00 | 32.5 | 49.5 | 100 | 26.8361 | 19.755 | 52.1706 | 152.8161 | 152.8161 | 0 | 0
2025-10-28 15:00 | 32.2 | 49.5 | 100 | 26.7437 | 19.6541 | 52.0331 | 148.4246 | 148.4246 | 0 | 0
2025-10-28 16:00 | 31.35 | 53.5 | 100 | 26.4693 | 19.7072 | 53.7162 | 157.7228 | 157.7228 | 0 | 0
2025-10-28 17:00 | 30.4 | 57.5 | 100 | 26.1615 | 19.7021 | 55.2561 | 164.0279 | 164.0279 | 0 | 0
2025-10-28 18:00 | 29.9 | 60.5 | 100 | 25.9969 | 19.7597 | 56.4638 | 171.2182 | 171.2182 | 0 | 0
2025-10-28 19:00 | 29.3 | 63.5 | 100 | 25.7995 | 19.7705 | 57.5748 | 176.1509 | 176.1509 | 0 | 0
2025-10-28 20:00 | 28.6 | 66.5 | 100 | 25.5684 | 19.7334 | 58.5864 | 178.768 | 178.768 | 0 | 0
2025-10-28 21:00 | 27.95 | 68.5 | 100 | 25.3529 | 19.6336 | 59.13 | 177.0419 | 177.0419 | 0 | 0
2025-10-28 22:00 | 27.45 | 70 | 70 | 25.1859 | 19.55 | 59.5194 | 122.7373 | 122.7373 | 0 | 0
2025-10-28 23:00 | 27 | 72 | 70 | 25.0341 | 19.5157 | 60.1495 | 123.5433 | 123.5433 | 0 | 0
2025-10-29 | 26.55 | 74 | 70 | 24.8814 | 19.4771 | 60.7622 | 124.1621 | 124.1621 | 0 | 0
2025-10-29 01:00 | 26.05 | 76 | 70 | 24.7109 | 19.4141 | 61.3297 | 124.0046 | 124.0046 | 0 | 0
2025-10-29 02:00 | 25.4 | 78.5 | 70 | 24.4876 | 19.3196 | 62.0013 | 123.2515 | 123.2515 | 0 | 0
2025-10-29 03:00 | 24.6 | 80.5 | 70 | 24.2103 | 19.1296 | 62.3561 | 119.0435 | 119.0435 | 0 | 0
2025-10-29 04:00 | 24.15 | 81.5 | 70 | 24.0527 | 19.0132 | 62.4997 | 116.2681 | 116.2681 | 0 | 0
2025-10-29 05:00 | 23.85 | 83 | 70 | 23.9472 | 18.9835 | 62.9221 | 116.5489 | 116.5489 | 0 | 0
2025-10-29 06:00 | 23.5 | 84.5 | 100 | 23.8234 | 18.9314 | 63.307 | 165.9059 | 165.9059 | 0 | 0
2025-10-29 07:00 | 24.6 | 79.5 | 100 | 24.2104 | 19.0701 | 61.9393 | 166.106 | 166.106 | 0 | 0
2025-10-29 08:00 | 27.25 | 68.5 | 100 | 25.1204 | 19.3727 | 58.7319 | 165.3265 | 165.3265 | 0 | 0
2025-10-29 09:00 | 29.75 | 60.5 | 100 | 25.9489 | 19.707 | 56.3623 | 168.5885 | 168.5885 | 0 | 0
2025-10-29 10:00 | 31.55 | 55 | 100 | 26.5283 | 19.9044 | 54.5672 | 168.6504 | 168.6504 | 0 | 0
2025-10-29 11:00 | 32.75 | 50.5 | 100 | 26.9099 | 19.9296 | 52.8147 | 162.1155 | 162.1155 | 0 | 0
2025-10-29 12:00 | 33.2 | 47.5 | 100 | 27.056 | 19.8094 | 51.408 | 151.4413 | 151.4413 | 0 | 0
2025-10-29 13:00 | 32.95 | 46 | 100 | 26.9844 | 19.5896 | 50.4825 | 139.1208 | 139.1208 | 0 | 0
2025-10-29 14:00 | 32.45 | 47.5 | 100 | 26.8263 | 19.5608 | 51.0804 | 140.7261 | 140.7261 | 0 | 0
2025-10-29 15:00 | 32 | 49 | 100 | 26.683 | 19.5431 | 51.6817 | 142.7495 | 142.7495 | 0 | 0
2025-10-29 16:00 | 31.5 | 50 | 100 | 26.5244 | 19.462 | 51.9848 | 141.0488 | 141.0488 | 0 | 0
2025-10-29 17:00 | 30.65 | 52 | 100 | 26.2515 | 19.3435 | 52.6316 | 139.3776 | 139.3776 | 0 | 0
2025-10-29 18:00 | 29.95 | 54.5 | 100 | 26.023 | 19.3064 | 53.5586 | 141.9018 | 141.9018 | 0 | 0
2025-10-29 19:00 | 29.5 | 58.5 | 100 | 25.8715 | 19.4625 | 55.2871 | 154.981 | 154.981 | 0 | 0
2025-10-29 20:00 | 28.85 | 63.5 | 100 | 25.6536 | 19.606 | 57.3289 | 168.8181 | 168.8181 | 0 | 0
2025-10-29 21:00 | 28.1 | 67.5 | 100 | 25.4034 | 19.6187 | 58.7676 | 175.0897 | 175.0897 | 0 | 0
2025-10-29 22:00 | 27.55 | 70 | 70 | 25.2191 | 19.5874 | 59.5862 | 123.9844 | 123.9844 | 0 | 0
2025-10-29 23:00 | 27.1 | 72 | 70 | 25.0675 | 19.5533 | 60.2184 | 124.8105 | 124.8105 | 0 | 0
2025-10-30 | 26.6 | 74 | 70 | 24.8983 | 19.4956 | 60.8039 | 124.8497 | 124.8497 | 0 | 0
2025-10-30 01:00 | 26.25 | 76 | 70 | 24.7788 | 19.4913 | 61.4616 | 126.5191 | 126.5191 | 0 | 0
2025-10-30 02:00 | 25.95 | 78 | 70 | 24.676 | 19.5024 | 62.1341 | 128.6433 | 128.6433 | 0 | 0
2025-10-30 03:00 | 25.5 | 77.5 | 70 | 24.5223 | 19.2958 | 61.6534 | 121.7317 | 121.7317 | 0 | 0
2025-10-30 04:00 | 25.05 | 77 | 70 | 24.3672 | 19.0911 | 61.1896 | 114.9595 | 114.9595 | 0 | 0
2025-10-30 05:00 | 24.55 | 79 | 70 | 24.193 | 19.0196 | 61.7277 | 114.4626 | 114.4626 | 0 | 0
2025-10-30 06:00 | 24.15 | 80.5 | 100 | 24.0528 | 18.9545 | 62.1032 | 162.3619 | 162.3619 | 0 | 0
2025-10-30 07:00 | 25.2 | 76 | 100 | 24.4194 | 19.0874 | 60.8462 | 162.6771 | 162.6771 | 0 | 0
2025-10-30 08:00 | 27.6 | 67.5 | 100 | 25.238 | 19.4328 | 58.4829 | 166.7386 | 166.7386 | 0 | 0
2025-10-30 09:00 | 29.9 | 60 | 100 | 25.9977 | 19.7222 | 56.206 | 168.5726 | 168.5726 | 0 | 0
2025-10-30 10:00 | 31.65 | 51 | 100 | 26.569 | 19.6008 | 52.5483 | 148.451 | 148.451 | 0 | 0
2025-10-30 11:00 | 32.7 | 44.5 | 100 | 26.9121 | 19.3733 | 49.5586 | 126.8459 | 126.8459 | 0 | 0
2025-10-30 12:00 | 33 | 42 | 100 | 27.012 | 19.2377 | 48.3178 | 116.3156 | 116.3156 | 0 | 0
2025-10-30 13:00 | 32.85 | 41 | 100 | 26.9687 | 19.0977 | 47.7234 | 108.5312 | 108.5312 | 0 | 0
2025-10-30 14:00 | 32.45 | 42.5 | 100 | 26.8403 | 19.1109 | 48.3989 | 112.0877 | 112.0877 | 0 | 0
2025-10-30 15:00 | 32 | 45.5 | 100 | 26.692 | 19.2365 | 49.8324 | 123.1373 | 123.1373 | 0 | 0
2025-10-30 16:00 | 31.3 | 50 | 100 | 26.4615 | 19.3957 | 51.892 | 138.1023 | 138.1023 | 0 | 0
2025-10-30 17:00 | 30.3 | 55.5 | 100 | 26.1334 | 19.5075 | 54.2109 | 152.2028 | 152.2028 | 0 | 0
2025-10-30 18:00 | 29.65 | 59 | 100 | 25.9191 | 19.5545 | 55.6006 | 159.7529 | 159.7529 | 0 | 0
2025-10-30 19:00 | 29.15 | 61.5 | 100 | 25.7538 | 19.566 | 56.5377 | 164.0182 | 164.0182 | 0 | 0
2025-10-30 20:00 | 28.4 | 64.5 | 100 | 25.5053 | 19.515 | 57.5431 | 166.109 | 166.109 | 0 | 0
2025-10-30 21:00 | 27.75 | 66.5 | 100 | 25.2887 | 19.4188 | 58.1074 | 164.6572 | 164.6572 | 0 | 0
2025-10-30 22:00 | 27.2 | 68 | 70 | 25.104 | 19.3195 | 58.4856 | 113.6389 | 113.6389 | 0 | 0
2025-10-30 23:00 | 26.55 | 70 | 70 | 24.8838 | 19.2123 | 59.0195 | 112.2449 | 112.2449 | 0 | 0
2025-10-31 | 25.8 | 72.5 | 70 | 24.6271 | 19.0941 | 59.6964 | 110.9344 | 110.9344 | 0 | 0
2025-10-31 01:00 | 25.15 | 75 | 70 | 24.4023 | 19.0063 | 60.3987 | 110.4692 | 110.4692 | 0 | 0
2025-10-31 02:00 | 24.6 | 77.5 | 70 | 24.2106 | 18.949 | 61.1299 | 110.898 | 110.898 | 0 | 0
2025-10-31 03:00 | 23.9 | 79.5 | 70 | 23.9647 | 18.7987 | 61.5598 | 108.0131 | 108.0131 | 0 | 0
2025-10-31 04:00 | 23.5 | 80 | 70 | 23.823 | 18.6728 | 61.5475 | 104.6414 | 104.6414 | 0 | 0
2025-10-31 05:00 | 23.35 | 80.5 | 70 | 23.7697 | 18.6437 | 61.6631 | 104.159 | 104.159 | 0 | 0
2025-10-31 06:00 | 23.3 | 80.5 | 100 | 23.7518 | 18.6252 | 61.6324 | 147.9217 | 147.9217 | 0 | 0
2025-10-31 07:00 | 24.7 | 74.5 | 100 | 24.246 | 18.8047 | 59.9486 | 148.3468 | 148.3468 | 0 | 0
2025-10-31 08:00 | 27.4 | 65 | 100 | 25.1734 | 19.1863 | 57.2366 | 152.1797 | 152.1797 | 0 | 0
2025-10-31 09:00 | 29.8 | 58 | 100 | 25.969 | 19.5328 | 55.1615 | 156.8144 | 156.8144 | 0 | 0
2025-10-31 10:00 | 31.5 | 51.5 | 100 | 26.521 | 19.5938 | 52.7212 | 148.7759 | 148.7759 | 0 | 0
2025-10-31 11:00 | 32.75 | 44.5 | 100 | 26.9275 | 19.3915 | 49.5626 | 127.3544 | 127.3544 | 0 | 0
2025-10-31 12:00 | 33.45 | 40 | 100 | 27.1565 | 19.1909 | 47.3594 | 110.0687 | 110.0687 | 0 | 0
2025-10-31 13:00 | 33.35 | 39 | 100 | 27.1291 | 19.0642 | 46.777 | 102.8446 | 102.8446 | 0 | 0
2025-10-31 14:00 | 32.8 | 40 | 100 | 26.9562 | 18.9902 | 47.1543 | 101.9391 | 101.9391 | 0 | 0
2025-10-31 15:00 | 32.25 | 42.5 | 100 | 26.7779 | 19.0491 | 48.3198 | 109.3761 | 109.3761 | 0 | 0
2025-10-31 16:00 | 31.45 | 45.5 | 100 | 26.5191 | 19.0611 | 49.6152 | 115.5879 | 115.5879 | 0 | 0
2025-10-31 17:00 | 30.5 | 49 | 100 | 26.2095 | 19.0482 | 51.0438 | 121.3638 | 121.3638 | 0 | 0
2025-10-31 18:00 | 29.8 | 52 | 100 | 25.9787 | 19.0592 | 52.2505 | 126.9095 | 126.9095 | 0 | 0
2025-10-31 19:00 | 29.2 | 53.5 | 100 | 25.7813 | 18.9745 | 52.7285 | 125.7562 | 125.7562 | 0 | 0
2025-10-31 20:00 | 28.55 | 55.5 | 100 | 25.5651 | 18.906 | 53.4074 | 126.0139 | 126.0139 | 0 | 0
2025-10-31 21:00 | 27.95 | 58 | 100 | 25.3634 | 18.8834 | 54.3162 | 128.941 | 128.941 | 0 | 0
2025-10-31 22:00 | 27.5 | 60 | 70 | 25.2111 | 18.8698 | 55.0349 | 91.9687 | 91.9687 | 0 | 0
2025-10-31 23:00 | 27.05 | 62 | 70 | 25.0581 | 18.8514 | 55.7373 | 93.4906 | 93.4906 | 0 | 0
2025-11-01 | 26.65 | 63.5 | 70 | 24.9216 | 18.8116 | 56.2255 | 93.8441 | 93.8441 | 0 | 0
2025-11-01 01:00 | 26.25 | 65 | 70 | 24.7845 | 18.7688 | 56.7023 | 94.0719 | 94.0719 | 0 | 0
2025-11-01 02:00 | 25.75 | 67.5 | 70 | 24.6118 | 18.7525 | 57.5471 | 95.979 | 95.979 | 0 | 0
2025-11-01 03:00 | 24.55 | 71 | 70 | 24.1939 | 18.5327 | 58.4569 | 92.7146 | 92.7146 | 0 | 0
2025-11-01 04:00 | 23.35 | 74.5 | 70 | 23.7689 | 18.2969 | 59.3201 | 88.8613 | 88.8613 | 0 | 0
2025-11-01 05:00 | 22.9 | 77 | 70 | 23.608 | 18.2726 | 60.087 | 90.2229 | 90.2229 | 0 | 0
2025-11-01 06:00 | 22.85 | 78 | 100 | 23.5902 | 18.3106 | 60.4434 | 131.608 | 131.608 | 0 | 0
2025-11-01 07:00 | 24.2 | 73 | 100 | 24.0706 | 18.5256 | 59.0935 | 134.5209 | 134.5209 | 0 | 0
2025-11-01 08:00 | 27 | 63 | 100 | 25.0405 | 18.9039 | 56.1468 | 137.0627 | 137.0627 | 0 | 0
2025-11-01 09:00 | 29.75 | 54 | 100 | 25.9594 | 19.2029 | 53.1814 | 135.9729 | 135.9729 | 0 | 0
2025-11-01 10:00 | 31.8 | 45.5 | 100 | 26.6294 | 19.1772 | 49.7169 | 119.9931 | 119.9931 | 0 | 0
2025-11-01 11:00 | 33.1 | 38.5 | 100 | 27.0536 | 18.9438 | 46.406 | 96.5644 | 96.5644 | 0 | 0
2025-11-01 12:00 | 33.5 | 35.5 | 100 | 27.1866 | 18.7735 | 44.8638 | 83.353 | 83.353 | 0 | 0
2025-11-01 13:00 | 33.4 | 34.5 | 100 | 27.159 | 18.6458 | 44.2864 | 76.1822 | 76.1822 | 0 | 0
2025-11-01 14:00 | 33.1 | 35 | 100 | 27.0644 | 18.6076 | 44.4947 | 75.8357 | 75.8357 | 0 | 0
2025-11-01 15:00 | 32.5 | 38 | 100 | 26.8684 | 18.7142 | 45.9778 | 86.5533 | 86.5533 | 0 | 0
2025-11-01 16:00 | 31.55 | 43 | 100 | 26.5566 | 18.8756 | 48.3435 | 103.0852 | 103.0852 | 0 | 0
2025-11-01 17:00 | 30.5 | 48.5 | 100 | 26.2104 | 19.0079 | 50.7848 | 118.6656 | 118.6656 | 0 | 0
2025-11-01 18:00 | 29.7 | 52.5 | 100 | 25.9456 | 19.0658 | 52.4452 | 127.905 | 127.905 | 0 | 0
2025-11-01 19:00 | 29.2 | 54 | 100 | 25.7806 | 19.014 | 52.9621 | 128.1389 | 128.1389 | 0 | 0
2025-11-01 20:00 | 28.65 | 56 | 100 | 25.5975 | 18.9782 | 53.679 | 129.791 | 129.791 | 0 | 0
2025-11-01 21:00 | 27.7 | 58.5 | 100 | 25.2794 | 18.8331 | 54.4353 | 127.5125 | 127.5125 | 0 | 0
2025-11-01 22:00 | 26.95 | 59.5 | 70 | 25.026 | 18.6423 | 54.5811 | 84.7439 | 84.7439 | 0 | 0
2025-11-01 23:00 | 26.6 | 61.5 | 70 | 24.9058 | 18.6574 | 55.3233 | 87.261 | 87.261 | 0 | 0
2025-11-02 | 26.2 | 65.5 | 70 | 24.7671 | 18.7843 | 56.8898 | 94.9697 | 94.9697 | 0 | 0
2025-11-02 01:00 | 25.8 | 69.5 | 70 | 24.6282 | 18.9008 | 58.4138 | 102.2438 | 102.2438 | 0 | 0
2025-11-02 02:00 | 25.45 | 72.5 | 70 | 24.5067 | 18.9627 | 59.5041 | 106.8537 | 106.8537 | 0 | 0
2025-11-02 03:00 | 25.15 | 71 | 70 | 24.4033 | 18.7556 | 58.7294 | 99.2676 | 99.2676 | 0 | 0
2025-11-02 04:00 | 25.05 | 69 | 70 | 24.369 | 18.5928 | 57.8528 | 92.5981 | 92.5981 | 0 | 0
2025-11-02 05:00 | 25.05 | 71 | 70 | 24.3686 | 18.7187 | 58.6787 | 98.1384 | 98.1384 | 0 | 0
2025-11-02 06:00 | 25.1 | 72 | 100 | 24.3857 | 18.8003 | 59.1125 | 144.9178 | 144.9178 | 0 | 0
2025-11-02 07:00 | 26.2 | 68.5 | 100 | 24.7656 | 18.9839 | 58.1704 | 148.1524 | 148.1524 | 0 | 0
2025-11-02 08:00 | 28.25 | 60.5 | 100 | 25.4604 | 19.1726 | 55.5878 | 144.8561 | 144.8561 | 0 | 0
2025-11-02 09:00 | 30.05 | 50 | 100 | 26.0629 | 18.985 | 51.337 | 119.9624 | 119.9624 | 0 | 0
2025-11-02 10:00 | 31.35 | 40 | 100 | 26.4999 | 18.5535 | 46.7007 | 83.8193 | 83.8193 | 0 | 0
2025-11-02 11:00 | 32.05 | 35 | 100 | 26.7345 | 18.3074 | 44.2443 | 63.9154 | 63.9154 | 0 | 0
2025-11-02 12:00 | 32.1 | 35.5 | 100 | 26.7491 | 18.3669 | 44.5268 | 67.3903 | 67.3903 | 0 | 0
2025-11-02 13:00 | 31.85 | 39 | 100 | 26.6611 | 18.613 | 46.3264 | 84.4102 | 84.4102 | 0 | 0
2025-11-02 14:00 | 31.5 | 42 | 100 | 26.543 | 18.7731 | 47.8013 | 96.8724 | 96.8724 | 0 | 0
2025-11-02 15:00 | 31.05 | 44 | 100 | 26.3954 | 18.8058 | 48.6946 | 102.0806 | 102.0806 | 0 | 0
2025-11-02 16:00 | 30.3 | 46.5 | 100 | 26.1498 | 18.7781 | 49.7113 | 105.5469 | 105.5469 | 0 | 0
2025-11-02 17:00 | 29.3 | 50 | 100 | 25.819 | 18.7352 | 51.0827 | 109.921 | 109.921 | 0 | 0
2025-11-02 18:00 | 28.35 | 54 | 100 | 25.5006 | 18.7249 | 52.6296 | 116.1025 | 116.1025 | 0 | 0
2025-11-02 19:00 | 27.55 | 57 | 100 | 25.2305 | 18.6732 | 53.698 | 118.5856 | 118.5856 | 0 | 0
2025-11-02 20:00 | 26.95 | 59 | 100 | 25.0264 | 18.6075 | 54.3568 | 118.8446 | 118.8446 | 0 | 0
2025-11-02 21:00 | 26.5 | 58.5 | 100 | 24.8734 | 18.417 | 53.9642 | 110.2363 | 110.2363 | 0 | 0
2025-11-02 22:00 | 26.15 | 57 | 70 | 24.7541 | 18.1944 | 53.1916 | 69.2942 | 69.2942 | 0 | 0
2025-11-02 23:00 | 25.65 | 58.5 | 70 | 24.5806 | 18.1249 | 53.6734 | 68.916 | 68.916 | 0 | 0
2025-11-03 | 24.95 | 61 | 70 | 24.3357 | 18.0469 | 54.4951 | 69.276 | 69.276 | 0 | 0
2025-11-03 01:00 | 24.35 | 62.5 | 70 | 24.1242 | 17.9332 | 54.9167 | 67.591 | 67.591 | 0 | 0
2025-11-03 02:00 | 23.75 | 65.5 | 70 | 23.911 | 17.9074 | 55.9248 | 69.7089 | 69.7089 | 0 | 0
2025-11-03 03:00 | 23.35 | 67.5 | 70 | 23.7681 | 17.8849 | 56.5781 | 70.9202 | 70.9202 | 0 | 0
2025-11-03 04:00 | 23.1 | 66.5 | 70 | 23.6781 | 17.7367 | 56.105 | 65.8942 | 65.8942 | 0 | 0
2025-11-03 05:00 | 22.55 | 66.5 | 70 | 23.479 | 17.5419 | 55.9345 | 60.546 | 60.546 | 0 | 0
2025-11-03 06:00 | 22.4 | 66.5 | 100 | 23.4244 | 17.4893 | 55.8869 | 84.4024 | 84.4024 | 0 | 0
2025-11-03 07:00 | 23.85 | 61.5 | 100 | 23.9465 | 17.6983 | 54.3533 | 85.839 | 85.839 | 0 | 0
2025-11-03 08:00 | 26.55 | 52.5 | 100 | 24.894 | 18.0164 | 51.3503 | 85.0095 | 85.0095 | 0 | 0
2025-11-03 09:00 | 28.95 | 47 | 100 | 25.7079 | 18.3871 | 49.516 | 90.4372 | 90.4372 | 0 | 0
2025-11-03 10:00 | 30.55 | 44 | 100 | 26.2351 | 18.6501 | 48.5221 | 95.5297 | 95.5297 | 0 | 0
2025-11-03 11:00 | 31.5 | 41 | 100 | 26.5454 | 18.6859 | 47.2733 | 91.2729 | 91.2729 | 0 | 0
2025-11-03 12:00 | 31.9 | 40 | 100 | 26.6745 | 18.7174 | 46.8708 | 90.6735 | 90.6735 | 0 | 0
2025-11-03 13:00 | 31.95 | 40.5 | 100 | 26.689 | 18.7767 | 47.1549 | 94.1641 | 94.1641 | 0 | 0
2025-11-03 14:00 | 31.7 | 42 | 100 | 26.6064 | 18.8338 | 47.8718 | 99.4838 | 99.4838 | 0 | 0
2025-11-03 15:00 | 31.4 | 43.5 | 100 | 26.5079 | 18.8719 | 48.5598 | 103.966 | 103.966 | 0 | 0
2025-11-03 16:00 | 30.95 | 45 | 100 | 26.3614 | 18.8581 | 49.1826 | 106.2621 | 106.2621 | 0 | 0
2025-11-03 17:00 | 30.25 | 47.5 | 100 | 26.1319 | 18.8431 | 50.2011 | 110.1572 | 110.1572 | 0 | 0
2025-11-03 18:00 | 29.7 | 51 | 100 | 25.9479 | 18.9459 | 51.7207 | 120.4545 | 120.4545 | 0 | 0
2025-11-03 19:00 | 29.05 | 55.5 | 100 | 25.7295 | 19.0776 | 53.62 | 133.3128 | 133.3128 | 0 | 0
2025-11-03 20:00 | 28.3 | 59 | 100 | 25.4785 | 19.0794 | 54.9293 | 138.7671 | 138.7671 | 0 | 0
2025-11-03 21:00 | 27.85 | 60 | 100 | 25.3281 | 18.9935 | 55.1858 | 136.5935 | 136.5935 | 0 | 0
2025-11-03 22:00 | 27.5 | 60.5 | 70 | 25.2107 | 18.9058 | 55.2592 | 93.5309 | 93.5309 | 0 | 0
2025-11-03 23:00 | 27 | 61.5 | 70 | 25.0415 | 18.799 | 55.4907 | 91.409 | 91.409 | 0 | 0
2025-11-04 | 26.4 | 63 | 70 | 24.8368 | 18.6887 | 55.8951 | 89.6845 | 89.6845 | 0 | 0
2025-11-04 01:00 | 25.7 | 65.5 | 70 | 24.5953 | 18.604 | 56.6725 | 89.6614 | 89.6614 | 0 | 0
2025-11-04 02:00 | 24.7 | 70 | 70 | 24.2466 | 18.5265 | 58.1117 | 91.5922 | 91.5922 | 0 | 0
2025-11-04 03:00 | 23.6 | 73 | 70 | 23.858 | 18.3023 | 58.8359 | 87.6888 | 87.6888 | 0 | 0
2025-11-04 04:00 | 22.9 | 73.5 | 70 | 23.6073 | 18.072 | 58.7394 | 81.4766 | 81.4766 | 0 | 0
2025-11-04 05:00 | 22.45 | 75.5 | 70 | 23.4451 | 18.0187 | 59.3176 | 81.6078 | 81.6078 | 0 | 0
2025-11-04 06:00 | 22.15 | 77.5 | 100 | 23.3367 | 18.0183 | 59.9411 | 118.8392 | 118.8392 | 0 | 0
2025-11-04 07:00 | 23.45 | 72 | 100 | 23.8044 | 18.1882 | 58.3629 | 119.133 | 119.133 | 0 | 0
2025-11-04 08:00 | 26.45 | 59.5 | 100 | 24.8558 | 18.4696 | 54.3725 | 113.7178 | 113.7178 | 0 | 0
2025-11-04 09:00 | 28.95 | 50.5 | 100 | 25.7033 | 18.6615 | 51.1742 | 107.3703 | 107.3703 | 0 | 0
2025-11-04 10:00 | 30.55 | 43.5 | 100 | 26.236 | 18.6092 | 48.2612 | 92.7982 | 92.7982 | 0 | 0
2025-11-04 11:00 | 32.1 | 35.5 | 100 | 26.7491 | 18.3684 | 44.5192 | 67.3062 | 67.3062 | 0 | 0
2025-11-04 12:00 | 33.35 | 31 | 100 | 27.1547 | 18.2898 | 42.3183 | 54.2418 | 54.2418 | 0 | 0
2025-11-04 13:00 | 34.45 | 26.5 | 100 | 27.5112 | 18.123 | 39.934 | 36.9756 | 36.9756 | 0 | 0
2025-11-04 14:00 | 34.65 | 24 | 100 | 27.5825 | 17.9069 | 38.5064 | 22.6137 | 22.6137 | 0 | 0
2025-11-04 15:00 | 33 | 35.5 | 100 | 27.0317 | 18.6262 | 44.7444 | 77.6694 | 77.6694 | 0 | 0
2025-11-04 16:00 | 31.1 | 50 | 100 | 26.3985 | 19.3315 | 51.7848 | 135.0001 | 135.0001 | 0 | 0
2025-11-04 17:00 | 29.8 | 55 | 100 | 25.9739 | 19.2969 | 53.7097 | 141.9173 | 141.9173 | 0 | 0
2025-11-04 18:00 | 28.85 | 54.5 | 100 | 25.6652 | 18.933 | 53.0587 | 125.5548 | 125.5548 | 0 | 0
2025-11-04 19:00 | 28.1 | 51 | 100 | 25.4205 | 18.4175 | 51.1455 | 98.5947 | 98.5947 | 0 | 0
2025-11-04 20:00 | 27.1 | 45 | 100 | 25.0874 | 17.6527 | 48.1513 | 58.7075 | 58.7075 | 0 | 0
2025-11-04 21:00 | 26.15 | 38.5 | 100 | 24.7629 | 16.8936 | 45.1501 | 19.9165 | 19.9165 | 0 | 0
2025-11-04 22:00 | 25.5 | 36.5 | 70 | 24.5354 | 16.5649 | 44.263 | 3.6475 | 3.6475 | 0 | 0
2025-11-04 23:00 | 24.8 | 38.5 | 70 | 24.2867 | 16.5054 | 45.1024 | 4.8436 | 4.8436 | 0 | 0
2025-11-05 | 24.15 | 39 | 70 | 24.054 | 16.3528 | 45.3074 | 1.9794 | 1.9794 | 0 | 0
2025-11-05 01:00 | 23.55 | 37.5 | 70 | 23.8372 | 16.0826 | 44.7185 | 0 | 0 | 0 | 0
2025-11-05 02:00 | 22.95 | 37 | 70 | 23.6184 | 15.8816 | 44.558 | 0 | 0 | 0 | 0
2025-11-05 03:00 | 22.75 | 36 | 70 | 23.5448 | 15.7627 | 44.1819 | 0 | 0 | 0 | 0
2025-11-05 04:00 | 22.8 | 36 | 70 | 23.5632 | 15.7765 | 44.1765 | 0 | 0 | 0 | 0
2025-11-05 05:00 | 22.35 | 40 | 70 | 23.3987 | 15.8997 | 45.7565 | 0 | 0 | 0 | 0
2025-11-05 06:00 | 21.9 | 44 | 100 | 23.2336 | 16.0116 | 47.2908 | 0 | 0 | 0 | 0
2025-11-05 07:00 | 23.15 | 42 | 100 | 23.6923 | 16.2581 | 46.5038 | 4.7188 | 4.7188 | 0 | 0
2025-11-05 08:00 | 25.95 | 35.5 | 100 | 24.6942 | 16.6205 | 43.83 | 5.0569 | 5.0569 | 0 | 0
2025-11-05 09:00 | 28.85 | 29.5 | 100 | 25.6969 | 16.9424 | 41.1201 | 3.2359 | 3.2359 | 0 | 0
2025-11-05 10:00 | 31.35 | 24.5 | 100 | 26.5343 | 17.1393 | 38.6301 | 0 | 0 | 0 | 0
2025-11-05 11:00 | 33.3 | 19 | 100 | 27.1769 | 17.0573 | 35.6144 | 0 | 0 | 0 | 0
2025-11-05 12:00 | 34.45 | 15.5 | 100 | 27.5527 | 16.931 | 33.5464 | 0 | 0 | 0 | 0
2025-11-05 13:00 | 34.7 | 16.5 | 100 | 27.6273 | 17.0946 | 34.119 | 0 | 0 | 0 | 0
2025-11-05 14:00 | 34 | 20.5 | 100 | 27.3933 | 17.3728 | 36.4642 | 0 | 0 | 0 | 0
2025-11-05 15:00 | 32.65 | 28 | 100 | 26.9437 | 17.8023 | 40.5886 | 29.5266 | 29.5266 | 0 | 0
2025-11-05 16:00 | 30.95 | 40 | 100 | 26.3718 | 18.4281 | 46.6252 | 79.3566 | 79.3566 | 0 | 0
2025-11-05 17:00 | 29.1 | 51 | 100 | 25.752 | 18.7463 | 51.4978 | 112.1792 | 112.1792 | 0 | 0
2025-11-05 18:00 | 27.8 | 59 | 100 | 25.3124 | 18.9032 | 54.719 | 131.4018 | 131.4018 | 0 | 0
2025-11-05 19:00 | 26.95 | 65 | 100 | 25.0222 | 19.0226 | 57.0229 | 145.1667 | 145.1667 | 0 | 0
2025-11-05 20:00 | 25.9 | 66.5 | 100 | 24.6638 | 18.7419 | 57.1815 | 135.219 | 135.219 | 0 | 0
2025-11-05 21:00 | 24.85 | 64.5 | 100 | 24.3 | 18.236 | 55.9052 | 111.413 | 111.413 | 0 | 0
2025-11-05 22:00 | 24.2 | 63.5 | 70 | 24.071 | 17.9433 | 55.2664 | 68.7821 | 68.7821 | 0 | 0
2025-11-05 23:00 | 23.55 | 65.5 | 70 | 23.8395 | 17.8366 | 55.853 | 67.7019 | 67.7019 | 0 | 0
2025-11-06 | 22.65 | 66 | 70 | 23.5152 | 17.5485 | 55.7695 | 60.2465 | 60.2465 | 0 | 0
2025-11-06 01:00 | 21.8 | 61.5 | 70 | 23.203 | 16.9964 | 53.8614 | 41.4896 | 41.4896 | 0 | 0
2025-11-06 02:00 | 21.05 | 56 | 70 | 22.9225 | 16.4381 | 51.7244 | 22.325 | 22.325 | 0 | 0
2025-11-06 03:00 | 20.75 | 58.5 | 70 | 22.8116 | 16.4775 | 52.6006 | 25.6544 | 25.6544 | 0 | 0
2025-11-06 04:00 | 20.95 | 65 | 70 | 22.8895 | 16.8995 | 54.9815 | 42.168 | 42.168 | 0 | 0
2025-11-06 05:00 | 20.8 | 68.5 | 70 | 22.8354 | 17.0364 | 56.2093 | 48.7455 | 48.7455 | 0 | 0
2025-11-06 06:00 | 20.45 | 68.5 | 100 | 22.7045 | 16.9137 | 56.1229 | 64.972 | 64.972 | 0 | 0
2025-11-06 07:00 | 21.75 | 59.5 | 100 | 23.1838 | 16.8666 | 53.0964 | 51.7391 | 51.7391 | 0 | 0
2025-11-06 08:00 | 24.8 | 46.5 | 100 | 24.2854 | 17.0468 | 48.4309 | 39.0626 | 39.0626 | 0 | 0
2025-11-06 09:00 | 27.85 | 40.5 | 100 | 25.3466 | 17.5424 | 46.2208 | 46.4301 | 46.4301 | 0 | 0
2025-11-06 10:00 | 30.35 | 31.5 | 100 | 26.1932 | 17.5157 | 42.1827 | 27.189 | 27.189 | 0 | 0
2025-11-06 11:00 | 32.25 | 19.5 | 100 | 26.8386 | 16.8667 | 35.9523 | 0 | 0 | 0 | 0
2025-11-06 12:00 | 33.4 | 15 | 100 | 27.2215 | 16.6525 | 33.3731 | 0 | 0 | 0 | 0
2025-11-06 13:00 | 33.7 | 17 | 100 | 27.3106 | 16.9301 | 34.48 | 0 | 0 | 0 | 0
2025-11-06 14:00 | 32.85 | 27 | 100 | 27.01 | 17.7565 | 40.0601 | 25.4054 | 25.4054 | 0 | 0
2025-11-06 15:00 | 31.35 | 34 | 100 | 26.5133 | 18.0117 | 43.6145 | 51.0485 | 51.0485 | 0 | 0
2025-11-06 16:00 | 29.9 | 40 | 100 | 26.0309 | 18.1113 | 46.3818 | 67.1295 | 67.1295 | 0 | 0
2025-11-06 17:00 | 28.5 | 50 | 100 | 25.555 | 18.4716 | 50.8195 | 99.2924 | 99.2924 | 0 | 0
2025-11-06 18:00 | 27.45 | 55 | 100 | 25.1985 | 18.494 | 52.7638 | 108.2325 | 108.2325 | 0 | 0
2025-11-06 19:00 | 26.6 | 57 | 100 | 24.9085 | 18.3471 | 53.3512 | 105.2534 | 105.2534 | 0 | 0
2025-11-06 20:00 | 25.65 | 58.5 | 100 | 24.5806 | 18.1244 | 53.6743 | 98.4604 | 98.4604 | 0 | 0
2025-11-06 21:00 | 24.65 | 58.5 | 100 | 24.2306 | 17.7837 | 53.3662 | 84.9543 | 84.9543 | 0 | 0
2025-11-06 22:00 | 23.85 | 54.5 | 70 | 23.9463 | 17.2624 | 51.5498 | 41.5207 | 41.5207 | 0 | 0
2025-11-06 23:00 | 23.1 | 52.5 | 70 | 23.6758 | 16.8956 | 50.6329 | 30.0902 | 30.0902 | 0 | 0
2025-11-07 | 22.2 | 55.5 | 70 | 23.3481 | 16.784 | 51.6649 | 30.3211 | 30.3211 | 0 | 0
2025-11-07 01:00 | 21.55 | 57 | 70 | 23.1089 | 16.6578 | 52.1407 | 28.6303 | 28.6303 | 0 | 0
2025-11-07 02:00 | 21.05 | 57 | 70 | 22.923 | 16.4941 | 52.0819 | 24.5889 | 24.5889 | 0 | 0
2025-11-07 03:00 | 20.35 | 57.5 | 70 | 22.6608 | 16.2931 | 52.1937 | 20.1497 | 20.1497 | 0 | 0
2025-11-07 04:00 | 19.85 | 59 | 70 | 22.4727 | 16.2092 | 52.6804 | 19.487 | 19.487 | 0 | 0
2025-11-07 05:00 | 19.45 | 61 | 70 | 22.3219 | 16.1815 | 53.3388 | 20.5724 | 20.5724 | 0 | 0
2025-11-07 06:00 | 18.95 | 61 | 100 | 22.1307 | 16.0168 | 53.2942 | 23.6476 | 23.6476 | 0 | 0
2025-11-07 07:00 | 20.15 | 53 | 100 | 22.5828 | 15.9879 | 50.567 | 12.188 | 12.188 | 0 | 0
2025-11-07 08:00 | 23.25 | 40 | 100 | 23.7284 | 16.1613 | 45.7009 | 0 | 0 | 0 | 0
2025-11-07 09:00 | 26.35 | 33.5 | 100 | 24.8352 | 16.5865 | 42.9424 | 0 | 0 | 0 | 0
2025-11-07 10:00 | 28.55 | 27.5 | 100 | 25.5977 | 16.6998 | 40.1561 | 0 | 0 | 0 | 0
2025-11-07 11:00 | 30.15 | 20 | 100 | 26.1471 | 16.435 | 36.3794 | 0 | 0 | 0 | 0
2025-11-07 12:00 | 31.4 | 17 | 100 | 26.5672 | 16.4313 | 34.6939 | 0 | 0 | 0 | 0
2025-11-07 13:00 | 32.2 | 15 | 100 | 26.834 | 16.4025 | 33.5219 | 0 | 0 | 0 | 0
2025-11-07 14:00 | 32.5 | 13.5 | 100 | 26.9356 | 16.3095 | 32.6629 | 0 | 0 | 0 | 0
2025-11-07 15:00 | 32.25 | 16.5 | 100 | 26.8464 | 16.5638 | 34.3332 | 0 | 0 | 0 | 0
2025-11-07 16:00 | 31.1 | 25 | 100 | 26.4517 | 17.1208 | 38.9039 | 0 | 0 | 0 | 0
2025-11-07 17:00 | 29.1 | 36 | 100 | 25.7723 | 17.5475 | 44.2772 | 38.0257 | 38.0257 | 0 | 0
2025-11-07 18:00 | 27.6 | 45 | 100 | 25.2577 | 17.8078 | 48.2461 | 64.4808 | 64.4808 | 0 | 0
2025-11-07 19:00 | 26.75 | 51.5 | 100 | 24.9632 | 18.0124 | 50.956 | 83.1326 | 83.1326 | 0 | 0
2025-11-07 20:00 | 25.9 | 56 | 100 | 24.6682 | 18.0428 | 52.6674 | 91.2648 | 91.2648 | 0 | 0
2025-11-07 21:00 | 25 | 56.5 | 100 | 24.3542 | 17.7735 | 52.619 | 81.4428 | 81.4428 | 0 | 0
2025-11-07 22:00 | 24.15 | 52 | 70 | 24.0536 | 17.203 | 50.5796 | 37.2169 | 37.2169 | 0 | 0
2025-11-07 23:00 | 23.15 | 47 | 70 | 23.6931 | 16.5734 | 48.4604 | 16.1767 | 16.1767 | 0 | 0
2025-11-08 | 22.1 | 47 | 70 | 23.3086 | 16.2522 | 48.4101 | 8.5881 | 8.5881 | 0 | 0
2025-11-08 01:00 | 21.35 | 49.5 | 70 | 23.0315 | 16.168 | 49.3266 | 9.2373 | 9.2373 | 0 | 0
2025-11-08 02:00 | 20.75 | 51 | 70 | 22.8079 | 16.0666 | 49.8607 | 8.3854 | 8.3854 | 0 | 0
2025-11-08 03:00 | 19.9 | 50.5 | 70 | 22.4866 | 15.7754 | 49.6784 | 1.2144 | 1.2144 | 0 | 0
2025-11-08 04:00 | 19.25 | 48 | 70 | 22.237 | 15.4447 | 48.8355 | 0 | 0 | 0 | 0
2025-11-08 05:00 | 19 | 45 | 70 | 22.1389 | 15.2137 | 47.8276 | 0 | 0 | 0 | 0
2025-11-08 06:00 | 18.85 | 42.5 | 100 | 22.0794 | 15.04 | 46.9896 | 0 | 0 | 0 | 0
2025-11-08 07:00 | 20.15 | 37 | 100 | 22.5737 | 15.1102 | 44.8545 | 0 | 0 | 0 | 0
2025-11-08 08:00 | 23.3 | 28.5 | 100 | 23.7452 | 15.4317 | 41.1054 | 0 | 0 | 0 | 0
2025-11-08 09:00 | 26.45 | 24 | 100 | 24.8752 | 15.8979 | 38.7115 | 0 | 0 | 0 | 0
2025-11-08 10:00 | 28.7 | 22 | 100 | 25.6551 | 16.2772 | 37.5011 | 0 | 0 | 0 | 0
2025-11-08 11:00 | 30.4 | 18.5 | 100 | 26.233 | 16.358 | 35.5746 | 0 | 0 | 0 | 0
2025-11-08 12:00 | 31.6 | 16.5 | 100 | 26.634 | 16.4301 | 34.3874 | 0 | 0 | 0 | 0
2025-11-08 13:00 | 32.25 | 15.5 | 100 | 26.8488 | 16.4684 | 33.7701 | 0 | 0 | 0 | 0
2025-11-08 14:00 | 32.15 | 17 | 100 | 26.8125 | 16.5973 | 34.5974 | 0 | 0 | 0 | 0
2025-11-08 15:00 | 31.2 | 23 | 100 | 26.4885 | 16.9618 | 37.8457 | 0 | 0 | 0 | 0
2025-11-08 16:00 | 29.65 | 33 | 100 | 25.9596 | 17.4543 | 42.8592 | 28.1954 | 28.1954 | 0 | 0
2025-11-08 17:00 | 28.1 | 46.5 | 100 | 25.4251 | 18.0797 | 49.0409 | 77.3344 | 77.3344 | 0 | 0
2025-11-08 18:00 | 27.1 | 53 | 100 | 25.0815 | 18.236 | 51.7181 | 94.2328 | 94.2328 | 0 | 0
2025-11-08 19:00 | 26.4 | 52.5 | 100 | 24.8424 | 17.9694 | 51.289 | 82.8794 | 82.8794 | 0 | 0
2025-11-08 20:00 | 25.4 | 53 | 100 | 24.4953 | 17.6757 | 51.2434 | 72.264 | 72.264 | 0 | 0
2025-11-08 21:00 | 24.25 | 54 | 100 | 24.0892 | 17.3649 | 51.4005 | 62.0086 | 62.0086 | 0 | 0
2025-11-08 22:00 | 23.3 | 56.5 | 70 | 23.7487 | 17.2076 | 52.2083 | 41.8728 | 41.8728 | 0 | 0
2025-11-08 23:00 | 22.55 | 58.5 | 70 | 23.477 | 17.078 | 52.8389 | 40.4827 | 40.4827 | 0 | 0
2025-11-09 | 21.65 | 60.5 | 70 | 23.1473 | 16.8914 | 53.4276 | 37.5894 | 37.5894 | 0 | 0
2025-11-09 01:00 | 20.75 | 61.5 | 70 | 22.8132 | 16.644 | 53.6464 | 32.238 | 32.238 | 0 | 0
2025-11-09 02:00 | 20.05 | 61 | 70 | 22.5497 | 16.383 | 53.3764 | 25.3003 | 25.3003 | 0 | 0
2025-11-09 03:00 | 19.65 | 59 | 70 | 22.3968 | 16.1461 | 52.6385 | 17.7453 | 17.7453 | 0 | 0
2025-11-09 04:00 | 19.45 | 57.5 | 70 | 22.3197 | 16.0031 | 52.1053 | 12.9796 | 12.9796 | 0 | 0
2025-11-09 05:00 | 19.25 | 59 | 70 | 22.2443 | 16.0153 | 52.6092 | 14.5997 | 14.5997 | 0 | 0
2025-11-09 06:00 | 19.2 | 59.5 | 100 | 22.2255 | 16.0251 | 52.7725 | 21.7575 | 21.7575 | 0 | 0
2025-11-09 07:00 | 20.45 | 55 | 100 | 22.6972 | 16.1931 | 51.2689 | 21.5558 | 21.5558 | 0 | 0
2025-11-09 08:00 | 23.65 | 46.5 | 100 | 23.8741 | 16.6967 | 48.2821 | 26.3504 | 26.3504 | 0 | 0
2025-11-09 09:00 | 26.95 | 42.5 | 100 | 25.0377 | 17.4271 | 46.9684 | 45.4609 | 45.4609 | 0 | 0
2025-11-09 10:00 | 29.1 | 42 | 100 | 25.7642 | 18.0406 | 47.1323 | 67.4258 | 67.4258 | 0 | 0
2025-11-09 11:00 | 30.5 | 38 | 100 | 26.2302 | 18.1266 | 45.4647 | 63.024 | 63.024 | 0 | 0
2025-11-09 12:00 | 31.2 | 34.5 | 100 | 26.4638 | 18.0209 | 43.8133 | 51.8359 | 51.8359 | 0 | 0
2025-11-09 13:00 | 31.2 | 33.5 | 100 | 26.466 | 17.9293 | 43.3014 | 46.3965 | 46.3965 | 0 | 0
2025-11-09 14:00 | 30.85 | 33.5 | 100 | 26.3527 | 17.8308 | 43.255 | 42.8503 | 42.8503 | 0 | 0
2025-11-09 15:00 | 30.4 | 35 | 100 | 26.2032 | 17.8352 | 43.9549 | 46.2729 | 46.2729 | 0 | 0
2025-11-09 16:00 | 29.75 | 37 | 100 | 25.9864 | 17.8185 | 44.852 | 49.838 | 49.838 | 0 | 0
2025-11-09 17:00 | 28.7 | 39.5 | 100 | 25.6341 | 17.7156 | 45.8896 | 50.9553 | 50.9553 | 0 | 0
2025-11-09 18:00 | 27.7 | 42.5 | 100 | 25.2939 | 17.6501 | 47.1179 | 54.0774 | 54.0774 | 0 | 0
2025-11-09 19:00 | 26.95 | 46.5 | 100 | 25.035 | 17.7171 | 48.782 | 63.5362 | 63.5362 | 0 | 0
2025-11-09 20:00 | 26.3 | 51 | 100 | 24.8088 | 17.8311 | 50.6156 | 75.2435 | 75.2435 | 0 | 0
2025-11-09 21:00 | 25.55 | 54.5 | 100 | 24.5472 | 17.8251 | 51.9262 | 80.4315 | 80.4315 | 0 | 0
2025-11-09 22:00 | 25.05 | 56.5 | 70 | 24.3717 | 17.7904 | 52.6336 | 57.4727 | 57.4727 | 0 | 0
2025-11-09 23:00 | 24.8 | 58 | 70 | 24.2835 | 17.8032 | 53.1891 | 59.3831 | 59.3831 | 0 | 0
2025-11-10 | 24.4 | 59 | 70 | 24.1422 | 17.7315 | 53.4893 | 58.4432 | 58.4432 | 0 | 0
2025-11-10 01:00 | 24.05 | 59.5 | 70 | 24.0178 | 17.6437 | 53.5961 | 56.5608 | 56.5608 | 0 | 0
2025-11-10 02:00 | 23.75 | 60 | 70 | 23.9107 | 17.5718 | 53.7176 | 55.1364 | 55.1364 | 0 | 0
2025-11-10 03:00 | 23.25 | 59.5 | 70 | 23.7311 | 17.3713 | 53.3966 | 49.3063 | 49.3063 | 0 | 0
2025-11-10 04:00 | 22.35 | 61 | 70 | 23.4046 | 17.1556 | 53.7715 | 45.0354 | 45.0354 | 0 | 0
2025-11-10 05:00 | 21.15 | 65 | 70 | 22.964 | 16.9702 | 54.9992 | 43.8083 | 43.8083 | 0 | 0
2025-11-10 06:00 | 20 | 69.5 | 100 | 22.5358 | 16.809 | 56.3554 | 62.0296 | 62.0296 | 0 | 0
2025-11-10 07:00 | 20.75 | 66.5 | 100 | 22.8157 | 16.9137 | 55.4468 | 62.2322 | 62.2322 | 0 | 0
2025-11-10 08:00 | 24.1 | 54.5 | 100 | 24.0357 | 17.3464 | 51.5791 | 62.1671 | 62.1671 | 0 | 0
2025-11-10 09:00 | 27.35 | 44 | 100 | 25.1735 | 17.6583 | 47.7241 | 56.8346 | 56.8346 | 0 | 0
2025-11-10 10:00 | 29.1 | 38 | 100 | 25.7696 | 17.7146 | 45.2193 | 47.7378 | 47.7378 | 0 | 0
2025-11-10 11:00 | 30.1 | 34 | 100 | 26.1066 | 17.6651 | 43.4036 | 37.8348 | 37.8348 | 0 | 0
2025-11-10 12:00 | 30.8 | 31 | 100 | 26.3414 | 17.5931 | 41.9718 | 28.8258 | 28.8258 | 0 | 0
2025-11-10 13:00 | 31.15 | 30.5 | 100 | 26.4563 | 17.6415 | 41.7543 | 29.5043 | 29.5043 | 0 | 0
2025-11-10 14:00 | 30.75 | 33 | 100 | 26.3212 | 17.7564 | 42.9988 | 39.2707 | 39.2707 | 0 | 0
2025-11-10 15:00 | 29.65 | 39 | 100 | 25.9504 | 17.9551 | 45.8279 | 59.0706 | 59.0706 | 0 | 0
2025-11-10 16:00 | 28.8 | 44.5 | 100 | 25.6614 | 18.1413 | 48.2993 | 76.5543 | 76.5543 | 0 | 0
2025-11-10 17:00 | 28.2 | 47.5 | 100 | 25.4576 | 18.185 | 49.5546 | 83.5129 | 83.5129 | 0 | 0
2025-11-10 18:00 | 27.5 | 49 | 100 | 25.2204 | 18.0733 | 50.0531 | 81.6387 | 81.6387 | 0 | 0
2025-11-10 19:00 | 26.7 | 50.5 | 100 | 24.9467 | 17.9242 | 50.5115 | 78.2333 | 78.2333 | 0 | 0
2025-11-10 20:00 | 25.85 | 54 | 100 | 24.6517 | 17.8894 | 51.8063 | 82.3464 | 82.3464 | 0 | 0
2025-11-10 21:00 | 25.2 | 58 | 100 | 24.4239 | 17.9388 | 53.313 | 90.2279 | 90.2279 | 0 | 0
2025-11-10 22:00 | 24.5 | 62 | 70 | 24.1772 | 17.9548 | 54.7473 | 67.5892 | 67.5892 | 0 | 0
2025-11-10 23:00 | 23.7 | 66.5 | 70 | 23.8932 | 17.9507 | 56.2898 | 71.7286 | 71.7286 | 0 | 0
2025-11-11 | 22.85 | 71.5 | 70 | 23.5888 | 17.939 | 57.9367 | 75.8657 | 75.8657 | 0 | 0
2025-11-11 01:00 | 21.85 | 77 | 70 | 23.227 | 17.8783 | 59.6292 | 78.7562 | 78.7562 | 0 | 0
2025-11-11 02:00 | 20.6 | 83.5 | 70 | 22.7686 | 17.7492 | 61.4845 | 80.1955 | 80.1955 | 0 | 0
2025-11-11 03:00 | 19.75 | 86 | 70 | 22.4516 | 17.5482 | 62.0173 | 76.3844 | 76.3844 | 0 | 0
2025-11-11 04:00 | 19.7 | 84 | 70 | 22.4315 | 17.4307 | 61.3091 | 71.6061 | 71.6061 | 0 | 0
2025-11-11 05:00 | 19.75 | 82 | 70 | 22.4491 | 17.3507 | 60.635 | 67.8698 | 67.8698 | 0 | 0
2025-11-11 06:00 | 19.75 | 79.5 | 100 | 22.4476 | 17.2264 | 59.7657 | 89.3024 | 89.3024 | 0 | 0
2025-11-11 07:00 | 21 | 71.5 | 100 | 22.9113 | 17.2697 | 57.3107 | 81.7793 | 81.7793 | 0 | 0
2025-11-11 08:00 | 24.05 | 58 | 100 | 24.0178 | 17.5509 | 52.9784 | 74.9395 | 74.9395 | 0 | 0
2025-11-11 09:00 | 27.25 | 47.5 | 100 | 25.1367 | 17.886 | 49.283 | 71.4637 | 71.4637 | 0 | 0
2025-11-11 10:00 | 29.3 | 38 | 100 | 25.8361 | 17.7736 | 45.2501 | 49.879 | 49.879 | 0 | 0
2025-11-11 11:00 | 30.5 | 29.5 | 100 | 26.2461 | 17.3795 | 41.1758 | 17.8455 | 17.8455 | 0 | 0
2025-11-11 12:00 | 31.3 | 26 | 100 | 26.5147 | 17.2666 | 39.4179 | 5.7928 | 5.7928 | 0 | 0
2025-11-11 13:00 | 31.7 | 26 | 100 | 26.6445 | 17.3673 | 39.4358 | 9.2487 | 9.2487 | 0 | 0
2025-11-11 14:00 | 31.25 | 32.5 | 100 | 26.4844 | 17.8502 | 42.8063 | 41.567 | 41.567 | 0 | 0
2025-11-11 15:00 | 30.1 | 41 | 100 | 26.0946 | 18.2574 | 46.9105 | 74.4851 | 74.4851 | 0 | 0
2025-11-11 16:00 | 29.1 | 46 | 100 | 25.7588 | 18.355 | 49.0916 | 87.55 | 87.55 | 0 | 0
2025-11-11 17:00 | 28.35 | 48 | 100 | 25.5073 | 18.2715 | 49.8246 | 87.7166 | 87.7166 | 0 | 0
2025-11-11 18:00 | 27.6 | 49.5 | 100 | 25.2538 | 18.1431 | 50.3012 | 85.1152 | 85.1152 | 0 | 0
2025-11-11 19:00 | 26.8 | 53 | 100 | 24.9793 | 18.1351 | 51.6376 | 90.387 | 90.387 | 0 | 0
2025-11-11 20:00 | 25.85 | 57 | 100 | 24.6505 | 18.0937 | 53.0845 | 94.8142 | 94.8142 | 0 | 0
2025-11-11 21:00 | 24.9 | 61.5 | 100 | 24.3181 | 18.0632 | 54.6665 | 100.0725 | 100.0725 | 0 | 0
2025-11-11 22:00 | 24.1 | 65.5 | 70 | 24.0355 | 18.0328 | 56.0215 | 73.0287 | 73.0287 | 0 | 0
2025-11-11 23:00 | 23.1 | 69 | 70 | 23.6785 | 17.8851 | 57.0519 | 72.07 | 72.07 | 0 | 0
2025-11-12 | 21.75 | 72.5 | 70 | 23.1887 | 17.5949 | 57.9167 | 67.0246 | 67.0246 | 0 | 0
2025-11-12 01:00 | 20.55 | 73.5 | 70 | 22.7446 | 17.2131 | 57.9075 | 57.4275 | 57.4275 | 0 | 0
2025-11-12 02:00 | 19.8 | 73 | 70 | 22.4624 | 16.9171 | 57.5317 | 49.1281 | 49.1281 | 0 | 0
2025-11-12 03:00 | 19.35 | 69.5 | 70 | 22.2894 | 16.581 | 56.2281 | 37.5608 | 37.5608 | 0 | 0
2025-11-12 04:00 | 18.9 | 67.5 | 70 | 22.1162 | 16.325 | 55.4745 | 29.4602 | 29.4602 | 0 | 0
2025-11-12 05:00 | 18.45 | 70 | 70 | 21.945 | 16.2917 | 56.2437 | 30.6265 | 30.6265 | 0 | 0
2025-11-12 06:00 | 18.35 | 71 | 100 | 21.9072 | 16.3055 | 56.5541 | 45.3079 | 45.3079 | 0 | 0
2025-11-12 07:00 | 19.7 | 65.5 | 100 | 22.4199 | 16.4998 | 54.8898 | 45.7561 | 45.7561 | 0 | 0
2025-11-12 08:00 | 22.85 | 53.5 | 100 | 23.5851 | 16.879 | 50.9502 | 43.392 | 43.392 | 0 | 0
2025-11-12 09:00 | 26.3 | 42 | 100 | 24.8134 | 17.1952 | 46.6596 | 36.2301 | 36.2301 | 0 | 0
2025-11-12 10:00 | 28.9 | 32 | 100 | 25.7105 | 17.1678 | 42.2982 | 15.8257 | 15.8257 | 0 | 0
2025-11-12 11:00 | 30.5 | 24.5 | 100 | 26.2553 | 16.933 | 38.6214 | 0 | 0 | 0 | 0
2025-11-12 12:00 | 31.55 | 20 | 100 | 26.6096 | 16.7602 | 36.2455 | 0 | 0 | 0 | 0
2025-11-12 13:00 | 32.15 | 18 | 100 | 26.8099 | 16.6986 | 35.1335 | 0 | 0 | 0 | 0
2025-11-12 14:00 | 31.6 | 24 | 100 | 26.6167 | 17.1551 | 38.3624 | 0 | 0 | 0 | 0
2025-11-12 15:00 | 30.15 | 34 | 100 | 26.123 | 17.6787 | 43.4102 | 38.3442 | 38.3442 | 0 | 0
2025-11-12 16:00 | 29.05 | 43 | 100 | 25.7463 | 18.103 | 47.621 | 71.9796 | 71.9796 | 0 | 0
2025-11-12 17:00 | 28.2 | 47 | 100 | 25.4582 | 18.1499 | 49.2972 | 80.9011 | 80.9011 | 0 | 0
2025-11-12 18:00 | 27.3 | 52 | 100 | 25.1502 | 18.23 | 51.3266 | 92.3603 | 92.3603 | 0 | 0
2025-11-12 19:00 | 26.55 | 61.5 | 100 | 24.8888 | 18.6422 | 55.2685 | 123.5758 | 123.5758 | 0 | 0
2025-11-12 20:00 | 25.75 | 67 | 100 | 24.612 | 18.7225 | 57.2886 | 134.5965 | 134.5965 | 0 | 0
2025-11-12 21:00 | 25 | 68.5 | 100 | 24.3517 | 18.5453 | 57.5827 | 129.1275 | 129.1275 | 0 | 0
2025-11-12 22:00 | 24.4 | 69 | 70 | 24.1414 | 18.3576 | 57.5325 | 85.3789 | 85.3789 | 0 | 0
2025-11-12 23:00 | 23.85 | 71 | 70 | 23.9468 | 18.2777 | 58.1076 | 84.8732 | 84.8732 | 0 | 0
2025-11-13 | 22.9 | 74 | 70 | 23.6074 | 18.1028 | 58.8886 | 82.4394 | 82.4394 | 0 | 0
2025-11-13 01:00 | 21.65 | 74.5 | 70 | 23.1527 | 17.6689 | 58.6006 | 70.5843 | 70.5843 | 0 | 0
2025-11-13 02:00 | 20.85 | 71 | 70 | 22.8553 | 17.1899 | 57.0749 | 54.5782 | 54.5782 | 0 | 0
2025-11-13 03:00 | 20.5 | 67 | 70 | 22.7224 | 16.8541 | 55.558 | 42.3327 | 42.3327 | 0 | 0
2025-11-13 04:00 | 20.1 | 66 | 70 | 22.5715 | 16.6631 | 55.1263 | 36.561 | 36.561 | 0 | 0
2025-11-13 05:00 | 19.3 | 68.5 | 70 | 22.2698 | 16.5148 | 55.8515 | 34.8625 | 34.8625 | 0 | 0
2025-11-13 06:00 | 18.7 | 70 | 100 | 22.0412 | 16.3802 | 56.2548 | 46.6394 | 46.6394 | 0 | 0
2025-11-13 07:00 | 20 | 63.5 | 100 | 22.5323 | 16.4998 | 54.2162 | 43.0612 | 43.0612 | 0 | 0
2025-11-13 08:00 | 23.45 | 50.5 | 100 | 23.8022 | 16.8885 | 49.8365 | 39.045 | 39.045 | 0 | 0
2025-11-13 09:00 | 26.75 | 44.5 | 100 | 24.9675 | 17.5145 | 47.8107 | 51.9314 | 51.9314 | 0 | 0
2025-11-13 10:00 | 28.75 | 44 | 100 | 25.6453 | 18.0939 | 47.991 | 72.9103 | 72.9103 | 0 | 0
2025-11-13 11:00 | 30.05 | 39.5 | 100 | 26.0808 | 18.1233 | 46.1064 | 65.6266 | 65.6266 | 0 | 0
2025-11-13 12:00 | 30.9 | 35 | 100 | 26.3658 | 17.9828 | 44.0055 | 51.2238 | 51.2238 | 0 | 0
2025-11-13 13:00 | 31.1 | 36.5 | 100 | 26.4273 | 18.1718 | 44.8188 | 61.6126 | 61.6126 | 0 | 0
2025-11-13 14:00 | 30.6 | 40 | 100 | 26.2588 | 18.3283 | 46.4999 | 74.8058 | 74.8058 | 0 | 0
2025-11-13 15:00 | 29.9 | 40 | 100 | 26.0309 | 18.1168 | 46.3437 | 66.7224 | 66.7224 | 0 | 0
2025-11-13 16:00 | 29.2 | 41.5 | 100 | 25.798 | 18.0289 | 46.9265 | 66.2498 | 66.2498 | 0 | 0
2025-11-13 17:00 | 28.2 | 44.5 | 100 | 25.4608 | 17.9585 | 48.128 | 69.0535 | 69.0535 | 0 | 0
2025-11-13 18:00 | 27.15 | 46.5 | 100 | 25.1033 | 17.7811 | 48.8104 | 65.7662 | 65.7662 | 0 | 0
2025-11-13 19:00 | 26.15 | 50.5 | 100 | 24.7572 | 17.7489 | 50.3478 | 71.1023 | 71.1023 | 0 | 0
2025-11-13 20:00 | 25.05 | 56.5 | 100 | 24.3717 | 17.7922 | 52.6164 | 81.9354 | 81.9354 | 0 | 0
2025-11-13 21:00 | 24 | 62.5 | 100 | 24 | 17.8141 | 54.7638 | 91.3276 | 91.3276 | 0 | 0
2025-11-13 22:00 | 23.3 | 67 | 70 | 23.7501 | 17.8399 | 56.322 | 68.8507 | 68.8507 | 0 | 0
2025-11-13 23:00 | 22.9 | 70 | 70 | 23.6066 | 17.8721 | 57.3498 | 72.4431 | 72.4431 | 0 | 0
2025-11-14 | 22.45 | 72.5 | 70 | 23.4443 | 17.8511 | 58.1439 | 74.0354 | 74.0354 | 0 | 0
2025-11-14 01:00 | 21.7 | 77 | 70 | 23.1721 | 17.8231 | 59.5453 | 77.0026 | 77.0026 | 0 | 0
2025-11-14 02:00 | 20.7 | 81.5 | 70 | 22.8047 | 17.6858 | 60.7892 | 76.6749 | 76.6749 | 0 | 0
2025-11-14 03:00 | 19.85 | 81.5 | 70 | 22.4865 | 17.3647 | 60.4764 | 67.7159 | 67.7159 | 0 | 0
2025-11-14 04:00 | 19.4 | 79 | 70 | 22.3147 | 17.0723 | 59.473 | 57.8553 | 57.8553 | 0 | 0
2025-11-14 05:00 | 19.1 | 77 | 70 | 22.1993 | 16.8644 | 58.7099 | 50.7561 | 50.7561 | 0 | 0
2025-11-14 06:00 | 18.75 | 75 | 100 | 22.064 | 16.6401 | 57.9499 | 61.8883 | 61.8883 | 0 | 0
2025-11-14 07:00 | 19.85 | 67.5 | 100 | 22.478 | 16.655 | 55.6035 | 53.7078 | 53.7078 | 0 | 0
2025-11-14 08:00 | 23.1 | 54 | 100 | 23.676 | 16.9908 | 51.1771 | 48.0792 | 48.0792 | 0 | 0
2025-11-14 09:00 | 26.45 | 45 | 100 | 24.8638 | 17.4572 | 47.9919 | 50.8356 | 50.8356 | 0 | 0
2025-11-14 10:00 | 28.7 | 38.5 | 100 | 25.6353 | 17.6409 | 45.3789 | 45.7162 | 45.7162 | 0 | 0
2025-11-14 11:00 | 30.25 | 30 | 100 | 26.1629 | 17.3613 | 41.3947 | 18.0292 | 18.0292 | 0 | 0
2025-11-14 12:00 | 31.1 | 26 | 100 | 26.4494 | 17.22 | 39.394 | 3.899 | 3.899 | 0 | 0
2025-11-14 13:00 | 31.2 | 27.5 | 100 | 26.4789 | 17.3837 | 40.1813 | 13.136 | 13.136 | 0 | 0
2025-11-14 14:00 | 30.7 | 30.5 | 100 | 26.3097 | 17.5237 | 41.6964 | 25.0519 | 25.0519 | 0 | 0
2025-11-14 15:00 | 29.8 | 35 | 100 | 26.0061 | 17.666 | 43.8615 | 39.9663 | 39.9663 | 0 | 0
2025-11-14 16:00 | 29.1 | 38.5 | 100 | 25.7689 | 17.7546 | 45.4677 | 50.2997 | 50.2997 | 0 | 0
2025-11-14 17:00 | 28.25 | 40 | 100 | 25.4824 | 17.6235 | 46.0442 | 48.3626 | 48.3626 | 0 | 0
2025-11-14 18:00 | 27.05 | 42.5 | 100 | 25.072 | 17.4549 | 47.0034 | 46.7627 | 46.7627 | 0 | 0
2025-11-14 19:00 | 26.1 | 45 | 100 | 24.7424 | 17.3465 | 47.9582 | 47.122 | 47.122 | 0 | 0
2025-11-14 20:00 | 25.25 | 47.5 | 100 | 24.4442 | 17.2569 | 48.8921 | 47.9446 | 47.9446 | 0 | 0
2025-11-14 21:00 | 24.2 | 50.5 | 100 | 24.0715 | 17.1239 | 49.9682 | 47.8427 | 47.8427 | 0 | 0
2025-11-14 22:00 | 23.1 | 55 | 70 | 23.6762 | 17.0504 | 51.5823 | 36.3115 | 36.3115 | 0 | 0
2025-11-14 23:00 | 22.1 | 60.5 | 70 | 23.313 | 17.0431 | 53.5111 | 41.4852 | 41.4852 | 0 | 0
2025-11-15 | 21.2 | 65 | 70 | 22.9825 | 16.9882 | 54.9973 | 44.1777 | 44.1777 | 0 | 0
2025-11-15 01:00 | 20.5 | 68 | 70 | 22.723 | 16.9063 | 55.929 | 44.6547 | 44.6547 | 0 | 0
2025-11-15 02:00 | 19.9 | 70 | 70 | 22.4984 | 16.7999 | 56.5057 | 43.5704 | 43.5704 | 0 | 0
2025-11-15 03:00 | 19.45 | 69.5 | 70 | 22.3275 | 16.6164 | 56.242 | 38.4266 | 38.4266 | 0 | 0
2025-11-15 04:00 | 19.05 | 68.5 | 70 | 22.1743 | 16.4266 | 55.8307 | 32.7936 | 32.7936 | 0 | 0
2025-11-15 05:00 | 18.55 | 69.5 | 70 | 21.9831 | 16.3027 | 56.0893 | 30.4739 | 30.4739 | 0 | 0
2025-11-15 06:00 | 18.3 | 69.5 | 100 | 21.8867 | 16.2159 | 56.0492 | 40.4046 | 40.4046 | 0 | 0
2025-11-15 07:00 | 19.65 | 63.5 | 100 | 22.3997 | 16.3798 | 54.1861 | 39.0043 | 39.0043 | 0 | 0
2025-11-15 08:00 | 22.95 | 52 | 100 | 23.6212 | 16.8205 | 50.376 | 39.0524 | 39.0524 | 0 | 0
2025-11-15 09:00 | 26.4 | 44 | 100 | 24.847 | 17.3696 | 47.5459 | 45.9441 | 45.9441 | 0 | 0
2025-11-15 10:00 | 28.7 | 38 | 100 | 25.6359 | 17.6006 | 45.1429 | 43.2974 | 43.2974 | 0 | 0
2025-11-15 11:00 | 29.95 | 31.5 | 100 | 26.0613 | 17.4106 | 42.1256 | 23.135 | 23.135 | 0 | 0
2025-11-15 12:00 | 30.65 | 28.5 | 100 | 26.2972 | 17.3316 | 40.6665 | 13.7167 | 13.7167 | 0 | 0
2025-11-15 13:00 | 30.8 | 28.5 | 100 | 26.3463 | 17.3695 | 40.6814 | 15.1326 | 15.1326 | 0 | 0
2025-11-15 14:00 | 30.35 | 30 | 100 | 26.1959 | 17.3836 | 41.4213 | 19.1655 | 19.1655 | 0 | 0
2025-11-15 15:00 | 29.6 | 33.5 | 100 | 25.9422 | 17.4816 | 43.1039 | 30.3068 | 30.3068 | 0 | 0
2025-11-15 16:00 | 28.85 | 39.5 | 100 | 25.6843 | 17.7613 | 45.9079 | 52.5273 | 52.5273 | 0 | 0
2025-11-15 17:00 | 27.9 | 43 | 100 | 25.3612 | 17.7507 | 47.3769 | 58.5876 | 58.5876 | 0 | 0
2025-11-15 18:00 | 26.95 | 43 | 100 | 25.0373 | 17.4614 | 47.21 | 47.8733 | 47.8733 | 0 | 0
2025-11-15 19:00 | 26.1 | 44 | 100 | 24.7429 | 17.2758 | 47.5218 | 42.8268 | 42.8268 | 0 | 0
2025-11-15 20:00 | 25.2 | 46.5 | 100 | 24.4268 | 17.1737 | 48.4608 | 43.2686 | 43.2686 | 0 | 0
2025-11-15 21:00 | 24.1 | 50.5 | 100 | 24.0358 | 17.0928 | 49.9476 | 46.6403 | 46.6403 | 0 | 0
2025-11-15 22:00 | 22.95 | 55 | 70 | 23.6218 | 17.0026 | 51.548 | 35.0009 | 35.0009 | 0 | 0
2025-11-15 23:00 | 22.1 | 58.5 | 70 | 23.3123 | 16.929 | 52.7455 | 36.5549 | 36.5549 | 0 | 0
2025-11-16 | 21.4 | 61 | 70 | 23.055 | 16.8359 | 53.558 | 36.5515 | 36.5515 | 0 | 0
2025-11-16 01:00 | 20.7 | 64 | 70 | 22.7957 | 16.7627 | 54.5266 | 37.3955 | 37.3955 | 0 | 0
2025-11-16 02:00 | 19.95 | 67 | 70 | 22.5155 | 16.6635 | 55.4546 | 37.4455 | 37.4455 | 0 | 0
2025-11-16 03:00 | 19.55 | 66 | 70 | 22.3633 | 16.474 | 55.0402 | 31.8067 | 31.8067 | 0 | 0
2025-11-16 04:00 | 19.4 | 64.5 | 70 | 22.3052 | 16.3463 | 54.5017 | 27.3469 | 27.3469 | 0 | 0
2025-11-16 05:00 | 19.25 | 66.5 | 70 | 22.2494 | 16.3968 | 55.1638 | 30.2612 | 30.2612 | 0 | 0
2025-11-16 06:00 | 19.35 | 69.5 | 100 | 22.2895 | 16.5823 | 56.1999 | 53.411 | 53.411 | 0 | 0
2025-11-16 07:00 | 20.7 | 67 | 100 | 22.7973 | 16.9249 | 55.5862 | 62.9312 | 62.9312 | 0 | 0
2025-11-16 08:00 | 23.65 | 57 | 100 | 23.8747 | 17.3571 | 52.4536 | 65.7771 | 65.7771 | 0 | 0
2025-11-16 09:00 | 26.95 | 44 | 100 | 25.0366 | 17.5399 | 47.6208 | 51.9622 | 51.9622 | 0 | 0
2025-11-16 10:00 | 29.25 | 33 | 100 | 25.8264 | 17.35 | 42.7874 | 23.9389 | 23.9389 | 0 | 0
2025-11-16 11:00 | 30.45 | 27 | 100 | 26.2341 | 17.149 | 39.8757 | 3.672 | 3.672 | 0 | 0
2025-11-16 12:00 | 31.2 | 24 | 100 | 26.4863 | 17.061 | 38.3442 | 0 | 0 | 0 | 0
2025-11-16 13:00 | 31.65 | 22.5 | 100 | 26.6364 | 17.0269 | 37.554 | 0 | 0 | 0 | 0
2025-11-16 14:00 | 31.45 | 24.5 | 100 | 26.5668 | 17.1682 | 38.6127 | 0 | 0 | 0 | 0
2025-11-16 15:00 | 30.3 | 33 | 100 | 26.174 | 17.6364 | 42.9119 | 34.4236 | 34.4236 | 0 | 0
2025-11-16 16:00 | 28.85 | 41.5 | 100 | 25.6817 | 17.9241 | 46.8425 | 62.1072 | 62.1072 | 0 | 0
2025-11-16 17:00 | 27.7 | 45.5 | 100 | 25.2912 | 17.881 | 48.4658 | 67.6489 | 67.6489 | 0 | 0
2025-11-16 18:00 | 26.9 | 47.5 | 100 | 25.0171 | 17.777 | 49.1886 | 67.086 | 67.086 | 0 | 0
2025-11-16 19:00 | 26 | 50.5 | 100 | 24.7052 | 17.7026 | 50.2971 | 69.098 | 69.098 | 0 | 0
2025-11-16 20:00 | 25.1 | 54 | 100 | 24.3898 | 17.6459 | 51.5686 | 72.3406 | 72.3406 | 0 | 0
2025-11-16 21:00 | 24.35 | 58 | 100 | 24.1245 | 17.6545 | 53.0263 | 78.542 | 78.542 | 0 | 0
2025-11-16 22:00 | 23.75 | 61 | 70 | 23.9108 | 17.6374 | 54.0704 | 57.462 | 57.462 | 0 | 0
2025-11-16 23:00 | 23.25 | 62 | 70 | 23.7314 | 17.5254 | 54.3306 | 55.4244 | 55.4244 | 0 | 0
2025-11-17 | 22.35 | 65 | 70 | 23.4058 | 17.3896 | 55.2476 | 54.5658 | 54.5658 | 0 | 0
2025-11-17 01:00 | 21.2 | 69.5 | 70 | 22.9846 | 17.2353 | 56.6118 | 54.3991 | 54.3991 | 0 | 0
2025-11-17 02:00 | 20.15 | 74 | 70 | 22.595 | 17.0961 | 57.9356 | 54.4128 | 54.4128 | 0 | 0
2025-11-17 03:00 | 19.3 | 77.5 | 70 | 22.2758 | 16.9623 | 58.9147 | 53.6233 | 53.6233 | 0 | 0
2025-11-17 04:00 | 19.05 | 79 | 70 | 22.1816 | 16.9438 | 59.355 | 54.2827 | 54.2827 | 0 | 0
2025-11-17 05:00 | 18.9 | 82 | 70 | 22.1264 | 17.0328 | 60.3174 | 58.9074 | 58.9074 | 0 | 0
2025-11-17 06:00 | 18.55 | 86 | 100 | 21.9953 | 17.0912 | 61.5331 | 90.5077 | 90.5077 | 0 | 0
2025-11-17 07:00 | 19.75 | 81 | 100 | 22.4485 | 17.3028 | 60.2371 | 93.4493 | 93.4493 | 0 | 0
2025-11-17 08:00 | 22.7 | 67 | 100 | 23.5336 | 17.6286 | 56.0986 | 89.6554 | 89.6554 | 0 | 0
2025-11-17 09:00 | 26 | 54 | 100 | 24.7037 | 17.9449 | 51.7913 | 83.7246 | 83.7246 | 0 | 0
2025-11-17 10:00 | 28.35 | 44.5 | 100 | 25.5111 | 18.0099 | 48.1259 | 70.461 | 70.461 | 0 | 0
2025-11-17 11:00 | 29.65 | 36.5 | 100 | 25.9541 | 17.7553 | 44.5434 | 45.7153 | 45.7153 | 0 | 0
2025-11-17 12:00 | 30.5 | 32 | 100 | 26.2413 | 17.6066 | 42.4155 | 30.9285 | 30.9285 | 0 | 0
2025-11-17 13:00 | 30.6 | 33.5 | 100 | 26.2712 | 17.7657 | 43.1946 | 40.0185 | 40.0185 | 0 | 0
2025-11-17 14:00 | 29.85 | 37 | 100 | 26.0193 | 17.8524 | 44.8405 | 50.6139 | 50.6139 | 0 | 0
2025-11-17 15:00 | 28.9 | 40 | 100 | 25.7003 | 17.8193 | 46.1366 | 55.3327 | 55.3327 | 0 | 0
2025-11-17 16:00 | 28 | 46 | 100 | 25.392 | 18.0118 | 48.7685 | 73.6061 | 73.6061 | 0 | 0
2025-11-17 17:00 | 26.95 | 51.5 | 100 | 25.0315 | 18.0801 | 50.9883 | 85.4621 | 85.4621 | 0 | 0
2025-11-17 18:00 | 26.05 | 54.5 | 100 | 24.7207 | 17.9932 | 52.0442 | 86.7166 | 86.7166 | 0 | 0
2025-11-17 19:00 | 25.35 | 58 | 100 | 24.4763 | 17.9925 | 53.3236 | 91.8983 | 91.8983 | 0 | 0
2025-11-17 20:00 | 24.6 | 61.5 | 100 | 24.2126 | 17.9611 | 54.5379 | 95.6225 | 95.6225 | 0 | 0
2025-11-17 21:00 | 23.8 | 64 | 100 | 23.9288 | 17.8374 | 55.2903 | 94.1385 | 94.1385 | 0 | 0
2025-11-17 22:00 | 23.15 | 65.5 | 70 | 23.6959 | 17.6984 | 55.677 | 63.4765 | 63.4765 | 0 | 0
2025-11-17 23:00 | 22.35 | 67.5 | 70 | 23.4065 | 17.5319 | 56.2046 | 60.7414 | 60.7414 | 0 | 0
2025-11-18 | 21.25 | 70 | 70 | 23.0033 | 17.2796 | 56.8194 | 56.1057 | 56.1057 | 0 | 0
2025-11-18 01:00 | 20.1 | 73.5 | 70 | 22.5759 | 17.0515 | 57.7606 | 52.9288 | 52.9288 | 0 | 0
2025-11-18 02:00 | 19.1 | 78 | 70 | 22.1999 | 16.9132 | 59.046 | 52.8062 | 52.8062 | 0 | 0
2025-11-18 03:00 | 18.65 | 79.5 | 70 | 22.0289 | 16.8203 | 59.4323 | 51.4927 | 51.4927 | 0 | 0
2025-11-18 04:00 | 18.6 | 79 | 70 | 22.0093 | 16.7776 | 59.2546 | 50.0115 | 50.0115 | 0 | 0
2025-11-18 05:00 | 18.4 | 80.5 | 70 | 21.9336 | 16.775 | 59.7 | 51.0659 | 51.0659 | 0 | 0
2025-11-18 06:00 | 18.2 | 82.5 | 100 | 21.858 | 16.7954 | 60.3005 | 75.7585 | 75.7585 | 0 | 0
2025-11-18 07:00 | 19.25 | 78.5 | 100 | 22.2574 | 16.993 | 59.2511 | 78.9651 | 78.9651 | 0 | 0
2025-11-18 08:00 | 22.15 | 67 | 100 | 23.3334 | 17.4326 | 55.9564 | 82.2808 | 82.2808 | 0 | 0
2025-11-18 09:00 | 25.3 | 57.5 | 100 | 24.459 | 17.9431 | 53.0968 | 89.1805 | 89.1805 | 0 | 0
2025-11-18 10:00 | 27.3 | 53 | 100 | 25.1494 | 18.3039 | 51.7599 | 96.676 | 96.676 | 0 | 0
2025-11-18 11:00 | 28.75 | 46.5 | 100 | 25.6422 | 18.2871 | 49.197 | 85.2291 | 85.2291 | 0 | 0
2025-11-18 12:00 | 30.05 | 39.5 | 100 | 26.0808 | 18.1201 | 46.1271 | 65.8478 | 65.8478 | 0 | 0
2025-11-18 13:00 | 30.5 | 39.5 | 100 | 26.2274 | 18.2537 | 46.2348 | 71.109 | 71.109 | 0 | 0
2025-11-18 14:00 | 29.95 | 43 | 100 | 26.0423 | 18.3799 | 47.8521 | 82.8726 | 82.8726 | 0 | 0
2025-11-18 15:00 | 29.1 | 45.5 | 100 | 25.7595 | 18.3163 | 48.8425 | 84.9933 | 84.9933 | 0 | 0
2025-11-18 16:00 | 28.05 | 54.5 | 100 | 25.4002 | 18.662 | 52.736 | 114.1057 | 114.1057 | 0 | 0
2025-11-18 17:00 | 26.8 | 67 | 100 | 24.9702 | 19.1051 | 57.8125 | 151.2885 | 151.2885 | 0 | 0
2025-11-18 18:00 | 25.8 | 73.5 | 100 | 24.6267 | 19.1595 | 60.09 | 162.2753 | 162.2753 | 0 | 0
2025-11-18 19:00 | 25.05 | 76.5 | 100 | 24.3674 | 19.0618 | 60.9311 | 161.7446 | 161.7446 | 0 | 0
2025-11-18 20:00 | 24.45 | 79 | 100 | 24.1581 | 18.983 | 61.6192 | 161.3044 | 161.3044 | 0 | 0
2025-11-18 21:00 | 23.7 | 81 | 100 | 23.894 | 18.8103 | 62.0077 | 156.1393 | 156.1393 | 0 | 0
2025-11-18 22:00 | 22.7 | 84 | 70 | 23.5376 | 18.59 | 62.6379 | 105.0718 | 105.0718 | 0 | 0
2025-11-18 23:00 | 21.65 | 88 | 70 | 23.1581 | 18.3928 | 63.5855 | 102.267 | 102.267 | 0 | 0
2025-11-19 | 20.55 | 91.5 | 70 | 22.7543 | 18.136 | 64.2857 | 97.2461 | 97.2461 | 0 | 0
2025-11-19 01:00 | 19.7 | 94 | 70 | 22.4378 | 17.9196 | 64.738 | 92.687 | 92.687 | 0 | 0
2025-11-19 02:00 | 19.2 | 95 | 70 | 22.2496 | 17.7676 | 64.842 | 88.9726 | 88.9726 | 0 | 0
2025-11-19 03:00 | 18.85 | 94.5 | 70 | 22.1162 | 17.6044 | 64.5171 | 83.9544 | 83.9544 | 0 | 0
2025-11-19 04:00 | 18.45 | 94.5 | 70 | 21.9633 | 17.4454 | 64.3455 | 79.4456 | 79.4456 | 0 | 0
2025-11-19 05:00 | 18 | 95 | 70 | 21.7905 | 17.2906 | 64.3233 | 75.4066 | 75.4066 | 0 | 0
2025-11-19 06:00 | 17.75 | 94.5 | 100 | 21.6935 | 17.1691 | 64.0598 | 102.3858 | 102.3858 | 0 | 0
2025-11-19 07:00 | 18.75 | 90.5 | 100 | 22.0752 | 17.3778 | 63.1306 | 106.7146 | 106.7146 | 0 | 0
2025-11-19 08:00 | 21.65 | 80.5 | 100 | 23.1551 | 17.9931 | 60.8168 | 120.9762 | 120.9762 | 0 | 0
2025-11-19 09:00 | 25 | 70.5 | 100 | 24.3513 | 18.6707 | 58.4143 | 137.0943 | 137.0943 | 0 | 0
2025-11-19 10:00 | 27.55 | 60.5 | 100 | 25.2274 | 18.9258 | 55.2525 | 134.0717 | 134.0717 | 0 | 0
2025-11-19 11:00 | 29.6 | 47 | 100 | 25.9216 | 18.5971 | 49.7025 | 98.6683 | 98.6683 | 0 | 0
2025-11-19 12:00 | 31.3 | 35 | 100 | 26.495 | 18.0929 | 44.0978 | 55.7424 | 55.7424 | 0 | 0
2025-11-19 13:00 | 32.05 | 31 | 100 | 26.7447 | 17.933 | 42.1172 | 41.0454 | 41.0454 | 0 | 0
2025-11-19 14:00 | 31.25 | 43 | 100 | 26.4613 | 18.7834 | 48.2356 | 99.1263 | 99.1263 | 0 | 0
2025-11-19 15:00 | 29.65 | 53.5 | 100 | 25.9278 | 19.1283 | 52.9056 | 132.1295 | 132.1295 | 0 | 0
2025-11-19 16:00 | 28.35 | 59.5 | 100 | 25.4945 | 19.1335 | 55.1813 | 141.8292 | 141.8292 | 0 | 0
2025-11-19 17:00 | 27.25 | 69 | 100 | 25.12 | 19.4077 | 58.9401 | 167.3781 | 167.3781 | 0 | 0
2025-11-19 18:00 | 26.35 | 72 | 100 | 24.8149 | 19.2704 | 59.7538 | 165.2596 | 165.2596 | 0 | 0
2025-11-19 19:00 | 25.45 | 74 | 100 | 24.5063 | 19.0586 | 60.1105 | 158.4768 | 158.4768 | 0 | 0
2025-11-19 20:00 | 24.5 | 78 | 100 | 24.1756 | 18.9422 | 61.2428 | 158.3224 | 158.3224 | 0 | 0
2025-11-19 21:00 | 23.6 | 83 | 100 | 23.8588 | 18.886 | 62.7361 | 161.7641 | 161.7641 | 0 | 0
2025-11-19 22:00 | 22.8 | 87.5 | 70 | 23.5743 | 18.8233 | 64.0184 | 114.8241 | 114.8241 | 0 | 0
2025-11-19 23:00 | 22 | 91 | 70 | 23.2866 | 18.6917 | 64.8733 | 113.4533 | 113.4533 | 0 | 0
2025-11-20 | 21 | 95 | 70 | 22.9226 | 18.494 | 65.7583 | 110.3576 | 110.3576 | 0 | 0
2025-11-20 01:00 | 20.2 | 98.5 | 70 | 22.6279 | 18.3409 | 66.5394 | 108.1771 | 108.1771 | 0 | 0
2025-11-20 02:00 | 19.6 | 100 | 70 | 22.404 | 18.1669 | 66.7236 | 103.9847 | 103.9847 | 0 | 0
2025-11-20 03:00 | 19.55 | 100 | 70 | 22.3852 | 18.146 | 66.6959 | 103.3709 | 103.3709 | 0 | 0
2025-11-20 04:00 | 19.4 | 100 | 70 | 22.3287 | 18.0843 | 66.614 | 101.536 | 101.536 | 0 | 0
2025-11-20 05:00 | 18.5 | 99 | 70 | 21.9858 | 17.6717 | 65.8268 | 88.7912 | 88.7912 | 0 | 0
2025-11-20 06:00 | 17.5 | 93.5 | 100 | 21.5956 | 17.0271 | 63.6335 | 95.6895 | 95.6895 | 0 | 0
2025-11-20 07:00 | 18.05 | 79.5 | 100 | 21.7977 | 16.6 | 59.2785 | 65.253 | 65.253 | 0 | 0
2025-11-20 08:00 | 21.05 | 64 | 100 | 22.9263 | 16.8834 | 54.5842 | 57.7417 | 57.7417 | 0 | 0
2025-11-20 09:00 | 24.35 | 62 | 100 | 24.1242 | 17.9057 | 54.6643 | 94.1465 | 94.1465 | 0 | 0
2025-11-20 10:00 | 26.75 | 64.5 | 100 | 24.9549 | 18.9192 | 56.6583 | 139.3867 | 139.3867 | 0 | 0
2025-11-20 11:00 | 28.95 | 56 | 100 | 25.6961 | 19.0848 | 53.7722 | 133.8196 | 133.8196 | 0 | 0
2025-11-20 12:00 | 30.75 | 45 | 100 | 26.2974 | 18.8005 | 49.0729 | 103.1907 | 103.1907 | 0 | 0
2025-11-20 13:00 | 31.15 | 45.5 | 100 | 26.4241 | 18.9699 | 49.4692 | 111.1705 | 111.1705 | 0 | 0
2025-11-20 14:00 | 30.2 | 54.5 | 100 | 26.1033 | 19.3973 | 53.6211 | 145.0757 | 145.0757 | 0 | 0
2025-11-20 15:00 | 29.2 | 61 | 100 | 25.7708 | 19.5496 | 56.288 | 162.0035 | 162.0035 | 0 | 0
2025-11-20 16:00 | 28.45 | 65.5 | 100 | 25.5206 | 19.6082 | 57.9999 | 171.2277 | 171.2277 | 0 | 0
2025-11-20 17:00 | 27.35 | 72.5 | 100 | 25.1506 | 19.6849 | 60.5402 | 184.2853 | 184.2853 | 0 | 0
2025-11-20 18:00 | 26.2 | 80 | 100 | 24.76 | 19.7305 | 63.0826 | 195.863 | 195.863 | 0 | 0
2025-11-20 19:00 | 25.2 | 85.5 | 100 | 24.417 | 19.6719 | 64.72 | 199.6886 | 199.6886 | 0 | 0
2025-11-20 20:00 | 24.35 | 88.5 | 100 | 24.1224 | 19.5049 | 65.3613 | 195.4454 | 195.4454 | 0 | 0
2025-11-20 21:00 | 23.7 | 88.5 | 100 | 23.8945 | 19.2414 | 64.9349 | 183.5026 | 183.5026 | 0 | 0
2025-11-20 22:00 | 23.3 | 87.5 | 70 | 23.7527 | 19.0232 | 64.2982 | 120.8889 | 120.8889 | 0 | 0
2025-11-20 23:00 | 23.05 | 87 | 70 | 23.6636 | 18.8956 | 63.96 | 116.5693 | 116.5693 | 0 | 0
2025-11-21 | 22.75 | 87.5 | 70 | 23.5563 | 18.8033 | 63.98 | 114.1489 | 114.1489 | 0 | 0
2025-11-21 01:00 | 22.3 | 89 | 70 | 23.3946 | 18.7052 | 64.2901 | 112.3036 | 112.3036 | 0 | 0
2025-11-21 02:00 | 21.45 | 91.5 | 70 | 23.0863 | 18.4966 | 64.7392 | 107.8545 | 107.8545 | 0 | 0
2025-11-21 03:00 | 20.95 | 94 | 70 | 22.9036 | 18.423 | 65.3637 | 107.4459 | 107.4459 | 0 | 0
2025-11-21 04:00 | 20.4 | 97.5 | 70 | 22.7018 | 18.3736 | 66.2933 | 108.4191 | 108.4191 | 0 | 0
2025-11-21 05:00 | 19.5 | 100 | 70 | 22.3664 | 18.1259 | 66.6575 | 102.6898 | 102.6898 | 0 | 0
2025-11-21 06:00 | 18.7 | 100 | 100 | 22.063 | 17.7987 | 66.2394 | 132.9222 | 132.9222 | 0 | 0
2025-11-21 07:00 | 18.45 | 99.5 | 100 | 21.967 | 17.6744 | 65.9479 | 127.2503 | 127.2503 | 0 | 0
2025-11-21 08:00 | 19.5 | 98.5 | 100 | 22.3654 | 18.0545 | 66.1303 | 142.0898 | 142.0898 | 0 | 0
2025-11-21 09:00 | 21.8 | 94.5 | 100 | 23.2152 | 18.7953 | 66.0118 | 169.9294 | 169.9294 | 0 | 0
2025-11-21 10:00 | 25.05 | 80.5 | 100 | 24.3665 | 19.3091 | 62.5421 | 177.1175 | 177.1175 | 0 | 0
2025-11-21 11:00 | 27.75 | 63 | 100 | 25.292 | 19.176 | 56.4588 | 148.223 | 148.223 | 0 | 0
2025-11-21 12:00 | 29.35 | 51.5 | 100 | 25.8332 | 18.8743 | 51.7803 | 117.5544 | 117.5544 | 0 | 0
2025-11-21 13:00 | 30.2 | 47 | 100 | 26.1166 | 18.7914 | 49.8909 | 106.4352 | 106.4352 | 0 | 0
2025-11-21 14:00 | 30 | 49.5 | 100 | 26.0476 | 18.929 | 51.0616 | 116.6161 | 116.6161 | 0 | 0
2025-11-21 15:00 | 29.25 | 53.5 | 100 | 25.7977 | 18.9951 | 52.7154 | 126.1192 | 126.1192 | 0 | 0
2025-11-21 16:00 | 28.4 | 60 | 100 | 25.5105 | 19.1904 | 55.4111 | 144.6622 | 144.6622 | 0 | 0
2025-11-21 17:00 | 27.4 | 65.5 | 100 | 25.173 | 19.2232 | 57.4304 | 154.0914 | 154.0914 | 0 | 0
2025-11-21 18:00 | 26.35 | 69 | 100 | 24.8165 | 19.0742 | 58.4323 | 152.3669 | 152.3669 | 0 | 0
2025-11-21 19:00 | 25.4 | 73.5 | 100 | 24.4892 | 19.0094 | 59.8503 | 155.3975 | 155.3975 | 0 | 0
2025-11-21 20:00 | 24.55 | 77 | 100 | 24.1932 | 18.9018 | 60.8413 | 155.0898 | 155.0898 | 0 | 0
2025-11-21 21:00 | 23.65 | 80 | 100 | 23.8763 | 18.7334 | 61.5639 | 151.39 | 151.39 | 0 | 0
2025-11-21 22:00 | 22.95 | 81.5 | 70 | 23.6268 | 18.5483 | 61.7845 | 101.6304 | 101.6304 | 0 | 0
2025-11-21 23:00 | 22.3 | 83 | 70 | 23.3929 | 18.3797 | 62.0297 | 97.812 | 97.812 | 0 | 0
2025-11-22 | 21.5 | 85 | 70 | 23.1019 | 18.1755 | 62.3861 | 93.3923 | 93.3923 | 0 | 0
2025-11-22 01:00 | 20.85 | 86 | 70 | 22.8627 | 17.9746 | 62.4484 | 88.3177 | 88.3177 | 0 | 0
2025-11-22 02:00 | 20.3 | 86.5 | 70 | 22.6583 | 17.787 | 62.3854 | 83.2892 | 83.2892 | 0 | 0
2025-11-22 03:00 | 19.6 | 88.5 | 70 | 22.3966 | 17.6141 | 62.784 | 79.8272 | 79.8272 | 0 | 0
2025-11-22 04:00 | 18.7 | 90.5 | 70 | 22.056 | 17.3587 | 63.0975 | 74.0718 | 74.0718 | 0 | 0
2025-11-22 05:00 | 17.85 | 90.5 | 70 | 21.729 | 17.0287 | 62.7869 | 64.9561 | 64.9561 | 0 | 0
2025-11-22 06:00 | 17.35 | 91.5 | 100 | 21.5356 | 16.8807 | 62.9363 | 87.9655 | 87.9655 | 0 | 0
2025-11-22 07:00 | 18.1 | 92 | 100 | 21.8268 | 17.1941 | 63.3513 | 100.6588 | 100.6588 | 0 | 0
2025-11-22 08:00 | 20.7 | 83.5 | 100 | 22.8058 | 17.7888 | 61.4786 | 115.6958 | 115.6958 | 0 | 0
2025-11-22 09:00 | 24.05 | 67 | 100 | 24.0177 | 18.1095 | 56.568 | 108.9422 | 108.9422 | 0 | 0
2025-11-22 10:00 | 26.95 | 49.5 | 100 | 25.0329 | 17.9384 | 50.0836 | 76.4734 | 76.4734 | 0 | 0
2025-11-22 11:00 | 29.15 | 35 | 100 | 25.7903 | 17.4858 | 43.7608 | 33.1314 | 33.1314 | 0 | 0
2025-11-22 12:00 | 30.85 | 26 | 100 | 26.3676 | 17.1575 | 39.3869 | 1.7783 | 1.7783 | 0 | 0
2025-11-22 13:00 | 32.1 | 21.5 | 100 | 26.7848 | 17.0351 | 37.018 | 0 | 0 | 0 | 0
2025-11-22 14:00 | 31.95 | 26 | 100 | 26.7252 | 17.4339 | 39.4309 | 11.2265 | 11.2265 | 0 | 0
2025-11-22 15:00 | 30.15 | 33.5 | 100 | 26.1239 | 17.6362 | 43.1594 | 35.7136 | 35.7136 | 0 | 0
2025-11-22 16:00 | 28.5 | 42.5 | 100 | 25.5636 | 17.8949 | 47.2599 | 63.0841 | 63.0841 | 0 | 0
2025-11-22 17:00 | 27.35 | 55.5 | 100 | 25.1643 | 18.4991 | 52.9213 | 108.7636 | 108.7636 | 0 | 0
2025-11-22 18:00 | 26.25 | 64.5 | 100 | 24.7847 | 18.7382 | 56.4474 | 131.8892 | 131.8892 | 0 | 0
2025-11-22 19:00 | 25.45 | 68.5 | 100 | 24.508 | 18.7098 | 57.7869 | 136.0926 | 136.0926 | 0 | 0
2025-11-22 20:00 | 24.45 | 70 | 100 | 24.1589 | 18.4371 | 57.9583 | 126.5739 | 126.5739 | 0 | 0
2025-11-22 21:00 | 23.35 | 71.5 | 100 | 23.7686 | 18.1238 | 58.0998 | 115.5367 | 115.5367 | 0 | 0
2025-11-22 22:00 | 22.1 | 69.5 | 70 | 23.3159 | 17.5557 | 56.8899 | 63.2077 | 63.2077 | 0 | 0
2025-11-22 23:00 | 20.7 | 62.5 | 70 | 22.795 | 16.6818 | 53.9876 | 34.0077 | 34.0077 | 0 | 0
2025-11-23 | 19.65 | 57 | 70 | 22.3956 | 16.0424 | 51.9347 | 13.3965 | 13.3965 | 0 | 0
2025-11-23 01:00 | 18.75 | 57 | 70 | 22.0511 | 15.7519 | 51.9091 | 6.6345 | 6.6345 | 0 | 0
2025-11-23 02:00 | 17.8 | 60.5 | 70 | 21.6858 | 15.6159 | 53.0616 | 6.5469 | 6.5469 | 0 | 0
2025-11-23 03:00 | 16.9 | 61 | 70 | 21.3335 | 15.3462 | 53.2298 | 0.811 | 0.811 | 0 | 0
2025-11-23 04:00 | 16.15 | 59 | 70 | 21.0347 | 15.0141 | 52.6448 | 0 | 0 | 0 | 0
2025-11-23 05:00 | 15.55 | 58 | 70 | 20.7941 | 14.7796 | 52.3982 | 0 | 0 | 0 | 0
2025-11-23 06:00 | 15.2 | 59.5 | 100 | 20.6548 | 14.7333 | 52.8864 | 0 | 0 | 0 | 0
2025-11-23 07:00 | 16.2 | 61 | 100 | 21.0564 | 15.1201 | 53.2436 | 0 | 0 | 0 | 0
2025-11-23 08:00 | 19.5 | 55 | 100 | 22.3372 | 15.8916 | 51.2143 | 11.2221 | 11.2221 | 0 | 0
2025-11-23 09:00 | 23.85 | 46.5 | 100 | 23.9461 | 16.7603 | 48.2836 | 28.3279 | 28.3279 | 0 | 0
2025-11-23 10:00 | 27 | 40 | 100 | 25.0566 | 17.2582 | 45.8447 | 34.7105 | 34.7105 | 0 | 0
2025-11-23 11:00 | 28.6 | 34.5 | 100 | 25.6065 | 17.2897 | 43.471 | 25.2511 | 25.2511 | 0 | 0
2025-11-23 12:00 | 29.75 | 29 | 100 | 25.999 | 17.1397 | 40.8793 | 8.3799 | 8.3799 | 0 | 0
2025-11-23 13:00 | 30.65 | 24 | 100 | 26.3058 | 16.9215 | 38.3735 | 0 | 0 | 0 | 0
2025-11-23 14:00 | 30.85 | 24.5 | 100 | 26.3707 | 17.0166 | 38.6299 | 0 | 0 | 0 | 0
2025-11-23 15:00 | 30.05 | 30 | 100 | 26.0969 | 17.3039 | 41.4021 | 16.409 | 16.409 | 0 | 0
2025-11-23 16:00 | 28.85 | 35.5 | 100 | 25.6893 | 17.4375 | 43.9932 | 32.853 | 32.853 | 0 | 0
2025-11-23 17:00 | 27.55 | 42.5 | 100 | 25.2429 | 17.6058 | 47.0825 | 52.2982 | 52.2982 | 0 | 0
2025-11-23 18:00 | 26.25 | 49.5 | 100 | 24.7923 | 17.7107 | 49.9431 | 68.1243 | 68.1243 | 0 | 0
2025-11-23 19:00 | 25.25 | 55 | 100 | 24.4422 | 17.7595 | 52.049 | 78.5303 | 78.5303 | 0 | 0
2025-11-23 20:00 | 24.3 | 60.5 | 100 | 24.1066 | 17.7929 | 54.0517 | 87.7839 | 87.7839 | 0 | 0
2025-11-23 21:00 | 23.85 | 63 | 100 | 23.9466 | 17.7927 | 54.9211 | 91.1975 | 91.1975 | 0 | 0
2025-11-23 22:00 | 23.6 | 64 | 70 | 23.8573 | 17.766 | 55.2432 | 64.0675 | 64.0675 | 0 | 0
2025-11-23 23:00 | 22.95 | 68 | 70 | 23.6242 | 17.7734 | 56.5994 | 67.9521 | 67.9521 | 0 | 0
2025-11-24 | 22.3 | 73 | 70 | 23.3899 | 17.8241 | 58.2817 | 73.732 | 73.732 | 0 | 0
2025-11-24 01:00 | 21.65 | 76 | 70 | 23.1533 | 17.7502 | 59.1609 | 74.1517 | 74.1517 | 0 | 0
2025-11-24 02:00 | 21.2 | 77 | 70 | 22.988 | 17.6371 | 59.3627 | 71.7942 | 71.7942 | 0 | 0
2025-11-24 03:00 | 20.45 | 74 | 70 | 22.7075 | 17.2036 | 58.0436 | 57.4797 | 57.4797 | 0 | 0
2025-11-24 04:00 | 19.35 | 73 | 70 | 22.2918 | 16.7564 | 57.4147 | 44.8369 | 44.8369 | 0 | 0
2025-11-24 05:00 | 18.7 | 76.5 | 70 | 22.0459 | 16.6946 | 58.4477 | 45.9379 | 45.9379 | 0 | 0
2025-11-24 06:00 | 18.45 | 78 | 100 | 21.9509 | 16.6755 | 58.883 | 66.4997 | 66.4997 | 0 | 0
2025-11-24 07:00 | 19.45 | 71.5 | 100 | 22.3288 | 16.7178 | 56.91 | 60.7579 | 60.7579 | 0 | 0
2025-11-24 08:00 | 22.2 | 56 | 100 | 23.3482 | 16.8173 | 51.8104 | 44.6551 | 44.6551 | 0 | 0
2025-11-24 09:00 | 25.5 | 45.5 | 100 | 24.5326 | 17.1996 | 48.0652 | 42.3476 | 42.3476 | 0 | 0
2025-11-24 10:00 | 27.9 | 42 | 100 | 25.3621 | 17.6769 | 46.8927 | 53.6881 | 53.6881 | 0 | 0
2025-11-24 11:00 | 29.35 | 35 | 100 | 25.8569 | 17.5412 | 43.7911 | 35.228 | 35.228 | 0 | 0
2025-11-24 12:00 | 30.5 | 25.5 | 100 | 26.2535 | 17.0217 | 39.1363 | 0 | 0 | 0 | 0
2025-11-24 13:00 | 31.05 | 20.5 | 100 | 26.4445 | 16.6905 | 36.5516 | 0 | 0 | 0 | 0
2025-11-24 14:00 | 30.95 | 20 | 100 | 26.4126 | 16.6196 | 36.3038 | 0 | 0 | 0 | 0
2025-11-24 15:00 | 30.1 | 23.5 | 100 | 26.1245 | 16.7404 | 38.1477 | 0 | 0 | 0 | 0
2025-11-24 16:00 | 28.7 | 30 | 100 | 25.6456 | 16.9442 | 41.3555 | 4.3804 | 4.3804 | 0 | 0
2025-11-24 17:00 | 27.05 | 40 | 100 | 25.0738 | 17.2687 | 45.8794 | 35.5284 | 35.5284 | 0 | 0
2025-11-24 18:00 | 25.5 | 50.5 | 100 | 24.531 | 17.5389 | 50.2111 | 63.2477 | 63.2477 | 0 | 0
2025-11-24 19:00 | 24.25 | 56.5 | 100 | 24.0891 | 17.5238 | 52.4163 | 71.6877 | 71.6877 | 0 | 0
2025-11-24 20:00 | 23.1 | 61.5 | 100 | 23.6773 | 17.443 | 54.1139 | 75.5443 | 75.5443 | 0 | 0
2025-11-24 21:00 | 22.05 | 65.5 | 100 | 23.2963 | 17.3123 | 55.3698 | 75.7974 | 75.7974 | 0 | 0
2025-11-24 22:00 | 21 | 66.5 | 70 | 22.9089 | 17.0015 | 55.4854 | 45.7293 | 45.7293 | 0 | 0
2025-11-24 23:00 | 19.9 | 64.5 | 70 | 22.4951 | 16.5166 | 54.5697 | 31.5762 | 31.5762 | 0 | 0
2025-11-25 | 18.85 | 62 | 70 | 22.0931 | 16.036 | 53.5957 | 17.6415 | 17.6415 | 0 | 0
2025-11-25 01:00 | 18 | 61.5 | 70 | 21.7644 | 15.7303 | 53.3866 | 9.9898 | 9.9898 | 0 | 0
2025-11-25 02:00 | 17.1 | 63.5 | 70 | 21.4143 | 15.5276 | 54.0172 | 6.9514 | 6.9514 | 0 | 0
2025-11-25 03:00 | 16.5 | 71 | 70 | 21.1842 | 15.6634 | 56.3556 | 16.0293 | 16.0293 | 0 | 0
2025-11-25 04:00 | 16.3 | 76.5 | 70 | 21.1099 | 15.8346 | 58.0387 | 24.2252 | 24.2252 | 0 | 0
2025-11-25 05:00 | 16 | 75.5 | 70 | 20.9898 | 15.6855 | 57.699 | 19.8619 | 19.8619 | 0 | 0
2025-11-25 06:00 | 15.65 | 74 | 100 | 20.8489 | 15.4994 | 57.214 | 20.4161 | 20.4161 | 0 | 0
2025-11-25 07:00 | 16.65 | 67.5 | 100 | 21.2405 | 15.5599 | 55.2523 | 15.3736 | 15.3736 | 0 | 0
2025-11-25 08:00 | 19.75 | 55 | 100 | 22.4324 | 15.9712 | 51.2176 | 13.8442 | 13.8442 | 0 | 0
2025-11-25 09:00 | 23.65 | 45 | 100 | 23.874 | 16.6033 | 47.6638 | 20.4932 | 20.4932 | 0 | 0
2025-11-25 10:00 | 26.8 | 39 | 100 | 24.9883 | 17.1257 | 45.3744 | 28.1575 | 28.1575 | 0 | 0
2025-11-25 11:00 | 28.8 | 28 | 100 | 25.6817 | 16.8086 | 40.3726 | 0 | 0 | 0 | 0
2025-11-25 12:00 | 29.95 | 17.5 | 100 | 26.0842 | 16.1646 | 35.1363 | 0 | 0 | 0 | 0
2025-11-25 13:00 | 30.4 | 14.5 | 100 | 26.2403 | 15.9802 | 33.5492 | 0 | 0 | 0 | 0
2025-11-25 14:00 | 30.4 | 14 | 100 | 26.2412 | 15.9317 | 33.2987 | 0 | 0 | 0 | 0
2025-11-25 15:00 | 29.6 | 19 | 100 | 25.9641 | 16.2184 | 35.9493 | 0 | 0 | 0 | 0
2025-11-25 16:00 | 28.05 | 31.5 | 100 | 25.4233 | 16.893 | 42.0529 | 5.9077 | 5.9077 | 0 | 0
2025-11-25 17:00 | 26.3 | 45 | 100 | 24.8118 | 17.4073 | 47.9945 | 49.4157 | 49.4157 | 0 | 0
2025-11-25 18:00 | 24.9 | 52.5 | 100 | 24.3197 | 17.4784 | 50.9282 | 64.1273 | 64.1273 | 0 | 0
2025-11-25 19:00 | 23.95 | 55.5 | 100 | 23.9821 | 17.3602 | 51.9485 | 64.1252 | 64.1252 | 0 | 0
2025-11-25 20:00 | 22.95 | 58 | 100 | 23.6223 | 17.1818 | 52.7243 | 60.9807 | 60.9807 | 0 | 0
2025-11-25 21:00 | 21.75 | 62 | 100 | 23.1848 | 17.0103 | 53.9994 | 59.993 | 59.993 | 0 | 0
2025-11-25 22:00 | 20.5 | 66.5 | 70 | 22.7222 | 16.8275 | 55.3863 | 41.2578 | 41.2578 | 0 | 0
2025-11-25 23:00 | 19.6 | 68 | 70 | 22.3835 | 16.5926 | 55.746 | 36.541 | 36.541 | 0 | 0
2025-11-26 | 18.9 | 67 | 70 | 22.1158 | 16.3009 | 55.2991 | 28.3928 | 28.3928 | 0 | 0
2025-11-26 01:00 | 18.15 | 65 | 70 | 21.8252 | 15.9479 | 54.5562 | 18.1449 | 18.1449 | 0 | 0
2025-11-26 02:00 | 17.6 | 63.5 | 70 | 21.6101 | 15.6925 | 54.0392 | 10.8699 | 10.8699 | 0 | 0
2025-11-26 03:00 | 17.25 | 69 | 70 | 21.4777 | 15.8301 | 55.7867 | 18.5436 | 18.5436 | 0 | 0
2025-11-26 04:00 | 16.95 | 75.5 | 70 | 21.3655 | 16.0205 | 57.8142 | 28.1188 | 28.1188 | 0 | 0
2025-11-26 05:00 | 16.5 | 76 | 70 | 21.1886 | 15.8835 | 57.9129 | 25.0961 | 25.0961 | 0 | 0
2025-11-26 06:00 | 16 | 76 | 100 | 20.9903 | 15.707 | 57.8557 | 29.664 | 29.664 | 0 | 0
2025-11-26 07:00 | 17 | 69.5 | 100 | 21.3801 | 15.7685 | 55.911 | 24.7617 | 24.7617 | 0 | 0
2025-11-26 08:00 | 20.35 | 55 | 100 | 22.6595 | 16.1616 | 51.2572 | 20.4145 | 20.4145 | 0 | 0
2025-11-26 09:00 | 24.2 | 46 | 100 | 24.0717 | 16.8338 | 48.1245 | 30.243 | 30.243 | 0 | 0
2025-11-26 10:00 | 26.65 | 42.5 | 100 | 24.9343 | 17.3366 | 46.9268 | 42.1982 | 42.1982 | 0 | 0
2025-11-26 11:00 | 27.85 | 36.5 | 100 | 25.3503 | 17.2354 | 44.3519 | 27.5018 | 27.5018 | 0 | 0
2025-11-26 12:00 | 28.6 | 31 | 100 | 25.6106 | 17.0015 | 41.821 | 8.3079 | 8.3079 | 0 | 0
2025-11-26 13:00 | 29 | 28.5 | 100 | 25.7487 | 16.8985 | 40.6343 | 0 | 0 | 0 | 0
2025-11-26 14:00 | 28.9 | 29 | 100 | 25.7143 | 16.9136 | 40.8793 | 1.1736 | 1.1736 | 0 | 0
2025-11-26 15:00 | 28.45 | 30.5 | 100 | 25.5604 | 16.9187 | 41.593 | 4.6717 | 4.6717 | 0 | 0
2025-11-26 16:00 | 27.6 | 32 | 100 | 25.269 | 16.8106 | 42.2817 | 4.3 | 4.3 | 0 | 0
2025-11-26 17:00 | 26.45 | 35 | 100 | 24.8693 | 16.7236 | 43.6132 | 7.4311 | 7.4311 | 0 | 0
2025-11-26 18:00 | 25.45 | 39.5 | 100 | 24.5169 | 16.7646 | 45.5271 | 17.1067 | 17.1067 | 0 | 0
2025-11-26 19:00 | 24.5 | 44 | 100 | 24.179 | 16.7909 | 47.3475 | 25.7157 | 25.7157 | 0 | 0
2025-11-26 20:00 | 23.7 | 47.5 | 100 | 23.8921 | 16.7748 | 48.6961 | 30.7649 | 30.7649 | 0 | 0
2025-11-26 21:00 | 23.15 | 48.5 | 100 | 23.6933 | 16.6677 | 49.0409 | 28.5595 | 28.5595 | 0 | 0
2025-11-26 22:00 | 22.55 | 49.5 | 70 | 23.4747 | 16.5419 | 49.3799 | 18.0114 | 18.0114 | 0 | 0
2025-11-26 23:00 | 21.35 | 52 | 70 | 23.0326 | 16.3119 | 50.2398 | 15.0578 | 15.0578 | 0 | 0
2025-11-27 | 19.7 | 55 | 70 | 22.4133 | 15.9527 | 51.2441 | 9.4904 | 9.4904 | 0 | 0
2025-11-27 01:00 | 18.45 | 59.5 | 70 | 21.9372 | 15.7793 | 52.7463 | 9.4953 | 9.4953 | 0 | 0
2025-11-27 02:00 | 17.65 | 63.5 | 70 | 21.6296 | 15.7092 | 54.0382 | 11.2432 | 11.2432 | 0 | 0
2025-11-27 03:00 | 17.25 | 64 | 70 | 21.4736 | 15.5998 | 54.1882 | 9.098 | 9.098 | 0 | 0
2025-11-27 04:00 | 17.6 | 61 | 70 | 21.6081 | 15.5746 | 53.2266 | 6.0342 | 6.0342 | 0 | 0
2025-11-27 05:00 | 17.55 | 60.5 | 70 | 21.5882 | 15.5344 | 53.0622 | 4.6825 | 4.6825 | 0 | 0
2025-11-27 06:00 | 17 | 62.5 | 100 | 21.3741 | 15.4486 | 53.6991 | 6.1748 | 6.1748 | 0 | 0
2025-11-27 07:00 | 17.95 | 59 | 100 | 21.743 | 15.5935 | 52.5596 | 6.658 | 6.658 | 0 | 0
2025-11-27 08:00 | 20.8 | 49.5 | 100 | 22.8259 | 16.0008 | 49.29 | 7.3392 | 7.3392 | 0 | 0
2025-11-27 09:00 | 24.3 | 42 | 100 | 24.1077 | 16.6014 | 46.4921 | 15.5888 | 15.5888 | 0 | 0
2025-11-27 10:00 | 26.55 | 38 | 100 | 24.9023 | 16.9778 | 44.9174 | 21.3005 | 21.3005 | 0 | 0
2025-11-27 11:00 | 27.45 | 34 | 100 | 25.2158 | 16.9288 | 43.1719 | 11.9701 | 11.9701 | 0 | 0
2025-11-27 12:00 | 28.15 | 30 | 100 | 25.4589 | 16.801 | 41.3393 | 0 | 0 | 0 | 0
2025-11-27 13:00 | 28.65 | 27 | 100 | 25.6322 | 16.6832 | 39.9165 | 0 | 0 | 0 | 0
2025-11-27 14:00 | 28.6 | 28.5 | 100 | 25.6135 | 16.7947 | 40.6372 | 0 | 0 | 0 | 0
2025-11-27 15:00 | 27.9 | 36 | 100 | 25.3679 | 17.2085 | 44.1383 | 25.7893 | 25.7893 | 0 | 0
2025-11-27 16:00 | 26.75 | 42.5 | 100 | 24.9688 | 17.3639 | 46.959 | 43.4718 | 43.4718 | 0 | 0
2025-11-27 17:00 | 25.7 | 46 | 100 | 24.6025 | 17.2933 | 48.3289 | 46.8717 | 46.8717 | 0 | 0
2025-11-27 18:00 | 24.85 | 51 | 100 | 24.3024 | 17.3644 | 50.2874 | 57.4479 | 57.4479 | 0 | 0
2025-11-27 19:00 | 24 | 55.5 | 100 | 24 | 17.3776 | 51.9506 | 64.6615 | 64.6615 | 0 | 0
2025-11-27 20:00 | 23.35 | 58 | 100 | 23.7669 | 17.3166 | 52.8004 | 65.8983 | 65.8983 | 0 | 0
2025-11-27 21:00 | 22.45 | 59.5 | 100 | 23.4408 | 17.1046 | 53.1878 | 60.0046 | 60.0046 | 0 | 0
2025-11-27 22:00 | 21.35 | 60 | 70 | 23.036 | 16.7643 | 53.1743 | 33.7372 | 33.7372 | 0 | 0
2025-11-27 23:00 | 20.55 | 61 | 70 | 22.738 | 16.5514 | 53.4197 | 29.3145 | 29.3145 | 0 | 0
2025-11-28 | 19.85 | 62 | 70 | 22.4746 | 16.3696 | 53.6859 | 25.7203 | 25.7203 | 0 | 0
2025-11-28 01:00 | 19.15 | 62.5 | 70 | 22.2085 | 16.1613 | 53.786 | 21.0634 | 21.0634 | 0 | 0
2025-11-28 02:00 | 18.65 | 63 | 70 | 22.0169 | 16.0192 | 53.9139 | 18.0668 | 18.0668 | 0 | 0
2025-11-28 03:00 | 18.2 | 60.5 | 70 | 21.8412 | 15.7479 | 53.0585 | 9.5169 | 9.5169 | 0 | 0
2025-11-28 04:00 | 17.7 | 57.5 | 70 | 21.6444 | 15.4411 | 52.0742 | 0 | 0 | 0 | 0
2025-11-28 05:00 | 17.25 | 57.5 | 70 | 21.4682 | 15.2976 | 52.0886 | 0 | 0 | 0 | 0
2025-11-28 06:00 | 16.85 | 58.5 | 100 | 21.3117 | 15.2167 | 52.4218 | 0 | 0 | 0 | 0
2025-11-28 07:00 | 17.65 | 55.5 | 100 | 21.6233 | 15.3303 | 51.4113 | 0 | 0 | 0 | 0
2025-11-28 08:00 | 20.35 | 47.5 | 100 | 22.6554 | 15.7537 | 48.5641 | 0 | 0 | 0 | 0
2025-11-28 09:00 | 23.55 | 41.5 | 100 | 23.8375 | 16.3493 | 46.2585 | 6.2205 | 6.2205 | 0 | 0
2025-11-28 10:00 | 25.65 | 41.5 | 100 | 24.5865 | 16.9678 | 46.3634 | 27.1612 | 27.1612 | 0 | 0
2025-11-28 11:00 | 26.75 | 41.5 | 100 | 24.9694 | 17.2941 | 46.489 | 38.7919 | 38.7919 | 0 | 0
2025-11-28 12:00 | 27.55 | 37.5 | 100 | 25.2471 | 17.2275 | 44.7813 | 29.1124 | 29.1124 | 0 | 0
2025-11-28 13:00 | 28 | 34.5 | 100 | 25.4033 | 17.1203 | 43.4381 | 19.5714 | 19.5714 | 0 | 0
2025-11-28 14:00 | 27.85 | 36.5 | 100 | 25.3504 | 17.2345 | 44.3588 | 27.5721 | 27.5721 | 0 | 0
2025-11-28 15:00 | 27.3 | 42 | 100 | 25.158 | 17.4933 | 46.8134 | 47.2291 | 47.2291 | 0 | 0
2025-11-28 16:00 | 26.5 | 46 | 100 | 24.8805 | 17.5414 | 48.4646 | 56.0005 | 56.0005 | 0 | 0
2025-11-28 17:00 | 25.7 | 47 | 100 | 24.6021 | 17.3626 | 48.7551 | 51.0372 | 51.0372 | 0 | 0
2025-11-28 18:00 | 25 | 50 | 100 | 24.3555 | 17.3463 | 49.8974 | 55.1928 | 55.1928 | 0 | 0
2025-11-28 19:00 | 24.2 | 55 | 100 | 24.0713 | 17.4124 | 51.7914 | 65.2178 | 65.2178 | 0 | 0
2025-11-28 20:00 | 23.35 | 58.5 | 100 | 23.767 | 17.3472 | 52.9972 | 67.7461 | 67.7461 | 0 | 0
2025-11-28 21:00 | 22.45 | 60 | 100 | 23.4409 | 17.1335 | 53.3806 | 61.7877 | 61.7877 | 0 | 0
2025-11-28 22:00 | 21.55 | 61 | 70 | 23.1105 | 16.8872 | 53.5824 | 37.8296 | 37.8296 | 0 | 0
2025-11-28 23:00 | 20.65 | 64 | 70 | 22.777 | 16.746 | 54.5161 | 36.9498 | 36.9498 | 0 | 0
2025-11-29 | 19.95 | 67.5 | 70 | 22.5158 | 16.6894 | 55.6294 | 38.5296 | 38.5296 | 0 | 0
2025-11-29 01:00 | 19.5 | 70.5 | 70 | 22.3472 | 16.685 | 56.5838 | 40.9187 | 40.9187 | 0 | 0
2025-11-29 02:00 | 19.1 | 72.5 | 70 | 22.1962 | 16.6429 | 57.1881 | 41.4706 | 41.4706 | 0 | 0
2025-11-29 03:00 | 18.6 | 74.5 | 70 | 22.006 | 16.5623 | 57.7582 | 40.9632 | 40.9632 | 0 | 0
2025-11-29 04:00 | 18.25 | 75.5 | 70 | 21.872 | 16.4845 | 58.0178 | 39.731 | 39.731 | 0 | 0
2025-11-29 05:00 | 17.95 | 75.5 | 70 | 21.7559 | 16.3772 | 57.9592 | 36.9773 | 36.9773 | 0 | 0
2025-11-29 06:00 | 17.55 | 76 | 100 | 21.6008 | 16.2574 | 58.0466 | 48.9912 | 48.9912 | 0 | 0
2025-11-29 07:00 | 18.45 | 71 | 100 | 21.9457 | 16.3413 | 56.5541 | 46.4291 | 46.4291 | 0 | 0
2025-11-29 08:00 | 21.2 | 60 | 100 | 22.9803 | 16.7141 | 53.1463 | 46.3464 | 46.3464 | 0 | 0
2025-11-29 09:00 | 24.2 | 52 | 100 | 24.0715 | 17.222 | 50.5587 | 53.4716 | 53.4716 | 0 | 0
2025-11-29 10:00 | 26.25 | 45.5 | 100 | 24.7942 | 17.4309 | 48.1775 | 50.732 | 50.732 | 0 | 0
2025-11-29 11:00 | 27.45 | 37.5 | 100 | 25.2129 | 17.1985 | 44.7707 | 28.0915 | 28.0915 | 0 | 0
2025-11-29 12:00 | 28.25 | 31 | 100 | 25.4919 | 16.9086 | 41.8115 | 5.1791 | 5.1791 | 0 | 0
2025-11-29 13:00 | 28.7 | 28.5 | 100 | 25.6474 | 16.8206 | 40.6349 | 0 | 0 | 0 | 0
2025-11-29 14:00 | 28.6 | 30.5 | 100 | 25.6112 | 16.9586 | 41.5931 | 5.9657 | 5.9657 | 0 | 0
2025-11-29 15:00 | 27.85 | 31.5 | 100 | 25.3551 | 16.8384 | 42.0537 | 4.1725 | 4.1725 | 0 | 0
2025-11-29 16:00 | 26.9 | 33 | 100 | 25.0268 | 16.697 | 42.7318 | 2.6613 | 2.6613 | 0 | 0
2025-11-29 17:00 | 25.9 | 38.5 | 100 | 24.6754 | 16.8223 | 45.1289 | 17.3914 | 17.3914 | 0 | 0
2025-11-29 18:00 | 24.95 | 42.5 | 100 | 24.3393 | 16.8239 | 46.7683 | 24.4516 | 24.4516 | 0 | 0
2025-11-29 19:00 | 24.05 | 44.5 | 100 | 24.018 | 16.688 | 47.5234 | 23.0459 | 23.0459 | 0 | 0
2025-11-29 20:00 | 23.05 | 47.5 | 100 | 23.6568 | 16.5736 | 48.646 | 23.8624 | 23.8624 | 0 | 0
2025-11-29 21:00 | 22.05 | 52 | 100 | 23.2918 | 16.533 | 50.2945 | 29.1413 | 29.1413 | 0 | 0
2025-11-29 22:00 | 21 | 58.5 | 70 | 22.9051 | 16.5634 | 52.5898 | 27.4345 | 27.4345 | 0 | 0
2025-11-29 23:00 | 20.05 | 65 | 70 | 22.552 | 16.593 | 54.7768 | 34.0056 | 34.0056 | 0 | 0
2025-11-30 | 19.35 | 69 | 70 | 22.2891 | 16.5566 | 56.0473 | 36.4519 | 36.4519 | 0 | 0
2025-11-30 01:00 | 18.85 | 71 | 70 | 22.0995 | 16.4804 | 56.6397 | 36.1596 | 36.1596 | 0 | 0
2025-11-30 02:00 | 18.3 | 73.5 | 70 | 21.8897 | 16.4068 | 57.3782 | 36.283 | 36.283 | 0 | 0
2025-11-30 03:00 | 17.8 | 77.5 | 70 | 21.6992 | 16.4158 | 58.5936 | 39.5588 | 39.5588 | 0 | 0
2025-11-30 04:00 | 17.35 | 81.5 | 70 | 21.5272 | 16.4339 | 59.7843 | 42.962 | 42.962 | 0 | 0
2025-11-30 05:00 | 16.85 | 84 | 70 | 21.3335 | 16.3606 | 60.4625 | 42.8298 | 42.8298 | 0 | 0
2025-11-30 06:00 | 16.45 | 85 | 100 | 21.1768 | 16.2561 | 60.6827 | 58.281 | 58.281 | 0 | 0
2025-11-30 07:00 | 17.3 | 78.5 | 100 | 21.5052 | 16.2812 | 58.8042 | 52.5211 | 52.5211 | 0 | 0
2025-11-30 08:00 | 20.3 | 63 | 100 | 22.6451 | 16.5741 | 54.0967 | 45.2426 | 45.2426 | 0 | 0
2025-11-30 09:00 | 23.95 | 49 | 100 | 23.9821 | 16.9503 | 49.3126 | 39.0952 | 39.0952 | 0 | 0
2025-11-30 10:00 | 26.3 | 39 | 100 | 24.8149 | 16.9786 | 45.3449 | 23.2293 | 23.2293 | 0 | 0
2025-11-30 11:00 | 27.4 | 31 | 100 | 25.201 | 16.6818 | 41.8041 | 0 | 0 | 0 | 0
2025-11-30 12:00 | 28.1 | 26.5 | 100 | 25.4454 | 16.5018 | 39.7047 | 0 | 0 | 0 | 0
2025-11-30 13:00 | 28.55 | 24.5 | 100 | 25.6012 | 16.4473 | 38.736 | 0 | 0 | 0 | 0
2025-11-30 14:00 | 28.4 | 28.5 | 100 | 25.5456 | 16.7405 | 40.6473 | 0 | 0 | 0 | 0
2025-11-30 15:00 | 27.75 | 36.5 | 100 | 25.3163 | 17.2032 | 44.3658 | 26.7393 | 26.7393 | 0 | 0
2025-11-30 16:00 | 26.65 | 42 | 100 | 24.9346 | 17.2959 | 46.734 | 40.2879 | 40.2879 | 0 | 0
2025-11-30 17:00 | 25.5 | 46 | 100 | 24.5324 | 17.2297 | 48.3102 | 44.7401 | 44.7401 | 0 | 0
2025-11-30 18:00 | 24.7 | 51 | 100 | 24.2493 | 17.3145 | 50.2721 | 55.7897 | 55.7897 | 0 | 0
2025-11-30 19:00 | 23.9 | 57 | 100 | 23.9643 | 17.4373 | 52.5455 | 69.2633 | 69.2633 | 0 | 0
2025-11-30 20:00 | 23.2 | 62.5 | 100 | 23.7135 | 17.5359 | 54.5429 | 80.6306 | 80.6306 | 0 | 0
2025-11-30 21:00 | 22.4 | 66 | 100 | 23.4243 | 17.4627 | 55.6657 | 82.3578 | 82.3578 | 0 | 0
2025-11-30 22:00 | 21.4 | 63.5 | 70 | 23.056 | 16.9746 | 54.4859 | 42.454 | 42.454 | 0 | 0
2025-11-30 23:00 | 20.4 | 57 | 70 | 22.6794 | 16.2851 | 51.9887 | 19.2341 | 19.2341 | 0 | 0
2025-12-01 | 19.65 | 54 | 70 | 22.3937 | 15.8837 | 50.899 | 6.9933 | 6.9933 | 0 | 0
2025-12-01 01:00 | 19.25 | 54.5 | 70 | 22.2413 | 15.7835 | 51.071 | 5.1593 | 5.1593 | 0 | 0
2025-12-01 02:00 | 18.85 | 56 | 70 | 22.0889 | 15.7324 | 51.584 | 5.3866 | 5.3866 | 0 | 0
2025-12-01 03:00 | 18.65 | 57 | 70 | 22.0125 | 15.7187 | 51.922 | 5.978 | 5.978 | 0 | 0
2025-12-01 04:00 | 18.8 | 56 | 70 | 22.0696 | 15.7164 | 51.5859 | 5.033 | 5.033 | 0 | 0
2025-12-01 05:00 | 18.8 | 55 | 70 | 22.0689 | 15.6659 | 51.2473 | 2.9711 | 2.9711 | 0 | 0
2025-12-01 06:00 | 18.55 | 55.5 | 100 | 21.9729 | 15.6124 | 51.4128 | 3.0829 | 3.0829 | 0 | 0
2025-12-01 07:00 | 19.2 | 53 | 100 | 22.2212 | 15.6908 | 50.5463 | 2.2552 | 2.2552 | 0 | 0
2025-12-01 08:00 | 21.5 | 46 | 100 | 23.0859 | 16.014 | 48.0115 | 2.6898 | 2.6898 | 0 | 0
2025-12-01 09:00 | 24.25 | 40.5 | 100 | 24.0899 | 16.4867 | 45.8809 | 9.2585 | 9.2585 | 0 | 0
2025-12-01 10:00 | 26.1 | 41.5 | 100 | 24.744 | 17.1001 | 46.4195 | 31.9688 | 31.9688 | 0 | 0
2025-12-01 11:00 | 27.1 | 42.5 | 100 | 25.0892 | 17.4713 | 46.9976 | 47.1769 | 47.1769 | 0 | 0
2025-12-01 12:00 | 27.85 | 38 | 100 | 25.3489 | 17.3506 | 45.0538 | 34.6158 | 34.6158 | 0 | 0
2025-12-01 13:00 | 28.25 | 35 | 100 | 25.4877 | 17.2277 | 43.7019 | 24.4948 | 24.4948 | 0 | 0
2025-12-01 14:00 | 27.95 | 36.5 | 100 | 25.3844 | 17.2607 | 44.3797 | 28.6935 | 28.6935 | 0 | 0
2025-12-01 15:00 | 27.3 | 37.5 | 100 | 25.1615 | 17.152 | 44.7828 | 26.8449 | 26.8449 | 0 | 0
2025-12-01 16:00 | 26.45 | 39 | 100 | 24.8671 | 17.0182 | 45.3839 | 25.0113 | 25.0113 | 0 | 0
2025-12-01 17:00 | 25.3 | 45 | 100 | 24.4624 | 17.1003 | 47.8563 | 38.3751 | 38.3751 | 0 | 0
2025-12-01 18:00 | 24.25 | 52 | 100 | 24.0893 | 17.2356 | 50.5974 | 54.3512 | 54.3512 | 0 | 0
2025-12-01 19:00 | 23.45 | 57 | 100 | 23.8029 | 17.2875 | 52.4407 | 63.5683 | 63.5683 | 0 | 0
2025-12-01 20:00 | 22.8 | 60 | 100 | 23.5683 | 17.2505 | 53.4673 | 66.315 | 66.315 | 0 | 0
2025-12-01 21:00 | 22.15 | 61.5 | 100 | 23.3316 | 17.1178 | 53.895 | 63.3303 | 63.3303 | 0 | 0
2025-12-01 22:00 | 21.2 | 64 | 70 | 22.9821 | 16.9341 | 54.6229 | 41.8049 | 41.8049 | 0 | 0
2025-12-01 23:00 | 19.95 | 67.5 | 70 | 22.5158 | 16.6889 | 55.6299 | 38.5327 | 38.5327 | 0 | 0
2025-12-02 | 18.7 | 70 | 70 | 22.0412 | 16.3796 | 56.2716 | 32.7495 | 32.7495 | 0 | 0
2025-12-02 01:00 | 17.65 | 72.5 | 70 | 21.6369 | 16.1313 | 56.9411 | 28.521 | 28.521 | 0 | 0
2025-12-02 02:00 | 17.05 | 74 | 70 | 21.4035 | 15.989 | 57.3468 | 26.1695 | 26.1695 | 0 | 0
2025-12-02 03:00 | 16.95 | 73.5 | 70 | 21.3638 | 15.9311 | 57.1808 | 24.4004 | 24.4004 | 0 | 0
2025-12-02 04:00 | 16.95 | 73.5 | 70 | 21.3638 | 15.9307 | 57.1813 | 24.4035 | 24.4035 | 0 | 0
2025-12-02 05:00 | 16.8 | 75 | 70 | 21.3061 | 15.9452 | 57.6344 | 25.8673 | 25.8673 | 0 | 0
2025-12-02 06:00 | 16.75 | 76 | 100 | 21.2872 | 15.972 | 57.9358 | 38.9025 | 38.9025 | 0 | 0
2025-12-02 07:00 | 17.7 | 71.5 | 100 | 21.6556 | 16.1025 | 56.6177 | 38.558 | 38.558 | 0 | 0
2025-12-02 08:00 | 20.4 | 60 | 100 | 22.6811 | 16.4477 | 53.042 | 36.8968 | 36.8968 | 0 | 0
2025-12-02 09:00 | 23.7 | 50 | 100 | 23.8923 | 16.9347 | 49.6812 | 40.0915 | 40.0915 | 0 | 0
2025-12-02 10:00 | 25.95 | 47 | 100 | 24.6893 | 17.4426 | 48.7848 | 53.7784 | 53.7784 | 0 | 0
2025-12-02 11:00 | 27.3 | 44.5 | 100 | 25.1561 | 17.6807 | 47.9372 | 58.4887 | 58.4887 | 0 | 0
2025-12-02 12:00 | 28.25 | 40.5 | 100 | 25.4818 | 17.6625 | 46.2761 | 50.7205 | 50.7205 | 0 | 0
2025-12-02 13:00 | 28.6 | 40.5 | 100 | 25.5995 | 17.7657 | 46.3446 | 54.6826 | 54.6826 | 0 | 0
2025-12-02 14:00 | 28.25 | 46.5 | 100 | 25.4755 | 18.1257 | 49.0918 | 79.3113 | 79.3113 | 0 | 0
2025-12-02 15:00 | 27.4 | 52.5 | 100 | 25.1837 | 18.2973 | 51.6043 | 96.1468 | 96.1468 | 0 | 0
2025-12-02 16:00 | 26.2 | 56.5 | 100 | 24.7715 | 18.177 | 52.991 | 97.5478 | 97.5478 | 0 | 0
2025-12-02 17:00 | 25 | 63 | 100 | 24.3528 | 18.1933 | 55.3323 | 107.5432 | 107.5432 | 0 | 0
2025-12-02 18:00 | 24.25 | 68.5 | 100 | 24.0885 | 18.271 | 57.291 | 118.0127 | 118.0127 | 0 | 0
2025-12-02 19:00 | 23.75 | 71.5 | 100 | 23.9113 | 18.2696 | 58.281 | 121.7548 | 121.7548 | 0 | 0
2025-12-02 20:00 | 23.15 | 74.5 | 100 | 23.6973 | 18.2237 | 59.2002 | 123.5283 | 123.5283 | 0 | 0
2025-12-02 21:00 | 22.35 | 75.5 | 100 | 23.4088 | 17.9828 | 59.2508 | 114.8129 | 114.8129 | 0 | 0
2025-12-02 22:00 | 21.4 | 76.5 | 70 | 23.0616 | 17.6843 | 59.2595 | 72.7603 | 72.7603 | 0 | 0
2025-12-02 23:00 | 20.2 | 81 | 70 | 22.6178 | 17.4699 | 60.4384 | 70.3655 | 70.3655 | 0 | 0
2025-12-03 | 19.15 | 86 | 70 | 22.2245 | 17.3182 | 61.784 | 69.9129 | 69.9129 | 0 | 0
2025-12-03 01:00 | 18.6 | 89.5 | 70 | 22.017 | 17.2725 | 62.7549 | 71.1523 | 71.1523 | 0 | 0
2025-12-03 02:00 | 18.15 | 91.5 | 70 | 21.8457 | 17.1898 | 63.2468 | 70.2668 | 70.2668 | 0 | 0
2025-12-03 03:00 | 17.9 | 92.5 | 70 | 21.7499 | 17.1381 | 63.4794 | 69.5109 | 69.5109 | 0 | 0
2025-12-03 04:00 | 17.9 | 93 | 70 | 21.7503 | 17.1606 | 63.6391 | 70.4626 | 70.4626 | 0 | 0
2025-12-03 05:00 | 17.9 | 92.5 | 70 | 21.7499 | 17.1381 | 63.4737 | 69.4767 | 69.4767 | 0 | 0
2025-12-03 06:00 | 17.75 | 92 | 100 | 21.6914 | 17.0579 | 63.2525 | 95.5318 | 95.5318 | 0 | 0
2025-12-03 07:00 | 18.3 | 89 | 100 | 21.9015 | 17.1338 | 62.4663 | 95.5224 | 95.5224 | 0 | 0
2025-12-03 08:00 | 20.65 | 78.5 | 100 | 22.7846 | 17.5112 | 59.7004 | 99.2138 | 99.2138 | 0 | 0
2025-12-03 09:00 | 23.6 | 67 | 100 | 23.8575 | 17.947 | 56.4231 | 102.6149 | 102.6149 | 0 | 0
2025-12-03 10:00 | 25.65 | 61 | 100 | 24.5797 | 18.2932 | 54.7 | 108.4108 | 108.4108 | 0 | 0
2025-12-03 11:00 | 27.1 | 53.5 | 100 | 25.0812 | 18.2725 | 51.9333 | 96.3702 | 96.3702 | 0 | 0
2025-12-03 12:00 | 28.25 | 45 | 100 | 25.477 | 18.0123 | 48.3769 | 72.0586 | 72.0586 | 0 | 0
2025-12-03 13:00 | 28.7 | 43.5 | 100 | 25.6293 | 18.0338 | 47.7824 | 70.3132 | 70.3132 | 0 | 0
2025-12-03 14:00 | 28.35 | 48 | 100 | 25.5073 | 18.2727 | 49.8135 | 87.6013 | 87.6013 | 0 | 0
2025-12-03 15:00 | 27.55 | 52 | 100 | 25.2348 | 18.3116 | 51.4179 | 95.7986 | 95.7986 | 0 | 0
2025-12-03 16:00 | 26.6 | 58.5 | 100 | 24.9076 | 18.4521 | 53.9942 | 111.5814 | 111.5814 | 0 | 0
2025-12-03 17:00 | 25.55 | 67.5 | 100 | 24.5429 | 18.6811 | 57.4305 | 133.7665 | 133.7665 | 0 | 0
2025-12-03 18:00 | 24.65 | 71.5 | 100 | 24.2289 | 18.6027 | 58.6752 | 135.6476 | 135.6476 | 0 | 0
2025-12-03 19:00 | 24 | 73 | 100 | 24 | 18.4525 | 58.9807 | 131.1751 | 131.1751 | 0 | 0
2025-12-03 20:00 | 23.4 | 74.5 | 100 | 23.7868 | 18.3174 | 59.3038 | 127.3579 | 127.3579 | 0 | 0
2025-12-03 21:00 | 22.6 | 77 | 100 | 23.4998 | 18.1604 | 59.9173 | 123.8357 | 123.8357 | 0 | 0
2025-12-03 22:00 | 21.65 | 82 | 70 | 23.1557 | 18.0743 | 61.3696 | 88.1971 | 88.1971 | 0 | 0
2025-12-03 23:00 | 20.7 | 87.5 | 70 | 22.8079 | 17.9934 | 62.9272 | 90.0491 | 90.0491 | 0 | 0
2025-12-04 | 19.85 | 91.5 | 70 | 22.4927 | 17.8578 | 63.9357 | 89.0475 | 89.0475 | 0 | 0
2025-12-04 01:00 | 19.3 | 93 | 70 | 22.2862 | 17.7126 | 64.197 | 85.9067 | 85.9067 | 0 | 0
2025-12-04 02:00 | 18.85 | 93 | 70 | 22.1151 | 17.5341 | 64.0007 | 80.8252 | 80.8252 | 0 | 0
2025-12-04 03:00 | 18.7 | 91.5 | 70 | 22.0568 | 17.405 | 63.4398 | 76.141 | 76.141 | 0 | 0
2025-12-04 04:00 | 18.8 | 89.5 | 70 | 22.0935 | 17.3501 | 62.8137 | 73.2086 | 73.2086 | 0 | 0
2025-12-04 05:00 | 18.7 | 88 | 70 | 22.0542 | 17.241 | 62.2765 | 69.1093 | 69.1093 | 0 | 0
2025-12-04 06:00 | 18.6 | 86.5 | 100 | 22.0148 | 17.1324 | 61.7381 | 92.8767 | 92.8767 | 0 | 0
2025-12-04 07:00 | 19.3 | 82 | 100 | 22.2788 | 17.1827 | 60.4533 | 90.051 | 90.051 | 0 | 0
2025-12-04 08:00 | 21.55 | 71 | 100 | 23.1146 | 17.4421 | 57.266 | 87.5647 | 87.5647 | 0 | 0
2025-12-04 09:00 | 24.3 | 59 | 100 | 24.1067 | 17.7005 | 53.4249 | 81.8135 | 81.8135 | 0 | 0
2025-12-04 10:00 | 26.25 | 47.5 | 100 | 24.7932 | 17.5722 | 49.0489 | 59.3176 | 59.3176 | 0 | 0
2025-12-04 11:00 | 27.65 | 37.5 | 100 | 25.2813 | 17.2568 | 44.7866 | 30.0794 | 30.0794 | 0 | 0
2025-12-04 12:00 | 28.65 | 33 | 100 | 25.6251 | 17.1799 | 42.7705 | 18.5035 | 18.5035 | 0 | 0
2025-12-04 13:00 | 29.2 | 31 | 100 | 25.8125 | 17.163 | 41.8456 | 13.7472 | 13.7472 | 0 | 0
2025-12-04 14:00 | 29.3 | 31.5 | 100 | 25.8453 | 17.2315 | 42.0971 | 17.2221 | 17.2221 | 0 | 0
2025-12-04 15:00 | 28.65 | 37 | 100 | 25.6204 | 17.5022 | 44.685 | 38.1538 | 38.1538 | 0 | 0
2025-12-04 16:00 | 27.25 | 45 | 100 | 25.1386 | 17.701 | 48.1647 | 60.2864 | 60.2864 | 0 | 0
2025-12-04 17:00 | 26 | 51 | 100 | 24.705 | 17.7339 | 50.5391 | 71.4741 | 71.4741 | 0 | 0
2025-12-04 18:00 | 25.15 | 56.5 | 100 | 24.4068 | 17.8246 | 52.6517 | 83.3184 | 83.3184 | 0 | 0
2025-12-04 19:00 | 24.35 | 62 | 100 | 24.1242 | 17.9046 | 54.6743 | 94.2441 | 94.2441 | 0 | 0
2025-12-04 20:00 | 23.7 | 66 | 100 | 23.8932 | 17.9223 | 56.0628 | 100.3278 | 100.3278 | 0 | 0
2025-12-04 21:00 | 23.2 | 68 | 100 | 23.7143 | 17.8635 | 56.676 | 100.5589 | 100.5589 | 0 | 0
2025-12-04 22:00 | 22.8 | 69 | 70 | 23.5703 | 17.7784 | 56.9263 | 68.909 | 68.909 | 0 | 0
2025-12-04 23:00 | 22.15 | 71 | 70 | 23.3346 | 17.6577 | 57.4714 | 67.3345 | 67.3345 | 0 | 0
2025-12-05 | 21.65 | 71.5 | 70 | 23.1516 | 17.5047 | 57.4974 | 63.5584 | 63.5584 | 0 | 0
2025-12-05 01:00 | 21.5 | 71.5 | 70 | 23.0963 | 17.4504 | 57.451 | 62.0789 | 62.0789 | 0 | 0
2025-12-05 02:00 | 21.15 | 72.5 | 70 | 22.9674 | 17.3777 | 57.7109 | 60.9576 | 60.9576 | 0 | 0
2025-12-05 03:00 | 20.95 | 71.5 | 70 | 22.8927 | 17.252 | 57.2921 | 56.7337 | 56.7337 | 0 | 0
2025-12-05 04:00 | 20.95 | 70 | 70 | 22.892 | 17.1721 | 56.7501 | 53.3184 | 53.3184 | 0 | 0
2025-12-05 05:00 | 20.55 | 71.5 | 70 | 22.7436 | 17.1092 | 57.178 | 52.8619 | 52.8619 | 0 | 0
2025-12-05 06:00 | 20.15 | 73 | 100 | 22.5944 | 17.0438 | 57.5969 | 74.7276 | 74.7276 | 0 | 0
2025-12-05 07:00 | 20.4 | 71.5 | 100 | 22.6874 | 17.056 | 57.1267 | 73.3687 | 73.3687 | 0 | 0
2025-12-05 08:00 | 21.5 | 67 | 100 | 23.0945 | 17.2042 | 55.7776 | 73.4781 | 73.4781 | 0 | 0
2025-12-05 09:00 | 23.35 | 62.5 | 100 | 23.7675 | 17.5899 | 54.5571 | 82.3757 | 82.3757 | 0 | 0
2025-12-05 10:00 | 25.25 | 57.5 | 100 | 24.4415 | 17.9265 | 53.077 | 88.4644 | 88.4644 | 0 | 0
2025-12-05 11:00 | 27 | 49.5 | 100 | 25.05 | 17.9538 | 50.1041 | 77.176 | 77.176 | 0 | 0
2025-12-05 12:00 | 28.1 | 42 | 100 | 25.4297 | 17.7367 | 46.9344 | 55.9976 | 55.9976 | 0 | 0
2025-12-05 13:00 | 28.25 | 38.5 | 100 | 25.484 | 17.5074 | 45.3301 | 41.091 | 41.091 | 0 | 0
2025-12-05 14:00 | 27.9 | 42.5 | 100 | 25.3616 | 17.7132 | 47.1387 | 56.1782 | 56.1782 | 0 | 0
2025-12-05 15:00 | 27.2 | 51 | 100 | 25.117 | 18.1255 | 50.8454 | 86.5559 | 86.5559 | 0 | 0
2025-12-05 16:00 | 26.45 | 54.5 | 100 | 24.8585 | 18.126 | 52.172 | 92.0817 | 92.0817 | 0 | 0
2025-12-05 17:00 | 25.55 | 58.5 | 100 | 24.5458 | 18.0931 | 53.6082 | 96.7589 | 96.7589 | 0 | 0
2025-12-05 18:00 | 24.25 | 69.5 | 100 | 24.0884 | 18.3335 | 57.6687 | 121.5869 | 121.5869 | 0 | 0
2025-12-05 19:00 | 23.1 | 76 | 100 | 23.6796 | 18.2925 | 59.7373 | 127.9459 | 127.9459 | 0 | 0
2025-12-05 20:00 | 22.15 | 78 | 100 | 23.3368 | 18.0478 | 60.0846 | 120.1452 | 120.1452 | 0 | 0
2025-12-05 21:00 | 21.55 | 78.5 | 100 | 23.1176 | 17.849 | 60.0236 | 112.6036 | 112.6036 | 0 | 0
2025-12-05 22:00 | 21.65 | 75 | 70 | 23.1529 | 17.6965 | 58.7744 | 71.6899 | 71.6899 | 0 | 0
2025-12-05 23:00 | 21.6 | 73.5 | 70 | 23.134 | 17.5967 | 58.2064 | 67.6753 | 67.6753 | 0 | 0
2025-12-06 | 20.95 | 76.5 | 70 | 22.8951 | 17.5185 | 59.0793 | 67.9846 | 67.9846 | 0 | 0
2025-12-06 01:00 | 19.9 | 82 | 70 | 22.5057 | 17.4086 | 60.6567 | 69.241 | 69.241 | 0 | 0
2025-12-06 02:00 | 18.85 | 87.5 | 70 | 22.1112 | 17.2756 | 62.1544 | 69.6368 | 69.6368 | 0 | 0
2025-12-06 03:00 | 18.55 | 85.5 | 70 | 21.9949 | 17.0668 | 61.3881 | 62.482 | 62.482 | 0 | 0
2025-12-06 04:00 | 18.55 | 82 | 70 | 21.9923 | 16.9022 | 60.2285 | 55.484 | 55.484 | 0 | 0
2025-12-06 05:00 | 18.05 | 86 | 70 | 21.8028 | 16.9006 | 61.3932 | 58.3285 | 58.3285 | 0 | 0
2025-12-06 06:00 | 17.55 | 90.5 | 100 | 21.6126 | 16.9136 | 62.6815 | 88.25 | 88.25 | 0 | 0
2025-12-06 07:00 | 17.95 | 89.5 | 100 | 21.7669 | 17.0228 | 62.4868 | 91.4536 | 91.4536 | 0 | 0
2025-12-06 08:00 | 20.1 | 79.5 | 100 | 22.5794 | 17.3581 | 59.8433 | 94.071 | 94.071 | 0 | 0
2025-12-06 09:00 | 23.25 | 66 | 100 | 23.732 | 17.7645 | 55.894 | 93.8023 | 93.8023 | 0 | 0
2025-12-06 10:00 | 25.65 | 56.5 | 100 | 24.5813 | 17.9955 | 52.7717 | 89.6779 | 89.6779 | 0 | 0
2025-12-06 11:00 | 27.1 | 50 | 100 | 25.0837 | 18.0221 | 50.3511 | 80.6285 | 80.6285 | 0 | 0
2025-12-06 12:00 | 28.1 | 44 | 100 | 25.4277 | 17.8908 | 47.8611 | 65.3887 | 65.3887 | 0 | 0
2025-12-06 13:00 | 28.55 | 41.5 | 100 | 25.5815 | 17.833 | 46.7875 | 58.7336 | 58.7336 | 0 | 0
2025-12-06 14:00 | 28 | 46.5 | 100 | 25.3915 | 18.0494 | 49.0066 | 76.0125 | 76.0125 | 0 | 0
2025-12-06 15:00 | 27.15 | 52.5 | 100 | 25.0989 | 18.2165 | 51.5048 | 92.6184 | 92.6184 | 0 | 0
2025-12-06 16:00 | 26.6 | 55.5 | 100 | 24.9094 | 18.2454 | 52.6628 | 98.462 | 98.462 | 0 | 0
2025-12-06 17:00 | 25.75 | 60.5 | 100 | 24.6145 | 18.2942 | 54.5317 | 107.8438 | 107.8438 | 0 | 0
2025-12-06 18:00 | 24.95 | 65.5 | 100 | 24.3348 | 18.3371 | 56.324 | 116.5112 | 116.5112 | 0 | 0
2025-12-06 19:00 | 24.4 | 69.5 | 100 | 24.1413 | 18.3884 | 57.7329 | 123.8723 | 123.8723 | 0 | 0
2025-12-06 20:00 | 23.85 | 74.5 | 100 | 23.9469 | 18.4865 | 59.4904 | 134.2588 | 134.2588 | 0 | 0
2025-12-06 21:00 | 23.1 | 78 | 100 | 23.68 | 18.4076 | 60.5077 | 135.1045 | 135.1045 | 0 | 0
2025-12-06 22:00 | 22.45 | 79.5 | 70 | 23.4462 | 18.2443 | 60.78 | 91.0202 | 91.0202 | 0 | 0
2025-12-06 23:00 | 22.05 | 81.5 | 70 | 23.3016 | 18.2006 | 61.349 | 91.3759 | 91.3759 | 0 | 0
2025-12-07 | 21.4 | 84 | 70 | 23.0648 | 18.0846 | 61.9731 | 89.9397 | 89.9397 | 0 | 0
2025-12-07 01:00 | 20.65 | 86 | 70 | 22.7885 | 17.8974 | 62.3557 | 86.0531 | 86.0531 | 0 | 0
2025-12-07 02:00 | 20.05 | 87 | 70 | 22.565 | 17.7154 | 62.4479 | 81.5664 | 81.5664 | 0 | 0
2025-12-07 03:00 | 19.55 | 85.5 | 70 | 22.3758 | 17.4479 | 61.731 | 72.9417 | 72.9417 | 0 | 0
2025-12-07 04:00 | 19.25 | 83.5 | 70 | 22.2608 | 17.2369 | 60.9428 | 65.6129 | 65.6129 | 0 | 0
2025-12-07 05:00 | 19.15 | 83.5 | 70 | 22.2228 | 17.1993 | 60.9067 | 64.5623 | 64.5623 | 0 | 0
2025-12-07 06:00 | 19 | 84.5 | 100 | 22.1663 | 17.1903 | 61.1884 | 92.8987 | 92.8987 | 0 | 0
2025-12-07 07:00 | 19.65 | 81.5 | 100 | 22.4111 | 17.2904 | 60.3818 | 93.5462 | 93.5462 | 0 | 0
2025-12-07 08:00 | 21.8 | 72 | 100 | 23.2069 | 17.5877 | 57.7009 | 94.3408 | 94.3408 | 0 | 0
2025-12-07 09:00 | 24.7 | 59.5 | 100 | 24.2481 | 17.8696 | 53.7316 | 88.9709 | 88.9709 | 0 | 0
2025-12-07 10:00 | 27.05 | 48 | 100 | 25.0681 | 17.8632 | 49.4291 | 70.9491 | 70.9491 | 0 | 0
2025-12-07 11:00 | 28.5 | 39.5 | 100 | 25.567 | 17.6634 | 45.8147 | 48.3316 | 48.3316 | 0 | 0
2025-12-07 12:00 | 29.55 | 34.5 | 100 | 25.9241 | 17.5573 | 43.5619 | 34.6237 | 34.6237 | 0 | 0
2025-12-07 13:00 | 30.3 | 32 | 100 | 26.1758 | 17.5498 | 42.4061 | 29.1039 | 29.1039 | 0 | 0
2025-12-07 14:00 | 30.35 | 32 | 100 | 26.1922 | 17.563 | 42.4151 | 29.6315 | 29.6315 | 0 | 0
2025-12-07 15:00 | 29.4 | 38 | 100 | 25.8692 | 17.8034 | 45.2652 | 50.9458 | 50.9458 | 0 | 0
2025-12-07 16:00 | 28.15 | 45.5 | 100 | 25.4429 | 18.0196 | 48.5823 | 73.1762 | 73.1762 | 0 | 0
2025-12-07 17:00 | 26.95 | 52 | 100 | 25.0312 | 18.115 | 51.2209 | 87.7738 | 87.7738 | 0 | 0
2025-12-07 18:00 | 25.95 | 55.5 | 100 | 24.6857 | 18.0277 | 52.4522 | 89.6773 | 89.6773 | 0 | 0
2025-12-07 19:00 | 25.1 | 51 | 100 | 24.3905 | 17.4458 | 50.3245 | 60.3226 | 60.3226 | 0 | 0
2025-12-07 20:00 | 23.95 | 48.5 | 100 | 23.9821 | 16.9183 | 49.108 | 37.1501 | 37.1501 | 0 | 0
2025-12-07 21:00 | 22.5 | 51.5 | 100 | 23.4569 | 16.6479 | 50.125 | 32.1451 | 32.1451 | 0 | 0
2025-12-07 22:00 | 21.4 | 56.5 | 70 | 23.0531 | 16.5847 | 51.8854 | 25.9026 | 25.9026 | 0 | 0
2025-12-07 23:00 | 20.6 | 64 | 70 | 22.7583 | 16.7297 | 54.495 | 36.4369 | 36.4369 | 0 | 0
2025-12-08 | 19.65 | 71 | 70 | 22.4044 | 16.764 | 56.7718 | 43.2531 | 43.2531 | 0 | 0
2025-12-08 01:00 | 18.75 | 76.5 | 70 | 22.0651 | 16.7131 | 58.4389 | 46.2867 | 46.2867 | 0 | 0
2025-12-08 02:00 | 18.05 | 80.5 | 70 | 21.7985 | 16.6471 | 59.5927 | 47.5573 | 47.5573 | 0 | 0
2025-12-08 03:00 | 17.85 | 80 | 70 | 21.7207 | 16.5507 | 59.3845 | 44.6798 | 44.6798 | 0 | 0
2025-12-08 04:00 | 17.85 | 78.5 | 70 | 21.7195 | 16.4809 | 58.8991 | 41.7846 | 41.7846 | 0 | 0
2025-12-08 05:00 | 17.6 | 81 | 70 | 21.6243 | 16.5044 | 59.6486 | 44.2077 | 44.2077 | 0 | 0
2025-12-08 06:00 | 17.2 | 84 | 100 | 21.4707 | 16.492 | 60.5073 | 65.7018 | 65.7018 | 0 | 0
2025-12-08 07:00 | 17.75 | 81 | 100 | 21.6827 | 16.5602 | 59.6713 | 65.1018 | 65.1018 | 0 | 0
2025-12-08 08:00 | 20.35 | 68 | 100 | 22.6667 | 16.8567 | 55.8518 | 61.4399 | 61.4399 | 0 | 0
2025-12-08 09:00 | 24 | 51.5 | 100 | 24 | 17.1282 | 50.3033 | 49.012 | 49.012 | 0 | 0
2025-12-08 10:00 | 27.05 | 36.5 | 100 | 25.0762 | 17.0128 | 44.2598 | 19.3084 | 19.3084 | 0 | 0
2025-12-08 11:00 | 29 | 24 | 100 | 25.7544 | 16.5235 | 38.4222 | 0 | 0 | 0 | 0
2025-12-08 12:00 | 30.15 | 18 | 100 | 26.1503 | 16.2589 | 35.3427 | 0 | 0 | 0 | 0
2025-12-08 13:00 | 30.85 | 17 | 100 | 26.3854 | 16.3182 | 34.7412 | 0 | 0 | 0 | 0
2025-12-08 14:00 | 31.25 | 17 | 100 | 26.5177 | 16.4042 | 34.691 | 0 | 0 | 0 | 0
2025-12-08 15:00 | 31.3 | 17.5 | 100 | 26.5331 | 16.4631 | 34.9498 | 0 | 0 | 0 | 0
2025-12-08 16:00 | 30.1 | 23.5 | 100 | 26.1244 | 16.7433 | 38.1327 | 0 | 0 | 0 | 0
2025-12-08 17:00 | 27.7 | 41 | 100 | 25.2952 | 17.5392 | 46.4061 | 46.8941 | 46.8941 | 0 | 0
2025-12-08 18:00 | 25.95 | 53.5 | 100 | 24.6866 | 17.8911 | 51.5875 | 81.2257 | 81.2257 | 0 | 0
2025-12-08 19:00 | 25.2 | 44.5 | 100 | 24.4273 | 17.0388 | 47.6064 | 34.9757 | 34.9757 | 0 | 0
2025-12-08 20:00 | 24.45 | 35.5 | 100 | 24.1619 | 16.2081 | 43.8209 | 0 | 0 | 0 | 0
2025-12-08 21:00 | 23.45 | 38 | 100 | 23.8009 | 16.0932 | 44.8766 | 0 | 0 | 0 | 0
2025-12-08 22:00 | 22.55 | 41.5 | 70 | 23.4727 | 16.0554 | 46.2815 | 0 | 0 | 0 | 0
2025-12-08 23:00 | 21.8 | 42 | 70 | 23.1959 | 15.8675 | 46.501 | 0 | 0 | 0 | 0
2025-12-09 | 21 | 39.5 | 70 | 22.8962 | 15.4912 | 45.6344 | 0 | 0 | 0 | 0
2025-12-09 01:00 | 20.3 | 38 | 70 | 22.6312 | 15.2087 | 45.1833 | 0 | 0 | 0 | 0
2025-12-09 02:00 | 19.55 | 38.5 | 70 | 22.3458 | 15.0268 | 45.4852 | 0 | 0 | 0 | 0
2025-12-09 03:00 | 18.75 | 41.5 | 70 | 22.0401 | 14.9599 | 46.6565 | 0 | 0 | 0 | 0
2025-12-09 04:00 | 18.05 | 44.5 | 70 | 21.7707 | 14.911 | 47.7783 | 0 | 0 | 0 | 0
2025-12-09 05:00 | 17.3 | 46 | 70 | 21.4784 | 14.7656 | 48.3928 | 0 | 0 | 0 | 0
2025-12-09 06:00 | 16.65 | 48.5 | 100 | 21.224 | 14.6918 | 49.2975 | 0 | 0 | 0 | 0
2025-12-09 07:00 | 17.2 | 49 | 100 | 21.4416 | 14.8802 | 49.363 | 0 | 0 | 0 | 0
2025-12-09 08:00 | 19.75 | 43.5 | 100 | 22.4253 | 15.3566 | 47.193 | 0 | 0 | 0 | 0
2025-12-09 09:00 | 23.55 | 35 | 100 | 23.837 | 15.9278 | 43.6599 | 0 | 0 | 0 | 0
2025-12-09 10:00 | 26.75 | 29.5 | 100 | 24.9769 | 16.397 | 41.128 | 0 | 0 | 0 | 0
2025-12-09 11:00 | 28.55 | 27 | 100 | 25.5982 | 16.6618 | 39.8997 | 0 | 0 | 0 | 0
2025-12-09 12:00 | 29.55 | 26 | 100 | 25.9368 | 16.8285 | 39.392 | 0 | 0 | 0 | 0
2025-12-09 13:00 | 29.8 | 27.5 | 100 | 26.018 | 17.0224 | 40.137 | 1.0255 | 1.0255 | 0 | 0
2025-12-09 14:00 | 29.3 | 31.5 | 100 | 25.8452 | 17.2323 | 42.0897 | 17.1433 | 17.1433 | 0 | 0
2025-12-09 15:00 | 28.3 | 38 | 100 | 25.5014 | 17.4819 | 45.1069 | 39.276 | 39.276 | 0 | 0
2025-12-09 16:00 | 26.95 | 47 | 100 | 25.0346 | 17.754 | 48.9966 | 65.6697 | 65.6697 | 0 | 0
2025-12-09 17:00 | 25.35 | 59.5 | 100 | 24.4759 | 18.0895 | 53.9743 | 98.1957 | 98.1957 | 0 | 0
2025-12-09 18:00 | 24.05 | 69 | 100 | 24.0177 | 18.2295 | 57.3964 | 116.7799 | 116.7799 | 0 | 0
2025-12-09 19:00 | 23.2 | 69.5 | 100 | 23.7145 | 17.9517 | 57.2641 | 106.0481 | 106.0481 | 0 | 0
2025-12-09 20:00 | 22.4 | 64.5 | 100 | 23.4239 | 17.377 | 55.0857 | 77.0046 | 77.0046 | 0 | 0
2025-12-09 21:00 | 21.8 | 61 | 100 | 23.2028 | 16.971 | 53.6297 | 57.1481 | 57.1481 | 0 | 0
2025-12-09 22:00 | 21.15 | 61 | 70 | 22.9622 | 16.7524 | 53.5146 | 34.4045 | 34.4045 | 0 | 0
2025-12-09 23:00 | 20.2 | 60.5 | 70 | 22.606 | 16.4072 | 53.2064 | 25.3633 | 25.3633 | 0 | 0
2025-12-10 | 19.2 | 60.5 | 70 | 22.2262 | 16.0756 | 53.1176 | 17.345 | 17.345 | 0 | 0
2025-12-10 01:00 | 18.35 | 64.5 | 70 | 21.9023 | 15.9913 | 54.4041 | 18.7541 | 18.7541 | 0 | 0
2025-12-10 02:00 | 17.8 | 71 | 70 | 21.6941 | 16.1132 | 56.4837 | 26.9769 | 26.9769 | 0 | 0
2025-12-10 03:00 | 17.45 | 73.5 | 70 | 21.5597 | 16.1062 | 57.2469 | 28.7536 | 28.7536 | 0 | 0
2025-12-10 04:00 | 17.2 | 71.5 | 70 | 21.4602 | 15.9274 | 56.5783 | 22.8264 | 22.8264 | 0 | 0
2025-12-10 05:00 | 16.85 | 68.5 | 70 | 21.3202 | 15.671 | 55.6 | 14.3408 | 14.3408 | 0 | 0
2025-12-10 06:00 | 15.9 | 64 | 100 | 20.9395 | 15.1535 | 54.1972 | 0 | 0 | 0 | 0
2025-12-10 07:00 | 16.05 | 58.5 | 100 | 20.9944 | 14.9604 | 52.495 | 0 | 0 | 0 | 0
2025-12-10 08:00 | 18.95 | 52 | 100 | 22.1246 | 15.5624 | 50.1968 | 0 | 0 | 0 | 0
2025-12-10 09:00 | 22.85 | 45.5 | 100 | 23.5835 | 16.3918 | 47.8301 | 14.2555 | 14.2555 | 0 | 0
2025-12-10 10:00 | 25.85 | 40 | 100 | 24.6573 | 16.9197 | 45.7408 | 22.9381 | 22.9381 | 0 | 0
2025-12-10 11:00 | 27.75 | 35 | 100 | 25.3176 | 17.0912 | 43.6417 | 19.4013 | 19.4013 | 0 | 0
2025-12-10 12:00 | 29 | 30.5 | 100 | 25.746 | 17.0687 | 41.5859 | 9.3329 | 9.3329 | 0 | 0
2025-12-10 13:00 | 29.8 | 26 | 100 | 26.0204 | 16.8904 | 39.3966 | 0 | 0 | 0 | 0
2025-12-10 14:00 | 30.1 | 23.5 | 100 | 26.1244 | 16.7417 | 38.1416 | 0 | 0 | 0 | 0
2025-12-10 15:00 | 29.1 | 31.5 | 100 | 25.7783 | 17.1771 | 42.0855 | 15.3684 | 15.3684 | 0 | 0
2025-12-10 16:00 | 27.1 | 43.5 | 100 | 25.0884 | 17.5443 | 47.4585 | 51.7856 | 51.7856 | 0 | 0
2025-12-10 17:00 | 25.35 | 52.5 | 100 | 24.4779 | 17.6252 | 51.0245 | 69.6321 | 69.6321 | 0 | 0
2025-12-10 18:00 | 24.15 | 59.5 | 100 | 24.0534 | 17.6789 | 53.6065 | 81.9575 | 81.9575 | 0 | 0
2025-12-10 19:00 | 23.1 | 63.5 | 100 | 23.6776 | 17.5615 | 54.8963 | 82.8503 | 82.8503 | 0 | 0
2025-12-10 20:00 | 22.05 | 67.5 | 100 | 23.2969 | 17.4249 | 56.1244 | 82.7195 | 82.7195 | 0 | 0
2025-12-10 21:00 | 21.2 | 69 | 100 | 22.9844 | 17.2072 | 56.4437 | 76.1945 | 76.1945 | 0 | 0
2025-12-10 22:00 | 20.45 | 69 | 70 | 22.7048 | 16.9424 | 56.2587 | 46.328 | 46.328 | 0 | 0
2025-12-10 23:00 | 19.7 | 69 | 70 | 22.4221 | 16.6792 | 56.1055 | 39.5345 | 39.5345 | 0 | 0
2025-12-11 | 19.1 | 69.5 | 70 | 22.1941 | 16.494 | 56.1745 | 35.282 | 35.282 | 0 | 0
2025-12-11 01:00 | 18.55 | 75 | 70 | 21.9872 | 16.5682 | 57.922 | 41.5542 | 41.5542 | 0 | 0
2025-12-11 02:00 | 17.9 | 84 | 70 | 21.7432 | 16.7515 | 60.7213 | 53.0655 | 53.0655 | 0 | 0
2025-12-11 03:00 | 17.45 | 88 | 70 | 21.5716 | 16.7634 | 61.8811 | 56.1906 | 56.1906 | 0 | 0
2025-12-11 04:00 | 17.1 | 88.5 | 70 | 21.4354 | 16.6525 | 61.9399 | 53.5853 | 53.5853 | 0 | 0
2025-12-11 05:00 | 16.55 | 90 | 70 | 21.2206 | 16.5085 | 62.256 | 50.7823 | 50.7823 | 0 | 0
2025-12-11 06:00 | 15.9 | 92 | 100 | 20.9651 | 16.3451 | 62.6947 | 68.278 | 68.278 | 0 | 0
2025-12-11 07:00 | 16.35 | 88.5 | 100 | 21.1403 | 16.3684 | 61.7334 | 65.7972 | 65.7972 | 0 | 0
2025-12-11 08:00 | 18.9 | 74 | 100 | 22.1208 | 16.6458 | 57.6469 | 60.9699 | 60.9699 | 0 | 0
2025-12-11 09:00 | 22.75 | 57 | 100 | 23.5495 | 17.0565 | 52.2902 | 54.8379 | 54.8379 | 0 | 0
2025-12-11 10:00 | 26.05 | 42 | 100 | 24.7263 | 17.1196 | 46.6401 | 33.6689 | 33.6689 | 0 | 0
2025-12-11 11:00 | 28.15 | 30 | 100 | 25.4589 | 16.7997 | 41.3448 | 0 | 0 | 0 | 0
2025-12-11 12:00 | 29.3 | 24 | 100 | 25.8558 | 16.5892 | 38.4413 | 0 | 0 | 0 | 0
2025-12-11 13:00 | 29.7 | 21.5 | 100 | 25.994 | 16.4635 | 37.1843 | 0 | 0 | 0 | 0
2025-12-11 14:00 | 29.8 | 21 | 100 | 26.0284 | 16.4419 | 36.9297 | 0 | 0 | 0 | 0
2025-12-11 15:00 | 28.8 | 31.5 | 100 | 25.6775 | 17.0933 | 42.0875 | 12.7886 | 12.7886 | 0 | 0
2025-12-11 16:00 | 26.85 | 45.5 | 100 | 25.0013 | 17.612 | 48.3249 | 58.018 | 58.018 | 0 | 0
2025-12-11 17:00 | 25.4 | 54.5 | 100 | 24.4948 | 17.7736 | 51.9 | 78.6371 | 78.6371 | 0 | 0
2025-12-11 18:00 | 24.55 | 60.5 | 100 | 24.1951 | 17.8777 | 54.15 | 91.3895 | 91.3895 | 0 | 0
2025-12-11 19:00 | 23.7 | 62 | 100 | 23.893 | 17.6776 | 54.498 | 85.5928 | 85.5928 | 0 | 0
2025-12-11 20:00 | 22.65 | 64 | 100 | 23.5147 | 17.4332 | 54.9827 | 78.774 | 78.774 | 0 | 0
2025-12-11 21:00 | 21.45 | 65.5 | 100 | 23.0754 | 17.102 | 55.2429 | 68.072 | 68.072 | 0 | 0
2025-12-11 22:00 | 20.4 | 67.5 | 70 | 22.6852 | 16.8445 | 55.7343 | 42.6629 | 42.6629 | 0 | 0
2025-12-11 23:00 | 19.55 | 71.5 | 70 | 22.3668 | 16.7518 | 56.9544 | 43.5913 | 43.5913 | 0 | 0
2025-12-12 | 18.9 | 74.5 | 70 | 22.1211 | 16.6688 | 57.8375 | 43.838 | 43.838 | 0 | 0
2025-12-12 01:00 | 18.4 | 75.5 | 70 | 21.9298 | 16.5376 | 58.0699 | 41.2461 | 41.2461 | 0 | 0
2025-12-12 02:00 | 17.8 | 75.5 | 70 | 21.6976 | 16.3225 | 57.9601 | 35.7815 | 35.7815 | 0 | 0
2025-12-12 03:00 | 17.3 | 79 | 70 | 21.5056 | 16.3026 | 58.9942 | 37.8863 | 37.8863 | 0 | 0
2025-12-12 04:00 | 17.05 | 86.5 | 70 | 21.4141 | 16.5453 | 61.3104 | 49.4666 | 49.4666 | 0 | 0
2025-12-12 05:00 | 17 | 90.5 | 70 | 21.3979 | 16.7016 | 62.5507 | 56.325 | 56.325 | 0 | 0
2025-12-12 06:00 | 16.8 | 90 | 100 | 21.319 | 16.6037 | 62.3345 | 76.2291 | 76.2291 | 0 | 0
2025-12-12 07:00 | 17.2 | 76.5 | 100 | 21.4644 | 16.1542 | 58.1747 | 46.0611 | 46.0611 | 0 | 0
2025-12-12 08:00 | 19.4 | 50 | 100 | 22.2957 | 15.5953 | 49.5172 | 0 | 0 | 0 | 0
2025-12-12 09:00 | 22.9 | 32 | 100 | 23.5991 | 15.5536 | 42.568 | 0 | 0 | 0 | 0
2025-12-12 10:00 | 26.25 | 27.5 | 100 | 24.8032 | 16.1111 | 40.3037 | 0 | 0 | 0 | 0
2025-12-12 11:00 | 28.35 | 25.5 | 100 | 25.5319 | 16.4813 | 39.2242 | 0 | 0 | 0 | 0
2025-12-12 12:00 | 29.25 | 24 | 100 | 25.839 | 16.575 | 38.4516 | 0 | 0 | 0 | 0
2025-12-12 13:00 | 29.65 | 24.5 | 100 | 25.9727 | 16.7154 | 38.6813 | 0 | 0 | 0 | 0
2025-12-12 14:00 | 29.8 | 25 | 100 | 26.0221 | 16.796 | 38.928 | 0 | 0 | 0 | 0
2025-12-12 15:00 | 29.4 | 28 | 100 | 25.8838 | 16.9554 | 40.4166 | 0.6025 | 0.6025 | 0 | 0
2025-12-12 16:00 | 28.1 | 35 | 100 | 25.4369 | 17.1815 | 43.7128 | 23.2675 | 23.2675 | 0 | 0
2025-12-12 17:00 | 26.3 | 41 | 100 | 24.8139 | 17.1173 | 46.266 | 32.3465 | 32.3465 | 0 | 0
2025-12-12 18:00 | 25.05 | 45 | 100 | 24.3742 | 17.0221 | 47.8428 | 35.8199 | 35.8199 | 0 | 0
2025-12-12 19:00 | 24.35 | 48.5 | 100 | 24.1252 | 17.0389 | 49.2017 | 42.0234 | 42.0234 | 0 | 0
2025-12-12 20:00 | 23.55 | 52 | 100 | 23.8384 | 17.0088 | 50.4961 | 46.2815 | 46.2815 | 0 | 0
2025-12-12 21:00 | 22.7 | 55 | 100 | 23.5308 | 16.9175 | 51.5412 | 47.354 | 47.354 | 0 | 0
2025-12-12 22:00 | 21.85 | 57 | 70 | 23.2198 | 16.7571 | 52.1759 | 31.0546 | 31.0546 | 0 | 0
2025-12-12 23:00 | 20.95 | 59 | 70 | 22.8867 | 16.5721 | 52.7943 | 28.3576 | 28.3576 | 0 | 0
2025-12-13 | 20.1 | 60 | 70 | 22.5679 | 16.3444 | 53.0574 | 23.6883 | 23.6883 | 0 | 0
2025-12-13 01:00 | 19.35 | 60 | 70 | 22.2831 | 16.0969 | 52.9931 | 17.6988 | 17.6988 | 0 | 0
2025-12-13 02:00 | 18.7 | 60.5 | 70 | 22.0343 | 15.9079 | 53.1256 | 13.6553 | 13.6553 | 0 | 0
2025-12-13 03:00 | 18.5 | 61.5 | 70 | 21.9579 | 15.8916 | 53.4529 | 14.1407 | 14.1407 | 0 | 0
2025-12-13 04:00 | 18.6 | 63.5 | 70 | 21.9979 | 16.0234 | 54.1287 | 18.9878 | 18.9878 | 0 | 0
2025-12-13 05:00 | 18.35 | 65.5 | 70 | 21.903 | 16.0378 | 54.7695 | 20.9568 | 20.9568 | 0 | 0
2025-12-13 06:00 | 17.85 | 66.5 | 100 | 21.7099 | 15.9168 | 55.0478 | 26.844 | 26.844 | 0 | 0
2025-12-13 07:00 | 18.3 | 65 | 100 | 21.8833 | 15.9975 | 54.5832 | 27.7887 | 27.7887 | 0 | 0
2025-12-13 08:00 | 20.4 | 58 | 100 | 22.68 | 16.3378 | 52.3582 | 30.782 | 30.782 | 0 | 0
2025-12-13 09:00 | 23.35 | 47.5 | 100 | 23.7657 | 16.6657 | 48.6753 | 27.1066 | 27.1066 | 0 | 0
2025-12-13 10:00 | 26.15 | 38 | 100 | 24.7631 | 16.8591 | 44.9207 | 17.6493 | 17.6493 | 0 | 0
2025-12-13 11:00 | 28.2 | 32.5 | 100 | 25.4734 | 17.0124 | 42.5321 | 12.1106 | 12.1106 | 0 | 0
2025-12-13 12:00 | 29.25 | 30.5 | 100 | 25.83 | 17.1305 | 41.6251 | 11.8936 | 11.8936 | 0 | 0
2025-12-13 13:00 | 29.2 | 32.5 | 100 | 25.8105 | 17.2842 | 42.5996 | 21.5667 | 21.5667 | 0 | 0
2025-12-13 14:00 | 28.65 | 36 | 100 | 25.6216 | 17.4175 | 44.2351 | 33.5456 | 33.5456 | 0 | 0
2025-12-13 15:00 | 28.15 | 37.5 | 100 | 25.4513 | 17.3933 | 44.8903 | 35.7062 | 35.7062 | 0 | 0
2025-12-13 16:00 | 27.1 | 43 | 100 | 25.0888 | 17.5027 | 47.2675 | 49.8834 | 49.8834 | 0 | 0
2025-12-13 17:00 | 25.65 | 53.5 | 100 | 24.5824 | 17.7877 | 51.5575 | 77.8766 | 77.8766 | 0 | 0
2025-12-13 18:00 | 24.7 | 62 | 100 | 24.2477 | 18.0234 | 54.8292 | 99.4907 | 99.4907 | 0 | 0
2025-12-13 19:00 | 24.15 | 66.5 | 100 | 24.0532 | 18.111 | 56.4612 | 109.0445 | 109.0445 | 0 | 0
2025-12-13 20:00 | 23.75 | 69.5 | 100 | 23.9112 | 18.1489 | 57.5054 | 114.4639 | 114.4639 | 0 | 0
2025-12-13 21:00 | 23.45 | 70 | 100 | 23.8042 | 18.0696 | 57.5852 | 111.8542 | 111.8542 | 0 | 0
2025-12-13 22:00 | 22.6 | 69 | 70 | 23.4978 | 17.7046 | 56.8946 | 67.1471 | 67.1471 | 0 | 0
2025-12-13 23:00 | 21.45 | 68.5 | 70 | 23.0766 | 17.2662 | 56.3651 | 54.7877 | 54.7877 | 0 | 0
2025-12-14 | 20.9 | 65.5 | 70 | 22.8712 | 16.91 | 55.1453 | 42.8178 | 42.8178 | 0 | 0
2025-12-14 01:00 | 20.35 | 62.5 | 70 | 22.6636 | 16.5604 | 53.9765 | 31.2971 | 31.2971 | 0 | 0
2025-12-14 02:00 | 19.5 | 62.5 | 70 | 22.3419 | 16.2747 | 53.8697 | 24.2167 | 24.2167 | 0 | 0
2025-12-14 03:00 | 19.2 | 60 | 70 | 22.2258 | 16.0473 | 52.987 | 16.5427 | 16.5427 | 0 | 0
2025-12-14 04:00 | 19.4 | 60.5 | 70 | 22.3025 | 16.1386 | 53.1694 | 19.1558 | 19.1558 | 0 | 0
2025-12-14 05:00 | 19.6 | 75.5 | 70 | 22.3883 | 16.9702 | 58.358 | 52.6266 | 52.6266 | 0 | 0
2025-12-14 06:00 | 20.1 | 85.5 | 100 | 22.5829 | 17.6585 | 61.9812 | 113.0032 | 113.0032 | 0 | 0
2025-12-14 07:00 | 21.05 | 81.5 | 100 | 22.9346 | 17.8176 | 60.9439 | 115.0562 | 115.0562 | 0 | 0
2025-12-14 08:00 | 22.6 | 72.5 | 100 | 23.4987 | 17.9059 | 58.2095 | 108.0726 | 108.0726 | 0 | 0
2025-12-14 09:00 | 24.15 | 61.5 | 100 | 24.0533 | 17.8038 | 54.4165 | 89.6488 | 89.6488 | 0 | 0
2025-12-14 10:00 | 25.05 | 55 | 100 | 24.372 | 17.6929 | 51.9983 | 75.9776 | 75.9776 | 0 | 0
2025-12-14 11:00 | 24.85 | 55.5 | 100 | 24.3016 | 17.6588 | 52.1593 | 75.4612 | 75.4612 | 0 | 0
2025-12-14 12:00 | 24.05 | 60 | 100 | 24.0178 | 17.6751 | 53.791 | 82.6485 | 82.6485 | 0 | 0
2025-12-14 13:00 | 23.7 | 60.5 | 100 | 23.8929 | 17.5858 | 53.9006 | 79.9597 | 79.9597 | 0 | 0
2025-12-14 14:00 | 24.25 | 53 | 100 | 24.0892 | 17.2985 | 51.0148 | 58.3342 | 58.3342 | 0 | 0
2025-12-14 15:00 | 24.7 | 52 | 100 | 24.2492 | 17.3795 | 50.6954 | 59.8578 | 59.8578 | 0 | 0
2025-12-14 16:00 | 24.2 | 58 | 100 | 24.0712 | 17.5998 | 53.0351 | 77.0571 | 77.0571 | 0 | 0
2025-12-14 17:00 | 23.45 | 62.5 | 100 | 23.8034 | 17.6213 | 54.6264 | 84.1093 | 84.1093 | 0 | 0
2025-12-14 18:00 | 22.6 | 69 | 100 | 23.4978 | 17.7052 | 56.8819 | 95.8046 | 95.8046 | 0 | 0
2025-12-14 19:00 | 22 | 72.5 | 100 | 23.2803 | 17.6861 | 57.9958 | 99.305 | 99.305 | 0 | 0
2025-12-14 20:00 | 21.6 | 74 | 100 | 23.1342 | 17.623 | 58.4099 | 98.531 | 98.531 | 0 | 0
2025-12-14 21:00 | 21.25 | 74 | 100 | 23.0051 | 17.4946 | 58.2894 | 93.4443 | 93.4443 | 0 | 0
2025-12-14 22:00 | 20.8 | 74 | 70 | 22.8381 | 17.3309 | 58.1465 | 60.9173 | 60.9173 | 0 | 0
2025-12-14 23:00 | 20.1 | 76.5 | 70 | 22.5776 | 17.2045 | 58.8235 | 59.5264 | 59.5264 | 0 | 0
2025-12-15 | 19.25 | 79.5 | 70 | 22.2581 | 17.0409 | 59.6099 | 57.4699 | 57.4699 | 0 | 0
2025-12-15 01:00 | 18.2 | 85 | 70 | 21.8599 | 16.9105 | 61.1338 | 58.0295 | 58.0295 | 0 | 0
2025-12-15 02:00 | 17.25 | 91 | 70 | 21.4961 | 16.8191 | 62.7731 | 59.7608 | 59.7608 | 0 | 0
2025-12-15 03:00 | 16.95 | 89.5 | 70 | 21.3775 | 16.6384 | 62.2134 | 53.9225 | 53.9225 | 0 | 0
2025-12-15 04:00 | 17 | 86 | 70 | 21.3941 | 16.5044 | 61.1309 | 47.9945 | 47.9945 | 0 | 0
2025-12-15 05:00 | 16.95 | 86 | 70 | 21.3745 | 16.4855 | 61.1192 | 47.5085 | 47.5085 | 0 | 0
2025-12-15 06:00 | 16.75 | 87 | 100 | 21.2968 | 16.4546 | 61.3803 | 67.6615 | 67.6615 | 0 | 0
2025-12-15 07:00 | 17.35 | 84.5 | 100 | 21.5297 | 16.569 | 60.7382 | 69.4261 | 69.4261 | 0 | 0
2025-12-15 08:00 | 19.75 | 73.5 | 100 | 22.4438 | 16.925 | 57.6817 | 70.9384 | 70.9384 | 0 | 0
2025-12-15 09:00 | 22.9 | 60.5 | 100 | 23.6047 | 17.3146 | 53.6832 | 69.3892 | 69.3892 | 0 | 0
2025-12-15 10:00 | 25.3 | 50.5 | 100 | 24.4609 | 17.4746 | 50.1697 | 60.8374 | 60.8374 | 0 | 0
2025-12-15 11:00 | 26.9 | 44 | 100 | 25.0195 | 17.519 | 47.6545 | 51.8263 | 51.8263 | 0 | 0
2025-12-15 12:00 | 28.35 | 40 | 100 | 25.5161 | 17.6511 | 46.0749 | 49.607 | 49.607 | 0 | 0
2025-12-15 13:00 | 29.65 | 35.5 | 100 | 25.9558 | 17.6611 | 44.1138 | 41.2638 | 41.2638 | 0 | 0
2025-12-15 14:00 | 30.45 | 31.5 | 100 | 26.226 | 17.5384 | 42.2141 | 28.3877 | 28.3877 | 0 | 0
2025-12-15 15:00 | 29.85 | 35.5 | 100 | 26.0219 | 17.7177 | 44.1476 | 43.4029 | 43.4029 | 0 | 0
2025-12-15 16:00 | 27.75 | 50.5 | 100 | 25.3035 | 18.2637 | 50.8215 | 91.8364 | 91.8364 | 0 | 0
2025-12-15 17:00 | 26 | 61 | 100 | 24.7006 | 18.4119 | 54.88 | 113.9094 | 113.9094 | 0 | 0
2025-12-15 18:00 | 25.3 | 61 | 100 | 24.4581 | 18.1677 | 54.6219 | 103.9285 | 103.9285 | 0 | 0
2025-12-15 19:00 | 24.5 | 64 | 100 | 24.177 | 18.08 | 55.5788 | 104.4882 | 104.4882 | 0 | 0
2025-12-15 20:00 | 23.6 | 70.5 | 100 | 23.8578 | 18.154 | 57.846 | 115.9834 | 115.9834 | 0 | 0
2025-12-15 21:00 | 23.05 | 74.5 | 100 | 23.6614 | 18.1853 | 59.1802 | 122.2011 | 122.2011 | 0 | 0
2025-12-15 22:00 | 22.75 | 75.5 | 70 | 23.5536 | 18.1309 | 59.4379 | 84.8018 | 84.8018 | 0 | 0
2025-12-15 23:00 | 22.5 | 74.5 | 70 | 23.463 | 17.981 | 58.959 | 79.6973 | 79.6973 | 0 | 0
2025-12-16 | 22.3 | 73 | 70 | 23.3899 | 17.8224 | 58.3206 | 73.987 | 73.987 | 0 | 0
2025-12-16 01:00 | 22.2 | 70.5 | 70 | 23.3527 | 17.6449 | 57.3471 | 66.9338 | 66.9338 | 0 | 0
2025-12-16 02:00 | 21.9 | 68.5 | 70 | 23.2423 | 17.4247 | 56.5093 | 59.2116 | 59.2116 | 0 | 0
2025-12-16 03:00 | 21.95 | 66 | 70 | 23.2597 | 17.3019 | 55.5932 | 53.7292 | 53.7292 | 0 | 0
2025-12-16 04:00 | 22.3 | 61 | 70 | 23.3864 | 17.1361 | 53.7935 | 44.805 | 44.805 | 0 | 0
2025-12-16 05:00 | 22.05 | 56.5 | 70 | 23.2933 | 16.7915 | 52.0441 | 31.6733 | 31.6733 | 0 | 0
2025-12-16 06:00 | 21.5 | 57 | 100 | 23.0904 | 16.6401 | 52.1511 | 40.4714 | 40.4714 | 0 | 0
2025-12-16 07:00 | 21.4 | 59.5 | 100 | 23.0543 | 16.7485 | 53.0546 | 47.6421 | 47.6421 | 0 | 0
2025-12-16 08:00 | 22.1 | 57.5 | 100 | 23.312 | 16.8672 | 52.4117 | 49.1524 | 49.1524 | 0 | 0
2025-12-16 09:00 | 23.4 | 52.5 | 100 | 23.7843 | 16.9916 | 50.6764 | 46.454 | 46.454 | 0 | 0
2025-12-16 10:00 | 24.5 | 48.5 | 100 | 24.1786 | 17.086 | 49.2224 | 43.7128 | 43.7128 | 0 | 0
2025-12-16 11:00 | 25.3 | 46 | 100 | 24.4622 | 17.1668 | 48.2959 | 42.6496 | 42.6496 | 0 | 0
2025-12-16 12:00 | 25.95 | 43.5 | 100 | 24.6908 | 17.1905 | 47.3212 | 39.4194 | 39.4194 | 0 | 0
2025-12-16 13:00 | 26.5 | 41 | 100 | 24.8833 | 17.1747 | 46.2995 | 34.5628 | 34.5628 | 0 | 0
2025-12-16 14:00 | 26.65 | 40.5 | 100 | 24.9356 | 17.1821 | 46.0971 | 33.9633 | 33.9633 | 0 | 0
2025-12-16 15:00 | 26.2 | 42 | 100 | 24.7786 | 17.1573 | 46.7104 | 35.7926 | 35.7926 | 0 | 0
2025-12-16 16:00 | 25.6 | 44 | 100 | 24.5682 | 17.1174 | 47.5075 | 37.8815 | 37.8815 | 0 | 0
2025-12-16 17:00 | 24.7 | 49 | 100 | 24.2496 | 17.178 | 49.4879 | 48.256 | 48.256 | 0 | 0
2025-12-16 18:00 | 23.6 | 57.5 | 100 | 23.8568 | 17.3645 | 52.7213 | 67.788 | 67.788 | 0 | 0
2025-12-16 19:00 | 22.55 | 68 | 100 | 23.4794 | 17.6278 | 56.5205 | 91.9135 | 91.9135 | 0 | 0
2025-12-16 20:00 | 21.4 | 77 | 100 | 23.0618 | 17.709 | 59.4842 | 105.9839 | 105.9839 | 0 | 0
2025-12-16 21:00 | 20.6 | 79.5 | 100 | 22.7665 | 17.5422 | 60.0931 | 102.1471 | 102.1471 | 0 | 0
2025-12-16 22:00 | 20.55 | 77 | 70 | 22.7465 | 17.3939 | 59.1903 | 65.4521 | 65.4521 | 0 | 0
2025-12-16 23:00 | 20.45 | 76.5 | 70 | 22.7088 | 17.3309 | 58.9838 | 63.3532 | 63.3532 | 0 | 0
2025-12-17 | 20.1 | 78.5 | 70 | 22.5788 | 17.3039 | 59.5779 | 64.2104 | 64.2104 | 0 | 0
2025-12-17 01:00 | 20.55 | 74 | 70 | 22.7449 | 17.2369 | 58.132 | 58.8349 | 58.8349 | 0 | 0
2025-12-17 02:00 | 21.3 | 64 | 70 | 23.0192 | 16.9639 | 54.7107 | 43.1257 | 43.1257 | 0 | 0
2025-12-17 03:00 | 22.15 | 56.5 | 70 | 23.33 | 16.823 | 52.0737 | 32.5959 | 32.5959 | 0 | 0
2025-12-17 04:00 | 22.75 | 54.5 | 70 | 23.5489 | 16.8994 | 51.4037 | 32.6163 | 32.6163 | 0 | 0
2025-12-17 05:00 | 22.7 | 55.5 | 70 | 23.5309 | 16.9436 | 51.7779 | 34.6909 | 34.6909 | 0 | 0
2025-12-17 06:00 | 22.75 | 57.5 | 100 | 23.5496 | 17.0807 | 52.5477 | 57.2387 | 57.2387 | 0 | 0
2025-12-17 07:00 | 22.9 | 60.5 | 100 | 23.6047 | 17.3108 | 53.7291 | 69.823 | 69.823 | 0 | 0
2025-12-17 08:00 | 23.1 | 63.5 | 100 | 23.6776 | 17.5587 | 54.936 | 83.2271 | 83.2271 | 0 | 0
2025-12-17 09:00 | 23.45 | 63.5 | 100 | 23.8035 | 17.6814 | 55.0283 | 87.8832 | 87.8832 | 0 | 0
2025-12-17 10:00 | 25 | 56.5 | 100 | 24.3542 | 17.7724 | 52.6334 | 81.5846 | 81.5846 | 0 | 0
2025-12-17 11:00 | 26.85 | 48.5 | 100 | 24.9994 | 17.8282 | 49.6647 | 71.3323 | 71.3323 | 0 | 0
2025-12-17 12:00 | 27.85 | 44 | 100 | 25.3433 | 17.8081 | 47.8531 | 62.9269 | 62.9269 | 0 | 0
2025-12-17 13:00 | 28.45 | 40.5 | 100 | 25.5492 | 17.7184 | 46.341 | 53.253 | 53.253 | 0 | 0
2025-12-17 14:00 | 28.4 | 38.5 | 100 | 25.5346 | 17.5447 | 45.3941 | 43.1306 | 43.1306 | 0 | 0
2025-12-17 15:00 | 27.7 | 42.5 | 100 | 25.2939 | 17.647 | 47.1419 | 54.3248 | 54.3248 | 0 | 0
2025-12-17 16:00 | 27.15 | 46 | 100 | 25.1037 | 17.7398 | 48.6237 | 63.9111 | 63.9111 | 0 | 0
2025-12-17 17:00 | 26.5 | 47.5 | 100 | 24.8797 | 17.6453 | 49.1526 | 62.8086 | 62.8086 | 0 | 0
2025-12-17 18:00 | 25.2 | 55.5 | 100 | 24.4246 | 17.7732 | 52.2749 | 80.2029 | 80.2029 | 0 | 0
2025-12-17 19:00 | 24.05 | 66 | 100 | 24.0178 | 18.045 | 56.2174 | 105.6353 | 105.6353 | 0 | 0
2025-12-17 20:00 | 23.25 | 72.5 | 100 | 23.7329 | 18.1442 | 58.4773 | 117.9347 | 117.9347 | 0 | 0
2025-12-17 21:00 | 22.5 | 75.5 | 100 | 23.4632 | 18.0379 | 59.3223 | 117.1984 | 117.1984 | 0 | 0
2025-12-17 22:00 | 21.6 | 78.5 | 70 | 23.136 | 17.8666 | 60.0772 | 79.5747 | 79.5747 | 0 | 0
2025-12-17 23:00 | 21.3 | 77 | 70 | 23.0249 | 17.6734 | 59.4136 | 72.9274 | 72.9274 | 0 | 0
2025-12-18 | 21.45 | 74.5 | 70 | 23.0791 | 17.5941 | 58.554 | 68.689 | 68.689 | 0 | 0
2025-12-18 01:00 | 21.3 | 77 | 70 | 23.0249 | 17.6735 | 59.414 | 72.9305 | 72.9305 | 0 | 0
2025-12-18 02:00 | 21.25 | 80 | 70 | 23.0078 | 17.8144 | 60.4861 | 79.3004 | 79.3004 | 0 | 0
2025-12-18 03:00 | 21.2 | 78.5 | 70 | 22.9886 | 17.716 | 59.9253 | 75.3494 | 75.3494 | 0 | 0
2025-12-18 04:00 | 20.9 | 77.5 | 70 | 22.8771 | 17.5509 | 59.4566 | 69.9559 | 69.9559 | 0 | 0
2025-12-18 05:00 | 20.65 | 78.5 | 70 | 22.7846 | 17.5104 | 59.7224 | 69.5895 | 69.5895 | 0 | 0
2025-12-18 06:00 | 20.15 | 79 | 100 | 22.5978 | 17.3499 | 59.7212 | 93.5766 | 93.5766 | 0 | 0
2025-12-18 07:00 | 20.05 | 79.5 | 100 | 22.5606 | 17.3383 | 59.8572 | 93.6141 | 93.6141 | 0 | 0
2025-12-18 08:00 | 20.9 | 79 | 100 | 22.8778 | 17.6311 | 59.9723 | 104.5642 | 104.5642 | 0 | 0
2025-12-18 09:00 | 23.05 | 69.5 | 100 | 23.6606 | 17.8973 | 57.2103 | 103.8707 | 103.8707 | 0 | 0
2025-12-18 10:00 | 24.45 | 62.5 | 100 | 24.1595 | 17.9706 | 54.9143 | 97.6064 | 97.6064 | 0 | 0
2025-12-18 11:00 | 23.95 | 65.5 | 100 | 23.9822 | 17.9799 | 55.9624 | 102.124 | 102.124 | 0 | 0
2025-12-18 12:00 | 22.8 | 71.5 | 100 | 23.5708 | 17.9214 | 57.9073 | 107.5402 | 107.5402 | 0 | 0
2025-12-18 13:00 | 21.8 | 77.5 | 100 | 23.2089 | 17.8872 | 59.7918 | 113.4106 | 113.4106 | 0 | 0
2025-12-18 14:00 | 22.4 | 76.5 | 100 | 23.4272 | 18.0562 | 59.6706 | 119.2533 | 119.2533 | 0 | 0
2025-12-18 15:00 | 22.95 | 74.5 | 100 | 23.6255 | 18.148 | 59.1425 | 120.7059 | 120.7059 | 0 | 0
2025-12-18 16:00 | 22.65 | 75.5 | 100 | 23.5175 | 18.093 | 59.4066 | 119.7066 | 119.7066 | 0 | 0
2025-12-18 17:00 | 22.55 | 76.5 | 100 | 23.4816 | 18.1115 | 59.7522 | 121.7436 | 121.7436 | 0 | 0
2025-12-18 18:00 | 22.55 | 76.5 | 100 | 23.4816 | 18.1115 | 59.7579 | 121.7969 | 121.7969 | 0 | 0
2025-12-18 19:00 | 22.25 | 78 | 100 | 23.3732 | 18.0822 | 60.2001 | 122.3816 | 122.3816 | 0 | 0
2025-12-18 20:00 | 21.95 | 80 | 100 | 23.2646 | 18.0781 | 60.8182 | 124.5263 | 124.5263 | 0 | 0
2025-12-18 21:00 | 22.1 | 78.5 | 100 | 23.3188 | 18.0532 | 60.327 | 121.7961 | 121.7961 | 0 | 0
2025-12-18 22:00 | 23.15 | 67.5 | 70 | 23.6962 | 17.8118 | 56.531 | 69.0644 | 69.0644 | 0 | 0
2025-12-18 23:00 | 22.35 | 72.5 | 70 | 23.4079 | 17.8117 | 58.1609 | 73.3576 | 73.3576 | 0 | 0
2025-12-19 | 20.2 | 88 | 70 | 22.6218 | 17.8216 | 62.9229 | 85.7852 | 85.7852 | 0 | 0
2025-12-19 01:00 | 20 | 89 | 70 | 22.5475 | 17.793 | 63.1814 | 85.6836 | 85.6836 | 0 | 0
2025-12-19 02:00 | 20 | 89.5 | 70 | 22.5478 | 17.818 | 63.3537 | 86.748 | 86.748 | 0 | 0
2025-12-19 03:00 | 19.7 | 92.5 | 70 | 22.4369 | 17.8465 | 64.2501 | 89.693 | 89.693 | 0 | 0
2025-12-19 04:00 | 19.85 | 93.5 | 70 | 22.4939 | 17.9547 | 64.6649 | 93.5439 | 93.5439 | 0 | 0
2025-12-19 05:00 | 20 | 92.5 | 70 | 22.5496 | 17.9661 | 64.3896 | 93.1455 | 93.1455 | 0 | 0
2025-12-19 06:00 | 20.05 | 90 | 100 | 22.5668 | 17.8624 | 63.5402 | 126.1815 | 126.1815 | 0 | 0
2025-12-19 07:00 | 19.95 | 87.5 | 100 | 22.5278 | 17.6995 | 62.6239 | 116.8759 | 116.8759 | 0 | 0
2025-12-19 08:00 | 20 | 85 | 100 | 22.5451 | 17.5956 | 61.7703 | 109.9408 | 109.9408 | 0 | 0
2025-12-19 09:00 | 20.1 | 83 | 100 | 22.5814 | 17.5331 | 61.1047 | 105.2462 | 105.2462 | 0 | 0
2025-12-19 10:00 | 20.05 | 79 | 100 | 22.5603 | 17.3128 | 59.6878 | 92.1145 | 92.1145 | 0 | 0
2025-12-19 11:00 | 20.15 | 71 | 100 | 22.5932 | 16.9392 | 56.9192 | 68.7109 | 68.7109 | 0 | 0
2025-12-19 12:00 | 20.25 | 65.5 | 100 | 22.6277 | 16.6865 | 55.0082 | 52.8237 | 52.8237 | 0 | 0
2025-12-19 13:00 | 20.15 | 65 | 100 | 22.5897 | 16.6258 | 54.8185 | 50.0422 | 50.0422 | 0 | 0
2025-12-19 14:00 | 19.75 | 65 | 100 | 22.4385 | 16.4888 | 54.7576 | 45.1353 | 45.1353 | 0 | 0
2025-12-19 15:00 | 19.55 | 62.5 | 100 | 22.361 | 16.2922 | 53.8661 | 35.1029 | 35.1029 | 0 | 0
2025-12-19 16:00 | 19.15 | 64 | 100 | 22.2094 | 16.2341 | 54.3354 | 34.8916 | 34.8916 | 0 | 0
2025-12-19 17:00 | 18.15 | 68.5 | 100 | 21.8279 | 16.1148 | 55.7276 | 35.9732 | 35.9732 | 0 | 0
2025-12-19 18:00 | 17.1 | 73 | 100 | 21.4222 | 15.9599 | 57.0574 | 35.5161 | 35.5161 | 0 | 0
2025-12-19 19:00 | 16.25 | 76 | 100 | 21.0895 | 15.794 | 57.8985 | 32.8732 | 32.8732 | 0 | 0
2025-12-19 20:00 | 15.5 | 77.5 | 100 | 20.792 | 15.5928 | 58.2842 | 27.4463 | 27.4463 | 0 | 0
2025-12-19 21:00 | 15.1 | 79 | 100 | 20.6329 | 15.5134 | 58.6979 | 26.2007 | 26.2007 | 0 | 0
2025-12-19 22:00 | 15.05 | 78.5 | 70 | 20.6123 | 15.4751 | 58.5455 | 17.0736 | 17.0736 | 0 | 0
2025-12-19 23:00 | 14.65 | 78.5 | 70 | 20.4509 | 15.3333 | 58.5269 | 13.7423 | 13.7423 | 0 | 0
2025-12-20 | 13.85 | 80.5 | 70 | 20.1275 | 15.1288 | 59.0797 | 10.3501 | 10.3501 | 0 | 0
2025-12-20 01:00 | 13.45 | 82.5 | 70 | 19.9657 | 15.0632 | 59.6345 | 10.1473 | 10.1473 | 0 | 0
2025-12-20 02:00 | 13.35 | 84 | 70 | 19.9261 | 15.0839 | 60.0489 | 11.5977 | 11.5977 | 0 | 0
2025-12-20 03:00 | 13.2 | 83 | 70 | 19.8634 | 14.9925 | 59.7704 | 8.8457 | 8.8457 | 0 | 0
2025-12-20 04:00 | 13.05 | 81 | 70 | 19.7995 | 14.8654 | 59.2212 | 4.6317 | 4.6317 | 0 | 0
2025-12-20 05:00 | 12.85 | 81.5 | 70 | 19.7174 | 14.8135 | 59.3583 | 3.7513 | 3.7513 | 0 | 0
2025-12-20 06:00 | 12.8 | 82.5 | 100 | 19.6978 | 14.8323 | 59.6242 | 6.8353 | 6.8353 | 0 | 0
2025-12-20 07:00 | 13.05 | 82 | 100 | 19.8006 | 14.9029 | 59.4773 | 8.6102 | 8.6102 | 0 | 0
2025-12-20 08:00 | 13.95 | 80 | 100 | 20.1679 | 15.146 | 58.9176 | 14.667 | 14.667 | 0 | 0
2025-12-20 09:00 | 15.4 | 76 | 100 | 20.7506 | 15.496 | 57.8041 | 22.3913 | 22.3913 | 0 | 0
2025-12-20 10:00 | 17 | 71.5 | 100 | 21.3818 | 15.8591 | 56.5402 | 30.0462 | 30.0462 | 0 | 0
2025-12-20 11:00 | 18.5 | 69 | 100 | 21.9635 | 16.2613 | 55.9056 | 41.3917 | 41.3917 | 0 | 0
2025-12-20 12:00 | 19.85 | 59.5 | 100 | 22.4731 | 16.2379 | 52.8259 | 29.1286 | 29.1286 | 0 | 0
2025-12-20 13:00 | 20.4 | 51 | 100 | 22.6761 | 15.9576 | 49.8534 | 8.3633 | 8.3633 | 0 | 0
2025-12-20 14:00 | 20.15 | 51 | 100 | 22.5817 | 15.8796 | 49.8553 | 5.8429 | 5.8429 | 0 | 0
2025-12-20 15:00 | 19.8 | 52.5 | 100 | 22.4498 | 15.8509 | 50.3838 | 6.9731 | 6.9731 | 0 | 0
2025-12-20 16:00 | 18.85 | 58 | 100 | 22.0903 | 15.8338 | 52.2624 | 13.6009 | 13.6009 | 0 | 0
2025-12-20 17:00 | 17.25 | 66 | 100 | 21.4752 | 15.6916 | 54.8327 | 18.4385 | 18.4385 | 0 | 0
2025-12-20 18:00 | 16 | 72.5 | 100 | 20.9871 | 15.5559 | 56.7953 | 20.927 | 20.927 | 0 | 0
2025-12-20 19:00 | 15.25 | 77 | 100 | 20.6914 | 15.4843 | 58.1033 | 23.108 | 23.108 | 0 | 0
2025-12-20 20:00 | 14.45 | 79 | 100 | 20.3704 | 15.2836 | 58.6469 | 18.2897 | 18.2897 | 0 | 0
2025-12-20 21:00 | 14.1 | 77 | 100 | 20.2261 | 15.0813 | 58.0634 | 9.623 | 9.623 | 0 | 0
2025-12-20 22:00 | 14.2 | 74.5 | 70 | 20.2644 | 15.0176 | 57.3461 | 3.5431 | 3.5431 | 0 | 0
2025-12-20 23:00 | 13.9 | 75 | 70 | 20.1426 | 14.9339 | 57.4956 | 1.9933 | 1.9933 | 0 | 0
2025-12-21 | 13.25 | 77.5 | 70 | 19.8785 | 14.8047 | 58.2191 | 0.7873 | 0.7873 | 0 | 0
2025-12-21 01:00 | 12.6 | 80.5 | 70 | 19.613 | 14.6891 | 59.0684 | 0.1612 | 0.1612 | 0 | 0
2025-12-21 02:00 | 12.1 | 82 | 70 | 19.4066 | 14.567 | 59.4978 | 0 | 0 | 0 | 0
2025-12-21 03:00 | 11.8 | 80.5 | 70 | 19.2796 | 14.4089 | 59.1242 | 0 | 0 | 0 | 0
2025-12-21 04:00 | 11.6 | 80 | 70 | 19.1953 | 14.3224 | 59.0117 | 0 | 0 | 0 | 0
2025-12-21 05:00 | 11.3 | 82 | 70 | 19.0713 | 14.2868 | 59.5592 | 0 | 0 | 0 | 0
2025-12-21 06:00 | 10.95 | 83.5 | 100 | 18.9252 | 14.2152 | 59.9765 | 0 | 0 | 0 | 0
2025-12-21 07:00 | 11.2 | 83 | 100 | 19.0303 | 14.2864 | 59.814 | 0 | 0 | 0 | 0
2025-12-21 08:00 | 12.75 | 79.5 | 100 | 19.6743 | 14.7059 | 58.7639 | 0 | 0 | 0 | 0
2025-12-21 09:00 | 15.25 | 72.5 | 100 | 20.6873 | 15.2994 | 56.7267 | 11.9354 | 11.9354 | 0 | 0
2025-12-21 10:00 | 17.5 | 64.5 | 100 | 21.572 | 15.709 | 54.3115 | 16.7606 | 16.7606 | 0 | 0
2025-12-21 11:00 | 19 | 57.5 | 100 | 22.1476 | 15.8607 | 52.0497 | 13.3295 | 13.3295 | 0 | 0
2025-12-21 12:00 | 19.95 | 51.5 | 100 | 22.5063 | 15.8484 | 49.9908 | 5.0202 | 5.0202 | 0 | 0
2025-12-21 13:00 | 20.55 | 48 | 100 | 22.7311 | 15.8414 | 48.7444 | 0 | 0 | 0 | 0
2025-12-21 14:00 | 20.9 | 48 | 100 | 22.8627 | 15.9476 | 48.7451 | 3.4185 | 3.4185 | 0 | 0
2025-12-21 15:00 | 21.1 | 52.5 | 100 | 22.9396 | 16.2621 | 50.3972 | 20.3906 | 20.3906 | 0 | 0
2025-12-21 16:00 | 20.4 | 63 | 100 | 22.6827 | 16.6078 | 54.1115 | 46.4547 | 46.4547 | 0 | 0
2025-12-21 17:00 | 18.9 | 72.5 | 100 | 22.1197 | 16.573 | 57.1304 | 56.4817 | 56.4817 | 0 | 0
2025-12-21 18:00 | 17.9 | 77 | 100 | 21.7377 | 16.4297 | 58.4179 | 56.1667 | 56.1667 | 0 | 0
2025-12-21 19:00 | 17.1 | 80.5 | 100 | 21.4287 | 16.2994 | 59.3795 | 55.043 | 55.043 | 0 | 0
2025-12-21 20:00 | 16.25 | 83.5 | 100 | 21.0963 | 16.1192 | 60.1513 | 51.5145 | 51.5145 | 0 | 0
2025-12-21 21:00 | 15.9 | 81.5 | 100 | 20.9555 | 15.9061 | 59.4851 | 41.9173 | 41.9173 | 0 | 0
2025-12-21 22:00 | 15.9 | 77.5 | 70 | 20.9519 | 15.7369 | 58.2737 | 22.3726 | 22.3726 | 0 | 0
2025-12-21 23:00 | 15.45 | 79 | 70 | 20.7735 | 15.6397 | 58.684 | 21.0951 | 21.0951 | 0 | 0
2025-12-22 | 14.75 | 81.5 | 70 | 20.4943 | 15.4909 | 59.361 | 19.2466 | 19.2466 | 0 | 0
2025-12-22 01:00 | 14.2 | 82.5 | 70 | 20.2723 | 15.333 | 59.6102 | 16.1496 | 16.1496 | 0 | 0
2025-12-22 02:00 | 13.65 | 83.5 | 70 | 20.0489 | 15.1749 | 59.8646 | 13.0551 | 13.0551 | 0 | 0
2025-12-22 03:00 | 13.4 | 83.5 | 70 | 19.9464 | 15.0844 | 59.8548 | 10.9523 | 10.9523 | 0 | 0
2025-12-22 04:00 | 13.4 | 82.5 | 70 | 19.9453 | 15.0468 | 59.5776 | 9.4341 | 9.4341 | 0 | 0
2025-12-22 05:00 | 13.15 | 82.5 | 70 | 19.8425 | 14.9582 | 59.5747 | 7.3781 | 7.3781 | 0 | 0
2025-12-22 06:00 | 12.75 | 83.5 | 100 | 19.6784 | 14.8522 | 59.8455 | 7.9724 | 7.9724 | 0 | 0
2025-12-22 07:00 | 13.3 | 81.5 | 100 | 19.9033 | 14.9738 | 59.2896 | 10.0642 | 10.0642 | 0 | 0
2025-12-22 08:00 | 15.35 | 74.5 | 100 | 20.7293 | 15.4177 | 57.316 | 17.8551 | 17.8551 | 0 | 0
2025-12-22 09:00 | 18.05 | 67.5 | 100 | 21.7885 | 16.0373 | 55.3112 | 31.3029 | 31.3029 | 0 | 0
2025-12-22 10:00 | 20.4 | 56 | 100 | 22.679 | 16.235 | 51.5807 | 23.8284 | 23.8284 | 0 | 0
2025-12-22 11:00 | 21.7 | 44.5 | 100 | 23.1597 | 15.9891 | 47.4163 | 0 | 0 | 0 | 0
2025-12-22 12:00 | 22.2 | 42 | 100 | 23.344 | 15.9866 | 46.4662 | 0 | 0 | 0 | 0
2025-12-22 13:00 | 22.5 | 42.5 | 100 | 23.4546 | 16.1034 | 46.6592 | 0 | 0 | 0 | 0
2025-12-22 14:00 | 22.55 | 43.5 | 100 | 23.4732 | 16.1795 | 47.0495 | 4.0561 | 4.0561 | 0 | 0
2025-12-22 15:00 | 22.25 | 47.5 | 100 | 23.364 | 16.3305 | 48.5809 | 15.332 | 15.332 | 0 | 0
2025-12-22 16:00 | 20.95 | 55.5 | 100 | 22.885 | 16.3822 | 51.4776 | 28.6208 | 28.6208 | 0 | 0
2025-12-22 17:00 | 19 | 63 | 100 | 22.1514 | 16.1367 | 53.9333 | 29.7586 | 29.7586 | 0 | 0
2025-12-22 18:00 | 17.7 | 67.5 | 100 | 21.6524 | 15.9162 | 55.3078 | 27.414 | 27.414 | 0 | 0
2025-12-22 19:00 | 16.95 | 71 | 100 | 21.3617 | 15.82 | 56.3601 | 27.9758 | 27.9758 | 0 | 0
2025-12-22 20:00 | 16.15 | 74.5 | 100 | 21.0486 | 15.6964 | 57.3782 | 27.4368 | 27.4368 | 0 | 0
2025-12-22 21:00 | 15.4 | 77 | 100 | 20.7517 | 15.5388 | 58.0756 | 24.6056 | 24.6056 | 0 | 0
2025-12-22 22:00 | 14.8 | 79 | 70 | 20.5121 | 15.4085 | 58.63 | 15.5374 | 15.5374 | 0 | 0
2025-12-22 23:00 | 14.25 | 80 | 70 | 20.2902 | 15.2534 | 58.8971 | 12.5857 | 12.5857 | 0 | 0
2025-12-23 | 13.75 | 80 | 70 | 20.0863 | 15.0763 | 58.8867 | 8.4803 | 8.4803 | 0 | 0
2025-12-23 01:00 | 13.25 | 80.5 | 70 | 19.8817 | 14.9187 | 59.0263 | 5.1989 | 5.1989 | 0 | 0
2025-12-23 02:00 | 12.75 | 81.5 | 70 | 19.6763 | 14.7787 | 59.3122 | 2.6965 | 2.6965 | 0 | 0
2025-12-23 03:00 | 12.35 | 82.5 | 70 | 19.5113 | 14.6745 | 59.5996 | 0.989 | 0.989 | 0 | 0
2025-12-23 04:00 | 12.15 | 84.5 | 70 | 19.4301 | 14.6747 | 60.1438 | 2.2647 | 2.2647 | 0 | 0
2025-12-23 05:00 | 12 | 86 | 70 | 19.369 | 14.6735 | 60.5467 | 3.1783 | 3.1783 | 0 | 0
2025-12-23 06:00 | 11.8 | 86.5 | 100 | 19.2859 | 14.6193 | 60.6818 | 3.209 | 3.209 | 0 | 0
2025-12-23 07:00 | 12.15 | 86.5 | 100 | 19.4321 | 14.7458 | 60.667 | 7.2268 | 7.2268 | 0 | 0
2025-12-23 08:00 | 14.05 | 83 | 100 | 20.2118 | 15.2995 | 59.7382 | 22.335 | 22.335 | 0 | 0
2025-12-23 09:00 | 17.25 | 74 | 100 | 21.482 | 16.0611 | 57.3307 | 39.5209 | 39.5209 | 0 | 0
2025-12-23 10:00 | 19.9 | 61.5 | 100 | 22.4933 | 16.3625 | 53.4895 | 35.541 | 35.541 | 0 | 0
2025-12-23 11:00 | 21.3 | 50.5 | 100 | 23.0134 | 16.2136 | 49.6536 | 15.6708 | 15.6708 | 0 | 0
2025-12-23 12:00 | 22.1 | 44.5 | 100 | 23.3078 | 16.1067 | 47.4295 | 3.2152 | 3.2152 | 0 | 0
2025-12-23 13:00 | 22.55 | 42 | 100 | 23.4728 | 16.0869 | 46.4733 | 0 | 0 | 0 | 0
2025-12-23 14:00 | 22.65 | 41 | 100 | 23.5093 | 16.0532 | 46.0889 | 0 | 0 | 0 | 0
2025-12-23 15:00 | 22.25 | 47 | 100 | 23.3639 | 16.2995 | 48.3987 | 13.6456 | 13.6456 | 0 | 0
2025-12-23 16:00 | 21 | 59 | 100 | 22.9053 | 16.5919 | 52.7639 | 40.7648 | 40.7648 | 0 | 0
2025-12-23 17:00 | 19.2 | 67 | 100 | 22.2306 | 16.4047 | 55.3277 | 44.1144 | 44.1144 | 0 | 0
2025-12-23 18:00 | 17.8 | 71.5 | 100 | 21.6945 | 16.1377 | 56.6278 | 39.7673 | 39.7673 | 0 | 0
2025-12-23 19:00 | 16.95 | 74.5 | 100 | 21.3647 | 15.9766 | 57.4756 | 37.3318 | 37.3318 | 0 | 0
2025-12-23 20:00 | 16.3 | 76 | 100 | 21.1095 | 15.8135 | 57.865 | 33.1702 | 33.1702 | 0 | 0
2025-12-23 21:00 | 15.85 | 77 | 100 | 20.9315 | 15.6972 | 58.1255 | 30.1686 | 30.1686 | 0 | 0
2025-12-23 22:00 | 15.45 | 78.5 | 70 | 20.773 | 15.6184 | 58.5462 | 20.3081 | 20.3081 | 0 | 0
2025-12-23 23:00 | 14.9 | 81 | 70 | 20.5543 | 15.5246 | 59.2443 | 19.8097 | 19.8097 | 0 | 0
2025-12-24 | 14.35 | 82.5 | 70 | 20.3332 | 15.3864 | 59.6404 | 17.5431 | 17.5431 | 0 | 0
2025-12-24 01:00 | 13.85 | 83.5 | 70 | 20.1306 | 15.2458 | 59.8969 | 14.8704 | 14.8704 | 0 | 0
2025-12-24 02:00 | 13.3 | 84.5 | 70 | 19.9062 | 15.0858 | 60.155 | 11.7707 | 11.7707 | 0 | 0
2025-12-24 03:00 | 12.8 | 86.5 | 70 | 19.702 | 14.9793 | 60.692 | 10.565 | 10.565 | 0 | 0
2025-12-24 04:00 | 12.6 | 88 | 70 | 19.6207 | 14.9607 | 61.0954 | 11.0831 | 11.0831 | 0 | 0
2025-12-24 05:00 | 12.45 | 88 | 70 | 19.5584 | 14.9066 | 61.0914 | 9.8141 | 9.8141 | 0 | 0
2025-12-24 06:00 | 12.2 | 87.5 | 100 | 19.4539 | 14.7982 | 60.9524 | 9.991 | 9.991 | 0 | 0
2025-12-24 07:00 | 12.8 | 85 | 100 | 19.7005 | 14.9245 | 60.2762 | 11.8809 | 11.8809 | 0 | 0
2025-12-24 08:00 | 15.05 | 79 | 100 | 20.6129 | 15.497 | 58.6607 | 25.327 | 25.327 | 0 | 0
2025-12-24 09:00 | 18.1 | 72 | 100 | 21.8113 | 16.2668 | 56.8195 | 44.7782 | 44.7782 | 0 | 0
2025-12-24 10:00 | 20.6 | 62.5 | 100 | 22.7575 | 16.6495 | 53.9529 | 47.1935 | 47.1935 | 0 | 0
2025-12-24 11:00 | 22 | 53.5 | 100 | 23.2739 | 16.6066 | 50.8399 | 33.6493 | 33.6493 | 0 | 0
2025-12-24 12:00 | 22.7 | 50 | 100 | 23.5297 | 16.6196 | 49.5822 | 29.1185 | 29.1185 | 0 | 0
2025-12-24 13:00 | 23.15 | 48.5 | 100 | 23.6933 | 16.6668 | 49.0437 | 28.5858 | 28.5858 | 0 | 0
2025-12-24 14:00 | 23.05 | 49.5 | 100 | 23.6571 | 16.697 | 49.4299 | 31.2091 | 31.2091 | 0 | 0
2025-12-24 15:00 | 22.45 | 52.5 | 100 | 23.4389 | 16.6896 | 50.5301 | 35.3946 | 35.3946 | 0 | 0
2025-12-24 16:00 | 21.35 | 59 | 100 | 23.0356 | 16.7068 | 52.8266 | 45.0382 | 45.0382 | 0 | 0
2025-12-24 17:00 | 19.8 | 67 | 100 | 22.4587 | 16.6109 | 55.4379 | 51.693 | 51.693 | 0 | 0
2025-12-24 18:00 | 19 | 69.5 | 100 | 22.1559 | 16.459 | 56.1578 | 49.1422 | 49.1422 | 0 | 0
2025-12-24 19:00 | 19.05 | 68.5 | 100 | 22.1743 | 16.4272 | 55.8241 | 46.7906 | 46.7906 | 0 | 0
2025-12-24 20:00 | 18.4 | 71 | 100 | 21.9264 | 16.3231 | 56.5592 | 45.912 | 45.912 | 0 | 0
2025-12-24 21:00 | 17.55 | 74.5 | 100 | 21.5995 | 16.1884 | 57.572 | 44.9672 | 44.9672 | 0 | 0
2025-12-24 22:00 | 17 | 77.5 | 70 | 21.3868 | 16.1278 | 58.4447 | 32.2228 | 32.2228 | 0 | 0
2025-12-24 23:00 | 15.9 | 84 | 70 | 20.9578 | 16.0108 | 60.2792 | 33.9079 | 33.9079 | 0 | 0
2025-12-25 | 14.9 | 89 | 70 | 20.562 | 15.8458 | 61.6047 | 33.1241 | 33.1241 | 0 | 0
2025-12-25 01:00 | 14.45 | 90.5 | 70 | 20.3816 | 15.7368 | 61.9697 | 31.3842 | 31.3842 | 0 | 0
2025-12-25 02:00 | 14.15 | 91.5 | 70 | 20.2607 | 15.6635 | 62.2127 | 30.2034 | 30.2034 | 0 | 0
2025-12-25 03:00 | 13.9 | 92.5 | 70 | 20.1599 | 15.6071 | 62.4607 | 29.4592 | 29.4592 | 0 | 0
2025-12-25 04:00 | 14 | 92.5 | 70 | 20.2007 | 15.645 | 62.4744 | 30.3839 | 30.3839 | 0 | 0
2025-12-25 05:00 | 14.05 | 92.5 | 70 | 20.221 | 15.6638 | 62.4806 | 30.8429 | 30.8429 | 0 | 0
2025-12-25 06:00 | 13.85 | 92.5 | 100 | 20.1395 | 15.5893 | 62.4487 | 41.3843 | 41.3843 | 0 | 0
2025-12-25 07:00 | 14.5 | 90 | 100 | 20.4013 | 15.7356 | 61.8245 | 44.2778 | 44.2778 | 0 | 0
2025-12-25 08:00 | 16.45 | 84.5 | 100 | 21.1763 | 16.2352 | 60.5222 | 56.949 | 56.949 | 0 | 0
2025-12-25 09:00 | 19.1 | 77.5 | 100 | 22.1996 | 16.8888 | 58.8719 | 73.9202 | 73.9202 | 0 | 0
2025-12-25 10:00 | 21 | 71 | 100 | 22.9111 | 17.244 | 57.1138 | 80.0047 | 80.0047 | 0 | 0
2025-12-25 11:00 | 22.05 | 65 | 100 | 23.2961 | 17.2837 | 55.1892 | 74.1405 | 74.1405 | 0 | 0
2025-12-25 12:00 | 23.1 | 60 | 100 | 23.677 | 17.3519 | 53.5426 | 70.2084 | 70.2084 | 0 | 0
2025-12-25 13:00 | 23.85 | 57 | 100 | 23.9464 | 17.4203 | 52.539 | 68.6799 | 68.6799 | 0 | 0
2025-12-25 14:00 | 24.1 | 55.5 | 100 | 24.0357 | 17.409 | 51.9954 | 66.1265 | 66.1265 | 0 | 0
2025-12-25 15:00 | 23.5 | 59.5 | 100 | 23.8211 | 17.4562 | 53.4559 | 73.6451 | 73.6451 | 0 | 0
2025-12-25 16:00 | 22.55 | 66 | 100 | 23.4789 | 17.514 | 55.7257 | 84.5608 | 84.5608 | 0 | 0
2025-12-25 17:00 | 21.4 | 72 | 100 | 23.0596 | 17.4403 | 57.6228 | 89.1162 | 89.1162 | 0 | 0
2025-12-25 18:00 | 20.35 | 76.5 | 100 | 22.6714 | 17.296 | 58.9095 | 88.6846 | 88.6846 | 0 | 0
2025-12-25 19:00 | 20.05 | 76.5 | 100 | 22.5588 | 17.186 | 58.8145 | 84.3821 | 84.3821 | 0 | 0
2025-12-25 20:00 | 19.65 | 78 | 100 | 22.4088 | 17.1144 | 59.2138 | 83.2811 | 83.2811 | 0 | 0
2025-12-25 21:00 | 19.35 | 79.5 | 100 | 22.2961 | 17.0784 | 59.6373 | 83.5061 | 83.5061 | 0 | 0
2025-12-25 22:00 | 19.25 | 79.5 | 70 | 22.2581 | 17.0409 | 59.6099 | 57.4699 | 57.4699 | 0 | 0
2025-12-25 23:00 | 18.9 | 81 | 70 | 22.1257 | 16.9834 | 60.0176 | 57.0882 | 57.0882 | 0 | 0
2025-12-26 | 18.5 | 82 | 70 | 21.9731 | 16.8831 | 60.2368 | 55.123 | 55.123 | 0 | 0
2025-12-26 01:00 | 18 | 83 | 70 | 21.7811 | 16.743 | 60.4284 | 52.1451 | 52.1451 | 0 | 0
2025-12-26 02:00 | 17.35 | 85.5 | 70 | 21.5306 | 16.6137 | 61.0633 | 50.5183 | 50.5183 | 0 | 0
2025-12-26 03:00 | 16.8 | 89.5 | 70 | 21.3186 | 16.5817 | 62.1779 | 52.4447 | 52.4447 | 0 | 0
2025-12-26 04:00 | 16.5 | 92.5 | 70 | 21.2031 | 16.5959 | 63.0243 | 54.8239 | 54.8239 | 0 | 0
2025-12-26 05:00 | 16.2 | 93 | 70 | 21.085 | 16.501 | 63.0911 | 52.6426 | 52.6426 | 0 | 0
2025-12-26 06:00 | 15.9 | 93 | 100 | 20.966 | 16.3865 | 63.0065 | 70.8373 | 70.8373 | 0 | 0
2025-12-26 07:00 | 16.15 | 91.5 | 100 | 21.0639 | 16.4194 | 62.6111 | 70.6325 | 70.6325 | 0 | 0
2025-12-26 08:00 | 17.5 | 87 | 100 | 21.5903 | 16.7375 | 61.5668 | 78.2158 | 78.2158 | 0 | 0
2025-12-26 09:00 | 19.35 | 80.5 | 100 | 22.2968 | 17.1278 | 59.9674 | 86.3924 | 86.3924 | 0 | 0
2025-12-26 10:00 | 21.2 | 73 | 100 | 22.9862 | 17.4232 | 57.907 | 89.4205 | 89.4205 | 0 | 0
2025-12-26 11:00 | 22.8 | 66.5 | 100 | 23.5697 | 17.6321 | 55.9807 | 89.6702 | 89.6702 | 0 | 0
2025-12-26 12:00 | 23.7 | 61.5 | 100 | 23.8929 | 17.6474 | 54.2988 | 83.7144 | 83.7144 | 0 | 0
2025-12-26 13:00 | 24.15 | 57.5 | 100 | 24.0535 | 17.5513 | 52.8209 | 74.4959 | 74.4959 | 0 | 0
2025-12-26 14:00 | 24.2 | 55 | 100 | 24.0713 | 17.4091 | 51.8253 | 65.5452 | 65.5452 | 0 | 0
2025-12-26 15:00 | 24 | 53.5 | 100 | 24 | 17.2479 | 51.1815 | 57.3647 | 57.3647 | 0 | 0
2025-12-26 16:00 | 23.1 | 56 | 100 | 23.6763 | 17.1083 | 52.0064 | 55.8461 | 55.8461 | 0 | 0
2025-12-26 17:00 | 21.4 | 63 | 100 | 23.0558 | 16.9446 | 54.3314 | 59.2471 | 59.2471 | 0 | 0
2025-12-26 18:00 | 20.2 | 68 | 100 | 22.6103 | 16.8001 | 55.8857 | 60.0836 | 60.0836 | 0 | 0
2025-12-26 19:00 | 19.65 | 69.5 | 100 | 22.4034 | 16.6852 | 56.2943 | 57.5858 | 57.5858 | 0 | 0
2025-12-26 20:00 | 19 | 71.5 | 100 | 22.1572 | 16.5573 | 56.8487 | 55.1593 | 55.1593 | 0 | 0
2025-12-26 21:00 | 18.15 | 77.5 | 100 | 21.8348 | 16.542 | 58.6734 | 61.2325 | 61.2325 | 0 | 0
2025-12-26 22:00 | 17.25 | 85 | 70 | 21.4911 | 16.554 | 60.8841 | 48.6276 | 48.6276 | 0 | 0
2025-12-26 23:00 | 16.5 | 89 | 70 | 21.2 | 16.4458 | 61.9508 | 48.5846 | 48.5846 | 0 | 0
2025-12-27 | 16.4 | 89.5 | 70 | 21.161 | 16.4295 | 62.0818 | 48.5004 | 48.5004 | 0 | 0
2025-12-27 01:00 | 16.35 | 89.5 | 70 | 21.1412 | 16.4102 | 62.0689 | 48.0027 | 48.0027 | 0 | 0
2025-12-27 02:00 | 16 | 90 | 70 | 21.003 | 16.2993 | 62.1364 | 45.4318 | 45.4318 | 0 | 0
2025-12-27 03:00 | 15.85 | 88.5 | 70 | 20.9419 | 16.1795 | 61.6528 | 41.3848 | 41.3848 | 0 | 0
2025-12-27 04:00 | 15.7 | 87 | 70 | 20.8808 | 16.0614 | 61.1748 | 37.3851 | 37.3851 | 0 | 0
2025-12-27 05:00 | 15.25 | 87.5 | 70 | 20.7012 | 15.9149 | 61.2428 | 34.0096 | 34.0096 | 0 | 0
2025-12-27 06:00 | 14.8 | 88 | 100 | 20.5206 | 15.7678 | 61.314 | 43.7809 | 43.7809 | 0 | 0
2025-12-27 07:00 | 15.4 | 85.5 | 100 | 20.7595 | 15.8886 | 60.6625 | 45.6564 | 45.6564 | 0 | 0
2025-12-27 08:00 | 17.5 | 78 | 100 | 21.5829 | 16.33 | 58.6991 | 53.9444 | 53.9444 | 0 | 0
2025-12-27 09:00 | 20.35 | 65.5 | 100 | 22.6653 | 16.722 | 55.0094 | 53.9281 | 53.9281 | 0 | 0
2025-12-27 10:00 | 22.65 | 54.5 | 100 | 23.5125 | 16.8732 | 51.324 | 44.8159 | 44.8159 | 0 | 0
2025-12-27 11:00 | 23.85 | 51.5 | 100 | 23.9462 | 17.0746 | 50.3322 | 47.7734 | 47.7734 | 0 | 0
2025-12-27 12:00 | 24.5 | 51 | 100 | 24.1783 | 17.2498 | 50.247 | 53.5336 | 53.5336 | 0 | 0
2025-12-27 13:00 | 25 | 49 | 100 | 24.3557 | 17.2756 | 49.5115 | 51.4697 | 51.4697 | 0 | 0
2025-12-27 14:00 | 25.2 | 47.5 | 100 | 24.4266 | 17.237 | 48.9184 | 47.7115 | 47.7115 | 0 | 0
2025-12-27 15:00 | 25.05 | 47 | 100 | 24.3738 | 17.1565 | 48.6883 | 44.0061 | 44.0061 | 0 | 0
2025-12-27 16:00 | 24.25 | 52 | 100 | 24.0893 | 17.2329 | 50.6248 | 54.6162 | 54.6162 | 0 | 0
2025-12-27 17:00 | 22.55 | 62.5 | 100 | 23.478 | 17.3101 | 54.4048 | 72.341 | 72.341 | 0 | 0
2025-12-27 18:00 | 21.05 | 71.5 | 100 | 22.9298 | 17.2867 | 57.3503 | 82.7024 | 82.7024 | 0 | 0
2025-12-27 19:00 | 20.35 | 75.5 | 100 | 22.6709 | 17.2437 | 58.5689 | 85.6536 | 85.6536 | 0 | 0
2025-12-27 20:00 | 19.9 | 76 | 100 | 22.502 | 17.105 | 58.609 | 80.8388 | 80.8388 | 0 | 0
2025-12-27 21:00 | 19.55 | 74 | 100 | 22.3684 | 16.8772 | 57.8247 | 69.9222 | 69.9222 | 0 | 0
2025-12-27 22:00 | 19.2 | 72.5 | 70 | 22.2343 | 16.6771 | 57.235 | 42.549 | 42.549 | 0 | 0
2025-12-27 23:00 | 18.45 | 74.5 | 70 | 21.9483 | 16.507 | 57.7587 | 39.769 | 39.769 | 0 | 0
2025-12-28 | 17.65 | 76 | 70 | 21.6397 | 16.2912 | 58.1052 | 35.4432 | 35.4432 | 0 | 0
2025-12-28 01:00 | 17.1 | 77 | 70 | 21.4256 | 16.1402 | 58.3366 | 32.392 | 32.392 | 0 | 0
2025-12-28 02:00 | 16.65 | 79.5 | 70 | 21.2508 | 16.089 | 59.0521 | 32.9445 | 32.9445 | 0 | 0
2025-12-28 03:00 | 16.45 | 83.5 | 70 | 21.1754 | 16.1905 | 60.2572 | 38.3233 | 38.3233 | 0 | 0
2025-12-28 04:00 | 16.35 | 88 | 70 | 21.1398 | 16.3459 | 61.6223 | 45.4137 | 45.4137 | 0 | 0
2025-12-28 05:00 | 16.05 | 90.5 | 70 | 21.0233 | 16.3389 | 62.3132 | 46.874 | 46.874 | 0 | 0
2025-12-28 06:00 | 15.6 | 92 | 100 | 20.8455 | 16.2296 | 62.6529 | 64.2824 | 64.2824 | 0 | 0
2025-12-28 07:00 | 16.05 | 88.5 | 100 | 21.0214 | 16.2553 | 61.6951 | 61.8724 | 61.8724 | 0 | 0
2025-12-28 08:00 | 18.2 | 74 | 100 | 21.8515 | 16.3947 | 57.5391 | 52.0786 | 52.0786 | 0 | 0
2025-12-28 09:00 | 21.5 | 54.5 | 100 | 23.0894 | 16.501 | 51.1921 | 31.7274 | 31.7274 | 0 | 0
2025-12-28 10:00 | 24.4 | 42 | 100 | 24.1435 | 16.6267 | 46.5308 | 16.9152 | 16.9152 | 0 | 0
2025-12-28 11:00 | 26.05 | 37.5 | 100 | 24.7284 | 16.7919 | 44.7113 | 14.6627 | 14.6627 | 0 | 0
2025-12-28 12:00 | 26.85 | 36 | 100 | 25.0076 | 16.9071 | 44.0964 | 15.8662 | 15.8662 | 0 | 0
2025-12-28 13:00 | 27.3 | 34 | 100 | 25.1643 | 16.8788 | 43.2202 | 11.1265 | 11.1265 | 0 | 0
2025-12-28 14:00 | 27.5 | 32.5 | 100 | 25.2343 | 16.8162 | 42.5458 | 6.0969 | 6.0969 | 0 | 0
2025-12-28 15:00 | 27.35 | 35 | 100 | 25.1807 | 16.9678 | 43.6878 | 16.2854 | 16.2854 | 0 | 0
2025-12-28 16:00 | 26.7 | 39 | 100 | 24.9538 | 17.0843 | 45.4455 | 27.9497 | 27.9497 | 0 | 0
2025-12-28 17:00 | 24.95 | 46.5 | 100 | 24.3385 | 17.0895 | 48.4857 | 41.0669 | 41.0669 | 0 | 0
2025-12-28 18:00 | 23.2 | 54 | 100 | 23.7122 | 17.017 | 51.2618 | 49.9071 | 49.9071 | 0 | 0
2025-12-28 19:00 | 22.3 | 59 | 100 | 23.3858 | 17.0197 | 53.0292 | 56.9541 | 56.9541 | 0 | 0
2025-12-28 20:00 | 21.4 | 63.5 | 100 | 23.056 | 16.9717 | 54.5298 | 61.0509 | 61.0509 | 0 | 0
2025-12-28 21:00 | 21 | 64 | 100 | 22.9077 | 16.8623 | 54.6319 | 57.632 | 57.632 | 0 | 0
2025-12-28 22:00 | 20.85 | 63.5 | 70 | 22.8515 | 16.7833 | 54.4249 | 37.8964 | 37.8964 | 0 | 0
2025-12-28 23:00 | 20.25 | 64.5 | 70 | 22.6271 | 16.6319 | 54.6822 | 34.9446 | 34.9446 | 0 | 0
2025-12-29 | 20.05 | 63 | 70 | 22.5508 | 16.4849 | 54.125 | 29.9551 | 29.9551 | 0 | 0
2025-12-29 01:00 | 20.15 | 60.5 | 70 | 22.5871 | 16.3863 | 53.2591 | 25.3176 | 25.3176 | 0 | 0
2025-12-29 02:00 | 20 | 61 | 70 | 22.5307 | 16.3621 | 53.4224 | 25.2109 | 25.2109 | 0 | 0
2025-12-29 03:00 | 20.35 | 62 | 70 | 22.6633 | 16.5322 | 53.8215 | 30.3288 | 30.3288 | 0 | 0
2025-12-29 04:00 | 20.6 | 63 | 70 | 22.7577 | 16.6707 | 54.2169 | 34.6937 | 34.6937 | 0 | 0
2025-12-29 05:00 | 20.6 | 63.5 | 70 | 22.758 | 16.6971 | 54.3955 | 35.8143 | 35.8143 | 0 | 0
2025-12-29 06:00 | 20.7 | 64 | 100 | 22.7957 | 16.7588 | 54.5883 | 53.9785 | 53.9785 | 0 | 0
2025-12-29 07:00 | 20.85 | 68 | 100 | 22.8537 | 17.0264 | 56.05 | 68.7597 | 68.7597 | 0 | 0
2025-12-29 08:00 | 21.85 | 70.5 | 100 | 23.2247 | 17.5194 | 57.2294 | 90.6097 | 90.6097 | 0 | 0
2025-12-29 09:00 | 23.45 | 66.5 | 100 | 23.8038 | 17.8613 | 56.2128 | 98.9951 | 98.9951 | 0 | 0
2025-12-29 10:00 | 25.05 | 61 | 100 | 24.3707 | 18.0819 | 54.5267 | 100.3373 | 100.3373 | 0 | 0
2025-12-29 11:00 | 26.5 | 55.5 | 100 | 24.8751 | 18.2085 | 52.6631 | 97.4391 | 97.4391 | 0 | 0
2025-12-29 12:00 | 27.5 | 49.5 | 100 | 25.22 | 18.1083 | 50.294 | 84.0545 | 84.0545 | 0 | 0
2025-12-29 13:00 | 27.6 | 46.5 | 100 | 25.2564 | 17.9172 | 48.9597 | 71.6586 | 71.6586 | 0 | 0
2025-12-29 14:00 | 27 | 49 | 100 | 25.0503 | 17.9098 | 49.9479 | 75.6372 | 75.6372 | 0 | 0
2025-12-29 15:00 | 26.15 | 53.5 | 100 | 24.7558 | 17.9511 | 51.7069 | 84.4518 | 84.4518 | 0 | 0
2025-12-29 16:00 | 24.85 | 62.5 | 100 | 24.3004 | 18.1063 | 55.1062 | 103.7622 | 103.7622 | 0 | 0
2025-12-29 17:00 | 23.55 | 71.5 | 100 | 23.8401 | 18.194 | 58.2389 | 119.1086 | 119.1086 | 0 | 0
2025-12-29 18:00 | 23 | 67.5 | 100 | 23.6422 | 17.7593 | 56.4689 | 96.4224 | 96.4224 | 0 | 0
2025-12-29 19:00 | 22.6 | 63 | 100 | 23.4963 | 17.3559 | 54.6124 | 74.8039 | 74.8039 | 0 | 0
2025-12-29 20:00 | 22 | 67 | 100 | 23.2784 | 17.3767 | 55.963 | 80.6921 | 80.6921 | 0 | 0
2025-12-29 21:00 | 21.8 | 67 | 100 | 23.205 | 17.3067 | 55.9057 | 77.9607 | 77.9607 | 0 | 0
2025-12-29 22:00 | 21.8 | 64 | 70 | 23.2039 | 17.138 | 54.7875 | 47.4185 | 47.4185 | 0 | 0
2025-12-29 23:00 | 21.6 | 61 | 70 | 23.129 | 16.9004 | 53.6324 | 38.5251 | 38.5251 | 0 | 0
2025-12-30 | 21.35 | 59 | 70 | 23.0356 | 16.7044 | 52.8547 | 31.7058 | 31.7058 | 0 | 0
2025-12-30 01:00 | 20.95 | 61.5 | 70 | 22.8879 | 16.709 | 53.7059 | 34.116 | 34.116 | 0 | 0
2025-12-30 02:00 | 20.75 | 61.5 | 70 | 22.8131 | 16.6417 | 53.6742 | 32.4139 | 32.4139 | 0 | 0
2025-12-30 03:00 | 21 | 57.5 | 70 | 22.9046 | 16.5051 | 52.26 | 25.3485 | 25.3485 | 0 | 0
2025-12-30 04:00 | 21.15 | 53 | 70 | 22.9585 | 16.3019 | 50.629 | 16.1021 | 16.1021 | 0 | 0
2025-12-30 05:00 | 21.05 | 50 | 70 | 22.9197 | 16.102 | 49.5214 | 8.3618 | 8.3618 | 0 | 0
2025-12-30 06:00 | 20.9 | 47.5 | 100 | 22.8624 | 15.9149 | 48.5994 | 2.098 | 2.098 | 0 | 0
2025-12-30 07:00 | 21 | 44.5 | 100 | 22.8985 | 15.7757 | 47.4915 | 0 | 0 | 0 | 0
2025-12-30 08:00 | 21.8 | 40.5 | 100 | 23.1953 | 15.7761 | 45.9538 | 0 | 0 | 0 | 0
2025-12-30 09:00 | 22.9 | 35 | 100 | 23.5997 | 15.7455 | 43.7432 | 0 | 0 | 0 | 0
2025-12-30 10:00 | 23.75 | 31.5 | 100 | 23.9094 | 15.7464 | 42.2563 | 0 | 0 | 0 | 0
2025-12-30 11:00 | 23.8 | 32.5 | 100 | 23.9276 | 15.826 | 42.6596 | 0 | 0 | 0 | 0
2025-12-30 12:00 | 23.55 | 35 | 100 | 23.837 | 15.9222 | 43.6948 | 0 | 0 | 0 | 0
2025-12-30 13:00 | 23.8 | 34.5 | 100 | 23.9277 | 15.9576 | 43.4784 | 0 | 0 | 0 | 0
2025-12-30 14:00 | 23.85 | 33.5 | 100 | 23.9457 | 15.9039 | 43.072 | 0 | 0 | 0 | 0
2025-12-30 15:00 | 23.6 | 35 | 100 | 23.8551 | 15.9347 | 43.6992 | 0 | 0 | 0 | 0
2025-12-30 16:00 | 23.35 | 36.5 | 100 | 23.7644 | 15.9635 | 44.3166 | 0 | 0 | 0 | 0
2025-12-30 17:00 | 22.5 | 43 | 100 | 23.4547 | 16.1293 | 46.8906 | 2.0939 | 2.0939 | 0 | 0
2025-12-30 18:00 | 21.85 | 47.5 | 100 | 23.2164 | 16.2057 | 48.5945 | 11.4905 | 11.4905 | 0 | 0
2025-12-30 19:00 | 21.9 | 47 | 100 | 23.2347 | 16.1916 | 48.4044 | 10.2377 | 10.2377 | 0 | 0
2025-12-30 20:00 | 21.7 | 49.5 | 100 | 23.1616 | 16.2767 | 49.3356 | 16.794 | 16.794 | 0 | 0
2025-12-30 21:00 | 21.45 | 51 | 100 | 23.0694 | 16.2856 | 49.8798 | 19.2471 | 19.2471 | 0 | 0
2025-12-30 22:00 | 21.35 | 50 | 70 | 23.0317 | 16.1975 | 49.5037 | 10.3667 | 10.3667 | 0 | 0
2025-12-30 23:00 | 21.25 | 48.5 | 70 | 22.9938 | 16.0809 | 48.9495 | 6.1334 | 6.1334 | 0 | 0
2025-12-31 | 21.3 | 48.5 | 70 | 23.0125 | 16.0953 | 48.954 | 6.512 | 6.512 | 0 | 0
2025-12-31 01:00 | 21.35 | 49.5 | 70 | 23.0315 | 16.1676 | 49.328 | 9.2465 | 9.2465 | 0 | 0
2025-12-31 02:00 | 21.35 | 50 | 70 | 23.0317 | 16.1964 | 49.5158 | 10.4433 | 10.4433 | 0 | 0
2025-12-31 03:00 | 21.35 | 52 | 70 | 23.0326 | 16.3102 | 50.2557 | 15.1591 | 15.1591 | 0 | 0
2025-12-31 04:00 | 20.95 | 55.5 | 70 | 22.885 | 16.3795 | 51.5083 | 20.2283 | 20.2283 | 0 | 0
2025-12-31 05:00 | 20.25 | 56.5 | 70 | 22.6226 | 16.2086 | 51.8087 | 17.0095 | 17.0095 | 0 | 0
2025-12-31 06:00 | 19.75 | 57.5 | 100 | 22.4339 | 16.1003 | 52.1208 | 21.8321 | 21.8321 | 0 | 0
2025-12-31 07:00 | 19.7 | 56.5 | 100 | 22.4143 | 16.0324 | 51.7625 | 18.1403 | 18.1403 | 0 | 0
2025-12-31 08:00 | 20.25 | 52 | 100 | 22.6201 | 15.967 | 50.1886 | 9.8368 | 9.8368 | 0 | 0
2025-12-31 09:00 | 21.1 | 47 | 100 | 22.9371 | 15.9509 | 48.3791 | 2.0898 | 2.0898 | 0 | 0
2025-12-31 10:00 | 21.75 | 43 | 100 | 23.1777 | 15.9129 | 46.8771 | 0 | 0 | 0 | 0
2025-12-31 11:00 | 22.2 | 42.5 | 100 | 23.3441 | 16.0144 | 46.678 | 0 | 0 | 0 | 0
2025-12-31 12:00 | 22.3 | 43 | 100 | 23.3811 | 16.0733 | 46.8742 | 0.0133 | 0.0133 | 0 | 0
2025-12-31 13:00 | 22.3 | 43 | 100 | 23.3811 | 16.0723 | 46.8803 | 0.0699 | 0.0699 | 0 | 0
2025-12-31 14:00 | 22.25 | 42.5 | 100 | 23.3625 | 16.0268 | 46.6937 | 0 | 0 | 0 | 0
2025-12-31 15:00 | 22 | 43 | 100 | 23.2703 | 15.983 | 46.892 | 0 | 0 | 0 | 0
2025-12-31 16:00 | 21.55 | 45 | 100 | 23.1041 | 15.9682 | 47.6545 | 0 | 0 | 0 | 0
2025-12-31 17:00 | 20.9 | 48.5 | 100 | 22.8629 | 15.9732 | 48.9492 | 5.2618 | 5.2618 | 0 | 0
2025-12-31 18:00 | 20.1 | 53.5 | 100 | 22.5642 | 16.0004 | 50.7279 | 13.1092 | 13.1092 | 0 | 0
2025-12-31 19:00 | 19.1 | 58 | 100 | 22.1863 | 15.9161 | 52.2532 | 16.1561 | 16.1561 | 0 | 0
2025-12-31 20:00 | 18.15 | 61.5 | 100 | 21.8226 | 15.7798 | 53.3897 | 15.9068 | 15.9068 | 0 | 0
2025-12-31 21:00 | 17.5 | 64 | 100 | 21.5715 | 15.6838 | 54.1802 | 15.6436 | 15.6436 | 0 | 0
2025-12-31 22:00 | 17.05 | 66.5 | 70 | 21.3972 | 15.6486 | 54.962 | 12.1367 | 12.1367 | 0 | 0
2025-12-31 23:00 | 16.8 | 68 | 70 | 21.3001 | 15.6323 | 55.4257 | 12.9329 | 12.9329 | 0 | 0