Drainage Design Calculation

BS EN 12056-2:2000 — Gravity Drainage Systems Inside Buildings

Quick Sizing — Total Design Flow & Pipe List

| Project Information |  |
| --- | --- |
| Project Name | Marina Commercial Tower |
| Project No. | MCT-2026-MEP-001 |
| Revision | P2 |
| Client | — |
| Prepared by | Hussein Ragab |
| Checked by | — |
| Date | 2026-10-20 |

Values in this report are displayed in SI (metric) units.

# 1.  Methodology & Standards

| Topic | Method / Reference |
| --- | --- |
| Design flow rate | Qww = K × √(ΣDU) — BS EN 12056-2 Clause 6.3.1 |
| Frequency factor K | Table 3: 0.5 dwellings/offices · 0.7 hospitals/hotels · 1.0 public · 1.2 labs |
| Stack capacity | Tables 11 & 12 (primary/secondary ventilated) |
| Branch capacity | Tables 4 & 7 (unventilated/ventilated) |
| Drain capacity | Colebrook-White equation, kb = 1.0 mm (Annex B) |
| Self-cleansing | Minimum velocity 0.7 m/s in horizontal drains (BS EN 16933-2:2017 # 10.2.1, drains < DN 300) |
| Pipe sizes | Rounded up to nearest practical DN: 32 · 40 · 50 · 75 · 100 · 150 · 200 · 250 · 300 mm |
| Uniform stack rule | If stack DN increases at any level, the larger DN is applied to the entire stack height for proper ventilation continuity |

# 2.  Design Inputs

| Parameter | Value |
| --- | --- |
| System type | System IV |
| Frequency factor K | Intermittent (dwelling, guesthouse, office) |
| Stack branch entry | Swept |
| Stack ventilation | Secondary |
| Filling degree (h/d) | 0.5 |
| Self-cleansing | Strict (0.7 m/s) |

# 3.  Design Assumptions

Design flow per BS EN 12056-2 Clause 6.3.1: Qww = K x sqrt(SigmaDU).

Continuous (Qc) and pumped (Qp) flows added without probability reduction (Clause 6.3.3).

Each Pipe List entry is sized as a single pipe carrying the design flow of its own fixture set (a quick per-pipe estimate).

Vertical pipes sized by flow capacity (BS EN 12056-2 stack tables); horizontal pipes sized for capacity AND self-cleansing velocity.

Pipe sizes rounded up to the nearest practical DN in the BS EN 12056 ladder.

System IV combined-drain flow uses the split-root basis — soil and waste rooted separately (Qtot = max(K x sqrt(SigmaDU_soil), largest soil DU) + max(K x sqrt(SigmaDU_waste) + Qc + Qp, largest waste DU), # 6.3.4), a conservative design margin; BS EN 12056-2 # 6.3.1 defines Qww on the combined DU sum, which would give a smaller value.

# 4.  Step-by-Step Calculation

Step 1: Total Design Flow (Cl. 6.3.1 / 6.3.3 / 6.3.4)

Formula: Qtot = max(K x sqrt(SigmaDU_soil), largest soil DU) + max(K x sqrt(SigmaDU_waste) + Qc + Qp, largest waste DU) (split-root, System IV separate pipes, # 6.3.4)

Substitution: K = 0.5 ¦ SigmaDU_soil = 645 -> Q_soil = 12.698 L/s ¦ SigmaDU_waste = 153, Qc = 0.000 L/s, Qp = 0.000 L/s -> Q_waste = 6.185 L/s

Result: Total design flow Qtot = 18.883 L/s

# 5.  Results

| Parameter | Value |
| --- | --- |
| Soil design flow (L/s) | 12.698 |
| Waste design flow, incl. Qc + Qp (L/s) | 6.185 |
| Continuous flow Qc (L/s) | — |
| Pumped flow Qp (L/s) | — |
| TOTAL design flow (L/s) | 18.883 |

# 6.  Schedules

Fixture Schedule

| Fixture | DU/unit | Qty | DU Total |
| --- | --- | --- | --- |
| WC — 6.0 L cistern | 2 | 300 | 600 |
| Urinal — single with cistern | 0.5 | 90 | 45 |
| Wash basin / Bidet | 0.3 | 270 | 81 |
| Floor gully DN 50 | 0.6 | 120 | 72 |

Pipe List — Selected Sizes  (combined pipes sized on one root of the summed DU, # 6.3.1)

| Ref | Type | Fixtures | SigmaDU | Design Q (L/s) | DN | Vent DN | Slope | Velocity (m/s) | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SB01 | Horizontal (soil) | WC×10, Urinal×3 | 21.5 | 2.318 | DN 100 | — | 1:100 | 0.68 | Qmax 2.5 L/s at h/d = 0.5 |
| WB01 | Horizontal (waste) | Wash basin / Bidet×9, Floor gully DN 50×4 | 5.1 | 1.129 | DN 100 | — | 1:100 | 0.56 | Qmax 2.5 L/s at h/d = 0.5 |
| SS01 | Vertical (soil) | WC×300, Urinal×90 | 645 | 12.698 | DN 150 | DN 80 | — | — | — |
| WS01 | Vertical (waste) | Wash basin / Bidet×270, Floor gully DN 50×120 | 153 | 6.185 | DN 100 | DN 50 | — | — | — |
| BD01 | Horizontal | WC×300, Urinal×90, Wash basin / Bidet×270, Floor gully DN 50×120 | 798 | 14.124 | DN 200 | — | 1:100 | 1.07 | Qmax 14.18 L/s at h/d = 0.5 |

# R.  Reference Standards

BS EN 12056-2:2000 — Gravity drainage systems inside buildings — sanitary pipework, layout and calculation (Clause 6 design-flow method).

BS EN 12056-2 Table 3 — Frequency factor K by usage type.

BS EN 12056-2 Tables 4, 7, 11 & 12 — Branch and stack hydraulic capacities (ventilated / unventilated).

BS EN 12056-2 Annex B — Colebrook-White partial-fill drain capacity, kb = 1.0 mm.

Engineer of record: Hussein Ragab

Generated by Drainage Sizer — BS EN 12056-2:2000 gravity drainage design.