Foam System — NFPA 11 Sizing

Low-Expansion Foam Quantity Calculation

Tank / dike / spill / loading-rack protection

| Project Information |  |
| --- | --- |
| Project Name | Marina Commercial Tower |
| Project No. | MCT-2026-MEP-001 |
| Revision | P2 |
| Client | — |
| Prepared by | Hussein Ragab |
| Checked by | — |
| Date | 2026-10-20 |

Values in this report are displayed in SI (metric) units.

# 1.  Methodology & Standards

| Reference | Application |
| --- | --- |
| NFPA 11 (2024 ed.) | Standard for Low-, Medium-, and High-Expansion Foam — Chapter 5 design tables for storage tanks, dikes, spills, and loading racks. |
| NFPA 30 (2018 ed.) | Flammable and Combustible Liquids Code — # 4.3 classification of liquids; # 6.4.1.2 heated-fuel promotion rule. |

# 2.  Design Inputs

System

| Parameter | Value |
| --- | --- |
| Foam concentrate | AFFF 3 % |
| Foam family | AFFF |
| Concentrate % | 3.0 % |
| Polar-compatible | No |
| Source | NFPA-Generic |
| Supplementary hose | Not included |
| Hazard count | 1 |

Hazards

| Hazard | Archetype + inputs |
| --- | --- |
| DB01 Generator diesel bund | Diked area — outdoor · A = 120.0 m² · fuel: Diesel #2 · method: low_level · R (mfr-listed) = 0.00 mm/min |

# 3.  Design Assumptions

Foam concentrate, discharge devices, and proportioning equipment are listed under UL 162 and used within their listing limits.

Application rates are taken from NFPA 11 (2024) Chapter 5 tables unless the row specifies a manufacturer-listed rate (AR foam on polar solvents, CAF, etc.).

Hydraulic pipe sizing, valve selection, and proportioner k-factor verification are out of scope of this calculation — covered by the manufacturer's flow-calc software.

All systems are sized AT the tabulated minimum application rate; the NFPA 11 reduced-time exception for above-minimum delivery rates (# 5.2.5.2.3) is therefore not invoked.

Supplementary hose-stream sizing per NFPA 11 # 5.9 is opt-in; flow is 50 gpm (190 L/min) per stream (# 5.9.2.3), count and operating time from Tables 5.9.2.2 and 5.9.2.4. Where the printed ft and m columns disagree the larger allowance is taken: 1 stream below 65 ft (19.812 m), 2 up to and including 36 m, else 3; 10 min below 35 ft (10.668 m), 20 min up to and including 95 ft (28.956 m), else 30 min. On the largest-single-hazard basis each tank carries the hose of its own diameter, inside that hazard's demand (# 5.2.2); a non-tank hazard carries none.

Below-the-seal seal-area application (Table 5.3.5.3.6.1): ENGINEER EXTENSION - the design area is the shell-to-dam annulus on the entered dam-to-shell distance W. NFPA 11 prints no below-seal area basis (Table 5.3.5.3.6.1 gives rate, time and outlet spacing only) - confirm the design area with the AHJ before issue.

Concentrate storage: Storage headroom (ruling 30a-2): NFPA 11 # 4.3.2.3.2.1 (expansion space) and # 4.3.2.3.2.3 (sediment-pocket volume added to the quantity needed) apply to ATMOSPHERIC concentrate tanks only - the tool adds the entered sediment-pocket volume to each separate tank set and then the thermal-expansion headroom (the clause prints no percentage; the allowance is an engineer input on the Storage card, seeded at the tool's documented 10 % convention, ruling D85 - the value used is printed in the storage step). A pressure / bladder tank (# 4.3.2.3.3) carries neither clause and is sized on the concentrate volume itself. The print gives no sediment-pocket volume - take it from the OEM tank datasheet (default 0 L).

# 4.  Step-by-Step Calculation

Step 1: Hazard 1: DB01 Generator diesel bund [Diked area]

Formula:

Substitution:

Result:

Note: Concentrate selected: AFFF 3 %

Step 2: Dike area

Formula: A (user input)

Substitution: A = 120.00 m²

Result: A = 120.00 m²

Step 3: NFPA 30 # 4.3 fuel class

Formula: Class II combustible liquid (100 °F ≤ FP < 140 °F) — short-duration row (NFPA 11)

Substitution: fuel: Diesel #2

Result: Class II combustible liquid (100 °F ≤ FP < 140 °F) — short-duration row (NFPA 11)

Step 4: Application rate

Formula: R from Table 5.7.3.2

Substitution: NFPA 11 # 5.7.3.2, Table 5.7.3.2 (Low-level foam discharge outlets)

Result: R = 4.10 mm/min

Step 5: Discharge duration

Formula: t per NFPA 11 # 5.7.3.2

Substitution: fuel class: II

Result: t = 20 min

Step 6: Foam solution flow

Formula: Q = R × A

Substitution: Q = 4.10 × 120.00

Result: Q = 492 L/min

Step 7: Foam solution volume

Formula: V_sol = Q × t

Substitution: V_sol = 492 × 20

Result: V_sol = 9840 L

Step 8: Foam concentrate volume

Formula: V_conc = V_sol × C% / 100

Substitution: V_conc = 9840 × 3.0 / 100

Result: V_conc = 295 L

Step 9: System totals — Largest single hazard (NFPA 11 # 5.2.2 flow / # 4.3.2.2 concentrate: DB01 Generator diesel bund)

Formula: V_total = max(V_sol_i + V_hose_i); V_conc = V_total × C% / 100 (NFPA 11 # 5.2.2 / # 4.3.2.2 — largest single-hazard demand, each tank with its own # 5.9 hose)

Substitution: V_total = V_sol (9840) + V_hose (0) of DB01 Generator diesel bund = 9840 L ; flow governed by DB01 Generator diesel bund ; C% = 3.0 %

Result: V_conc_total = 295 L

Note: Concentrate: AFFF 3 % (AFFF, 3.0 %)

Step 10: Foam concentrate storage tank sizing

Formula: V_set = (V_conc_set + V_sediment) × thermal_exp per separate tank set (atmospheric: thermal_exp as entered on the Storage card, seed 1.10, + pocket; bladder: 1.00, no pocket); V_required = V_primary + V_reserve; pick smallest N × tank per set

Substitution: V_conc = 295 L ; reserve = 1.0× ; bladder tank ; sediment pocket = 0 L per set ; thermal_exp = 1.00 ; V_primary = 295 L ; V_reserve = 295 L ; V_required = 590 L

Result: 1 × NAFFCO BT-500 primary + 1 × NAFFCO BT-500 reserve (separate, NFPA 11 # 4.3.2.5.2.2) (500 L each) = 1000 L installed (over-spec 410 L)

Note: Reserve basis — NFPA 11 # 4.3.2.5.2.1: a reserve supply "to meet the design requirements for the worst-case fire scenario and put the system back into service after operation" (sized here as reserve factor × primary, default 1.0). # 4.3.2.5.2.2 permits it in separate tanks/compartments, in drums or cans on the premises, or from an approved outside source within 24 hours; other methods need written AHJ approval (# 4.3.2.5.2.3). Storage headroom (ruling 30a-2): NFPA 11 # 4.3.2.3.2.1 (expansion space) and # 4.3.2.3.2.3 (sediment-pocket volume added to the quantity needed) apply to ATMOSPHERIC concentrate tanks only - the tool adds the entered sediment-pocket volume to each separate tank set and then the thermal-expansion headroom (the clause prints no percentage; the allowance is an engineer input on the Storage card, seeded at the tool's documented 10 % convention, ruling D85 - the value used is printed in the storage step). A pressure / bladder tank (# 4.3.2.3.3) carries neither clause and is sized on the concentrate volume itself. The print gives no sediment-pocket volume - take it from the OEM tank datasheet (default 0 L).

# 5.  Results

| Parameter | Value |
| --- | --- |
| Foam solution flow Q_total | 492 L/min |
| Foam solution volume V_sol | 9,840 L |
| Foam concentrate volume | 295 L |
| Water volume | 9,545 L |
| Total concentrate | 295 L |
| Concentrate storage | 2 × NAFFCO BT-500 (500 L each) → 1,000 L installed (reserve 1.0× primary, supply-quantity basis: NFPA 11 # 4.3.2.5.2) |
| Detection & actuation | UV/IR flame detectors + manual pull stations (deluge-type actuation). Per NFPA 72 — both automatic detection (NFPA 11 # 4.9.2) and manual actuation (NFPA 11 # 4.9.3) shall be provided. Final detector selection, spacing, and zoning to be coordinated with the AHJ. |

Per-hazard breakdown

| Hazard | Sizing |
| --- | --- |
| DB01 Generator diesel bund | Q = 492 L/min · V_sol = 9,840 L · V_conc = 295 L |

Water supply requirements (hand-off)

| Parameter | Requirement |
| --- | --- |
| Maximum foam-solution flow at the system inlet (the water supply must deliver this; water fraction = Q x (1 - C%)) | 492 L/min (130 gpm) ; water fraction 477 L/min (126 gpm) |
| Total water volume (tank sizing convention) | 9,545 L (2,521 gal = 9.5 m³ effective capacity) |
| Governing discharge time | 20 min (primary; hazard setting the volume: DB01 Generator diesel bund) |
| Provision | Water supply from an approved source per NFPA 22 (tanks) / NFPA 24 (private fire service mains); fire pump per NFPA 20 where required. Residual pressure at the foam system inlet is set by the hydraulic design (NFPA 13 / NFPA 11) — out of scope of this demand calculation. |

# R.  Reference Standards

NFPA 11 (2024 ed.) — Standard for Low-, Medium-, and High-Expansion Foam — Chapter 5 design tables for storage tanks, dikes, spills, and loading racks.

NFPA 30 (2018 ed.) — Flammable and Combustible Liquids Code — # 4.3 classification of liquids; # 6.4.1.2 heated-fuel promotion rule.

UL 162 — Standard for Foam Equipment and Liquid Concentrates — listing standard for foam concentrates and discharge devices.

Engineer of record: Hussein Ragab

Generated by Foam Calculator — NFPA 11 sizing.