## Foam Equipment
Foam System — NFPA 11 Sizing
Foam System Equipment Schedule
Project: Marina Commercial Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: - ¦ By: Hussein Ragab ¦ Chkd: - ¦ Rev: P2 ¦ Date: 2026-10-20
Unit system: SI ¦ Basis: NFPA 11 (2024) Chapter 5; NFPA 30 (2018) # 4.3 + # 6.4.1.2
Foam system equipment
Ref | Equipment / parameter | Selection / description | Qty | Capacity (each) | Total | Basis (clause)
FC-1 | Foam concentrate | AFFF 3 % — AFFF, 3.0 % induction, hydrocarbon (non-polar) | — | — | 295 | NFPA-Generic · Foam concentrate, discharge devices, and proportioning equipment are listed under UL 162 and used within their listing limits.
ST-1 | Concentrate storage — primary | NAFFCO BT-500 — NAFFCO bladder tank, 750 mm dia × 1,900 mm, 12.0 bar working pressure | 1 | 500 | 500 | supply-quantity basis: NFPA 11 # 4.3.2.5.2
ST-2 | Concentrate storage — reserve | NAFFCO BT-500 — NAFFCO bladder tank, 750 mm dia × 1,900 mm, 12.0 bar working pressure | 1 | 500 | 500 | reserve (separate, NFPA 11 # 4.3.2.5.2.2)
ST-3 | Storage — installed vs required | 1,000 L installed against 590 L required (primary 295 L + reserve 295 L; reserve 1.0× primary) | 2 | 500 | 1000 | supply-quantity basis: NFPA 11 # 4.3.2.5.2
PR-1 | Proportioning equipment | Bladder-tank proportioning — NAFFCO BT-500 at 12.0 bar; source: NAFFCO bladder tank catalogue | 2 | — | — | Foam concentrate, discharge devices, and proportioning equipment are listed under UL 162 and used within their listing limits.
DD-1 | Discharge devices | low-level outlet (count not sized by the demand calc — see citation) | — | — | — | Foam concentrate, discharge devices, and proportioning equipment are listed under UL 162 and used within their listing limits.
FL-1 | Foam-solution flow (design) | Governing demand at the design application rate | — | — | 492 | Largest single hazard (NFPA 11 # 5.2.2 flow / # 4.3.2.2 concentrate: DB01 Generator diesel bund)
FL-2 | Foam-solution volume | Solution delivered over the design discharge time | — | — | 9840 | Largest single hazard (NFPA 11 # 5.2.2 flow / # 4.3.2.2 concentrate: DB01 Generator diesel bund)
WS-1 | Water supply (hand-off) | Maximum foam-solution flow at the system inlet (incl. foam hose streams); the supply delivers it, water fraction = Q x (1 - C%); provision per NFPA 22 (tanks) / NFPA 24 (mains), fire pump per NFPA 20 where required | — | 492 | 9545 | NFPA 22 / NFPA 24 / NFPA 20
DA-1 | Detection & actuation | UV/IR flame detectors + manual pull stations (deluge-type actuation). Per NFPA 72 — both automatic detection (NFPA 11 # 4.9.2) and manual actuation (NFPA 11 # 4.9.3) shall be provided. Final detector selection, spacing, and zoning to be coordinated with the AHJ. | — | — | — | NFPA 72
Reference standards
Reference |  | Application
NFPA 11 (2024 ed.) |  | Standard for Low-, Medium-, and High-Expansion Foam — Chapter 5 design tables for storage tanks, dikes, spills, and loading racks.
NFPA 30 (2018 ed.) |  | Flammable and Combustible Liquids Code — # 4.3 classification of liquids; # 6.4.1.2 heated-fuel promotion rule.
UL 162 |  | Standard for Foam Equipment and Liquid Concentrates — listing standard for foam concentrates and discharge devices.

## Hazard Schedule
Foam System — NFPA 11 Sizing
Per-hazard design schedule
Project: Marina Commercial Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: - ¦ By: Hussein Ragab ¦ Chkd: - ¦ Rev: P2 ¦ Date: 2026-10-20
Unit system: SI ¦ Sizing basis: Largest single hazard (NFPA 11 # 5.2.2 flow / # 4.3.2.2 concentrate: DB01 Generator diesel bund)
Hazard | Archetype | Q (L/min) | V_sol (L) | V_conc (L) | Discharge devices
DB01 Generator diesel bund | Diked area — outdoor | 492 | 9840 | 295 | —