Ventilation Calculation Report

ASHRAE 62.1-2022 / ASHRAE 62.2-2025

| Project Information |  |
| --- | --- |
| Project Name | Marina Commercial Tower |
| Project No. | MCT-2026-MEP-001 |
| Revision | P2 |
| Client | — |
| Prepared by | Hussein Ragab |
| Checked by | — |
| Date | 2026-10-20 |

Values in this report are displayed in SI (metric) units.  Calculated in SI units - the project's saved unit system; computed from the standards' printed SI values, which differ slightly from an I-P calculation.

# 1.  Methodology & Standards

| Method | Formula |
| --- | --- |
| 62.1 fresh (Vbz) | Vbz = Rp * Pz + Ra * Az (ASHRAE 62.1 Table 6-1) |
| 62.1 exhaust | Ve = rate * area or rate * count (ASHRAE 62.1 Table 6-2) |
| Attached extract (transfer air) | Vf = max(Vbz, sum(Ve,attached) * (1 + bal%)); Ve = max(sum(Ve,attached), Vf * (1 - bal%)) — attached rooms draw their share via transfer air, any remainder is exhausted from the main space itself |
| 62.2 continuous | Extract = kitchen + sum(bath) + sum(laundry); Fresh = max(Extract * (1 + balance%), Qtot) — the # 4.1.1 whole-dwelling rate is a floor (# 4.1) |
| 62.2 whole-dwelling Qtot | Qtot = 0.15*A + 3.5*(Nbr+1) L/s (Eq. 4-1b) [0.03*CFA + 7.5*(Nbr+1) CFM (Eq. 4-1a)]; Nbr not to be less than 1; + 3.5 L/s (7.5 CFM) per additional occupant entered (# 4.1.3); rounded to the nearest whole unit as Tables 4-1a/4-1b print |
| 62.2 non-continuous | Fresh = Qtot; exhaust = demand-controlled local exhaust (Table 5-1) — listed separately, excluded from the floor balance and the FAHU extract total |
| ACH spaces | Primary = Volume * ACH / 3.6 [L/s]; balance% sets the opposite stream |
| Extract Only spaces | Ve = sum(qty * rate) over the extract rows; Fresh = 0 by definition (makeup outside the FAHU system) |
| Dedicated fan extract | Fan duty = sum(routed extract * typicality qty); routed flows are EXCLUDED from the FAHU extract; makeup air = transfer air (ASHRAE 62.1-2022 # 6.5) |
| Fan operation (continuous / intermittent) | Continuous fans: duty counts in Net = Fresh - FAHU extract - continuous fan extract, and the FAHU carries the makeup inside the parent space's fresh air. Intermittent fans: EXCLUDED from the pressure balance and take no FAHU makeup — the space is balanced as if the routed extract did not exist; the fan duty itself is unchanged |

# 2.  Design Assumptions

Apartment whole-dwelling fresh-air rates follow ASHRAE 62.2-2025; space ventilation rates follow ASHRAE 62.1-2022 (Tables 6-1 and 6-2).

62.1 breathing-zone outdoor airflow uses the additive people-plus-area model: Vbz = Rp*Pz + Ra*Az, with Rp/Ra read from Table 6-1 for the selected space type. The issued fresh air is the breathing-zone outdoor airflow Vbz (Eq 6-1). Ez = 1.0 is assumed for Table 6-4 'ceiling supply of cool air'; for any other Table 6-4 configuration Voz = Vbz / Ez (Eq 6-2), and Addendum j multiplies by the air-density factor Eρ (Table 6-5; 1.00 at or below 158 m intake elevation). Neither Ez nor Eρ is applied by this tool.

Exhaust (local) airflow follows ASHRAE 62.1 Table 6-2 on the basis printed for each row — EITHER a per-area rate (x the room's own area) OR a per-fixture rate (x the fixture count), never a combination or the larger of the two; the table prints one basis per row. Rows printed with two values (continuous / intermittent operation) are offered as separate types. Attached rows are printed EXACT (qty x printed rate, 1 dp) and the space's attached exhaust is rounded up ONCE, on the row total, to a whole L/s (whole CFM in I-P) - one private toilet at 12.5 L/s issues 13, two issue 25 whether entered as one row of 2 or two rows of 1. ASHRAE 62.1-2022 prints the rates only and no rounding rule; the single round-up is this tool's convention (Table 6-2 rates are minimums). Where rows are routed to dedicated fans, the whole-unit total is shared out by rounding each share down and giving the remainder to the largest share, so the FAHU and fan shares add up to the space total. Fixture counts are user-supplied. Arenas prints no SI rate (Table 6-2, note B): in an SI report its rate is the engineer's direct entry.

Unit systems: each system follows the standard's OWN printed values - an I-P report is computed from the printed cfm rates (Tables 6-1 and 6-2, the fixture rates, 62.2 Eq 4-1a) and rounded up to whole CFM; an SI report from the printed L/s rates (62.2 Eq 4-1b) and whole L/s. The two are not conversions of one another and give slightly different results. Engineer-entered values (overrides, the ACH method, direct entries, custom fixtures, typed bathroom / laundry rates) are stored in SI and, in an I-P report, converted and rounded up once to a whole CFM (for attached-extract rows, once on the space total) - so every space, floor and FAHU total is the sum of the whole numbers printed for it. The indicative FAHU selection is always made on the SI total, printed beside each envelope.

Public-bathroom fixture exhaust rates (private/public water closets, urinals and shower heads) are the intermittent per-fixture values printed in both ASHRAE 62.1-2022 Table 6-2 and IMC 2021 Table 403.3.1.1.

Attached extract spaces (transfer-air rooms): per-area Table 6-2 rates use each attached room's OWN area. The main space receives all supply air at sum(attached extract) * (1 + balance%), floored at its own Vbz; air transfers to the attached rooms through door undercuts or transfer grilles. Total extract is the larger of the attached-room total and the pressure balance fresh * (1 - balance%) — any difference is exhausted from the main space itself (local extract).

Manual overrides: the engineer's entered value is always used in the totals, and overridden fields are highlighted amber in the application. This report flags every overridden value (final and component).

62.2 continuous mode: whole-dwelling extract is the sum of kitchen, bathroom and laundry fan rates; fresh air = the LARGER of extract*(1 + balance%) and the # 4.1.1 whole-dwelling rate Qtot [0.15*A + 3.5*(Nbr+1) L/s (Eq. 4-1b); 0.03*CFA + 7.5*(Nbr+1) CFM (Eq. 4-1a)] - # 4.1 requires a continuous rate not less than # 4.1.1 through # 4.1.4 (engineer ruling 2026-09-05; the # 4.1.3 adder of 3.5 L/s (7.5 CFM) per additional occupant is applied where entered). Non-continuous mode uses Qtot alone, with Nbr taken as not less than 1 (per the standard), independent of the exhaust total. Qtot is rounded to the nearest whole unit, the rounding Tables 4-1a / 4-1b print.

Non-continuous apartments: their exhaust is DEMAND-CONTROLLED local exhaust (ASHRAE 62.2-2025 Table 5-1's own title) and, like an intermittent fan, is listed separately ('Intermittent - excl.' columns) and excluded from every floor pressure figure and from the FAHU extract total (engineer ruling 2026-09-05). The apartment's fresh air still counts in full.

Kitchen exhaust minimums are enforced per mode on the ACH-derived value for any apartment WITH a kitchen (kitchen area > 0): 25 L/s (50 CFM) continuous (engineering floor — 62.2-2025 Table 5-2 sets 5 ACH with no numeric floor), 50 L/s (100 CFM) non-continuous (62.2-2025 Table 5-1, vented range hood). A kitchen area of 0 means the apartment has no kitchen: kitchen exhaust = 0, no minimum applied, in both modes. A typed kitchen-exhaust value below the mode minimum is raised to it in BOTH modes: 25 L/s (50 CFM) continuous, 50 L/s (100 CFM) non-continuous (engineer ruling 2026-08-24).

Bathroom rates: where the apartment's '62.2 printed rate' option is selected, the printed ASHRAE 62.2-2025 value for the mode is used — Table 5-1 (non-continuous / demand-controlled local exhaust) 50 cfm (25 L/s), Table 5-2 (continuous local exhaust) 20 cfm (10 L/s); otherwise the engineer's typed rate.

Dwelling-unit fresh air is floored at the smallest printed cell of ASHRAE 62.2-2025 Table 4-1b, 14 L/s (<47 m2, 1 bedroom), and of Table 4-1a, 30 CFM (<500 ft2, 1 bedroom). IBC 2018 # 1202.1: natural ventilation per # 1202.5 or mechanical ventilation per the IMC; a dwelling unit whose tested air infiltration rate is less than 5 air changes per hour at 50 Pa shall be mechanically ventilated per IMC # 403. IBC prints no per-dwelling airflow.

ACH-driven spaces convert air changes to a primary stream (Volume*ACH/3.6 [L/s]); the balance% then sets the opposite (supply or extract) stream to achieve the intended room pressure.

Extract routed to a dedicated fan is excluded from the FAHU extract totals (the fan performs that duty). Where the routed extract belongs to an attached room of a Standard-mode space, its makeup air reaches the room as transfer air through the parent space and is already included in that space's fresh air — ASHRAE 62.1-2022 # 6.5 permits exhaust makeup air to be any combination of outdoor air, recirculated air, or transfer air. Extract Only spaces receive no FAHU makeup by definition (their makeup is provided outside the FAHU system, e.g. louvres or adjacent areas).

Fans flagged INTERMITTENT (on-demand operation — timers, sensors) are excluded from every floor and building pressure figure, and their served extract takes no FAHU makeup: the space balance is computed as if that extract did not exist, so its fresh air can fall back to the Table 6-1 breathing-zone minimum. Makeup while the fan runs is transfer air (ASHRAE 62.1-2022 # 6.5 permits exhaust makeup air to be any combination of outdoor air, recirculated air, or transfer air); providing an adequate transfer path is a design responsibility outside this calculation. The fan is still sized for the full routed extract.

Standard-space (62.1) figures are computed from the printed values of the report's unit system (I-P: Table 6-1 cfm rates on the area in ft2, Table 6-2 cfm rates, fixture cfm; SI: the L/s rates) and rounded up in that system; engineer-entered values (overrides, the ACH method, direct entries, custom fixtures) are stored in SI and converted at the report boundary. The 62.2 dwelling formulas are evaluated natively in each unit system, using the standard's dual printed equations, and every 62.2 rate is carried as its printed SI / I-P PAIR - an I-P report prints the printed cfm values (100 / 50 / 20 cfm; 62.2 Tables 5-1 and 5-2), never a re-converted SI figure; the record stores SI and the SI result is unchanged by the display choice.

Default occupant densities (editable AHJ values): the automatic people count of a Standard space is density x area, rounded up; a people count typed by the engineer is used as typed.

AHJ basis: Occupant density, Office Space 5 #/100 m2 (default)

AHJ basis: Occupant density, Conference / Meeting 50 #/100 m2 (default)

AHJ basis: Occupant density, Reception Areas 30 #/100 m2 (default)

AHJ basis: Occupant density, Break Rooms 50 #/100 m2 (default)

AHJ basis: Occupant density, Corridors (Office) 0 #/100 m2 (default)

# 3.  Spaces — ASHRAE 62.1-2022

Open Plan Office

| Parameter | Value |
| --- | --- |
| Mode | Standard |
| Type | Office Space |
| Area | 820 m² |
| People | 41 |
| Balance % | 10% |
| Uplift over Vbz | 0% |
| Fresh Air | 349 L/s |
| Extract | 315 L/s (280 in attached spaces + 35 local) |

Attached extract spaces — served by transfer air from Open Plan Office

| Attached Space | Qty | Extract (L/s) | How calculated | Air Source | Extract Via |
| --- | --- | --- | --- | --- | --- |
| Male / Female WCs | 10 | 250.0 | Per-fixture (Table 6-2) = 25 L/s; × Qty 10 = 250.0 L/s | Transfer from Open Plan Office | FAHU |
| Janitor Closet | 1 | 30.0 | Area-based (Table 6-2): 6 m² × 5 L/s/m² = 30.0 L/s | Transfer from Open Plan Office | FAHU |
| Open Plan Office (local extract) |  | 35 | Pressure-balance remainder (fresh × (1 − bal%)) | Exhausted in main space | FAHU |
| TOTAL |  | 315 |  |  |  |

Step 1: Open Plan Office — transfer-air supply

Formula: Vf = max(Vbz, ΣVe,att × (1 + bal%)); Ve = max(ΣVe,att, Vf × (1 − bal%))

Substitution: ΣVe,att = 280 L/s; 280 × (1 + 0.10) = 308.0; Vbz = 349 L/s (Table 6-1, Office Space); Ve = max(280, 349 × 0.90) = 315

Result: Fresh 349 L/s, Extract 315 L/s

Note: All supply enters the main space; the attached rooms draw their extract via transfer air (door undercut / grille). The balance% surplus keeps the main space positively pressurised. The pressure balance requires more extract than the attached rooms take, so 35 L/s is exhausted from the main space itself.

Meeting Room

| Parameter | Value |
| --- | --- |
| Mode | Standard |
| Type | Conference / Meeting |
| Area | 45 m² |
| People | 23 |
| Balance % | 10% |
| Uplift over Vbz | 0% |
| Fresh Air | 71 L/s |
| Extract | 64 L/s |

Step 2: Meeting Room — breathing-zone outdoor air

Formula: Vbz = Rp*Pz + Ra*Az (ASHRAE 62.1 Table 6-1)

Substitution: People Pz = 23, Area Az = 45 m²; Rp/Ra per Table 6-1; Vbz = 71 L/s (Table 6-1, Conference / Meeting)

Result: Fresh 71 L/s, Extract 64 L/s

Note: The issued fresh air is Vbz (Eq 6-1); Ez = 1.0 is assumed for Table 6-4 'ceiling supply of cool air'. For another Table 6-4 configuration Voz = Vbz / Ez (Eq 6-2), and Addendum j multiplies by Eρ (Table 6-5) - neither is applied here.

Floor Reception

| Parameter | Value |
| --- | --- |
| Mode | Standard |
| Type | Reception Areas |
| Area | 40 m² |
| People | 12 |
| Balance % | 10% |
| Uplift over Vbz | 0% |
| Fresh Air | 42 L/s |
| Extract | 38 L/s |

Step 3: Floor Reception — breathing-zone outdoor air

Formula: Vbz = Rp*Pz + Ra*Az (ASHRAE 62.1 Table 6-1)

Substitution: People Pz = 12, Area Az = 40 m²; Rp/Ra per Table 6-1; Vbz = 42 L/s (Table 6-1, Reception Areas)

Result: Fresh 42 L/s, Extract 38 L/s

Note: The issued fresh air is Vbz (Eq 6-1); Ez = 1.0 is assumed for Table 6-4 'ceiling supply of cool air'. For another Table 6-4 configuration Voz = Vbz / Ez (Eq 6-2), and Addendum j multiplies by Eρ (Table 6-5) - neither is applied here.

Pantry / Break Room

| Parameter | Value |
| --- | --- |
| Mode | Standard |
| Type | Break Rooms |
| Area | 30 m² |
| People | 15 |
| Balance % | 10% |
| Uplift over Vbz | 0% |
| Fresh Air | 56 L/s |
| Extract | 51 L/s (45 in attached spaces + 6 local) |

Attached extract spaces — served by transfer air from Pantry / Break Room

| Attached Space | Qty | Extract (L/s) | How calculated | Air Source | Extract Via |
| --- | --- | --- | --- | --- | --- |
| Pantry Extract | 1 | 45.0 | Area-based (Table 6-2): 30 m² × 1.5 L/s/m² = 45.0 L/s | Transfer from Pantry / Break Room | FAHU |
| Pantry / Break Room (local extract) |  | 6 | Pressure-balance remainder (fresh × (1 − bal%)) | Exhausted in main space | FAHU |
| TOTAL |  | 51 |  |  |  |

Step 4: Pantry / Break Room — transfer-air supply

Formula: Vf = max(Vbz, ΣVe,att × (1 + bal%)); Ve = max(ΣVe,att, Vf × (1 − bal%))

Substitution: ΣVe,att = 45 L/s; 45 × (1 + 0.10) = 49.5; Vbz = 56 L/s (Table 6-1, Break Rooms); Ve = max(45, 56 × 0.90) = 51

Result: Fresh 56 L/s, Extract 51 L/s

Note: All supply enters the main space; the attached rooms draw their extract via transfer air (door undercut / grille). The balance% surplus keeps the main space positively pressurised. The pressure balance requires more extract than the attached rooms take, so 6 L/s is exhausted from the main space itself.

Lift Lobby / Corridor

| Parameter | Value |
| --- | --- |
| Mode | Standard |
| Type | Corridors (Office) |
| Area | 110 m² |
| People | 0 |
| Balance % | 10% |
| Uplift over Vbz | 0% |
| Fresh Air | 33 L/s |
| Extract | 30 L/s |

Step 5: Lift Lobby / Corridor — breathing-zone outdoor air

Formula: Vbz = Rp*Pz + Ra*Az (ASHRAE 62.1 Table 6-1)

Substitution: People Pz = 0, Area Az = 110 m²; Rp/Ra per Table 6-1; Vbz = 33 L/s (Table 6-1, Corridors (Office))

Result: Fresh 33 L/s, Extract 30 L/s

Note: The issued fresh air is Vbz (Eq 6-1); Ez = 1.0 is assumed for Table 6-4 'ceiling supply of cool air'. For another Table 6-4 configuration Voz = Vbz / Ez (Eq 6-2), and Addendum j multiplies by Eρ (Table 6-5) - neither is applied here.

# 4.  Floors

| Floor | Fresh (L/s) | Extract (L/s) | To Fans (L/s) | Intermittent — excl. (L/s) | Net (L/s) |
| --- | --- | --- | --- | --- | --- |
| Typical Office Floor | 622 | 562 | — | — | +60 |

Typical Office Floor — Breakdown

| Item | Fresh (L/s) | Extract (L/s) |
| --- | --- | --- |
| Open Plan Office×1 | 349 | 315 |
| Meeting Room×2 | 142 | 128 |
| Floor Reception×1 | 42 | 38 |
| Pantry / Break Room×1 | 56 | 51 |
| Lift Lobby / Corridor×1 | 33 | 30 |
| TOTAL | 622 | 562 |

# 5.  FAHU

FAHU-01

| Parameter | Value |
| --- | --- |
| Total Fresh (L/s) | 6220 |
| Total Extract (L/s) | 5620 |

| Served Floor | Qty | Fresh (L/s) | Extract (L/s) |
| --- | --- | --- | --- |
| Typical Office Floor | 10 | 6220 | 5620 |

| Parameter | Value |
| --- | --- |
| Preliminary unit type | Single recovery wheel + heat pipes |
| Indicative envelope L x W x H | 5638 x 2650 x 3600 mm |
| Selection basis | Envelope selected on the SI total 6,220 L/s (TAH-150 band, 7,252 L/s) |
| Operating weight (per unit) | 3,250 kg |
| Foundation (concrete plinth) | 5838 x 2850 x 200 mm high (unit + 100 mm all around) |
| Basis | Reference supplier selection envelope |

⚠ Advisory

• FAHU envelope is preliminary — for space planning only; obtain the actual manufacturer selection as the design progresses.

# R.  Reference Standards

ASHRAE 62.1-2022 — Ventilation for Acceptable Indoor Air Quality — Table 6-1 (minimum rates), Table 6-2 (exhaust rates).

ASHRAE 62.2-2025 — Ventilation and Acceptable IAQ in Residential Buildings — # 4.1 (not less than # 4.1.1 through # 4.1.4; # 4.1.3 occupant adder applied where entered; # 4.1.2 / # 4.1.4 credits not taken) and # 4.1.1 (Tables 4-1a/4-1b): total ventilation rate Qtot = 0.15*A + 3.5*(Nbr+1) L/s (Eq. 4-1b, SI) [0.03*A + 7.5*(Nbr+1) CFM (Eq. 4-1a, I-P)]; Nbr not to be less than 1; # 4.1.3 + 3.5 L/s (7.5 cfm) for each additional person; Table 5-1 demand-controlled and Table 5-2 continuous local exhaust rates, printed SI / I-P pairs.

IMC 2021 # Table 403.3.1.1 — Public-bathroom fixture exhaust rates — per water closet / urinal (note e) and per shower head (intermittent operation).

IBC 2018 # 1202.1 — Natural ventilation per # 1202.5 or mechanical ventilation per the IMC; a dwelling unit whose tested air infiltration rate is less than 5 air changes per hour (blower door at 50 Pa, IECC R402.4.1.2) shall be ventilated by mechanical means per IMC # 403. IBC prints no per-dwelling airflow; the per-dwelling floor applied by this tool - 14 L/s (30 CFM) - is the smallest printed cell of ASHRAE 62.2-2025 Table 4-1b (Table 4-1a).

Reference FAHU selections — TROSTEN TAH catalogue (TAH-008 to TAH-450 TFM), 373-21,378 L/s — INDICATIVE.

Engineer of record: Hussein Ragab

Created by Hussein Ragab