## Summary
Ventilation Calculation — Summary
Fresh Air (Ventilation) Calculator — ASHRAE 62.1-2022 / ASHRAE 62.2-2025
Project: | Marina Commercial Tower
Project No.: | MCT-2026-MEP-001
Client: | -
Date: | 2026-10-20
Prepared by: | Hussein Ragab
Checked by: | -
Revision: | P2
Apartment types | 0
Spaces | 5
Floors | 1
FAHU units | 1
Extract fans | 0
Building Fresh (L/s) | 6220
Building Extract (L/s) | 5620
Building Net (L/s) | 600
Override disclosure | every override flagged
Reference | Application
ASHRAE 62.1-2022 | Space ventilation — Tables 6-1 / 6-2 (Vbz, exhaust)
ASHRAE 62.2-2025 | Dwelling ventilation — # 4.1 / # 4.1.1 Eq 4-1a/4-1b (Qtot floor), Tables 5-1/5-2 printed pairs
IMC 2021 | Table 403.3.1.1 per-fixture exhaust (corroborating)
IBC 2018 | Section 1202.1 — natural ventilation per 1202.5 or mechanical per the IMC; a dwelling unit tested below 5 air changes per hour at 50 Pa is ventilated mechanically per IMC Section 403. No per-dwelling airflow printed
TROSTEN TAH catalogue | Indicative FAHU envelopes — reference selections only

## Apartments
Apartments — ASHRAE 62.2-2025
Fresh Air (Ventilation) Calculator — ASHRAE 62.1-2022 / ASHRAE 62.2-2025
Project: Marina Commercial Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: - ¦ By: Hussein Ragab ¦ Chkd: - ¦ Rev: P2 ¦ Date: 2026-10-20
Calculated in SI units - the project's saved unit system; computed from the standards' printed SI values, which differ slightly from an I-P calculation - values in SI units, airflow in L/s, area in m². Inputs and results only (step-by-step derivations are in the Word report).
Name | Mode | Area (m²) | Bedrooms | Extra Occupants | Qtot (L/s) | Kitchen (L/s) | Kitchen Basis | Baths | Bath Rate (L/s) | Bath Basis | Bath Total (L/s) | Laundry | Laundry Rate (L/s) | Laundry Basis | Laundry Total (L/s) | Total Extract (L/s) | Fresh (L/s) | Method | Override
Qtot basis - ASHRAE 62.2-2025 # 4.1.1 Eq 4-1b: Qtot = 0.15 x Afloor + 3.5 x (Nbr + 1) [L/s; Afloor in m2; Nbr = bedrooms, not less than 1], + 3.5 x each additional occupant entered (# 4.1.3). Rounded to the nearest whole L/s as Tables 4-1a / 4-1b print. Floor 14 L/s per dwelling = the smallest printed cell of ASHRAE 62.2-2025 Table 4-1b (<47 m2, 1 bedroom: 14 L/s) / Table 4-1a (<500 ft2, 1 bedroom: 30 cfm), pdf p.8 / printed p.6.

## Spaces
Spaces — ASHRAE 62.1-2022
Fresh Air (Ventilation) Calculator — ASHRAE 62.1-2022 / ASHRAE 62.2-2025
Project: Marina Commercial Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: - ¦ By: Hussein Ragab ¦ Chkd: - ¦ Rev: P2 ¦ Date: 2026-10-20
Calculated in SI units - the project's saved unit system; computed from the standards' printed SI values, which differ slightly from an I-P calculation - values in SI units, airflow in L/s, area in m². Inputs and results only (step-by-step derivations are in the Word report).
Name | Basis | Type | Area (m²) | People | Rp (L/s/person) | Ra (L/s/m²) | Rp x Pz (L/s) | Ra x Az (L/s) | Qty | Rate (L/s) | ACH | Balance % | Uplift % | Fresh (L/s) | Extract (L/s) | Rate Reference | Extract To | Override
Open Plan Office | Standard | Office Space | 820 | 41 | 2.5 | 0.3 | 102.5 | 246 | — | — | — | 10 | 0 | 349 | 315 | ASHRAE 62.1-2022 Table 6-1, Eq 6-1 | FAHU
└ Male / Female WCs | attached | Toilets—public (Continuous) | — | — | — | — | — | — | 10 | 25 | — | — | — | — | 250 | ASHRAE 62.1-2022 Table 6-2 | FAHU
└ Janitor Closet | attached | Janitor closets, trash rooms, recycling | 6 | — | — | — | — | — | 1 | 30 | — | — | — | — | 30 | ASHRAE 62.1-2022 Table 6-2 | FAHU
Meeting Room | Standard | Conference / Meeting | 45 | 23 | 2.5 | 0.3 | 57.5 | 13.5 | — | — | — | 10 | 0 | 71 | 64 | ASHRAE 62.1-2022 Table 6-1, Eq 6-1 | FAHU
Floor Reception | Standard | Reception Areas | 40 | 12 | 2.5 | 0.3 | 30 | 12 | — | — | — | 10 | 0 | 42 | 38 | ASHRAE 62.1-2022 Table 6-1, Eq 6-1 | FAHU
Pantry / Break Room | Standard | Break Rooms | 30 | 15 | 2.5 | 0.6 | 37.5 | 18 | — | — | — | 10 | 0 | 56 | 51 | ASHRAE 62.1-2022 Table 6-1, Eq 6-1 | FAHU
└ Pantry Extract | attached | Kitchenettes | 30 | — | — | — | — | — | 1 | 45 | — | — | — | — | 45 | ASHRAE 62.1-2022 Table 6-2 | FAHU
Lift Lobby / Corridor | Standard | Corridors (Office) | 110 | 0 | 0 | 0.3 | 0 | 33 | — | — | — | 10 | 0 | 33 | 30 | ASHRAE 62.1-2022 Table 6-1, Eq 6-1 | FAHU
Default occupant densities (editable AHJ values): the automatic people count is density x area, rounded up; a typed people count is used as typed.
AHJ basis: Occupant density, Office Space 5 #/100 m2 (default)
AHJ basis: Occupant density, Conference / Meeting 50 #/100 m2 (default)
AHJ basis: Occupant density, Reception Areas 30 #/100 m2 (default)
AHJ basis: Occupant density, Break Rooms 50 #/100 m2 (default)
AHJ basis: Occupant density, Corridors (Office) 0 #/100 m2 (default)

## Floors
Floors
Fresh Air (Ventilation) Calculator — ASHRAE 62.1-2022 / ASHRAE 62.2-2025
Project: Marina Commercial Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: - ¦ By: Hussein Ragab ¦ Chkd: - ¦ Rev: P2 ¦ Date: 2026-10-20
Calculated in SI units - the project's saved unit system; computed from the standards' printed SI values, which differ slightly from an I-P calculation - values in SI units, airflow in L/s, area in m². Inputs and results only (step-by-step derivations are in the Word report).
Floor / Item | Kind | Qty | Fresh ea (L/s) | Extract ea (L/s) | Fresh (L/s) | Extract (L/s) | To Fans (L/s) | Intermittent — excl. (L/s) | Net (L/s) | Pressure
Typical Office Floor | floor | — | — | — | 622 | 562 | — | — | 60 | OK
└ Open Plan Office | space | 1 | 349 | 315 | 349 | 315 | — | — | —
└ Meeting Room | space | 2 | 71 | 64 | 142 | 128 | — | — | —
└ Floor Reception | space | 1 | 42 | 38 | 42 | 38 | — | — | —
└ Pantry / Break Room | space | 1 | 56 | 51 | 56 | 51 | — | — | —
└ Lift Lobby / Corridor | space | 1 | 33 | 30 | 33 | 30 | — | — | —

## FAHU
FAHU — preliminary sizing
Fresh Air (Ventilation) Calculator — ASHRAE 62.1-2022 / ASHRAE 62.2-2025
Project: Marina Commercial Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: - ¦ By: Hussein Ragab ¦ Chkd: - ¦ Rev: P2 ¦ Date: 2026-10-20
Calculated in SI units - the project's saved unit system; computed from the standards' printed SI values, which differ slightly from an I-P calculation - values in SI units, airflow in L/s, area in m². Inputs and results only (step-by-step derivations are in the Word report).
FAHU / Floor | Recovery | Qty | Fresh (L/s) | Extract (L/s) | Intermittent — excl. (L/s) | Selection basis (L/s) | Units | Envelope L (mm) | Envelope W (mm) | Envelope H (mm) | Weight (kg)
FAHU-01 | Single recovery wheel + heat pipes | — | 6220 | 5620 | — | 6220 | 1 | 5638 | 2650 | 3600 | 3250
└ Typical Office Floor |  | 10 | 6220 | 5620 | — | — | — | — | — | — | —
FAHU-01: Envelope selected on the SI total 6,220 L/s (TAH-150 band, 7,252 L/s)
FAHU envelopes are PRELIMINARY reference-supplier selections for space planning only — obtain actual manufacturer selections as the design progresses.

## Fans
Dedicated Extract Fans
Fresh Air (Ventilation) Calculator — ASHRAE 62.1-2022 / ASHRAE 62.2-2025
Project: Marina Commercial Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: - ¦ By: Hussein Ragab ¦ Chkd: - ¦ Rev: P2 ¦ Date: 2026-10-20
Calculated in SI units - the project's saved unit system; computed from the standards' printed SI values, which differ slightly from an I-P calculation - values in SI units, airflow in L/s, area in m². Inputs and results only (step-by-step derivations are in the Word report).
Fan / Served extract | Space | Operation | Unit Extract (L/s) | Qty | Auto Qty | Total (L/s) | Notes
Fan-routed extract is EXCLUDED from the FAHU extract totals. CONTINUOUS fans count in the floor/building pressure balance; for Standard-mode spaces their makeup air reaches the served room as transfer air through its parent space and is already included in that space's fresh air (ASHRAE 62.1-2022 # 6.5: exhaust makeup air is permitted to be any combination of outdoor air, recirculated air, or transfer air). INTERMITTENT fans are excluded from the pressure balance and take no FAHU makeup — the space is balanced as if the routed extract did not exist, and makeup is transfer air drawn only while the fan runs. Extract Only spaces receive no FAHU makeup by definition.