## OVERALL
CALCULATED LOADS | [20 empty] | SELECTED EQUIPMENT
Unit Reference | Zone | Area Served | AREA |  |  | Total Cooling Load |  | Sensible Load |  |  | Total Heating Load |  | On coil temperature (DB/WB) |  | Off coil temperature (DB/WB) |  | Air Flow Rate |  |  | Cooling Load Density | Selected Qty |  | Selected Total Cooling (each) |  | Selected Sensible (each) |  | Selected Air Flow (each) |  | Selected Indoor Power (each) |  | Within Tolerance |  | Total Dev % |  | Sensible Dev % |  | Flow Dev %
|  |  | Each Space ft² | Each Zone ft² | Total ft² | Each Zone MBH | Total MBH | Each Space MBH | Each Zone MBH | Total MBH | Each Zone MBH | Total MBH | Each Zone Deg.F. | Total Deg.F. | Each Zone Deg.F. | Total Deg.F. | Air flow rate CFM | Zone flow rate CFM | Total air flow rate CFM | (BTU/h·ft²) | Each Zone | Total | Each Zone (each) MBH | Total MBH | Each Zone (each) MBH | Total MBH | Each Zone (each) CFM | Total CFM | Each Zone (each) kW | Total kW | Each Zone | Total | Each Zone | Total | Each Zone | Total | Each Zone | Total
CHWAHUs-CAV-2-DeckMultiZone | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.8 | 31.4 | 31.4 | 149.1 | 0 | 14.1 | N/A | 76.4 / 63.8 | N/A | 55.8 / 54.6 | 1454 | 1454 | 7097 | 45.4 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.2%) | N/A | +11.6% | N/A | +16.2% | N/A | +26.8%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
CHWAHUs-CAV-3-DeckMultizone | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.8 | 31.4 | 31.4 | 149.1 | 0 | 14.1 | N/A | 76.4 / 63.8 | N/A | 55.8 / 54.6 | 1454 | 1454 | 7097 | 45.4 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.2%) | N/A | +11.6% | N/A | +16.2% | N/A | +26.8%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
CHWAHUs-CAV-DualDuact | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.8 | 31.4 | 31.4 | 149.1 | 0 | 14.1 | N/A | 76.4 / 63.8 | N/A | 55.8 / 54.6 | 1454 | 1454 | 7097 | 45.4 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.2%) | N/A | +11.6% | N/A | +16.2% | N/A | +26.8%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
CHWAHUs-CAV-Make-upAirDOAS | Zone 1 | B-IRRIGATION ROOM | 150.7 | 4342.2 | 4342.2 | N/A | N/A | 3.5 | 160.8 | 160.8 | N/A | N/A | N/A | N/A | N/A | N/A | 0 |  | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | B-PUMP ROOM | 183 |  |  |  |  | 3.2 | [8 empty] | 0
|  | B-SWIM P PUMP ROOM | 402.6 |  |  |  |  | 8.7 | [8 empty] | 0
|  | G-BACK KITCHEN | 161.5 |  |  |  |  | 12.4 | [8 empty] | 0
|  | G-CAFE HALL | 807.3 |  |  |  |  | 31.9 | [8 empty] | 0
|  | G-ELECTRICAL ROOM | 64.6 |  |  |  |  | 11.3 | [8 empty] | 0
|  | G-GYM | 861.1 |  |  |  |  | 31.4 | [8 empty] | 0
|  | G-HALL | 818.1 |  |  |  |  | 25.3 | [8 empty] | 0
|  | G-ICT | 75.3 |  |  |  |  | 9.4 | [8 empty] | 0
|  | G-SECURITY ROOM | 53.8 |  |  |  |  | 2.4 | [8 empty] | 0
|  | G-TOILET | 247.6 |  |  |  |  | 6 | [8 empty] | 0
|  | G-WASTE ROOM | 32.3 |  |  |  |  | 0.8 | [8 empty] | 0
|  | G-YOGA | 484.4 |  |  |  |  | 15.5 | [8 empty] | 0
CHWAHUs-CAV-SingleZone | Zone 1 | B-IRRIGATION ROOM | 150.7 | 4342.2 | 4342.2 | N/A | 185.3 | 3.5 | 160.8 | 156.3 | 0 | 10.6 | N/A | 76.6 / 65.9 | N/A | 60.2 / 59.1 | 190 | 8825 | 8825 | 42.7 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+10.8%) | N/A | +7.7% | N/A | +10.8% | N/A | +2%
|  | B-PUMP ROOM | 183 |  |  |  |  | 3.2 | [8 empty] | 177
|  | B-SWIM P PUMP ROOM | 402.6 |  |  |  |  | 8.7 | [8 empty] | 475
|  | G-BACK KITCHEN | 161.5 |  |  |  |  | 12.4 | [8 empty] | 675
|  | G-CAFE HALL | 807.3 |  |  |  |  | 31.9 | [8 empty] | 1741
|  | G-ELECTRICAL ROOM | 64.6 |  |  |  |  | 11.3 | [8 empty] | 613
|  | G-GYM | 861.1 |  |  |  |  | 31.4 | [8 empty] | 1711
|  | G-HALL | 818.1 |  |  |  |  | 25.3 | [8 empty] | 1376
|  | G-ICT | 75.3 |  |  |  |  | 9.4 | [8 empty] | 515
|  | G-SECURITY ROOM | 53.8 |  |  |  |  | 2.4 | [8 empty] | 133
|  | G-TOILET | 247.6 |  |  |  |  | 6 | [8 empty] | 330
|  | G-WASTE ROOM | 32.3 |  |  |  |  | 0.8 | [8 empty] | 44
|  | G-YOGA | 484.4 |  |  |  |  | 15.5 | [8 empty] | 845
CHWAHUs-CAV-TerminalReheat | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 176 | 31.4 | 31.4 | 146.5 | 62.8 |  | N/A | 74.9 / 63.3 | N/A | 55.8 / 54.7 | 1454 | 1454 | 7097 | 44.7 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+18.2%) | N/A | +13.4% | N/A | +18.2% | N/A | +26.8%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 31 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 50.5 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 12.1 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 24.8 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 63.9 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 22.5 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 18.9 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 6.5 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 7 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 4.9 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 1.6 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
CHWAHUs-VAV | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.7 | 31.4 | 31.4 | 149 | 6.2 |  | N/A | 76.4 / 63.8 | N/A | 55.8 / 54.6 | 1454 | 1454 | 7046 | 45.4 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.2%) | N/A | +11.6% | N/A | +16.2% | N/A | +27.7%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 3.6 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 5.3 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0.9 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0.2 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 6.4 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0.2 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0.1 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0.2 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0.1 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
CHWAHUs-VAV-1-FanDualDuct | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.8 | 31.4 | 31.4 | 149.1 | 0 | 14.1 | N/A | 76.4 / 63.8 | N/A | 55.8 / 54.6 | 1454 | 1454 | 7046 | 45.4 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.2%) | N/A | +11.6% | N/A | +16.2% | N/A | +27.7%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
CHWAHUs-VAV-2-FanDualDuct | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.5 | 31.4 | 31.4 | 149.1 | 0 | 4.7 | N/A | 76.4 / 63.8 | N/A | 55.8 / 54.6 | 1454 | 1454 | 7046 | 45.3 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.2%) | N/A | +11.8% | N/A | +16.2% | N/A | +27.7%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
CHWAHUs-VVT | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.2 | 31.4 | 31.4 | 149.2 | 0 | 14.7 | N/A | 76.3 / 64.8 | N/A | 58.0 / 56.9 | 1711 | 1711 | 8289 | 45.2 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.1%) | N/A | +12% | N/A | +16.1% | N/A | +8.6%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 845 | 845 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1376 | 1376 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 330 | 330 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 675 | 675 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1741 | 1741 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 613 | 613 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 515 | 515 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 177 | 177 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 190 | 190 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 133 | 133 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 44 | 44 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
PackagedRooftopUnits-CAV-2-DeckM | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 185.7 | 31.4 | 31.4 | 155.9 | 0 | 80.6 | N/A | 76.4 / 63.4 | N/A | 55.0 / 53.8 | 1454 | 1454 | 7097 | 47.1 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+11.1%) | N/A | +7.4% | N/A | +11.1% | N/A | +26.8%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
PackagedRooftopUnits-CAV-3-DeckM | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 179 | 31.4 | 31.4 | 149.1 | 0 | 14.6 | N/A | 76.4 / 63.4 | N/A | 55.0 / 53.8 | 1454 | 1454 | 7097 | 45.4 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.2%) | N/A | +11.5% | N/A | +16.2% | N/A | +26.8%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
PackagedRooftopUnits-CAV-DualDuc | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 185.7 | 31.4 | 31.4 | 155.9 | 0 | 80.6 | N/A | 76.4 / 63.4 | N/A | 55.0 / 53.8 | 1454 | 1454 | 7097 | 47.1 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+11.1%) | N/A | +7.4% | N/A | +11.1% | N/A | +26.8%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
PackagedRooftopUnits-CAV-Make-up | Zone 1 | B-IRRIGATION ROOM | 150.7 | 4342.2 | 4342.2 | N/A | N/A | 3.5 | 160.8 | 160.8 | N/A | N/A | N/A | N/A | N/A | N/A | 0 |  | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | B-PUMP ROOM | 183 |  |  |  |  | 3.2 | [8 empty] | 0
|  | B-SWIM P PUMP ROOM | 402.6 |  |  |  |  | 8.7 | [8 empty] | 0
|  | G-BACK KITCHEN | 161.5 |  |  |  |  | 12.4 | [8 empty] | 0
|  | G-CAFE HALL | 807.3 |  |  |  |  | 31.9 | [8 empty] | 0
|  | G-ELECTRICAL ROOM | 64.6 |  |  |  |  | 11.3 | [8 empty] | 0
|  | G-GYM | 861.1 |  |  |  |  | 31.4 | [8 empty] | 0
|  | G-HALL | 818.1 |  |  |  |  | 25.3 | [8 empty] | 0
|  | G-ICT | 75.3 |  |  |  |  | 9.4 | [8 empty] | 0
|  | G-SECURITY ROOM | 53.8 |  |  |  |  | 2.4 | [8 empty] | 0
|  | G-TOILET | 247.6 |  |  |  |  | 6 | [8 empty] | 0
|  | G-WASTE ROOM | 32.3 |  |  |  |  | 0.8 | [8 empty] | 0
|  | G-YOGA | 484.4 |  |  |  |  | 15.5 | [8 empty] | 0
PackagedRooftopUnits-CAV-Termina | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 175.4 | 31.4 | 31.4 | 145.6 | 62.8 |  | N/A | 74.0 / 62.6 | N/A | 55.0 / 53.9 | 1454 | 1454 | 7097 | 44.5 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+19.0%) | N/A | +13.7% | N/A | +19% | N/A | +26.8%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 31 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 50.5 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 12.1 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 24.8 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 63.9 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 22.5 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 18.9 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 6.5 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 7 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 4.9 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 1.6 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
PackagedRooftopUnits-VAV | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.9 | 31.4 | 31.4 | 149.1 | 6.2 |  | N/A | 76.3 / 63.4 | N/A | 55.0 / 53.8 | 1454 | 1454 | 7046 | 45.4 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.2%) | N/A | +11.5% | N/A | +16.2% | N/A | +27.7%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 3.6 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 5.3 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0.9 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0.2 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 6.4 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0.2 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0.1 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0.2 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0.1 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
PackagedRooftopUnits-VAV-1-FanDu | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 179 | 31.4 | 31.4 | 149.1 | 0 | 15.5 | N/A | 76.4 / 63.4 | N/A | 55.0 / 53.8 | 1454 | 1454 | 7046 | 45.4 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.2%) | N/A | +11.5% | N/A | +16.2% | N/A | +27.7%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
PackagedRooftopUnits-VAV-2-FanDu | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.8 | 31.4 | 31.4 | 149.1 | 0 | 14.6 | N/A | 76.4 / 63.4 | N/A | 55.0 / 53.8 | 1454 | 1454 | 7046 | 45.4 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.2%) | N/A | +11.6% | N/A | +16.2% | N/A | +27.7%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
PackagedRooftopUnits-VVT | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.2 | 31.4 | 31.4 | 149.2 | 0 | 14.7 | N/A | 76.3 / 64.8 | N/A | 58.0 / 56.9 | 1711 | 1711 | 8289 | 45.2 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.1%) | N/A | +12% | N/A | +16.1% | N/A | +8.6%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 845 | 845 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1376 | 1376 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 330 | 330 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 675 | 675 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1741 | 1741 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 613 | 613 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 515 | 515 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 177 | 177 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 190 | 190 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 133 | 133 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 44 | 44 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
PackagedVerticalUnits-CAV-Single | Zone 1 | B-IRRIGATION ROOM | 150.7 | 4342.2 | 4342.2 | N/A | 185.3 | 3.5 | 160.8 | 156.3 | 0 | 10.6 | N/A | 76.6 / 65.9 | N/A | 60.2 / 59.1 | 190 | 8825 | 8825 | 42.7 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+10.8%) | N/A | +7.7% | N/A | +10.8% | N/A | +2%
|  | B-PUMP ROOM | 183 |  |  |  |  | 3.2 | [8 empty] | 177
|  | B-SWIM P PUMP ROOM | 402.6 |  |  |  |  | 8.7 | [8 empty] | 475
|  | G-BACK KITCHEN | 161.5 |  |  |  |  | 12.4 | [8 empty] | 675
|  | G-CAFE HALL | 807.3 |  |  |  |  | 31.9 | [8 empty] | 1741
|  | G-ELECTRICAL ROOM | 64.6 |  |  |  |  | 11.3 | [8 empty] | 613
|  | G-GYM | 861.1 |  |  |  |  | 31.4 | [8 empty] | 1711
|  | G-HALL | 818.1 |  |  |  |  | 25.3 | [8 empty] | 1376
|  | G-ICT | 75.3 |  |  |  |  | 9.4 | [8 empty] | 515
|  | G-SECURITY ROOM | 53.8 |  |  |  |  | 2.4 | [8 empty] | 133
|  | G-TOILET | 247.6 |  |  |  |  | 6 | [8 empty] | 330
|  | G-WASTE ROOM | 32.3 |  |  |  |  | 0.8 | [8 empty] | 44
|  | G-YOGA | 484.4 |  |  |  |  | 15.5 | [8 empty] | 845
PackagedVerticalUnits-CAV-Termin | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 176 | 31.4 | 31.4 | 146.5 | 62.8 |  | N/A | 74.9 / 63.3 | N/A | 55.8 / 54.7 | 1454 | 1454 | 7097 | 44.7 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+18.2%) | N/A | +13.4% | N/A | +18.2% | N/A | +26.8%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 31 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 50.5 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 12.1 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 24.8 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 63.9 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 22.5 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 18.9 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 6.5 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 7 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 4.9 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 1.6 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
PackagedVerticalUnits-VAV | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.9 | 31.4 | 31.4 | 149.1 | 6.2 |  | N/A | 76.3 / 63.4 | N/A | 55.0 / 53.8 | 1454 | 1454 | 7046 | 45.4 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.2%) | N/A | +11.5% | N/A | +16.2% | N/A | +27.7%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 3.6 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 5.3 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0.9 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0.2 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 6.4 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0.2 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0.1 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0.2 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0.1 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
PackagedVerticalUnits-VVT | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.2 | 31.4 | 31.4 | 149.2 | 0 | 14.7 | N/A | 76.3 / 64.8 | N/A | 58.0 / 56.9 | 1711 | 1711 | 8289 | 45.2 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.1%) | N/A | +12% | N/A | +16.1% | N/A | +8.6%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 845 | 845 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1376 | 1376 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 330 | 330 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 675 | 675 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1741 | 1741 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 613 | 613 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 515 | 515 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 177 | 177 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 190 | 190 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 133 | 133 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 44 | 44 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
SplitAHUs-CAV-2-DeckMultiZone | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.8 | 31.4 | 31.4 | 149.1 | 0 | 14.1 | N/A | 76.4 / 63.8 | N/A | 55.8 / 54.6 | 1454 | 1454 | 7097 | 45.4 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.2%) | N/A | +11.6% | N/A | +16.2% | N/A | +26.8%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
SplitAHUs-CAV-3-DeckMultizone | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.8 | 31.4 | 31.4 | 149.1 | 0 | 14.1 | N/A | 76.4 / 63.8 | N/A | 55.8 / 54.6 | 1454 | 1454 | 7097 | 45.4 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.2%) | N/A | +11.6% | N/A | +16.2% | N/A | +26.8%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
SplitAHUs-CAV-DualDuact | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.8 | 31.4 | 31.4 | 149.1 | 0 | 14.1 | N/A | 76.4 / 63.8 | N/A | 55.8 / 54.6 | 1454 | 1454 | 7097 | 45.4 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.2%) | N/A | +11.6% | N/A | +16.2% | N/A | +26.8%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
SplitAHUs-CAV-Make-upAirDOAS | Zone 1 | B-IRRIGATION ROOM | 150.7 | 4342.2 | 4342.2 | N/A | N/A | 3.5 | 160.8 | 160.8 | N/A | N/A | N/A | N/A | N/A | N/A | 0 |  | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | B-PUMP ROOM | 183 |  |  |  |  | 3.2 | [8 empty] | 0
|  | B-SWIM P PUMP ROOM | 402.6 |  |  |  |  | 8.7 | [8 empty] | 0
|  | G-BACK KITCHEN | 161.5 |  |  |  |  | 12.4 | [8 empty] | 0
|  | G-CAFE HALL | 807.3 |  |  |  |  | 31.9 | [8 empty] | 0
|  | G-ELECTRICAL ROOM | 64.6 |  |  |  |  | 11.3 | [8 empty] | 0
|  | G-GYM | 861.1 |  |  |  |  | 31.4 | [8 empty] | 0
|  | G-HALL | 818.1 |  |  |  |  | 25.3 | [8 empty] | 0
|  | G-ICT | 75.3 |  |  |  |  | 9.4 | [8 empty] | 0
|  | G-SECURITY ROOM | 53.8 |  |  |  |  | 2.4 | [8 empty] | 0
|  | G-TOILET | 247.6 |  |  |  |  | 6 | [8 empty] | 0
|  | G-WASTE ROOM | 32.3 |  |  |  |  | 0.8 | [8 empty] | 0
|  | G-YOGA | 484.4 |  |  |  |  | 15.5 | [8 empty] | 0
SplitAHUs-CAV-SingleZone | Zone 1 | B-IRRIGATION ROOM | 150.7 | 4342.2 | 4342.2 | N/A | 185.3 | 3.5 | 160.8 | 156.3 | 0 | 10.6 | N/A | 76.6 / 65.9 | N/A | 60.2 / 59.1 | 190 | 8825 | 8825 | 42.7 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+10.8%) | N/A | +7.7% | N/A | +10.8% | N/A | +2%
|  | B-PUMP ROOM | 183 |  |  |  |  | 3.2 | [8 empty] | 177
|  | B-SWIM P PUMP ROOM | 402.6 |  |  |  |  | 8.7 | [8 empty] | 475
|  | G-BACK KITCHEN | 161.5 |  |  |  |  | 12.4 | [8 empty] | 675
|  | G-CAFE HALL | 807.3 |  |  |  |  | 31.9 | [8 empty] | 1741
|  | G-ELECTRICAL ROOM | 64.6 |  |  |  |  | 11.3 | [8 empty] | 613
|  | G-GYM | 861.1 |  |  |  |  | 31.4 | [8 empty] | 1711
|  | G-HALL | 818.1 |  |  |  |  | 25.3 | [8 empty] | 1376
|  | G-ICT | 75.3 |  |  |  |  | 9.4 | [8 empty] | 515
|  | G-SECURITY ROOM | 53.8 |  |  |  |  | 2.4 | [8 empty] | 133
|  | G-TOILET | 247.6 |  |  |  |  | 6 | [8 empty] | 330
|  | G-WASTE ROOM | 32.3 |  |  |  |  | 0.8 | [8 empty] | 44
|  | G-YOGA | 484.4 |  |  |  |  | 15.5 | [8 empty] | 845
SplitAHUs-CAV-TerminalReheat | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 176 | 31.4 | 31.4 | 146.5 | 62.8 |  | N/A | 74.9 / 63.3 | N/A | 55.8 / 54.7 | 1454 | 1454 | 7097 | 44.7 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+18.2%) | N/A | +13.4% | N/A | +18.2% | N/A | +26.8%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 31 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 50.5 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 12.1 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 24.8 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 63.9 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 22.5 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 18.9 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 6.5 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 7 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 4.9 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 1.6 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
SplitAHUs-VAV | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.7 | 31.4 | 31.4 | 149 | 6.2 |  | N/A | 76.4 / 63.8 | N/A | 55.8 / 54.6 | 1454 | 1454 | 7046 | 45.4 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.2%) | N/A | +11.6% | N/A | +16.2% | N/A | +27.7%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 3.6 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 5.3 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0.9 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0.2 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 6.4 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0.2 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0.1 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0.2 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0.1 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
SplitAHUs-VAV-1-FanDualDuct | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.8 | 31.4 | 31.4 | 149.1 | 0 | 14.1 | N/A | 76.4 / 63.8 | N/A | 55.8 / 54.6 | 1454 | 1454 | 7046 | 45.4 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.2%) | N/A | +11.6% | N/A | +16.2% | N/A | +27.7%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
SplitAHUs-VAV-2-FanDualDuct | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.5 | 31.4 | 31.4 | 149.1 | 0 | 4.7 | N/A | 76.4 / 63.8 | N/A | 55.8 / 54.6 | 1454 | 1454 | 7046 | 45.3 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.2%) | N/A | +11.8% | N/A | +16.2% | N/A | +27.7%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
SplitAHUs-VVT | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.2 | 31.4 | 31.4 | 149.2 | 0 | 14.7 | N/A | 76.3 / 64.8 | N/A | 58.0 / 56.9 | 1711 | 1711 | 8289 | 45.2 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.1%) | N/A | +12% | N/A | +16.1% | N/A | +8.6%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 845 | 845 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1376 | 1376 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 330 | 330 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 675 | 675 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1741 | 1741 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 613 | 613 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 515 | 515 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 177 | 177 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 190 | 190 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 133 | 133 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 44 | 44 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
TerminalUnits-2-PipeFanCoil | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | 36.9 |  | 31.4 | 30.8 |  | 4 |  | 76.3 / 65.6 | N/A | 59.6 / 58.6 | N/A | 1711 | 1711 |  | N/A | 1 |  | 41.6281 | N/A | 33.9167 | N/A | 1599.7544 | N/A | 0.3 | N/A | No (+10.1%) | N/A | +12.8% | N/A | +10.1% | N/A | -6.5% | N/A
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | 18.3 |  | 15.5 | 14.9 |  | 2.2 |  | 76.5 / 66.1 |  | 60.1 / 59.1 |  | 845 | 845 |  |  | 1 |  | 17.8455 |  | 15.2523 |  | 699.2304 |  | 0.125 |  | Yes |  | -2.5% |  | +2.4% |  | -17.3%
| Zone 3 | G-HALL | 818.1 | 818.1 |  | 30.1 |  | 25.3 | 24.4 |  | 3.2 |  | 76.5 / 66.1 |  | 60.0 / 59.1 |  | 1376 | 1376 |  |  | 1 |  | 30.4363 |  | 26.0346 |  | 1199.2861 |  | 0.2 |  | Yes |  | +1.1% |  | +6.7% |  | -12.8%
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | 7.7 |  | 6 | 6 |  | 0.7 |  | 76.1 / 65.9 |  | 59.3 / 58.3 |  | 330 | 330 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | Yes |  | +0.1% |  | +0.7% |  | -24.2%
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | 13.6 |  | 12.4 | 12.4 |  | 0.2 |  | 75.9 / 64.5 |  | 58.9 / 57.8 |  | 675 | 675 |  |  | 1 |  | 16.4806 |  | 13.1367 |  | 599.643 |  | 0.08 |  | Yes |  | +21.2% |  | +5.9% |  | -11.2%
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | 37.2 |  | 31.9 | 31.4 |  | 4.4 |  | 76.4 / 65.6 |  | 59.7 / 58.7 |  | 1741 | 1741 |  |  | 1 |  | 41.6281 |  | 33.9167 |  | 1599.7544 |  | 0.3 |  | Yes |  | +11.9% |  | +8% |  | -8.1%
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | 11.8 |  | 11.3 | 11.3 |  | 0.2 |  | 75.9 / 64.1 |  | 58.9 / 57.7 |  | 613 | 613 |  |  | 1 |  | 16.4806 |  | 13.1367 |  | 599.643 |  | 0.08 |  | No (+16.3%) |  | +39.7% |  | +16.3% |  | -2.2%
| Zone 8 | G-ICT | 75.3 | 75.3 |  | 10 |  | 9.4 | 9.5 |  | 0.1 |  | 75.9 / 64.3 |  | 58.9 / 57.8 |  | 515 | 515 |  |  | 1 |  | 13.6486 |  | 10.8506 |  | 500.0557 |  | 0.08 |  | No (+14.2%) |  | +36.5% |  | +14.2% |  | -2.9%
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | 4.5 |  | 3.2 | 3.2 |  | 0 |  | 76.2 / 66.5 |  | 59.3 / 58.4 |  | 177 | 177 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+88.7%) |  | +71.4% |  | +88.7% |  | +41.3%
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | 4.5 |  | 3.5 | 3.4 |  | 0 |  | 76.1 / 66.2 |  | 59.5 / 58.6 |  | 190 | 190 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+77.6%) |  | +71.4% |  | +77.6% |  | +31.6%
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | 2.7 |  | 2.4 | 2.3 |  | 0.2 |  | 76.5 / 65.8 |  | 60.2 / 59.2 |  | 133 | 133 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+162.6%) |  | +185.6% |  | +162.6% |  | +88%
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | 1 |  | 0.8 | 0.7 |  | 0 |  | 76.0 / 66.4 |  | 60.3 / 59.4 |  | 44 | 44 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+762.8%) |  | +671.1% |  | +762.8% |  | +468.2%
TerminalUnits-4-PipeFanCoil | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | 36.9 |  | 31.4 | 30.8 |  | 4 |  | 76.3 / 65.6 | N/A | 59.6 / 58.6 | N/A | 1711 | 1711 |  | N/A | 1 |  | 41.6281 | N/A | 33.9167 | N/A | 1599.7544 | N/A | 0.3 | N/A | No (+10.1%) | N/A | +12.8% | N/A | +10.1% | N/A | -6.5% | N/A
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | 18.3 |  | 15.5 | 14.9 |  | 2.2 |  | 76.5 / 66.1 |  | 60.1 / 59.1 |  | 845 | 845 |  |  | 1 |  | 17.8455 |  | 15.2523 |  | 699.2304 |  | 0.125 |  | Yes |  | -2.5% |  | +2.4% |  | -17.3%
| Zone 3 | G-HALL | 818.1 | 818.1 |  | 30.1 |  | 25.3 | 24.4 |  | 3.2 |  | 76.5 / 66.1 |  | 60.0 / 59.1 |  | 1376 | 1376 |  |  | 1 |  | 30.4363 |  | 26.0346 |  | 1199.2861 |  | 0.2 |  | Yes |  | +1.1% |  | +6.7% |  | -12.8%
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | 7.7 |  | 6 | 6 |  | 0.7 |  | 76.1 / 65.9 |  | 59.3 / 58.3 |  | 330 | 330 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | Yes |  | +0.1% |  | +0.7% |  | -24.2%
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | 13.6 |  | 12.4 | 12.4 |  | 0.2 |  | 75.9 / 64.5 |  | 58.9 / 57.8 |  | 675 | 675 |  |  | 1 |  | 16.4806 |  | 13.1367 |  | 599.643 |  | 0.08 |  | Yes |  | +21.2% |  | +5.9% |  | -11.2%
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | 37.2 |  | 31.9 | 31.4 |  | 4.4 |  | 76.4 / 65.6 |  | 59.7 / 58.7 |  | 1741 | 1741 |  |  | 1 |  | 41.6281 |  | 33.9167 |  | 1599.7544 |  | 0.3 |  | Yes |  | +11.9% |  | +8% |  | -8.1%
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | 11.8 |  | 11.3 | 11.3 |  | 0.2 |  | 75.9 / 64.1 |  | 58.9 / 57.7 |  | 613 | 613 |  |  | 1 |  | 16.4806 |  | 13.1367 |  | 599.643 |  | 0.08 |  | No (+16.3%) |  | +39.7% |  | +16.3% |  | -2.2%
| Zone 8 | G-ICT | 75.3 | 75.3 |  | 10 |  | 9.4 | 9.5 |  | 0.1 |  | 75.9 / 64.3 |  | 58.9 / 57.8 |  | 515 | 515 |  |  | 1 |  | 13.6486 |  | 10.8506 |  | 500.0557 |  | 0.08 |  | No (+14.2%) |  | +36.5% |  | +14.2% |  | -2.9%
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | 4.5 |  | 3.2 | 3.2 |  | 0 |  | 76.2 / 66.5 |  | 59.3 / 58.4 |  | 177 | 177 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+88.7%) |  | +71.4% |  | +88.7% |  | +41.3%
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | 4.5 |  | 3.5 | 3.4 |  | 0 |  | 76.1 / 66.2 |  | 59.5 / 58.6 |  | 190 | 190 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+77.6%) |  | +71.4% |  | +77.6% |  | +31.6%
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | 2.7 |  | 2.4 | 2.3 |  | 0.2 |  | 76.5 / 65.8 |  | 60.2 / 59.2 |  | 133 | 133 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+162.6%) |  | +185.6% |  | +162.6% |  | +88%
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | 1 |  | 0.8 | 0.7 |  | 0 |  | 76.0 / 66.4 |  | 60.3 / 59.4 |  | 44 | 44 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+762.8%) |  | +671.1% |  | +762.8% |  | +468.2%
TerminalUnits-ActiveChilledBeam | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | 17.4 | 237.2 | 31.4 | 17.4 | 144.5 | 13.7 | 12.6 | 76.6 / 63.1 | N/A | 62.4 / 58.0 | N/A | 1711 |  |  |  | 1 |  | 25.8299 | N/A | 20.9164 | N/A | 1000.1114 | N/A | 0.15 | N/A | No (+20.2%) | N/A | +48.4% | N/A | +20.2% | N/A | -41.5% | N/A
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | 8.7 |  | 15.5 | 8.7 |  | 6.9 |  | 76.2 / 63.5 |  | 61.9 / 58.3 |  | 845 |  |  |  | 1 |  | 13.6486 |  | 10.8506 |  | 500.0557 |  | 0.08 |  | No (+24.7%) |  | +56.9% |  | +24.7% |  | -40.8%
| Zone 3 | G-HALL | 818.1 | 818.1 |  | 14.2 |  | 25.3 | 14.2 |  | 10.1 |  | 76.2 / 63.5 |  | 61.9 / 58.4 |  | 1376 |  |  |  | 1 |  | 17.8455 |  | 15.2523 |  | 699.2304 |  | 0.125 |  | Yes |  | +25.7% |  | +7.4% |  | -49.2%
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | 3.5 |  | 6 | 3.5 |  | 2.5 |  | 76.1 / 64.5 |  | 61.3 / 59.3 |  | 330 |  |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+72.6%) |  | +120.3% |  | +72.6% |  | -24.2%
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | 7.4 |  | 12.4 | 7.4 |  | 3.8 |  | 76.0 / 61.1 |  | 60.7 / 55.3 |  | 675 |  |  |  | 1 |  | 10.2023 |  | 8.3597 |  | 400.4683 |  | 0.08 |  | No (+13.0%) |  | +37.9% |  | +13% |  | -40.7%
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | 18.5 |  | 31.9 | 18.5 |  | 12.7 |  | 76.0 / 62.7 |  | 61.2 / 57.3 |  | 1741 |  |  |  | 1 |  | 25.8299 |  | 20.9164 |  | 1000.1114 |  | 0.15 |  | No (+13.1%) |  | +39.6% |  | +13.1% |  | -42.6%
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | 6.7 |  | 11.3 | 6.7 |  | 3.5 |  | 75.8 / 60.0 |  | 60.6 / 54.1 |  | 613 |  |  |  | 1 |  | 8.1209 |  | 6.756 |  | 300.881 |  | 0.05 |  | Yes |  | +21.2% |  | +0.8% |  | -50.9%
| Zone 8 | G-ICT | 75.3 | 75.3 |  | 5.7 |  | 9.4 | 5.7 |  | 2.9 |  | 75.8 / 60.3 |  | 60.5 / 54.4 |  | 515 |  |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | Yes |  | +35.3% |  | +6% |  | -51.5%
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | 1.9 |  | 3.2 | 1.9 |  | 0.9 |  | 76.1 / 66.1 |  | 61.2 / 61.1 |  | 177 |  |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+217.9%) |  | +305.9% |  | +217.9% |  | +41.3%
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | 2 |  | 3.5 | 2 |  | 1.1 |  | 76.2 / 64.8 |  | 61.7 / 59.7 |  | 190 |  |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+202.0%) |  | +285.6% |  | +202% |  | +31.6%
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | 1.4 |  | 2.4 | 1.4 |  | 0.9 |  | 76.3 / 62.4 |  | 62.1 / 57.2 |  | 133 |  |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+331.4%) |  | +450.8% |  | +331.4% |  | +88%
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | 0.4 |  | 0.8 | 0.4 |  | 0.3 |  | 76.1 / 64.4 |  | 62.9 / 59.7 |  | 44 |  |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+1409.9%) |  | +1827.9% |  | +1409.9% |  | +468.2%
TerminalUnits-GroundSourceHeatPu | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | 36.9 |  | 31.4 | 30.8 |  | 4 |  | 76.3 / 65.6 | N/A | 59.6 / 58.6 | N/A | 1711 | 1711 |  | N/A | 1 |  | 41.6281 | N/A | 33.9167 | N/A | 1599.7544 | N/A | 0.3 | N/A | No (+10.1%) | N/A | +12.8% | N/A | +10.1% | N/A | -6.5% | N/A
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | 18.3 |  | 15.5 | 14.9 |  | 2.2 |  | 76.5 / 66.1 |  | 60.1 / 59.1 |  | 845 | 845 |  |  | 1 |  | 17.8455 |  | 15.2523 |  | 699.2304 |  | 0.125 |  | Yes |  | -2.5% |  | +2.4% |  | -17.3%
| Zone 3 | G-HALL | 818.1 | 818.1 |  | 30.1 |  | 25.3 | 24.4 |  | 3.2 |  | 76.5 / 66.1 |  | 60.0 / 59.1 |  | 1376 | 1376 |  |  | 1 |  | 30.4363 |  | 26.0346 |  | 1199.2861 |  | 0.2 |  | Yes |  | +1.1% |  | +6.7% |  | -12.8%
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | 7.7 |  | 6 | 6 |  | 0.7 |  | 76.1 / 65.9 |  | 59.3 / 58.3 |  | 330 | 330 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | Yes |  | +0.1% |  | +0.7% |  | -24.2%
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | 13.6 |  | 12.4 | 12.4 |  | 0.2 |  | 75.9 / 64.5 |  | 58.9 / 57.8 |  | 675 | 675 |  |  | 1 |  | 16.4806 |  | 13.1367 |  | 599.643 |  | 0.08 |  | Yes |  | +21.2% |  | +5.9% |  | -11.2%
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | 37.2 |  | 31.9 | 31.4 |  | 4.4 |  | 76.4 / 65.6 |  | 59.7 / 58.7 |  | 1741 | 1741 |  |  | 1 |  | 41.6281 |  | 33.9167 |  | 1599.7544 |  | 0.3 |  | Yes |  | +11.9% |  | +8% |  | -8.1%
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | 11.8 |  | 11.3 | 11.3 |  | 0.2 |  | 75.9 / 64.1 |  | 58.9 / 57.7 |  | 613 | 613 |  |  | 1 |  | 16.4806 |  | 13.1367 |  | 599.643 |  | 0.08 |  | No (+16.3%) |  | +39.7% |  | +16.3% |  | -2.2%
| Zone 8 | G-ICT | 75.3 | 75.3 |  | 10 |  | 9.4 | 9.5 |  | 0.1 |  | 75.9 / 64.3 |  | 58.9 / 57.8 |  | 515 | 515 |  |  | 1 |  | 13.6486 |  | 10.8506 |  | 500.0557 |  | 0.08 |  | No (+14.2%) |  | +36.5% |  | +14.2% |  | -2.9%
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | 4.5 |  | 3.2 | 3.2 |  | 0 |  | 76.2 / 66.5 |  | 59.3 / 58.4 |  | 177 | 177 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+88.7%) |  | +71.4% |  | +88.7% |  | +41.3%
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | 4.5 |  | 3.5 | 3.4 |  | 0 |  | 76.1 / 66.2 |  | 59.5 / 58.6 |  | 190 | 190 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+77.6%) |  | +71.4% |  | +77.6% |  | +31.6%
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | 2.7 |  | 2.4 | 2.3 |  | 0.2 |  | 76.5 / 65.8 |  | 60.2 / 59.2 |  | 133 | 133 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+162.6%) |  | +185.6% |  | +162.6% |  | +88%
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | 1 |  | 0.8 | 0.7 |  | 0 |  | 76.0 / 66.4 |  | 60.3 / 59.4 |  | 44 | 44 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+762.8%) |  | +671.1% |  | +762.8% |  | +468.2%
TerminalUnits-GroundwaterSourceH | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | 36.9 |  | 31.4 | 30.8 |  | 4 |  | 76.3 / 65.6 | N/A | 59.6 / 58.6 | N/A | 1711 | 1711 |  | N/A | 1 |  | 41.6281 | N/A | 33.9167 | N/A | 1599.7544 | N/A | 0.3 | N/A | No (+10.1%) | N/A | +12.8% | N/A | +10.1% | N/A | -6.5% | N/A
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | 18.3 |  | 15.5 | 14.9 |  | 2.2 |  | 76.5 / 66.1 |  | 60.1 / 59.1 |  | 845 | 845 |  |  | 1 |  | 17.8455 |  | 15.2523 |  | 699.2304 |  | 0.125 |  | Yes |  | -2.5% |  | +2.4% |  | -17.3%
| Zone 3 | G-HALL | 818.1 | 818.1 |  | 30.1 |  | 25.3 | 24.4 |  | 3.2 |  | 76.5 / 66.1 |  | 60.0 / 59.1 |  | 1376 | 1376 |  |  | 1 |  | 30.4363 |  | 26.0346 |  | 1199.2861 |  | 0.2 |  | Yes |  | +1.1% |  | +6.7% |  | -12.8%
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | 7.7 |  | 6 | 6 |  | 0.7 |  | 76.1 / 65.9 |  | 59.3 / 58.3 |  | 330 | 330 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | Yes |  | +0.1% |  | +0.7% |  | -24.2%
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | 13.6 |  | 12.4 | 12.4 |  | 0.2 |  | 75.9 / 64.5 |  | 58.9 / 57.8 |  | 675 | 675 |  |  | 1 |  | 16.4806 |  | 13.1367 |  | 599.643 |  | 0.08 |  | Yes |  | +21.2% |  | +5.9% |  | -11.2%
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | 37.2 |  | 31.9 | 31.4 |  | 4.4 |  | 76.4 / 65.6 |  | 59.7 / 58.7 |  | 1741 | 1741 |  |  | 1 |  | 41.6281 |  | 33.9167 |  | 1599.7544 |  | 0.3 |  | Yes |  | +11.9% |  | +8% |  | -8.1%
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | 11.8 |  | 11.3 | 11.3 |  | 0.2 |  | 75.9 / 64.1 |  | 58.9 / 57.7 |  | 613 | 613 |  |  | 1 |  | 16.4806 |  | 13.1367 |  | 599.643 |  | 0.08 |  | No (+16.3%) |  | +39.7% |  | +16.3% |  | -2.2%
| Zone 8 | G-ICT | 75.3 | 75.3 |  | 10 |  | 9.4 | 9.5 |  | 0.1 |  | 75.9 / 64.3 |  | 58.9 / 57.8 |  | 515 | 515 |  |  | 1 |  | 13.6486 |  | 10.8506 |  | 500.0557 |  | 0.08 |  | No (+14.2%) |  | +36.5% |  | +14.2% |  | -2.9%
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | 4.5 |  | 3.2 | 3.2 |  | 0 |  | 76.2 / 66.5 |  | 59.3 / 58.4 |  | 177 | 177 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+88.7%) |  | +71.4% |  | +88.7% |  | +41.3%
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | 4.5 |  | 3.5 | 3.4 |  | 0 |  | 76.1 / 66.2 |  | 59.5 / 58.6 |  | 190 | 190 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+77.6%) |  | +71.4% |  | +77.6% |  | +31.6%
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | 2.7 |  | 2.4 | 2.3 |  | 0.2 |  | 76.5 / 65.8 |  | 60.2 / 59.2 |  | 133 | 133 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+162.6%) |  | +185.6% |  | +162.6% |  | +88%
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | 1 |  | 0.8 | 0.7 |  | 0 |  | 76.0 / 66.4 |  | 60.3 / 59.4 |  | 44 | 44 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+762.8%) |  | +671.1% |  | +762.8% |  | +468.2%
TerminalUnits-InductionBeam | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | 20.6 | 212.6 | 31.4 | 20.2 | 131.8 | 10.2 | 11.8 | 75.9 / 64.5 | N/A | 59.5 / 58.5 | N/A | 1711 |  |  |  | 1 |  | 25.8299 | N/A | 20.9164 | N/A | 1000.1114 | N/A | 0.15 | N/A | Yes | N/A | +25.4% | N/A | +3.5% | N/A | -41.5% | N/A
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | 10.7 |  | 15.5 | 10.2 |  | 5.6 |  | 76.2 / 64.8 |  | 59.5 / 58.5 |  | 845 |  |  |  | 1 |  | 13.6486 |  | 10.8506 |  | 500.0557 |  | 0.08 |  | Yes |  | +27.6% |  | +6.4% |  | -40.8%
| Zone 3 | G-HALL | 818.1 | 818.1 |  | 16.9 |  | 25.3 | 16.2 |  | 8.2 |  | 76.4 / 65.1 |  | 60.1 / 59.1 |  | 1376 |  |  |  | 1 |  | 19.6198 |  | 16.9925 |  | 900.524 |  | 0.15 |  | Yes |  | +16.1% |  | +4.9% |  | -34.6%
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | 4.5 |  | 6 | 4 |  | 1.7 |  | 76.2 / 65.1 |  | 59.5 / 58.5 |  | 330 |  |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+51.0%) |  | +71.4% |  | +51% |  | -24.2%
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | 8.7 |  | 12.4 | 8.7 |  | 2.6 |  | 75.8 / 63.1 |  | 57.9 / 56.5 |  | 675 |  |  |  | 1 |  | 13.6486 |  | 10.8506 |  | 500.0557 |  | 0.08 |  | No (+24.7%) |  | +56.9% |  | +24.7% |  | -25.9%
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | 20.7 |  | 31.9 | 20.7 |  | 9.9 |  | 76.6 / 64.8 |  | 60.1 / 58.9 |  | 1741 |  |  |  | 1 |  | 25.8299 |  | 20.9164 |  | 1000.1114 |  | 0.15 |  | Yes |  | +24.8% |  | +1% |  | -42.6%
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | 7.8 |  | 11.3 | 7.8 |  | 2.5 |  | 75.9 / 62.2 |  | 58.2 / 55.5 |  | 613 |  |  |  | 1 |  | 10.2023 |  | 8.3597 |  | 400.4683 |  | 0.08 |  | Yes |  | +30.8% |  | +7.2% |  | -34.7%
| Zone 8 | G-ICT | 75.3 | 75.3 |  | 6.6 |  | 9.4 | 6.6 |  | 1.7 |  | 75.9 / 62.5 |  | 58.2 / 55.9 |  | 515 |  |  |  | 1 |  | 8.1209 |  | 6.756 |  | 300.881 |  | 0.05 |  | Yes |  | +23% |  | +2.4% |  | -41.6%
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | 2.7 |  | 3.2 | 2.2 |  | 0.6 |  | 76.2 / 65.5 |  | 58.9 / 58.0 |  | 177 |  |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+174.5%) |  | +185.6% |  | +174.5% |  | +41.3%
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | 2.7 |  | 3.5 | 2.3 |  | 0.7 |  | 76.1 / 65.1 |  | 59.1 / 58.1 |  | 190 |  |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+162.6%) |  | +185.6% |  | +162.6% |  | +31.6%
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | 1.6 |  | 2.4 | 1.6 |  | 0.6 |  | 76.3 / 64.3 |  | 59.8 / 58.5 |  | 133 |  |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+277.5%) |  | +382% |  | +277.5% |  | +88%
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | 0.5 |  | 0.8 | 0.5 |  | 0.2 |  | 76.0 / 65.4 |  | 60.3 / 59.4 |  | 44 |  |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+1107.9%) |  | +1442.3% |  | +1107.9% |  | +468.2%
TerminalUnits-PackagedDXFanCoil | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | 36.9 |  | 31.4 | 30.8 |  | 4 |  | 76.3 / 65.6 | N/A | 59.6 / 58.6 | N/A | 1711 | 1711 |  | N/A | 1 |  | 41.6281 | N/A | 33.9167 | N/A | 1599.7544 | N/A | 0.3 | N/A | No (+10.1%) | N/A | +12.8% | N/A | +10.1% | N/A | -6.5% | N/A
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | 18.3 |  | 15.5 | 14.9 |  | 2.2 |  | 76.5 / 66.1 |  | 60.1 / 59.1 |  | 845 | 845 |  |  | 1 |  | 17.8455 |  | 15.2523 |  | 699.2304 |  | 0.125 |  | Yes |  | -2.5% |  | +2.4% |  | -17.3%
| Zone 3 | G-HALL | 818.1 | 818.1 |  | 30.1 |  | 25.3 | 24.4 |  | 3.2 |  | 76.5 / 66.1 |  | 60.0 / 59.1 |  | 1376 | 1376 |  |  | 1 |  | 30.4363 |  | 26.0346 |  | 1199.2861 |  | 0.2 |  | Yes |  | +1.1% |  | +6.7% |  | -12.8%
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | 7.7 |  | 6 | 6 |  | 0.7 |  | 76.1 / 65.9 |  | 59.3 / 58.3 |  | 330 | 330 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | Yes |  | +0.1% |  | +0.7% |  | -24.2%
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | 13.6 |  | 12.4 | 12.4 |  | 0.2 |  | 75.9 / 64.5 |  | 58.9 / 57.8 |  | 675 | 675 |  |  | 1 |  | 16.4806 |  | 13.1367 |  | 599.643 |  | 0.08 |  | Yes |  | +21.2% |  | +5.9% |  | -11.2%
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | 37.2 |  | 31.9 | 31.4 |  | 4.4 |  | 76.4 / 65.6 |  | 59.7 / 58.7 |  | 1741 | 1741 |  |  | 1 |  | 41.6281 |  | 33.9167 |  | 1599.7544 |  | 0.3 |  | Yes |  | +11.9% |  | +8% |  | -8.1%
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | 11.8 |  | 11.3 | 11.3 |  | 0.2 |  | 75.9 / 64.1 |  | 58.9 / 57.7 |  | 613 | 613 |  |  | 1 |  | 16.4806 |  | 13.1367 |  | 599.643 |  | 0.08 |  | No (+16.3%) |  | +39.7% |  | +16.3% |  | -2.2%
| Zone 8 | G-ICT | 75.3 | 75.3 |  | 10 |  | 9.4 | 9.5 |  | 0.1 |  | 75.9 / 64.3 |  | 58.9 / 57.8 |  | 515 | 515 |  |  | 1 |  | 13.6486 |  | 10.8506 |  | 500.0557 |  | 0.08 |  | No (+14.2%) |  | +36.5% |  | +14.2% |  | -2.9%
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | 4.5 |  | 3.2 | 3.2 |  | 0 |  | 76.2 / 66.5 |  | 59.3 / 58.4 |  | 177 | 177 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+88.7%) |  | +71.4% |  | +88.7% |  | +41.3%
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | 4.5 |  | 3.5 | 3.4 |  | 0 |  | 76.1 / 66.2 |  | 59.5 / 58.6 |  | 190 | 190 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+77.6%) |  | +71.4% |  | +77.6% |  | +31.6%
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | 2.7 |  | 2.4 | 2.3 |  | 0.2 |  | 76.5 / 65.8 |  | 60.2 / 59.2 |  | 133 | 133 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+162.6%) |  | +185.6% |  | +162.6% |  | +88%
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | 1 |  | 0.8 | 0.7 |  | 0 |  | 76.0 / 66.4 |  | 60.3 / 59.4 |  | 44 | 44 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+762.8%) |  | +671.1% |  | +762.8% |  | +468.2%
TerminalUnits-SplitDXFanCoil | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | 36.9 |  | 31.4 | 30.8 |  | 4 |  | 76.3 / 65.6 | N/A | 59.6 / 58.6 | N/A | 1711 | 1711 |  | N/A | 1 |  | 41.6281 | N/A | 33.9167 | N/A | 1599.7544 | N/A | 0.3 | N/A | No (+10.1%) | N/A | +12.8% | N/A | +10.1% | N/A | -6.5% | N/A
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | 18.3 |  | 15.5 | 14.9 |  | 2.2 |  | 76.5 / 66.1 |  | 60.1 / 59.1 |  | 845 | 845 |  |  | 1 |  | 17.8455 |  | 15.2523 |  | 699.2304 |  | 0.125 |  | Yes |  | -2.5% |  | +2.4% |  | -17.3%
| Zone 3 | G-HALL | 818.1 | 818.1 |  | 30.1 |  | 25.3 | 24.4 |  | 3.2 |  | 76.5 / 66.1 |  | 60.0 / 59.1 |  | 1376 | 1376 |  |  | 1 |  | 30.4363 |  | 26.0346 |  | 1199.2861 |  | 0.2 |  | Yes |  | +1.1% |  | +6.7% |  | -12.8%
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | 7.7 |  | 6 | 6 |  | 0.7 |  | 76.1 / 65.9 |  | 59.3 / 58.3 |  | 330 | 330 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | Yes |  | +0.1% |  | +0.7% |  | -24.2%
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | 13.6 |  | 12.4 | 12.4 |  | 0.2 |  | 75.9 / 64.5 |  | 58.9 / 57.8 |  | 675 | 675 |  |  | 1 |  | 16.4806 |  | 13.1367 |  | 599.643 |  | 0.08 |  | Yes |  | +21.2% |  | +5.9% |  | -11.2%
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | 37.2 |  | 31.9 | 31.4 |  | 4.4 |  | 76.4 / 65.6 |  | 59.7 / 58.7 |  | 1741 | 1741 |  |  | 1 |  | 41.6281 |  | 33.9167 |  | 1599.7544 |  | 0.3 |  | Yes |  | +11.9% |  | +8% |  | -8.1%
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | 11.8 |  | 11.3 | 11.3 |  | 0.2 |  | 75.9 / 64.1 |  | 58.9 / 57.7 |  | 613 | 613 |  |  | 1 |  | 16.4806 |  | 13.1367 |  | 599.643 |  | 0.08 |  | No (+16.3%) |  | +39.7% |  | +16.3% |  | -2.2%
| Zone 8 | G-ICT | 75.3 | 75.3 |  | 10 |  | 9.4 | 9.5 |  | 0.1 |  | 75.9 / 64.3 |  | 58.9 / 57.8 |  | 515 | 515 |  |  | 1 |  | 13.6486 |  | 10.8506 |  | 500.0557 |  | 0.08 |  | No (+14.2%) |  | +36.5% |  | +14.2% |  | -2.9%
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | 4.5 |  | 3.2 | 3.2 |  | 0 |  | 76.2 / 66.5 |  | 59.3 / 58.4 |  | 177 | 177 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+88.7%) |  | +71.4% |  | +88.7% |  | +41.3%
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | 4.5 |  | 3.5 | 3.4 |  | 0 |  | 76.1 / 66.2 |  | 59.5 / 58.6 |  | 190 | 190 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+77.6%) |  | +71.4% |  | +77.6% |  | +31.6%
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | 2.7 |  | 2.4 | 2.3 |  | 0.2 |  | 76.5 / 65.8 |  | 60.2 / 59.2 |  | 133 | 133 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+162.6%) |  | +185.6% |  | +162.6% |  | +88%
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | 1 |  | 0.8 | 0.7 |  | 0 |  | 76.0 / 66.4 |  | 60.3 / 59.4 |  | 44 | 44 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+762.8%) |  | +671.1% |  | +762.8% |  | +468.2%
TerminalUnits-VRF | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | 36.9 |  | 31.4 | 30.8 |  | 4 |  | 76.3 / 65.6 | N/A | 59.6 / 58.6 | N/A | 1711 | 1711 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | 18.3 |  | 15.5 | 14.9 |  | 2.2 |  | 76.5 / 66.1 |  | 60.1 / 59.1 |  | 845 | 845 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | 30.1 |  | 25.3 | 24.4 |  | 3.2 |  | 76.5 / 66.1 |  | 60.0 / 59.1 |  | 1376 | 1376 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | 7.7 |  | 6 | 6 |  | 0.7 |  | 76.1 / 65.9 |  | 59.3 / 58.3 |  | 330 | 330 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | 13.6 |  | 12.4 | 12.4 |  | 0.2 |  | 75.9 / 64.5 |  | 58.9 / 57.8 |  | 675 | 675 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | 37.2 |  | 31.9 | 31.4 |  | 4.4 |  | 76.4 / 65.6 |  | 59.7 / 58.7 |  | 1741 | 1741 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | 11.8 |  | 11.3 | 11.3 |  | 0.2 |  | 75.9 / 64.1 |  | 58.9 / 57.7 |  | 613 | 613 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | 10 |  | 9.4 | 9.5 |  | 0.1 |  | 75.9 / 64.3 |  | 58.9 / 57.8 |  | 515 | 515 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | 4.5 |  | 3.2 | 3.2 |  | 0 |  | 76.2 / 66.5 |  | 59.3 / 58.4 |  | 177 | 177 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | 4.5 |  | 3.5 | 3.4 |  | 0 |  | 76.1 / 66.2 |  | 59.5 / 58.6 |  | 190 | 190 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | 2.7 |  | 2.4 | 2.3 |  | 0.2 |  | 76.5 / 65.8 |  | 60.2 / 59.2 |  | 133 | 133 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | 1 |  | 0.8 | 0.7 |  | 0 |  | 76.0 / 66.4 |  | 60.3 / 59.4 |  | 44 | 44 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
TerminalUnits-WaterSourceHeatPum | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | 36.9 |  | 31.4 | 30.8 |  | 4 |  | 76.3 / 65.6 | N/A | 59.6 / 58.6 | N/A | 1711 | 1711 |  | N/A | 1 |  | 41.6281 | N/A | 33.9167 | N/A | 1599.7544 | N/A | 0.3 | N/A | No (+10.1%) | N/A | +12.8% | N/A | +10.1% | N/A | -6.5% | N/A
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | 18.3 |  | 15.5 | 14.9 |  | 2.2 |  | 76.5 / 66.1 |  | 60.1 / 59.1 |  | 845 | 845 |  |  | 1 |  | 17.8455 |  | 15.2523 |  | 699.2304 |  | 0.125 |  | Yes |  | -2.5% |  | +2.4% |  | -17.3%
| Zone 3 | G-HALL | 818.1 | 818.1 |  | 30.1 |  | 25.3 | 24.4 |  | 3.2 |  | 76.5 / 66.1 |  | 60.0 / 59.1 |  | 1376 | 1376 |  |  | 1 |  | 30.4363 |  | 26.0346 |  | 1199.2861 |  | 0.2 |  | Yes |  | +1.1% |  | +6.7% |  | -12.8%
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | 7.7 |  | 6 | 6 |  | 0.7 |  | 76.1 / 65.9 |  | 59.3 / 58.3 |  | 330 | 330 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | Yes |  | +0.1% |  | +0.7% |  | -24.2%
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | 13.6 |  | 12.4 | 12.4 |  | 0.2 |  | 75.9 / 64.5 |  | 58.9 / 57.8 |  | 675 | 675 |  |  | 1 |  | 16.4806 |  | 13.1367 |  | 599.643 |  | 0.08 |  | Yes |  | +21.2% |  | +5.9% |  | -11.2%
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | 37.2 |  | 31.9 | 31.4 |  | 4.4 |  | 76.4 / 65.6 |  | 59.7 / 58.7 |  | 1741 | 1741 |  |  | 1 |  | 41.6281 |  | 33.9167 |  | 1599.7544 |  | 0.3 |  | Yes |  | +11.9% |  | +8% |  | -8.1%
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | 11.8 |  | 11.3 | 11.3 |  | 0.2 |  | 75.9 / 64.1 |  | 58.9 / 57.7 |  | 613 | 613 |  |  | 1 |  | 16.4806 |  | 13.1367 |  | 599.643 |  | 0.08 |  | No (+16.3%) |  | +39.7% |  | +16.3% |  | -2.2%
| Zone 8 | G-ICT | 75.3 | 75.3 |  | 10 |  | 9.4 | 9.5 |  | 0.1 |  | 75.9 / 64.3 |  | 58.9 / 57.8 |  | 515 | 515 |  |  | 1 |  | 13.6486 |  | 10.8506 |  | 500.0557 |  | 0.08 |  | No (+14.2%) |  | +36.5% |  | +14.2% |  | -2.9%
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | 4.5 |  | 3.2 | 3.2 |  | 0 |  | 76.2 / 66.5 |  | 59.3 / 58.4 |  | 177 | 177 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+88.7%) |  | +71.4% |  | +88.7% |  | +41.3%
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | 4.5 |  | 3.5 | 3.4 |  | 0 |  | 76.1 / 66.2 |  | 59.5 / 58.6 |  | 190 | 190 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+77.6%) |  | +71.4% |  | +77.6% |  | +31.6%
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | 2.7 |  | 2.4 | 2.3 |  | 0.2 |  | 76.5 / 65.8 |  | 60.2 / 59.2 |  | 133 | 133 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+162.6%) |  | +185.6% |  | +162.6% |  | +88%
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | 1 |  | 0.8 | 0.7 |  | 0 |  | 76.0 / 66.4 |  | 60.3 / 59.4 |  | 44 | 44 |  |  | 1 |  | 7.7114 |  | 6.0395 |  | 250.0278 |  | 0.05 |  | No (+762.8%) |  | +671.1% |  | +762.8% |  | +468.2%
Undefined-CAV-SingleZone | Zone 1 | B-IRRIGATION ROOM | 150.7 | 4342.2 | 4342.2 | N/A | 185.3 | 3.5 | 160.8 | 156.3 | 0 | 10.6 | N/A | 76.6 / 65.9 | N/A | 60.2 / 59.1 | 190 | 8825 | 8825 | 42.7 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+10.8%) | N/A | +7.7% | N/A | +10.8% | N/A | +2%
|  | B-PUMP ROOM | 183 |  |  |  |  | 3.2 | [8 empty] | 177
|  | B-SWIM P PUMP ROOM | 402.6 |  |  |  |  | 8.7 | [8 empty] | 475
|  | G-BACK KITCHEN | 161.5 |  |  |  |  | 12.4 | [8 empty] | 675
|  | G-CAFE HALL | 807.3 |  |  |  |  | 31.9 | [8 empty] | 1741
|  | G-ELECTRICAL ROOM | 64.6 |  |  |  |  | 11.3 | [8 empty] | 613
|  | G-GYM | 861.1 |  |  |  |  | 31.4 | [8 empty] | 1711
|  | G-HALL | 818.1 |  |  |  |  | 25.3 | [8 empty] | 1376
|  | G-ICT | 75.3 |  |  |  |  | 9.4 | [8 empty] | 515
|  | G-SECURITY ROOM | 53.8 |  |  |  |  | 2.4 | [8 empty] | 133
|  | G-TOILET | 247.6 |  |  |  |  | 6 | [8 empty] | 330
|  | G-WASTE ROOM | 32.3 |  |  |  |  | 0.8 | [8 empty] | 44
|  | G-YOGA | 484.4 |  |  |  |  | 15.5 | [8 empty] | 845
Undefined-CAV-TerminalReheat | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 175.4 | 31.4 | 31.4 | 145.6 | 62.8 |  | N/A | 74.0 / 62.6 | N/A | 55.0 / 53.9 | 1454 | 1454 | 7097 | 44.5 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+19.0%) | N/A | +13.7% | N/A | +19% | N/A | +26.8%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 31 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 50.5 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 12.1 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 24.8 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 63.9 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 22.5 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 18.9 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 6.5 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 7 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 4.9 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 1.6 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
Undefined-VAV | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.9 | 31.4 | 31.4 | 149.1 | 6.2 |  | N/A | 76.3 / 63.4 | N/A | 55.0 / 53.8 | 1454 | 1454 | 7046 | 45.4 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.2%) | N/A | +11.5% | N/A | +16.2% | N/A | +27.7%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 3.6 |  | N/A |  | N/A |  | 718 | 718 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 5.3 |  | N/A |  | N/A |  | 1170 | 1170 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0.9 |  | N/A |  | N/A |  | 280 | 280 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0.2 |  | N/A |  | N/A |  | 574 | 574 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 6.4 |  | N/A |  | N/A |  | 1479 | 1479 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0.2 |  | N/A |  | N/A |  | 521 | 521 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0.1 |  | N/A |  | N/A |  | 438 | 438 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 150 | 150 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 162 | 162 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0.2 |  | N/A |  | N/A |  | 113 | 113 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0.1 |  | N/A |  | N/A |  | 37 | 37 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
Undefined-VVT | Zone 1 | G-GYM | 861.1 | 861.1 | 3939.6 | N/A | 178.2 | 31.4 | 31.4 | 149.2 | 0 | 14.7 | N/A | 76.3 / 64.8 | N/A | 58.0 / 56.9 | 1711 | 1711 | 8289 | 45.2 | N/A | 3 | N/A | 66.5026 | N/A | 57.7334 | N/A | 3000.3341 | N/A | 0.8 | N/A | No (+16.1%) | N/A | +12% | N/A | +16.1% | N/A | +8.6%
| Zone 2 | G-YOGA | 484.4 | 484.4 |  | N/A |  | 15.5 | 15.5 |  | 0 |  | N/A |  | N/A |  | 845 | 845 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 3 | G-HALL | 818.1 | 818.1 |  | N/A |  | 25.3 | 25.3 |  | 0 |  | N/A |  | N/A |  | 1376 | 1376 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 4 | G-TOILET | 247.6 | 247.6 |  | N/A |  | 6 | 6 |  | 0 |  | N/A |  | N/A |  | 330 | 330 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 161.5 |  | N/A |  | 12.4 | 12.4 |  | 0 |  | N/A |  | N/A |  | 675 | 675 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 807.3 |  | N/A |  | 31.9 | 31.9 |  | 0 |  | N/A |  | N/A |  | 1741 | 1741 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 64.6 |  | N/A |  | 11.3 | 11.3 |  | 0 |  | N/A |  | N/A |  | 613 | 613 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 8 | G-ICT | 75.3 | 75.3 |  | N/A |  | 9.4 | 9.4 |  | 0 |  | N/A |  | N/A |  | 515 | 515 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 9 | B-PUMP ROOM | 183 | 183 |  | N/A |  | 3.2 | 3.2 |  | 0 |  | N/A |  | N/A |  | 177 | 177 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 150.7 |  | N/A |  | 3.5 | 3.5 |  | 0 |  | N/A |  | N/A |  | 190 | 190 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 53.8 |  | N/A |  | 2.4 | 2.4 |  | 0 |  | N/A |  | N/A |  | 133 | 133 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 32.3 |  | N/A |  | 0.8 | 0.8 |  | 0 |  | N/A |  | N/A |  | 44 | 44 |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A
OVERALL | All systems | Installed (Qty × each) | N/A | N/A |  | N/A |  | N/A | N/A |  | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## COMPACT
CALCULATED LOADS (COMPACT) | [10 empty] | SELECTED EQUIPMENT (COMPACT)
Unit Reference | Zone | Area Served | AREA | Total Cooling Load | Sensible Load | Total Heating Load | On coil temperature (DB/WB) | Off coil temperature (DB/WB) | Air Flow Rate | Cooling Load Density | Selected Qty | Selected Total Cooling (each) | Selected Sensible (each) | Selected Air Flow (each) | Selected Indoor Power (each) | Within Tolerance | Total Dev % | Sensible Dev % | Flow Dev %
|  |  | ft² | MBH | MBH | MBH | Deg.F. | Deg.F. | CFM | (BTU/h·ft²) |  | MBH | MBH | CFM | kW
CHWAHUs-CAV-2-DeckMultiZone | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.8 | 149.1 | 14.1 | 76.4 / 63.8 | 55.8 / 54.6 | 7097 | 45.4 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.2%) | +11.6% | +16.2% | +26.8%
CHWAHUs-CAV-3-DeckMultizone | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.8 | 149.1 | 14.1 | 76.4 / 63.8 | 55.8 / 54.6 | 7097 | 45.4 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.2%) | +11.6% | +16.2% | +26.8%
CHWAHUs-CAV-DualDuact | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.8 | 149.1 | 14.1 | 76.4 / 63.8 | 55.8 / 54.6 | 7097 | 45.4 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.2%) | +11.6% | +16.2% | +26.8%
CHWAHUs-CAV-Make-upAirDOAS | Zone 1 | B-IRRIGATION ROOM, B-PUMP ROOM, B-SWIM P PUMP ROOM, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-GYM, G-HALL, G-ICT, G-SECURITY ROOM, G-TOILET, G-WASTE ROOM and G-YOGA | 4342.2 | N/A | 160.8 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
CHWAHUs-CAV-SingleZone | Zone 1 | B-IRRIGATION ROOM, B-PUMP ROOM, B-SWIM P PUMP ROOM, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-GYM, G-HALL, G-ICT, G-SECURITY ROOM, G-TOILET, G-WASTE ROOM and G-YOGA | 4342.2 | 185.3 | 156.3 | 10.6 | 76.6 / 65.9 | 60.2 / 59.1 | 8825 | 42.7 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+10.8%) | +7.7% | +10.8% | +2%
CHWAHUs-CAV-TerminalReheat | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 176 | 146.5 | 306.5 | 74.9 / 63.3 | 55.8 / 54.7 | 7097 | 44.7 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+18.2%) | +13.4% | +18.2% | +26.8%
CHWAHUs-VAV | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.7 | 149 | 23.2 | 76.4 / 63.8 | 55.8 / 54.6 | 7046 | 45.4 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.2%) | +11.6% | +16.2% | +27.7%
CHWAHUs-VAV-1-FanDualDuct | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.8 | 149.1 | 14.1 | 76.4 / 63.8 | 55.8 / 54.6 | 7046 | 45.4 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.2%) | +11.6% | +16.2% | +27.7%
CHWAHUs-VAV-2-FanDualDuct | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.5 | 149.1 | 4.7 | 76.4 / 63.8 | 55.8 / 54.6 | 7046 | 45.3 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.2%) | +11.8% | +16.2% | +27.7%
CHWAHUs-VVT | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.2 | 149.2 | 14.7 | 76.3 / 64.8 | 58.0 / 56.9 | 8289 | 45.2 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.1%) | +12% | +16.1% | +8.6%
PackagedRooftopUnits-CAV-2-DeckM | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 185.7 | 155.9 | 80.6 | 76.4 / 63.4 | 55.0 / 53.8 | 7097 | 47.1 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+11.1%) | +7.4% | +11.1% | +26.8%
PackagedRooftopUnits-CAV-3-DeckM | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 179 | 149.1 | 14.6 | 76.4 / 63.4 | 55.0 / 53.8 | 7097 | 45.4 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.2%) | +11.5% | +16.2% | +26.8%
PackagedRooftopUnits-CAV-DualDuc | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 185.7 | 155.9 | 80.6 | 76.4 / 63.4 | 55.0 / 53.8 | 7097 | 47.1 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+11.1%) | +7.4% | +11.1% | +26.8%
PackagedRooftopUnits-CAV-Make-up | Zone 1 | B-IRRIGATION ROOM, B-PUMP ROOM, B-SWIM P PUMP ROOM, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-GYM, G-HALL, G-ICT, G-SECURITY ROOM, G-TOILET, G-WASTE ROOM and G-YOGA | 4342.2 | N/A | 160.8 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
PackagedRooftopUnits-CAV-Termina | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 175.4 | 145.6 | 306.5 | 74.0 / 62.6 | 55.0 / 53.9 | 7097 | 44.5 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+19.0%) | +13.7% | +19% | +26.8%
PackagedRooftopUnits-VAV | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.9 | 149.1 | 23.2 | 76.3 / 63.4 | 55.0 / 53.8 | 7046 | 45.4 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.2%) | +11.5% | +16.2% | +27.7%
PackagedRooftopUnits-VAV-1-FanDu | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 179 | 149.1 | 15.5 | 76.4 / 63.4 | 55.0 / 53.8 | 7046 | 45.4 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.2%) | +11.5% | +16.2% | +27.7%
PackagedRooftopUnits-VAV-2-FanDu | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.8 | 149.1 | 14.6 | 76.4 / 63.4 | 55.0 / 53.8 | 7046 | 45.4 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.2%) | +11.6% | +16.2% | +27.7%
PackagedRooftopUnits-VVT | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.2 | 149.2 | 14.7 | 76.3 / 64.8 | 58.0 / 56.9 | 8289 | 45.2 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.1%) | +12% | +16.1% | +8.6%
PackagedVerticalUnits-CAV-Single | Zone 1 | B-IRRIGATION ROOM, B-PUMP ROOM, B-SWIM P PUMP ROOM, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-GYM, G-HALL, G-ICT, G-SECURITY ROOM, G-TOILET, G-WASTE ROOM and G-YOGA | 4342.2 | 185.3 | 156.3 | 10.6 | 76.6 / 65.9 | 60.2 / 59.1 | 8825 | 42.7 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+10.8%) | +7.7% | +10.8% | +2%
PackagedVerticalUnits-CAV-Termin | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 176 | 146.5 | 306.5 | 74.9 / 63.3 | 55.8 / 54.7 | 7097 | 44.7 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+18.2%) | +13.4% | +18.2% | +26.8%
PackagedVerticalUnits-VAV | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.9 | 149.1 | 23.2 | 76.3 / 63.4 | 55.0 / 53.8 | 7046 | 45.4 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.2%) | +11.5% | +16.2% | +27.7%
PackagedVerticalUnits-VVT | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.2 | 149.2 | 14.7 | 76.3 / 64.8 | 58.0 / 56.9 | 8289 | 45.2 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.1%) | +12% | +16.1% | +8.6%
SplitAHUs-CAV-2-DeckMultiZone | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.8 | 149.1 | 14.1 | 76.4 / 63.8 | 55.8 / 54.6 | 7097 | 45.4 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.2%) | +11.6% | +16.2% | +26.8%
SplitAHUs-CAV-3-DeckMultizone | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.8 | 149.1 | 14.1 | 76.4 / 63.8 | 55.8 / 54.6 | 7097 | 45.4 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.2%) | +11.6% | +16.2% | +26.8%
SplitAHUs-CAV-DualDuact | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.8 | 149.1 | 14.1 | 76.4 / 63.8 | 55.8 / 54.6 | 7097 | 45.4 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.2%) | +11.6% | +16.2% | +26.8%
SplitAHUs-CAV-Make-upAirDOAS | Zone 1 | B-IRRIGATION ROOM, B-PUMP ROOM, B-SWIM P PUMP ROOM, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-GYM, G-HALL, G-ICT, G-SECURITY ROOM, G-TOILET, G-WASTE ROOM and G-YOGA | 4342.2 | N/A | 160.8 | N/A | N/A | N/A | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
SplitAHUs-CAV-SingleZone | Zone 1 | B-IRRIGATION ROOM, B-PUMP ROOM, B-SWIM P PUMP ROOM, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-GYM, G-HALL, G-ICT, G-SECURITY ROOM, G-TOILET, G-WASTE ROOM and G-YOGA | 4342.2 | 185.3 | 156.3 | 10.6 | 76.6 / 65.9 | 60.2 / 59.1 | 8825 | 42.7 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+10.8%) | +7.7% | +10.8% | +2%
SplitAHUs-CAV-TerminalReheat | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 176 | 146.5 | 306.5 | 74.9 / 63.3 | 55.8 / 54.7 | 7097 | 44.7 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+18.2%) | +13.4% | +18.2% | +26.8%
SplitAHUs-VAV | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.7 | 149 | 23.2 | 76.4 / 63.8 | 55.8 / 54.6 | 7046 | 45.4 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.2%) | +11.6% | +16.2% | +27.7%
SplitAHUs-VAV-1-FanDualDuct | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.8 | 149.1 | 14.1 | 76.4 / 63.8 | 55.8 / 54.6 | 7046 | 45.4 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.2%) | +11.6% | +16.2% | +27.7%
SplitAHUs-VAV-2-FanDualDuct | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.5 | 149.1 | 4.7 | 76.4 / 63.8 | 55.8 / 54.6 | 7046 | 45.3 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.2%) | +11.8% | +16.2% | +27.7%
SplitAHUs-VVT | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.2 | 149.2 | 14.7 | 76.3 / 64.8 | 58.0 / 56.9 | 8289 | 45.2 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.1%) | +12% | +16.1% | +8.6%
TerminalUnits-2-PipeFanCoil | Zone 1 | G-GYM | 861.1 | 36.9 | 30.8 | 4 | 76.3 / 65.6 | 59.6 / 58.6 | 1711 |  | 1 | 41.6281 | 33.9167 | 1599.7544 | 0.3 | No (+10.1%) | +12.8% | +10.1% | -6.5%
| Zone 2 | G-YOGA | 484.4 | 18.3 | 14.9 | 2.2 | 76.5 / 66.1 | 60.1 / 59.1 | 845 |  | 1 | 17.8455 | 15.2523 | 699.2304 | 0.125 | Yes | -2.5% | +2.4% | -17.3%
| Zone 3 | G-HALL | 818.1 | 30.1 | 24.4 | 3.2 | 76.5 / 66.1 | 60.0 / 59.1 | 1376 |  | 1 | 30.4363 | 26.0346 | 1199.2861 | 0.2 | Yes | +1.1% | +6.7% | -12.8%
| Zone 4 | G-TOILET | 247.6 | 7.7 | 6 | 0.7 | 76.1 / 65.9 | 59.3 / 58.3 | 330 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | Yes | +0.1% | +0.7% | -24.2%
| Zone 5 | G-BACK KITCHEN | 161.5 | 13.6 | 12.4 | 0.2 | 75.9 / 64.5 | 58.9 / 57.8 | 675 |  | 1 | 16.4806 | 13.1367 | 599.643 | 0.08 | Yes | +21.2% | +5.9% | -11.2%
| Zone 6 | G-CAFE HALL | 807.3 | 37.2 | 31.4 | 4.4 | 76.4 / 65.6 | 59.7 / 58.7 | 1741 |  | 1 | 41.6281 | 33.9167 | 1599.7544 | 0.3 | Yes | +11.9% | +8% | -8.1%
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 11.8 | 11.3 | 0.2 | 75.9 / 64.1 | 58.9 / 57.7 | 613 |  | 1 | 16.4806 | 13.1367 | 599.643 | 0.08 | No (+16.3%) | +39.7% | +16.3% | -2.2%
| Zone 8 | G-ICT | 75.3 | 10 | 9.5 | 0.1 | 75.9 / 64.3 | 58.9 / 57.8 | 515 |  | 1 | 13.6486 | 10.8506 | 500.0557 | 0.08 | No (+14.2%) | +36.5% | +14.2% | -2.9%
| Zone 9 | B-PUMP ROOM | 183 | 4.5 | 3.2 | 0 | 76.2 / 66.5 | 59.3 / 58.4 | 177 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+88.7%) | +71.4% | +88.7% | +41.3%
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 4.5 | 3.4 | 0 | 76.1 / 66.2 | 59.5 / 58.6 | 190 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+77.6%) | +71.4% | +77.6% | +31.6%
| Zone 11 | G-SECURITY ROOM | 53.8 | 2.7 | 2.3 | 0.2 | 76.5 / 65.8 | 60.2 / 59.2 | 133 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+162.6%) | +185.6% | +162.6% | +88%
| Zone 12 | G-WASTE ROOM | 32.3 | 1 | 0.7 | 0 | 76.0 / 66.4 | 60.3 / 59.4 | 44 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+762.8%) | +671.1% | +762.8% | +468.2%
| TOTAL | All zones | 3939.6 | 178.3 | 150.3 | 15.2 |  |  | 8350 | N/A | 12 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
TerminalUnits-4-PipeFanCoil | Zone 1 | G-GYM | 861.1 | 36.9 | 30.8 | 4 | 76.3 / 65.6 | 59.6 / 58.6 | 1711 |  | 1 | 41.6281 | 33.9167 | 1599.7544 | 0.3 | No (+10.1%) | +12.8% | +10.1% | -6.5%
| Zone 2 | G-YOGA | 484.4 | 18.3 | 14.9 | 2.2 | 76.5 / 66.1 | 60.1 / 59.1 | 845 |  | 1 | 17.8455 | 15.2523 | 699.2304 | 0.125 | Yes | -2.5% | +2.4% | -17.3%
| Zone 3 | G-HALL | 818.1 | 30.1 | 24.4 | 3.2 | 76.5 / 66.1 | 60.0 / 59.1 | 1376 |  | 1 | 30.4363 | 26.0346 | 1199.2861 | 0.2 | Yes | +1.1% | +6.7% | -12.8%
| Zone 4 | G-TOILET | 247.6 | 7.7 | 6 | 0.7 | 76.1 / 65.9 | 59.3 / 58.3 | 330 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | Yes | +0.1% | +0.7% | -24.2%
| Zone 5 | G-BACK KITCHEN | 161.5 | 13.6 | 12.4 | 0.2 | 75.9 / 64.5 | 58.9 / 57.8 | 675 |  | 1 | 16.4806 | 13.1367 | 599.643 | 0.08 | Yes | +21.2% | +5.9% | -11.2%
| Zone 6 | G-CAFE HALL | 807.3 | 37.2 | 31.4 | 4.4 | 76.4 / 65.6 | 59.7 / 58.7 | 1741 |  | 1 | 41.6281 | 33.9167 | 1599.7544 | 0.3 | Yes | +11.9% | +8% | -8.1%
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 11.8 | 11.3 | 0.2 | 75.9 / 64.1 | 58.9 / 57.7 | 613 |  | 1 | 16.4806 | 13.1367 | 599.643 | 0.08 | No (+16.3%) | +39.7% | +16.3% | -2.2%
| Zone 8 | G-ICT | 75.3 | 10 | 9.5 | 0.1 | 75.9 / 64.3 | 58.9 / 57.8 | 515 |  | 1 | 13.6486 | 10.8506 | 500.0557 | 0.08 | No (+14.2%) | +36.5% | +14.2% | -2.9%
| Zone 9 | B-PUMP ROOM | 183 | 4.5 | 3.2 | 0 | 76.2 / 66.5 | 59.3 / 58.4 | 177 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+88.7%) | +71.4% | +88.7% | +41.3%
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 4.5 | 3.4 | 0 | 76.1 / 66.2 | 59.5 / 58.6 | 190 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+77.6%) | +71.4% | +77.6% | +31.6%
| Zone 11 | G-SECURITY ROOM | 53.8 | 2.7 | 2.3 | 0.2 | 76.5 / 65.8 | 60.2 / 59.2 | 133 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+162.6%) | +185.6% | +162.6% | +88%
| Zone 12 | G-WASTE ROOM | 32.3 | 1 | 0.7 | 0 | 76.0 / 66.4 | 60.3 / 59.4 | 44 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+762.8%) | +671.1% | +762.8% | +468.2%
| TOTAL | All zones | 3939.6 | 178.3 | 150.3 | 15.2 |  |  | 8350 | N/A | 12 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
TerminalUnits-ActiveChilledBeam | Zone 1 | G-GYM | 861.1 | 17.4 | 17.4 | 13.7 | 76.6 / 63.1 | 62.4 / 58.0 | 1711 |  | 1 | 25.8299 | 20.9164 | 1000.1114 | 0.15 | No (+20.2%) | +48.4% | +20.2% | -41.5%
| Zone 2 | G-YOGA | 484.4 | 8.7 | 8.7 | 6.9 | 76.2 / 63.5 | 61.9 / 58.3 | 845 |  | 1 | 13.6486 | 10.8506 | 500.0557 | 0.08 | No (+24.7%) | +56.9% | +24.7% | -40.8%
| Zone 3 | G-HALL | 818.1 | 14.2 | 14.2 | 10.1 | 76.2 / 63.5 | 61.9 / 58.4 | 1376 |  | 1 | 17.8455 | 15.2523 | 699.2304 | 0.125 | Yes | +25.7% | +7.4% | -49.2%
| Zone 4 | G-TOILET | 247.6 | 3.5 | 3.5 | 2.5 | 76.1 / 64.5 | 61.3 / 59.3 | 330 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+72.6%) | +120.3% | +72.6% | -24.2%
| Zone 5 | G-BACK KITCHEN | 161.5 | 7.4 | 7.4 | 3.8 | 76.0 / 61.1 | 60.7 / 55.3 | 675 |  | 1 | 10.2023 | 8.3597 | 400.4683 | 0.08 | No (+13.0%) | +37.9% | +13% | -40.7%
| Zone 6 | G-CAFE HALL | 807.3 | 18.5 | 18.5 | 12.7 | 76.0 / 62.7 | 61.2 / 57.3 | 1741 |  | 1 | 25.8299 | 20.9164 | 1000.1114 | 0.15 | No (+13.1%) | +39.6% | +13.1% | -42.6%
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 6.7 | 6.7 | 3.5 | 75.8 / 60.0 | 60.6 / 54.1 | 613 |  | 1 | 8.1209 | 6.756 | 300.881 | 0.05 | Yes | +21.2% | +0.8% | -50.9%
| Zone 8 | G-ICT | 75.3 | 5.7 | 5.7 | 2.9 | 75.8 / 60.3 | 60.5 / 54.4 | 515 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | Yes | +35.3% | +6% | -51.5%
| Zone 9 | B-PUMP ROOM | 183 | 1.9 | 1.9 | 0.9 | 76.1 / 66.1 | 61.2 / 61.1 | 177 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+217.9%) | +305.9% | +217.9% | +41.3%
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 2 | 2 | 1.1 | 76.2 / 64.8 | 61.7 / 59.7 | 190 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+202.0%) | +285.6% | +202% | +31.6%
| Zone 11 | G-SECURITY ROOM | 53.8 | 1.4 | 1.4 | 0.9 | 76.3 / 62.4 | 62.1 / 57.2 | 133 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+331.4%) | +450.8% | +331.4% | +88%
| Zone 12 | G-WASTE ROOM | 32.3 | 0.4 | 0.4 | 0.3 | 76.1 / 64.4 | 62.9 / 59.7 | 44 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+1409.9%) | +1827.9% | +1409.9% | +468.2%
| TOTAL | All zones | 3939.6 | 237.2 | 144.5 | 12.6 |  |  | 8350 | 60.2 | 12 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
TerminalUnits-GroundSourceHeatPu | Zone 1 | G-GYM | 861.1 | 36.9 | 30.8 | 4 | 76.3 / 65.6 | 59.6 / 58.6 | 1711 |  | 1 | 41.6281 | 33.9167 | 1599.7544 | 0.3 | No (+10.1%) | +12.8% | +10.1% | -6.5%
| Zone 2 | G-YOGA | 484.4 | 18.3 | 14.9 | 2.2 | 76.5 / 66.1 | 60.1 / 59.1 | 845 |  | 1 | 17.8455 | 15.2523 | 699.2304 | 0.125 | Yes | -2.5% | +2.4% | -17.3%
| Zone 3 | G-HALL | 818.1 | 30.1 | 24.4 | 3.2 | 76.5 / 66.1 | 60.0 / 59.1 | 1376 |  | 1 | 30.4363 | 26.0346 | 1199.2861 | 0.2 | Yes | +1.1% | +6.7% | -12.8%
| Zone 4 | G-TOILET | 247.6 | 7.7 | 6 | 0.7 | 76.1 / 65.9 | 59.3 / 58.3 | 330 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | Yes | +0.1% | +0.7% | -24.2%
| Zone 5 | G-BACK KITCHEN | 161.5 | 13.6 | 12.4 | 0.2 | 75.9 / 64.5 | 58.9 / 57.8 | 675 |  | 1 | 16.4806 | 13.1367 | 599.643 | 0.08 | Yes | +21.2% | +5.9% | -11.2%
| Zone 6 | G-CAFE HALL | 807.3 | 37.2 | 31.4 | 4.4 | 76.4 / 65.6 | 59.7 / 58.7 | 1741 |  | 1 | 41.6281 | 33.9167 | 1599.7544 | 0.3 | Yes | +11.9% | +8% | -8.1%
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 11.8 | 11.3 | 0.2 | 75.9 / 64.1 | 58.9 / 57.7 | 613 |  | 1 | 16.4806 | 13.1367 | 599.643 | 0.08 | No (+16.3%) | +39.7% | +16.3% | -2.2%
| Zone 8 | G-ICT | 75.3 | 10 | 9.5 | 0.1 | 75.9 / 64.3 | 58.9 / 57.8 | 515 |  | 1 | 13.6486 | 10.8506 | 500.0557 | 0.08 | No (+14.2%) | +36.5% | +14.2% | -2.9%
| Zone 9 | B-PUMP ROOM | 183 | 4.5 | 3.2 | 0 | 76.2 / 66.5 | 59.3 / 58.4 | 177 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+88.7%) | +71.4% | +88.7% | +41.3%
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 4.5 | 3.4 | 0 | 76.1 / 66.2 | 59.5 / 58.6 | 190 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+77.6%) | +71.4% | +77.6% | +31.6%
| Zone 11 | G-SECURITY ROOM | 53.8 | 2.7 | 2.3 | 0.2 | 76.5 / 65.8 | 60.2 / 59.2 | 133 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+162.6%) | +185.6% | +162.6% | +88%
| Zone 12 | G-WASTE ROOM | 32.3 | 1 | 0.7 | 0 | 76.0 / 66.4 | 60.3 / 59.4 | 44 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+762.8%) | +671.1% | +762.8% | +468.2%
| TOTAL | All zones | 3939.6 | 178.3 | 150.3 | 15.2 |  |  | 8350 | N/A | 12 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
TerminalUnits-GroundwaterSourceH | Zone 1 | G-GYM | 861.1 | 36.9 | 30.8 | 4 | 76.3 / 65.6 | 59.6 / 58.6 | 1711 |  | 1 | 41.6281 | 33.9167 | 1599.7544 | 0.3 | No (+10.1%) | +12.8% | +10.1% | -6.5%
| Zone 2 | G-YOGA | 484.4 | 18.3 | 14.9 | 2.2 | 76.5 / 66.1 | 60.1 / 59.1 | 845 |  | 1 | 17.8455 | 15.2523 | 699.2304 | 0.125 | Yes | -2.5% | +2.4% | -17.3%
| Zone 3 | G-HALL | 818.1 | 30.1 | 24.4 | 3.2 | 76.5 / 66.1 | 60.0 / 59.1 | 1376 |  | 1 | 30.4363 | 26.0346 | 1199.2861 | 0.2 | Yes | +1.1% | +6.7% | -12.8%
| Zone 4 | G-TOILET | 247.6 | 7.7 | 6 | 0.7 | 76.1 / 65.9 | 59.3 / 58.3 | 330 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | Yes | +0.1% | +0.7% | -24.2%
| Zone 5 | G-BACK KITCHEN | 161.5 | 13.6 | 12.4 | 0.2 | 75.9 / 64.5 | 58.9 / 57.8 | 675 |  | 1 | 16.4806 | 13.1367 | 599.643 | 0.08 | Yes | +21.2% | +5.9% | -11.2%
| Zone 6 | G-CAFE HALL | 807.3 | 37.2 | 31.4 | 4.4 | 76.4 / 65.6 | 59.7 / 58.7 | 1741 |  | 1 | 41.6281 | 33.9167 | 1599.7544 | 0.3 | Yes | +11.9% | +8% | -8.1%
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 11.8 | 11.3 | 0.2 | 75.9 / 64.1 | 58.9 / 57.7 | 613 |  | 1 | 16.4806 | 13.1367 | 599.643 | 0.08 | No (+16.3%) | +39.7% | +16.3% | -2.2%
| Zone 8 | G-ICT | 75.3 | 10 | 9.5 | 0.1 | 75.9 / 64.3 | 58.9 / 57.8 | 515 |  | 1 | 13.6486 | 10.8506 | 500.0557 | 0.08 | No (+14.2%) | +36.5% | +14.2% | -2.9%
| Zone 9 | B-PUMP ROOM | 183 | 4.5 | 3.2 | 0 | 76.2 / 66.5 | 59.3 / 58.4 | 177 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+88.7%) | +71.4% | +88.7% | +41.3%
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 4.5 | 3.4 | 0 | 76.1 / 66.2 | 59.5 / 58.6 | 190 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+77.6%) | +71.4% | +77.6% | +31.6%
| Zone 11 | G-SECURITY ROOM | 53.8 | 2.7 | 2.3 | 0.2 | 76.5 / 65.8 | 60.2 / 59.2 | 133 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+162.6%) | +185.6% | +162.6% | +88%
| Zone 12 | G-WASTE ROOM | 32.3 | 1 | 0.7 | 0 | 76.0 / 66.4 | 60.3 / 59.4 | 44 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+762.8%) | +671.1% | +762.8% | +468.2%
| TOTAL | All zones | 3939.6 | 178.3 | 150.3 | 15.2 |  |  | 8350 | N/A | 12 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
TerminalUnits-InductionBeam | Zone 1 | G-GYM | 861.1 | 20.6 | 20.2 | 10.2 | 75.9 / 64.5 | 59.5 / 58.5 | 1711 |  | 1 | 25.8299 | 20.9164 | 1000.1114 | 0.15 | Yes | +25.4% | +3.5% | -41.5%
| Zone 2 | G-YOGA | 484.4 | 10.7 | 10.2 | 5.6 | 76.2 / 64.8 | 59.5 / 58.5 | 845 |  | 1 | 13.6486 | 10.8506 | 500.0557 | 0.08 | Yes | +27.6% | +6.4% | -40.8%
| Zone 3 | G-HALL | 818.1 | 16.9 | 16.2 | 8.2 | 76.4 / 65.1 | 60.1 / 59.1 | 1376 |  | 1 | 19.6198 | 16.9925 | 900.524 | 0.15 | Yes | +16.1% | +4.9% | -34.6%
| Zone 4 | G-TOILET | 247.6 | 4.5 | 4 | 1.7 | 76.2 / 65.1 | 59.5 / 58.5 | 330 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+51.0%) | +71.4% | +51% | -24.2%
| Zone 5 | G-BACK KITCHEN | 161.5 | 8.7 | 8.7 | 2.6 | 75.8 / 63.1 | 57.9 / 56.5 | 675 |  | 1 | 13.6486 | 10.8506 | 500.0557 | 0.08 | No (+24.7%) | +56.9% | +24.7% | -25.9%
| Zone 6 | G-CAFE HALL | 807.3 | 20.7 | 20.7 | 9.9 | 76.6 / 64.8 | 60.1 / 58.9 | 1741 |  | 1 | 25.8299 | 20.9164 | 1000.1114 | 0.15 | Yes | +24.8% | +1% | -42.6%
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 7.8 | 7.8 | 2.5 | 75.9 / 62.2 | 58.2 / 55.5 | 613 |  | 1 | 10.2023 | 8.3597 | 400.4683 | 0.08 | Yes | +30.8% | +7.2% | -34.7%
| Zone 8 | G-ICT | 75.3 | 6.6 | 6.6 | 1.7 | 75.9 / 62.5 | 58.2 / 55.9 | 515 |  | 1 | 8.1209 | 6.756 | 300.881 | 0.05 | Yes | +23% | +2.4% | -41.6%
| Zone 9 | B-PUMP ROOM | 183 | 2.7 | 2.2 | 0.6 | 76.2 / 65.5 | 58.9 / 58.0 | 177 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+174.5%) | +185.6% | +174.5% | +41.3%
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 2.7 | 2.3 | 0.7 | 76.1 / 65.1 | 59.1 / 58.1 | 190 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+162.6%) | +185.6% | +162.6% | +31.6%
| Zone 11 | G-SECURITY ROOM | 53.8 | 1.6 | 1.6 | 0.6 | 76.3 / 64.3 | 59.8 / 58.5 | 133 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+277.5%) | +382% | +277.5% | +88%
| Zone 12 | G-WASTE ROOM | 32.3 | 0.5 | 0.5 | 0.2 | 76.0 / 65.4 | 60.3 / 59.4 | 44 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+1107.9%) | +1442.3% | +1107.9% | +468.2%
| TOTAL | All zones | 3939.6 | 212.6 | 131.8 | 11.8 |  |  | 8350 | 54 | 12 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
TerminalUnits-PackagedDXFanCoil | Zone 1 | G-GYM | 861.1 | 36.9 | 30.8 | 4 | 76.3 / 65.6 | 59.6 / 58.6 | 1711 |  | 1 | 41.6281 | 33.9167 | 1599.7544 | 0.3 | No (+10.1%) | +12.8% | +10.1% | -6.5%
| Zone 2 | G-YOGA | 484.4 | 18.3 | 14.9 | 2.2 | 76.5 / 66.1 | 60.1 / 59.1 | 845 |  | 1 | 17.8455 | 15.2523 | 699.2304 | 0.125 | Yes | -2.5% | +2.4% | -17.3%
| Zone 3 | G-HALL | 818.1 | 30.1 | 24.4 | 3.2 | 76.5 / 66.1 | 60.0 / 59.1 | 1376 |  | 1 | 30.4363 | 26.0346 | 1199.2861 | 0.2 | Yes | +1.1% | +6.7% | -12.8%
| Zone 4 | G-TOILET | 247.6 | 7.7 | 6 | 0.7 | 76.1 / 65.9 | 59.3 / 58.3 | 330 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | Yes | +0.1% | +0.7% | -24.2%
| Zone 5 | G-BACK KITCHEN | 161.5 | 13.6 | 12.4 | 0.2 | 75.9 / 64.5 | 58.9 / 57.8 | 675 |  | 1 | 16.4806 | 13.1367 | 599.643 | 0.08 | Yes | +21.2% | +5.9% | -11.2%
| Zone 6 | G-CAFE HALL | 807.3 | 37.2 | 31.4 | 4.4 | 76.4 / 65.6 | 59.7 / 58.7 | 1741 |  | 1 | 41.6281 | 33.9167 | 1599.7544 | 0.3 | Yes | +11.9% | +8% | -8.1%
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 11.8 | 11.3 | 0.2 | 75.9 / 64.1 | 58.9 / 57.7 | 613 |  | 1 | 16.4806 | 13.1367 | 599.643 | 0.08 | No (+16.3%) | +39.7% | +16.3% | -2.2%
| Zone 8 | G-ICT | 75.3 | 10 | 9.5 | 0.1 | 75.9 / 64.3 | 58.9 / 57.8 | 515 |  | 1 | 13.6486 | 10.8506 | 500.0557 | 0.08 | No (+14.2%) | +36.5% | +14.2% | -2.9%
| Zone 9 | B-PUMP ROOM | 183 | 4.5 | 3.2 | 0 | 76.2 / 66.5 | 59.3 / 58.4 | 177 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+88.7%) | +71.4% | +88.7% | +41.3%
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 4.5 | 3.4 | 0 | 76.1 / 66.2 | 59.5 / 58.6 | 190 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+77.6%) | +71.4% | +77.6% | +31.6%
| Zone 11 | G-SECURITY ROOM | 53.8 | 2.7 | 2.3 | 0.2 | 76.5 / 65.8 | 60.2 / 59.2 | 133 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+162.6%) | +185.6% | +162.6% | +88%
| Zone 12 | G-WASTE ROOM | 32.3 | 1 | 0.7 | 0 | 76.0 / 66.4 | 60.3 / 59.4 | 44 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+762.8%) | +671.1% | +762.8% | +468.2%
| TOTAL | All zones | 3939.6 | 178.3 | 150.3 | 15.2 |  |  | 8350 | N/A | 12 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
TerminalUnits-SplitDXFanCoil | Zone 1 | G-GYM | 861.1 | 36.9 | 30.8 | 4 | 76.3 / 65.6 | 59.6 / 58.6 | 1711 |  | 1 | 41.6281 | 33.9167 | 1599.7544 | 0.3 | No (+10.1%) | +12.8% | +10.1% | -6.5%
| Zone 2 | G-YOGA | 484.4 | 18.3 | 14.9 | 2.2 | 76.5 / 66.1 | 60.1 / 59.1 | 845 |  | 1 | 17.8455 | 15.2523 | 699.2304 | 0.125 | Yes | -2.5% | +2.4% | -17.3%
| Zone 3 | G-HALL | 818.1 | 30.1 | 24.4 | 3.2 | 76.5 / 66.1 | 60.0 / 59.1 | 1376 |  | 1 | 30.4363 | 26.0346 | 1199.2861 | 0.2 | Yes | +1.1% | +6.7% | -12.8%
| Zone 4 | G-TOILET | 247.6 | 7.7 | 6 | 0.7 | 76.1 / 65.9 | 59.3 / 58.3 | 330 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | Yes | +0.1% | +0.7% | -24.2%
| Zone 5 | G-BACK KITCHEN | 161.5 | 13.6 | 12.4 | 0.2 | 75.9 / 64.5 | 58.9 / 57.8 | 675 |  | 1 | 16.4806 | 13.1367 | 599.643 | 0.08 | Yes | +21.2% | +5.9% | -11.2%
| Zone 6 | G-CAFE HALL | 807.3 | 37.2 | 31.4 | 4.4 | 76.4 / 65.6 | 59.7 / 58.7 | 1741 |  | 1 | 41.6281 | 33.9167 | 1599.7544 | 0.3 | Yes | +11.9% | +8% | -8.1%
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 11.8 | 11.3 | 0.2 | 75.9 / 64.1 | 58.9 / 57.7 | 613 |  | 1 | 16.4806 | 13.1367 | 599.643 | 0.08 | No (+16.3%) | +39.7% | +16.3% | -2.2%
| Zone 8 | G-ICT | 75.3 | 10 | 9.5 | 0.1 | 75.9 / 64.3 | 58.9 / 57.8 | 515 |  | 1 | 13.6486 | 10.8506 | 500.0557 | 0.08 | No (+14.2%) | +36.5% | +14.2% | -2.9%
| Zone 9 | B-PUMP ROOM | 183 | 4.5 | 3.2 | 0 | 76.2 / 66.5 | 59.3 / 58.4 | 177 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+88.7%) | +71.4% | +88.7% | +41.3%
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 4.5 | 3.4 | 0 | 76.1 / 66.2 | 59.5 / 58.6 | 190 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+77.6%) | +71.4% | +77.6% | +31.6%
| Zone 11 | G-SECURITY ROOM | 53.8 | 2.7 | 2.3 | 0.2 | 76.5 / 65.8 | 60.2 / 59.2 | 133 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+162.6%) | +185.6% | +162.6% | +88%
| Zone 12 | G-WASTE ROOM | 32.3 | 1 | 0.7 | 0 | 76.0 / 66.4 | 60.3 / 59.4 | 44 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+762.8%) | +671.1% | +762.8% | +468.2%
| TOTAL | All zones | 3939.6 | 178.3 | 150.3 | 15.2 |  |  | 8350 | N/A | 12 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
TerminalUnits-VRF | Zone 1 | G-GYM | 861.1 | 36.9 | 30.8 | 4 | 76.3 / 65.6 | 59.6 / 58.6 | 1711 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Zone 2 | G-YOGA | 484.4 | 18.3 | 14.9 | 2.2 | 76.5 / 66.1 | 60.1 / 59.1 | 845 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Zone 3 | G-HALL | 818.1 | 30.1 | 24.4 | 3.2 | 76.5 / 66.1 | 60.0 / 59.1 | 1376 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Zone 4 | G-TOILET | 247.6 | 7.7 | 6 | 0.7 | 76.1 / 65.9 | 59.3 / 58.3 | 330 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Zone 5 | G-BACK KITCHEN | 161.5 | 13.6 | 12.4 | 0.2 | 75.9 / 64.5 | 58.9 / 57.8 | 675 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Zone 6 | G-CAFE HALL | 807.3 | 37.2 | 31.4 | 4.4 | 76.4 / 65.6 | 59.7 / 58.7 | 1741 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 11.8 | 11.3 | 0.2 | 75.9 / 64.1 | 58.9 / 57.7 | 613 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Zone 8 | G-ICT | 75.3 | 10 | 9.5 | 0.1 | 75.9 / 64.3 | 58.9 / 57.8 | 515 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Zone 9 | B-PUMP ROOM | 183 | 4.5 | 3.2 | 0 | 76.2 / 66.5 | 59.3 / 58.4 | 177 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 4.5 | 3.4 | 0 | 76.1 / 66.2 | 59.5 / 58.6 | 190 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Zone 11 | G-SECURITY ROOM | 53.8 | 2.7 | 2.3 | 0.2 | 76.5 / 65.8 | 60.2 / 59.2 | 133 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| Zone 12 | G-WASTE ROOM | 32.3 | 1 | 0.7 | 0 | 76.0 / 66.4 | 60.3 / 59.4 | 44 |  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| TOTAL | All zones | 3939.6 | 178.3 | 150.3 | 15.2 |  |  | 8350 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
TerminalUnits-WaterSourceHeatPum | Zone 1 | G-GYM | 861.1 | 36.9 | 30.8 | 4 | 76.3 / 65.6 | 59.6 / 58.6 | 1711 |  | 1 | 41.6281 | 33.9167 | 1599.7544 | 0.3 | No (+10.1%) | +12.8% | +10.1% | -6.5%
| Zone 2 | G-YOGA | 484.4 | 18.3 | 14.9 | 2.2 | 76.5 / 66.1 | 60.1 / 59.1 | 845 |  | 1 | 17.8455 | 15.2523 | 699.2304 | 0.125 | Yes | -2.5% | +2.4% | -17.3%
| Zone 3 | G-HALL | 818.1 | 30.1 | 24.4 | 3.2 | 76.5 / 66.1 | 60.0 / 59.1 | 1376 |  | 1 | 30.4363 | 26.0346 | 1199.2861 | 0.2 | Yes | +1.1% | +6.7% | -12.8%
| Zone 4 | G-TOILET | 247.6 | 7.7 | 6 | 0.7 | 76.1 / 65.9 | 59.3 / 58.3 | 330 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | Yes | +0.1% | +0.7% | -24.2%
| Zone 5 | G-BACK KITCHEN | 161.5 | 13.6 | 12.4 | 0.2 | 75.9 / 64.5 | 58.9 / 57.8 | 675 |  | 1 | 16.4806 | 13.1367 | 599.643 | 0.08 | Yes | +21.2% | +5.9% | -11.2%
| Zone 6 | G-CAFE HALL | 807.3 | 37.2 | 31.4 | 4.4 | 76.4 / 65.6 | 59.7 / 58.7 | 1741 |  | 1 | 41.6281 | 33.9167 | 1599.7544 | 0.3 | Yes | +11.9% | +8% | -8.1%
| Zone 7 | G-ELECTRICAL ROOM | 64.6 | 11.8 | 11.3 | 0.2 | 75.9 / 64.1 | 58.9 / 57.7 | 613 |  | 1 | 16.4806 | 13.1367 | 599.643 | 0.08 | No (+16.3%) | +39.7% | +16.3% | -2.2%
| Zone 8 | G-ICT | 75.3 | 10 | 9.5 | 0.1 | 75.9 / 64.3 | 58.9 / 57.8 | 515 |  | 1 | 13.6486 | 10.8506 | 500.0557 | 0.08 | No (+14.2%) | +36.5% | +14.2% | -2.9%
| Zone 9 | B-PUMP ROOM | 183 | 4.5 | 3.2 | 0 | 76.2 / 66.5 | 59.3 / 58.4 | 177 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+88.7%) | +71.4% | +88.7% | +41.3%
| Zone 10 | B-IRRIGATION ROOM | 150.7 | 4.5 | 3.4 | 0 | 76.1 / 66.2 | 59.5 / 58.6 | 190 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+77.6%) | +71.4% | +77.6% | +31.6%
| Zone 11 | G-SECURITY ROOM | 53.8 | 2.7 | 2.3 | 0.2 | 76.5 / 65.8 | 60.2 / 59.2 | 133 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+162.6%) | +185.6% | +162.6% | +88%
| Zone 12 | G-WASTE ROOM | 32.3 | 1 | 0.7 | 0 | 76.0 / 66.4 | 60.3 / 59.4 | 44 |  | 1 | 7.7114 | 6.0395 | 250.0278 | 0.05 | No (+762.8%) | +671.1% | +762.8% | +468.2%
| TOTAL | All zones | 3939.6 | 178.3 | 150.3 | 15.2 |  |  | 8350 | N/A | 12 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Undefined-CAV-SingleZone | Zone 1 | B-IRRIGATION ROOM, B-PUMP ROOM, B-SWIM P PUMP ROOM, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-GYM, G-HALL, G-ICT, G-SECURITY ROOM, G-TOILET, G-WASTE ROOM and G-YOGA | 4342.2 | 185.3 | 156.3 | 10.6 | 76.6 / 65.9 | 60.2 / 59.1 | 8825 | 42.7 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+10.8%) | +7.7% | +10.8% | +2%
Undefined-CAV-TerminalReheat | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 175.4 | 145.6 | 306.5 | 74.0 / 62.6 | 55.0 / 53.9 | 7097 | 44.5 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+19.0%) | +13.7% | +19% | +26.8%
Undefined-VAV | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.9 | 149.1 | 23.2 | 76.3 / 63.4 | 55.0 / 53.8 | 7046 | 45.4 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.2%) | +11.5% | +16.2% | +27.7%
Undefined-VVT | Zone 1, Zone 2, Zone 3, Zone 4, Zone 5, Zone 6, Zone 7, Zone 8, Zone 9, Zone 10, Zone 11 and Zone 12 | G-GYM, G-YOGA, G-HALL, G-TOILET, G-BACK KITCHEN, G-CAFE HALL, G-ELECTRICAL ROOM, G-ICT, B-PUMP ROOM, B-IRRIGATION ROOM, G-SECURITY ROOM and G-WASTE ROOM | 3939.6 | 178.2 | 149.2 | 14.7 | 76.3 / 64.8 | 58.0 / 56.9 | 8289 | 45.2 | 3 | 66.5026 | 57.7334 | 3000.3341 | 0.8 | No (+16.1%) | +12% | +16.1% | +8.6%
OVERALL | All systems | Installed (Qty × each) | 187979.4 | 7976.9 | 7058.4 | 2238.5 | N/A | N/A | 337109 | N/A | 210 | 8603.408 | 7369.0317 | 373619.992 | 93.43 | N/A | N/A | N/A | N/A

## Run Inputs
Run input | Value
Machine Type | Chilled Water
Weather / Delta T | Delta_T5
Coil Temperature | 24/17
Manufacturer | CARRIER
TU grain | One machine per zone
Match field | Sensible load
Tolerance mode | + oversize only
Tolerance (%) | 10
Cap field | (none)
Cap value | (none)
Report units | IP
Zones selected | 142
Zones outside tolerance | 98
Jobs skipped | 16 — 13 VRF (extracted to Excel only); 3 DOAS / no cooling coil
Max units per job | 10
Other coil short flag | more than 10 % below design (the Total or Sensible coil field a pick was not sized on)
Jobs with other coil short | 0
Columns omitted (all 0) | Fresh Air: column omitted because HAP printed 0 CFM in every row that carries a value.