Kitchen Hood Extract Calculation

ASHRAE 154-2016 · Applications 2019 Ch 34 · Preliminary / approximate calculations

Hood reference: KH-01

| Project Information |  |
| --- | --- |
| Project Name | Marina Commercial Tower |
| Project No. | MCT-2026-MEP-001 |
| Revision | P2 |
| Client | — |
| Prepared by | Hussein Ragab |
| Checked by | — |
| Date | 2026-10-20 |

Values in this report are displayed in SI (metric) units.  Rates printed by a standard (cfm per linear foot, L/s per metre) are shown as printed and are never re-converted.

# 1.  Methodology

Exhaust flow is taken from the appliance duty class and the hood style, applied per linear metre of hood. Type II hoods use the minimum net exhaust rates printed in ANSI/ASHRAE Standard 154-2016 Table 4. Type I hoods must be listed to UL 710 (154-2016 # 4.1.1); where no listed rate is supplied, the typical range for listed hoods in ASHRAE Handbook — HVAC Applications 2019 Chapter 34 Table 5 is used at the selected design point. The duty class is that of the heaviest appliance beneath the hood (Type I: Chapter 34 p. 34.13; Type II: 154-2016 # 4.4.1).

# 2.  Inputs

Hood

| Parameter | Value |
| --- | --- |
| Tag | KH-01 |
| Style | Wall-mounted canopy |
| Type | Type I |
| Length | 4.500 m |
| Duty | medium |
| Rate | 300 cfm/ft |
| Rate basis | typical listed-hood range (Applications 2019 Ch 34 Table 5) |
| Required extract flow | 2,090 L/s |
| Minimum overhangs | end 152 mm, front 305 mm |

# 3.  Assumptions

The duty class entered is that of the heaviest-duty appliance installed beneath the hood.

Hood length is the overall length of the hood, not the appliance line-up.

Where a manufacturer's UL 710 listed rate is entered, that rate governs over any tabulated typical value.

Make-up air percentage is an engineering input: ASHRAE 154-2016 Section 6 sets replacement-air principles but publishes no percentage.

# 4.  Step-by-Step Calculation

Step 1: Hood duty classification

Formula: duty = heaviest duty of appliances under hood (Ch 34 p. 34.13; duty groups per 154-2016 Table 1)

Substitution: appliances = (duty set directly)

Result: medium

Step 2: Typical listed Type I hood exhaust rate

Formula: rate from Ch 34 Table 5 range (design point: high)

Substitution: hood_style = Wall-mounted canopy; duty = medium; range [cfm/ft] = 200-300; rate [cfm/ft] = 300

Result: 300 cfm/ft

Step 3: Exhaust flow

Formula: Q = rate x hood length

Substitution: rate [cfm/ft] = 300; rate [m3/s per m] = 0.46452; L [m] = 4.5

Result: 2.0903 m3/s

# 5.  Results

Hood mounting (ASHRAE 154-2016 # 4.3.3)

| Parameter | Value |
| --- | --- |
| Front lower edge above cooking surface | max 1219 mm |
| Front lower edge above finished floor | min 1981 mm |
| Inside hood height | min 610 mm |
| Clearance to combustibles (# 4.8.1, Type I) | min 457 mm unless listed to a reduced clearance |
| Basis | 154-2016 # 4.3.3.1 — reported, not checked |
| Scope | # 4.3 is headed Type II Hood Sizing; applied to Type I by engineering judgement |

Make-up air

| Parameter | Value |
| --- | --- |
| Dedicated make-up | 1,777 L/s |
| Transfer / infiltration (balance) | 313 L/s |
| Net exhaust | 2,090 L/s |
| Internal-discharge limit (# 4.5.1) | 209 L/s — within |
| Terminal velocity at hood lip (# 6.1.1) | max 0.25 m/s (50 fpm as printed) |

Extract duct

| Parameter | Value |
| --- | --- |
| Required area | 0.249 m² |
| Design velocity | 8.40 m/s |
| Candidate size | 500 x 500 mm — 8.36 m/s |
| Candidate size | 550 x 500 mm — 7.60 m/s |
| Candidate size | 600 x 450 mm — 7.74 m/s |

Energy — ASHRAE 90.1 (advisory)

| Parameter | Value |
| --- | --- |
| Position | not applicable — facility total 2,091 L/s is below 2360 L/s, so Table 6.5.7.2.2 is not assessed (90.1-2022 SI # 6.5.7.2.2) |

# 6.  Notes

⚠ Advisory

• ASHRAE 154-2016 # 4.1.1: Type I hoods must be listed (UL 710/710B/710C) and installed per their listing; typical rates are design guidance, the listing governs.

• Grease removal devices are not sized by this tool: ASHRAE 154-2016 # 4.6.1 requires them in accordance with the hood's listing, and the standard publishes no filter face velocity — take the filter count and velocity from the listing / manufacturer's data for the extract flow above.

• ASHRAE 154-2016 # 6.1.1: terminal velocity of air introduced near the hood shall not exceed 50 fpm (0.25 m/s) at the hood's lowest edges. # 6.2.1 permits transfer air from areas other than the kitchen as replacement air, and Addendum m (2021) requires that transfer air to meet the air-classification requirements of ASHRAE 62.1 (the addendum's foreword treats kitchen replacement air as 62.1 Class 2 air); transfer-air openings are sized for 0.381 m/s (75 fpm) on free area (# 6.1.2).

• AHJ basis: Make-up air band minimum 75 % of extract (default)

• AHJ basis: Make-up air band maximum 95 % of extract (default)

• ASHRAE 90.1 figures are reported as an energy advisory only. The extract flow is as required by the governing ventilation standard and is not reduced to meet them.

# R.  Reference Standards

ANSI/ASHRAE Standard 154-2016 — Ventilation for Commercial Cooking Operations — hood type, appliance duty classification, Type II net exhaust rates, overhangs, internal-discharge make-up limit, duct velocity minimum

ASHRAE Handbook - HVAC Applications 2019, Ch 34 — Kitchen Ventilation — typical exhaust flow rates for listed Type I hoods by hood style and appliance duty

ANSI/ASHRAE/IES Standard 90.1-2022 (SI edition) — Energy Standard — maximum net exhaust flow rate per linear metre of hood (advisory in this tool)

Hood Extract Calculations — Hussein Ragab