## Hood
KITCHEN HOOD EXTRACT · ANSI/ASHRAE 154-2016 + APPLICATIONS 2019 CH 34 · PRELIMINARY / APPROXIMATE CALCULATIONS
Hood reference: KH-01
Project: Marina Commercial Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: - ¦ By: Hussein Ragab ¦ Chkd: - ¦ Rev: P2 ¦ Date: 2026-10-20
Units: SI ¦ rates printed by a standard (cfm per linear foot, L/s per metre) are shown as printed and are never re-converted
Hood
Tag | KH-01
Style | Wall-mounted canopy
Type | Type I
Length | 4.5 | m
Duty | medium
Rate | 300 | cfm/ft
Rate basis | typical listed-hood range (Applications 2019 Ch 34 Table 5)
Required extract flow | 2090 | L/s
Minimum overhangs | end 152 mm, front 305 mm
Hood mounting (ASHRAE 154-2016 # 4.3.3)
Front lower edge above cooking surface | max 1219 mm
Front lower edge above finished floor | min 1981 mm
Inside hood height | min 610 mm
Clearance to combustibles (# 4.8.1, Type I) | min 457 mm unless listed to a reduced clearance
Basis | 154-2016 # 4.3.3.1 — reported, not checked
Scope | # 4.3 is headed Type II Hood Sizing; applied to Type I by engineering judgement
Make-up air
Dedicated make-up | 1777 | L/s
Transfer / infiltration (balance) | 313 | L/s
Net exhaust | 2090 | L/s
Internal-discharge limit (# 4.5.1) | 209 L/s — within
Terminal velocity at hood lip (# 6.1.1) | max 0.25 m/s (50 fpm as printed)
Extract duct
Required area | 0.249 | m²
Design velocity | 8.4 | m/s
Candidate size | 500 x 500 mm — 8.36 m/s
Candidate size | 550 x 500 mm — 7.60 m/s
Candidate size | 600 x 450 mm — 7.74 m/s
Energy — ASHRAE 90.1 (advisory)
Position | not applicable — facility total 2,091 L/s is below 2360 L/s, so Table 6.5.7.2.2 is not assessed (90.1-2022 SI # 6.5.7.2.2)
Reference standards
Reference | Application
ANSI/ASHRAE Standard 154-2016 | hood type, appliance duty classification, Type II net exhaust rates, overhangs, internal-discharge make-up limit, duct velocity minimum
ASHRAE Handbook - HVAC Applications 2019, Ch 34 | typical exhaust flow rates for listed Type I hoods by hood style and appliance duty
ANSI/ASHRAE/IES Standard 90.1-2022 (SI edition) | maximum net exhaust flow rate per linear metre of hood (advisory in this tool)
NFPA 96 | grease-duct construction and fire protection; referenced in duct output, no flow calculated from it
UL 710 / 710B / 710C | a listed Type I hood's rate governs over any tabulated typical value (ASHRAE 154-2016 # 4.1.1)
Notes
ASHRAE 154-2016 # 4.1.1: Type I hoods must be listed (UL 710/710B/710C) and installed per their listing; typical rates are design guidance, the listing governs.
Grease removal devices are not sized by this tool: ASHRAE 154-2016 # 4.6.1 requires them in accordance with the hood's listing, and the standard publishes no filter face velocity — take the filter count and velocity from the listing / manufacturer's data for the extract flow above.
ASHRAE 154-2016 # 6.1.1: terminal velocity of air introduced near the hood shall not exceed 50 fpm (0.25 m/s) at the hood's lowest edges. # 6.2.1 permits transfer air from areas other than the kitchen as replacement air, and Addendum m (2021) requires that transfer air to meet the air-classification requirements of ASHRAE 62.1 (the addendum's foreword treats kitchen replacement air as 62.1 Class 2 air); transfer-air openings are sized for 0.381 m/s (75 fpm) on free area (# 6.1.2).
AHJ basis: Make-up air band minimum 75 % of extract (default)
AHJ basis: Make-up air band maximum 95 % of extract (default)
ASHRAE 90.1 figures are reported as an energy advisory only. The extract flow is as required by the governing ventilation standard and is not reduced to meet them.