LPG Gas Consumption & Tank Sizing

NFPA 58 / BS 6400-3 appliance-schedule method

| Project Information |  |
| --- | --- |
| Project Name | Marina Commercial Tower |
| Project No. | MCT-2026-MEP-001 |
| Revision | P2 |
| Client | — |
| Prepared by | Hussein Ragab |
| Checked by | — |
| Date | 2026-10-20 |

Values in this report are displayed in SI (metric) units.  Working units: m3/hr, kg/day, US gallons.

# 1.  Methodology & Standards

Gas demand is built from an appliance schedule per premises: each appliance's input rating (NFPA 54 Table A.5.3.2.1) is diversified within a domestic premises by the BS 6400-3 Table A.1 factors and count rule (a commercial premises is taken at connected load x the commercial diversity factor), then converted to an LPG volume at the selected mix CV (BS 6400-3 A.2). For an infrastructure connection the deliverable is the peak design flow rate. For on-site storage the daily LPG consumption (peak x operating-hours/day) gives the autonomy of the selected tanks at the filling limit (80 % here; NFPA 58 Table 7.4.2.3(a)); the peak is checked against the tank's natural vaporization and a vaporizer is sized if required (NFPA 58 Ch. 11).

Provenance: appliance input ratings are NFPA 54 Table A.5.3.2.1 and the within-premises diversity of a domestic premises is BS 6400-3 Table A.1 (both code); a commercial premises uses the commercial diversity factor stated on the AHJ basis line. The appliance-set composition and the operating-hours/day per premises type are project assumptions (editable) - confirm against the actual load schedule per project.

# 2.  Design Inputs

| Parameter | Value |
| --- | --- |
| LPG mix | LPG 60/40 (propane/butane) |
| Cross-premises diversity | none |
| Supply | On-site tank |
| Usable fill | 80 % |
| Installation | aboveground |
| Vaporizer assessed | yes |
| Design level / min ambient | 25 % / 5 degC |
| Supplier refill cycle | 7 days |

Appliance-schedule demand

| Premises type | Contribution |
| --- | --- |
| Restaurant (large) | 2 units, peak 202.2 kW/unit x div 1.00, 293.8 kg/day |
| Restaurant (small) | 4 units, peak 123.1 kW/unit x div 1.00, 286.1 kg/day |

# 3.  Design Assumptions

Peak demand is built from an APPLIANCE SCHEDULE per premises: each appliance's input rating (NFPA 54 Table A.5.3.2.1, or nameplate) is diversified WITHIN a DOMESTIC premises by the BS 6400-3 Table A.1 factors and count rule (<=2 appliances -> factor 1, >2 -> Table A.1); a COMMERCIAL premises is taken at its CONNECTED load x the commercial diversity factor (see the AHJ basis line - Table A.1 is a domestic meter-sizing table). The appliance set and the equivalent operating hours/day per premises type are project assumptions (editable), NOT code values - confirm per project.

Heat input is converted to an LPG volume via the selected mix calorific value (BS 6400-3 A.2: kW x 3.6 / CV). The mix CV is the mass-weighted total heating value of the composition (NFPA 58 (2024) Table B.1.2(b), total heating value 49,920 / 49,140 kJ/kg: propane 49.92 / butane 49.14 MJ/kg) times the CoolProp vapour density at 15 degC / 101.325 kPa; the mix composition is stated in mole %.

Across premises the peaks are summed at CONNECTED load by default (no population-diversity credit). An optional cross-premises factor (manual, per NFPA 54 # 5.3.2.3 Exception, or the Velander statistical estimate) may be applied to the PEAK ONLY; the daily energy (tank-autonomy basis) is never diversity-reduced.

Where the cross-premises factor is enabled it is applied PER PREMISES ROW (N = that row's unit count) — the conservative granularity, since separate rows are typically distinct buildings/uses. The Pipe Sizing mode pools coincidence over the whole served network instead, so its design flow can sit slightly below this page's on multi-row jobs.

Commercial premises daily energy = connected load x commercial diversity factor x operating hours/day: every appliance is assumed to run at its full rated input for all of the operating hours. Set the operating hours/day as equivalent full-load hours for the actual use.

The commercial premises appliance sets are representative defaults. A gas supplier's planning figure for the same premises type may be higher; the appliances actually connected govern - enter the project's appliance schedule (nameplate inputs) in the Library.

Tanks are filled to 80 % liquid by volume; the tool's 80 % default is the commercial-propane cell of NFPA 58 (2024) Table 7.4.2.3(a), 40 F (4.4 C) row, aboveground containers 0-1200 gal (7.4.3.2(A) fixed-gauge basis) - containers over 1200 gal and underground / mounded containers take Tables 7.4.2.3(b) / (c), which this tool does not read (the result warnings say so per tank). This fill sizes the LPG charge, the loaded weight and the natural-vaporization liquid available.

Autonomy is the usable DRAWDOWN - the fill limit (80 %) minus a low-level reserve (25 %) = 55 % - divided by the average daily consumption. The reserve (refill heel) is a project / operational basis, NOT a code value; confirm per project.

Natural (passive) vaporization is a first-principles still-air heat balance mdot = h x A_wetted x (T_amb - T_boil) / L (latent heat + boiling point NFPA 58 (2024) Annex B Table B.1.2(b); Churchill-Chu free-convection h; NFPA 58 publishes no still-air vaporization rate) at the design minimum ambient (ground temperature at tank depth for an underground / mounded tank) and low liquid level (a conservative worst case); a vaporizer is sized where peak demand exceeds this capacity (NFPA 58 Ch. 11). FEI continuous-draw cross-check withheld: the FEI sheet is not filed in ref/ (ruling 31a-3, 2026-09-05).

Tank tare weights: Superior Propane 'Propane Tank Volume Capacity' p.1 (source: CSA B149HB), approx. tare weight, saddles / skids excluded; sizes the sheet does not print are interpolated on its ladder and marked 'tare typical'. Dimensions are typical catalogue values - confirm against the supplied tank's plate.

AHJ basis: Commercial premises diversity factor (x connected load) 1 (default)

# 4.  Step-by-Step Calculation

Step 1: LPG mix

Formula: row from mix library

Substitution: LPG 60/40 (propane/butane)

Result: LPG 60/40 (propane/butane)

Note: Composition 60 % propane by MOLE (not by mass). LPG CV 106.7 MJ/m3 vapour, vapour 2.1529 kg/m3, liquid 0.5432 kg/L. CoolProp HEOS Propane[0.6]&n-Butane[0.4] (mole) @ 15 degC; NG->LPG from CV (HHV NFPA 58 Table B.1.2(b); NG 38.7 MJ/m3)

Step 2: Restaurant (large) x2

Formula: peak = connected kW x commercial factor ; daily = peak x hours ; LPG = kW*3.6/CV

Substitution: peak 202.22 kW/premises (connected 202.22), 10 h/day

Result: peak 13.646 m3/hr ; 293.79 kg/day

Note: Ratings NFPA 54 Table A.5.3.2.1; commercial premises: connected load x commercial diversity factor 1 (AHJ basis).

Step 3: Restaurant (small) x4

Formula: peak = connected kW x commercial factor ; daily = peak x hours ; LPG = kW*3.6/CV

Substitution: peak 123.09 kW/premises (connected 123.09), 8 h/day

Result: peak 16.613 m3/hr ; 286.12 kg/day

Note: Ratings NFPA 54 Table A.5.3.2.1; commercial premises: connected load x commercial diversity factor 1 (AHJ basis).

Step 4: Totals

Formula: sum over premises

Substitution: peak 30.259 m3/hr (65.14 kg/hr)

Result: daily = 579.9 kg (1067.6 L = 282.0 US gal/day)

Step 5: Tank combination + autonomy

Formula: drawdown = sum(gal*count) * (fill - reserve) ; autonomy = drawdown / daily

Substitution: 4x1000 = 4000 gal installed x (80% fill - 25% reserve) = 2200 gal drawdown

Result: autonomy = 2200 gal / 282 gal/day = 7.8 days

Note: Fill limit 80 % - the 80 % default is the commercial-propane cell of NFPA 58 (2024) Table 7.4.2.3(a), 40 F (4.4 C) row, aboveground containers 0-1200 gal (7.4.3.2(A) fixed-gauge basis); the low-level reserve (25%) is a project / operational basis, NOT a code value.

Step 6: Natural vaporization (worst case, heat balance)

Formula: mdot = h*A_wetted*dT/L [still-air heat balance; Churchill-Chu h; NFPA 58 Table B.1.2(b) L, BP]

Substitution: combo 4x1000, T_amb=5C (ambient), level=25%, T_boil=-14C @ 1 barg [CoolProp HEOS], h=3.7 W/m2K

Result: 15.54 kg/hr capacity vs 65.14 kg/hr demand

Note: First principles (still air, aboveground basis). Latent heat + boiling point NFPA 58 Table B.1.2(b); NFPA 58 publishes no still-air vaporization rate (its fire-exposure relief formula is not used); confirm vs the tank maker's continuous-draw curve.

Step 7: Vaporizer (throughput match)

Formula: smallest rated kg/hr >= peak demand

Substitution: demand 65.1 kg/hr

Result: selected Electric (immersion) 80 kg/h

# 5.  Results

| Parameter | Value |
| --- | --- |
| Peak demand | 30.26 m3/hr (65.14 kg/hr) |
| Daily consumption | 579.9 kg/day (282.0 US gal/day) |
| Tanks selected | 4 x 1000 gal |
| Fill limit (NFPA 58 Table 7.4.2.3(a)) | 80 % (printed maximum 82 % for this mix, Table 7.4.2.3(a) 40 F) |
| Low-level reserve (refill heel) | 25 % (project basis) |
| Usable drawdown | 55 % |
| Installed / usable drawdown | 4000 / 2200 US gal |
| Loaded weight (all tanks) | 9,760 kg |
| Autonomy achieved | 7.8 days |
| Natural vaporization (still-air heat balance) | 15.54 kg/hr |
| Vaporizer required? | Yes |

Refill interval by capacity

| Capacity | Refill interval (single tank) |
| --- | --- |
| 250 US gal | 0.5 days |
| 500 US gal | 1.0 days |
| 1000 US gal | 2.0 days (selected) |
| 2000 US gal | 3.9 days |
| 4000 US gal | 7.8 days |
| 6000 US gal | 11.7 days |
| 12000 US gal | 23.4 days |
| 18000 US gal | 35.1 days |
| 30000 US gal | 58.5 days |

# 6.  Equipment Schedule

| Item | Specification |
| --- | --- |
| LPG storage tank 1 | 4 x 1000 US gal (3,785 L) water capacity; horizontal 1,041 mm dia x 4,902 mm long; empty (tare) approx. 795 kg, full (loaded) approx. 2,440 kg (800 US gal LPG per tank at the fill limit); dimensions typical, confirm with maker. Siting (NFPA 58 Table 6.4.1.1, aboveground): min sep to building / property line 25 ft (7.6 m), between containers 3 ft (1 m); 25 ft reducible per NFPA 58 # 6.4.1.3. |
| LPG vaporizer | 1 x Electric (immersion) 80 kg/h (80 kg/hr); approx. 11 kW |
| Protection | Vehicular barrier protection required where the container is within 10 ft (3 m) of a public vehicular thoroughfare (NFPA 58 # 6.8.1.2). |
| Relief valves | Pressure relief valves are container-mounted (vendor-supplied); relief discharge >= 5 ft (1.5 m) horizontally to building openings below the discharge and >= 10 ft (3.0 m) to ignition sources / direct-vent appliance openings / mechanical air intakes (NFPA 58 Table 6.4.4.3, ASME filled at point of use). |

⚠ Advisory

• Basis: PEAK demand = appliance input ratings (NFPA 54 Table A.5.3.2.1 / nameplate) x BS 6400-3 Table A.1 diversity WITHIN each DOMESTIC premises (Table A.1 is a meter-sizing table, meters up to 6 m3/h); a COMMERCIAL premises is taken at CONNECTED load x the commercial diversity factor (see the AHJ basis line); across premises the peak is summed at CONNECTED load (no population-diversity credit). Daily energy (tank autonomy) is never diversity-reduced. Appliance-set composition and operating hours/day are project assumptions - confirm per project.

# R.  Reference Standards

NFPA 54 (2021) / ANSI Z223.1 — National Fuel Gas Code — appliance input ratings (Table A.5.3.2.1, e.g. freestanding domestic range 65,000 Btu/hr; nameplate governs per # 5.3.2.1 / B.3.1); vapour pipe sizing (Table 6.4.2 Cr/Y + Annex B.5, with the Annex B.3.4 specific-gravity multiplier for gases other than propane); diversity permitted but unquantified (# 5.3.2.1 full connected load; # 5.3.2.3 Exception allows designer-established factors).

BS 6400-3 (2007) — LPG demand method (Annex A): demand = Sigma(kW x Table A.1 diversity) x 3.6 / CV. Table A.1 within-premises diversity factors + count rule (<=2 appliances -> factor 1, >2 -> Table A.1), applied to DOMESTIC premises only - Table A.1 is a meter-sizing table and the standard's # 1 Scope covers meters not exceeding 6 m3/h. Commercial premises are taken at connected load x the commercial diversity factor (AHJ basis line). Nominal 37 mbar propane 2nd-stage operating pressure.

BS EN 1555-2 (2025) — Plastics piping systems for the supply of gaseous fuels - PE pipes: Table 2 SDR 11 minimum wall thicknesses e_min (footnote c: 3,0 mm minimum for SDR 11) - the PE pipe bores (bore = OD - 2 x e_min).

BS 5482-1 (2005) / IGEM/UP/2 Ed 2 — LPG pipework permissible design pressure drop (BS 5482-1 # 11.4.4.2 / IGEM/UP/2 Table 1, per-fuel rows): 2.5 mbar while OP <= 42 mbar (LPG propane) or <= 33 mbar (LPG butane); above that ceiling 10% of OP. The tool takes the row of the predominant fuel (propane > 50% of the mix -> propane row; otherwise butane row). BS 5482-1 # 11.4.4.2: the 2.5 mbar is measured from the regulator outlet to any draw-off point; IGEM/UP/2 Table 1 note 2: outlet of the regulator on the bulk tank / cylinder to the plant manual isolation valve (vapour phase). BS 5482-1 # 11.4.4.2 / Annex B.2 split it 0.5 mbar service + 2.0 mbar installation pipework. Variable-friction low-pressure flow (IGEM/UP/2 A3.1; friction f per A3.2); medium-pressure per A3.1(b); per-fitting equivalent lengths per A3.3; gas velocity per # 4.2.3 Table 2.

BS 6891 (2015) — Annex A.2 eq (A.1) low-pressure flow equation (identical to IGEM/UP/2 A3.1) with the eq (A.2) smooth-pipe friction factor and its printed efficiency factors e (0.86 steel, 0.95 copper, 0.97 PE) - the 'bs6891' method; Table A.3 assumed copper bores (13 / 19 / 25 / 32 mm for 15 / 22 / 28 / 35 mm tube) are the copper ladder's bores. Tables A.3 / A.4 are the method's printed goldens, not tabulated inputs. Butane cylinder supply: nominal 28 mbar (BS 6891:2015 Table 7, BS 3016 cylinder single-stage regulator row; BS 5482-1:2005 Scope and Table 3 notes: butane from cylinders at 28 mbar). Table 7 prints no butane final-stage row - enter the regulator's set pressure for a bulk butane final stage.

NFPA 58 (2024) — LP-Gas Code — maximum permitted filling limit (Table 7.4.2.3(a), 40 F row, aboveground containers to 1200 gal; 7.4.3.2(A)); total heating values, latent heat + boiling point (Annex B Table B.1.2(b)) used by the first-principles still-air natural-vaporization heat balance (NFPA 58 publishes no still-air vaporization rate; the fire-exposure relief formula is not used); container separation distances (Table 6.4.1.1; # 6.5.2.4 underground / mounded between-container minimum); relief-discharge + vehicular-barrier protection.

Cross-premises diversity — OPTIONAL (default off = connected load). 'Manual' = a designer-established factor (NFPA 54 # 5.3.2.3 Exception). 'Statistical' = the Velander / Rusck coincidence factor CF(N) = floor + (1 - floor)/sqrt(N) - an ENGINEERING ESTIMATE, not a published code value (no population-diversity curve is held). Applied to PEAK only; daily energy is never reduced.

Vaporization coefficient — Natural-vaporization convection coefficient = Churchill-Chu free convection (ASHRAE Fundamentals / textbook), a first-principles ambient rate NFPA 58 does not publish. No vendor continuous-draw table is used (the FEI sheet is not filed in the tool's reference set - engineer ruling 31a-3, 2026-09-05).

Superior Propane 'Propane Tank Volume Capacity' (source CSA B149HB) — Empty (tare) weights; untabulated ladder sizes interpolated and labelled typical. Tank dimensions are generic ASME horizontal-vessel values with no supplier sheet in the reference set - confirm with the selected tank maker.

Generated by the LPG Calculator (Tool 31a).