## Demand & Tanks
LPG Consumption & Tank Sizing — Schedule
NFPA 58 / BS 6400-3 appliance-schedule method — units m3/hr, US gal, kg
Project: Marina Commercial Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: - ¦ By: Hussein Ragab ¦ Chkd: - ¦ Rev: P2 ¦ Date: 2026-10-20
Mix: LPG 60/40 (propane/butane) ¦ Supply: tank ¦ Installation: aboveground ¦ Usable fill 80 %
Appliance-schedule demand
Premises type | Units | Cross-div | Peak LPG m3/hr | Daily LPG kg/day | Daily LPG L/day | Source / basis
Restaurant (large) | 2 | 1 | 13.646 | 293.8 | 540.8 | commercial premises: connected load x commercial diversity factor 1 (AHJ basis); Appliance set + operating hours = project assumption (editable). Ratings: NFPA 54 Table A.5.3.2.1 / nameplate; diversity: BS 6400-3 Table A.1 (domestic premises) or connected load x the commercial factor (commercial).
Restaurant (small) | 4 | 1 | 16.613 | 286.1 | 526.7 | commercial premises: connected load x commercial diversity factor 1 (AHJ basis); Appliance set + operating hours = project assumption (editable). Ratings: NFPA 54 Table A.5.3.2.1 / nameplate; diversity: BS 6400-3 Table A.1 (domestic premises) or connected load x the commercial factor (commercial).
Totals: peak 30.26 m3/hr (65.14 kg/hr) ¦ daily 579.9 kg (282.0 US gal/day)
Tank schedule
Tank | Count | Water cap. US gal/tank | Fill US gal/tank | Empty (tare) kg/tank | Full (loaded) kg/tank | Dimensions | Min separation (NFPA 58 Table 6.4.1.1)
1000 gal | 4 | 1000 | 800 | 795 | 2440 | 1041 x 4902 mm horizontal (dimensions typical, confirm with maker) | min sep to building / property line 25 ft (7.6 m), between containers 3 ft (1 m); 25 ft reducible per NFPA 58 # 6.4.1.3.
Autonomy 7.8 days (installed 4000 gal, usable drawdown 2200 gal @ 55 %) ¦ Natural vaporization 15.54 kg/hr (still-air heat balance) ¦ Vaporizer: Electric (immersion) 80 kg/h
Equipment schedule (ancillaries)
Item | Specification
LPG vaporizer | 1 x Electric (immersion) 80 kg/h (80 kg/hr); 11 kW
Protection | Vehicular barrier protection required where the container is within 10 ft (3 m) of a public vehicular thoroughfare (NFPA 58 # 6.8.1.2).
Relief valves | Pressure relief valves are container-mounted (vendor-supplied); relief discharge >= 5 ft (1.5 m) horizontally to building openings below the discharge and >= 10 ft (3.0 m) to ignition sources / direct-vent appliance openings / mechanical air intakes (NFPA 58 Table 6.4.4.3, ASME filled at point of use).
AHJ basis: Commercial premises diversity factor (x connected load) 1 (default)
Commercial premises daily energy = connected load x commercial diversity factor x operating hours/day: every appliance is assumed to run at its full rated input for all of the operating hours. Set the operating hours/day as equivalent full-load hours for the actual use.
The commercial premises appliance sets are representative defaults. A gas supplier's planning figure for the same premises type may be higher; the appliances actually connected govern - enter the project's appliance schedule (nameplate inputs) in the Library.
Appliance ratings NFPA 54 Table A.5.3.2.1; within-premises diversity BS 6400-3 Table A.1 for domestic premises, connected load x the commercial diversity factor for commercial premises. Appliance set + hours = project assumption. Generated by the LPG Calculator (Tool 31a).