## Equipment Schedule
Pool Equipment Sizing — Equipment Schedule
Project: Marina Commercial Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: - ¦ By: Hussein Ragab ¦ Chkd: - ¦ Rev: P2 ¦ Date: 2026-10-20
Unit system: SI · Method: International (PWTAG-based, v2.0)
Item | Qty | Duty / key data | Model | Sizing basis
Design circulation flow | - | 128.4 m3/h (T = 2.50 h) | - | Turnover time - swimming pool 2.5 h (AHJ default)
Filter battery | 2 | A >= 5.14 m2 at 25 m/h | C D2000 (sand, single medium — 1.2 m bed) | Filtration velocity cap - sand filters, fresh water (AHJ default)
Backwash flow | - | 94.2 m3/h | - | one filter at a time
Indicative circulation pump | 2 | 128.4 m3/h @ 8.8 m TDH | P2 5.5 kW | smallest head margin above TDH — confirm on the datasheet (not a BEP selection)
TDH breakdown | - | static 1.50 m + friction 1.71 m (incl. 10 % SF) + filter 5.10 m + strainer 0.51 m | - | filter dP 50 kPa (user entry) — confirm with the vendor
Pipe — Pump suction header | - | 128.403 m3/h; ID >= 158.9 mm; ID 166.2 mm @ 1.64 m/s | suction | Pipe velocity cap - suction side (AHJ default)
Pipe — Return header | - | 128.403 m3/h; ID >= 137.6 mm; ID 166.2 mm @ 1.64 m/s | return | Pipe velocity cap - return / pressure side (AHJ default)
Pipe — Backwash waste | - | 94.2 m3/h; ID >= 117.9 mm | backwash_waste | Pipe velocity cap - return / pressure side (AHJ default)
Pipe — Gutter drop (gravity) | - | 128.403 m3/h | gravity | gravity: size by hydraulic calculation (industry practice; informative: MAHC 4.7.1.7.2.3)
Balance / surge tank | 1 | 21.0 m3 effective | - | DIN 19643-1:2012 # 9.5.4 Eq (14)-(17)
AHJ basis
AHJ basis: Turnover time - swimming pool 2.5 h (default)
AHJ basis: Filtration velocity cap - sand filters, fresh water 25 m/h (default)
AHJ basis: Pipe velocity cap - suction side 1.8 m/s (default)
AHJ basis: Pipe velocity cap - return / pressure side 2.4 m/s (default)
Advisories
⚠ Backwash sized at the PWTAG # 7.3.4 minimum fluidisation velocity (30 m/h) — confirm against the selected filter manufacturer's backwash requirement; if it is higher, untick Auto on 'Backwash velocity' (Filtration) and type it.
⚠ Line 'Gutter drop (gravity)' is a GRAVITY line — size by hydraulic calculation at design flow (industry practice; informative: MAHC 4.7.1.7.2.3); no velocity-cap sizing applied.
⚠ Feed the final tank volume back to M1 (balance_tank_volume_m3) — the turnover check uses pool + tank volume (system-volume convention; informative: MAHC 4.7.1.10.3.2).
Reference |  | Application
PWTAG Code of Practice 2013 |  | Pool water treatment practice — turnover Table 2, bathing load Table 1 + circulation rate # 5.10.3, medium-rate filtration # 7.1.3, backwash # 7.3
DIN 19643-1:2012-11 |  | Treatment of water of swimming pools — deck-level hydraulics # 9.2, balance-tank equations # 9.5.4
BS EN 15288-1/-2:2008 |  | Swimming pools — classification and safety
BS EN ISO 1452-2:2009 |  | PVC-U pressure pipe series — circulation main bores (Table 2, PN10)
Industry defaults (labeled) |  | Values with no printed equivalent in the governing set carry an informative source note (e.g. the precoat/cartridge filtration rates) and stay user-editable; the pipe velocity caps are editable AHJ values (section 3)
Selection libraries (filters, pumps) |  | Indicative typical commercial equipment, identified by engineering size — starter data, fully user-editable. Confirm against the vendor datasheet before specifying