Swimming Pool Load Simulation Report

Outdoor Pool Thermal Analysis

Open-Meteo Weather Data

| Project Information |  |
| --- | --- |
| Project Name | Marina Commercial Tower |
| Project No. | MCT-2026-MEP-001 |
| Revision | P2 |
| Client | — |
| Prepared by | Hussein Ragab |
| Checked by | — |
| Date | 2026-10-20 |

Values in this report are displayed in SI (metric) units.

# 1.  Methodology & Standards

| Reference | Application |
| --- | --- |
| Shah (2014) — Outdoor Pool Evaporation, ASHRAE Trans. SE-14-001 | Eq. (7), p. 8, wind-driven forced-convection evaporation: E0 = 0.00005·(u/0.15)^0.7·(P_w − P_a), floored by the calm natural-convection value (ASHRAE HVAC Applications 2007 Ch. 4 Eq. 1 at zero wind). An OCCUPIED pool applies Eq. (5), p. 4 — Eocc/E0 = 1.9 − 21·(ρ_r − ρ_w) + 5.3·N*, with (ρ_r − ρ_w) used = min(max(ρ_r − ρ_w, 0), 0.0421 kg/m³): held at the Table 6, p. 7 verified limit, an engineer extension (ruling R2-01, 2026-09-23; Shah gives no rule above it) — on that E0. Table 14, p. 13 prescribes Eq. (5) on the largest of Shah Eq. (1), (2), (7); this tool's E0 floor is ASHRAE Eq. 1 (1.4 to 2.7 x Shah Table 4 at calm) — an engineer extension (ruling D29, 2026-09-22). The ASHRAE activity factor is not applied outdoors (engineer ruling 19a-4, 2026-09-05). This run: Shah 2014 Eq. (7), p. 8, floored by ASHRAE 2007 Ch. 4 Eq. 1 at zero wind (engineer extension; Shah p. 9 and Table 14 p. 13 take the largest of his own Eq. (1), (2) and (7)) (unoccupied outdoor pool). |
| Arden Buck (1981) — Vapour Pressure | Saturation vapour pressure equation for T ≥ 0°C (over liquid water) and T < 0°C (over ice). More accurate than Antoine equation near 0°C. |
| McAdams (1954) — Convective Coefficient | h_cv = 5.68 + 3.94·u [W/(m²·°C)] for forced convection from an open water surface to ambient air. Lineage: McAdams p. 207 Eq. 34 / Table XI (Jürges, smooth surface) h = 0.99 + 0.21·V' in I-P; the printed conversion is 5.62 + 3.91·u — the engine's coded pair is about 1 % higher (slightly conservative on the loss side). Jurges' data behind McAdams p. 207 Eq. 34 are for air parallel to a vertical plate; McAdams' Schack air-temperature correction and his low-velocity rule (take the larger of forced and natural convection, p. 210) are not applied; the coded pair is 5.68 + 3.94 u against the printed conversion 5.62 + 3.91 u. Table XI prints this linear row for velocities below 16 ft/s (4.88 m/s) only; above it McAdams prints h = 0.50 V'^0.78, which meets the linear row at 16 ft/s (both 4.35) and falls below it above (10.57 against 11.49 at 50 ft/s, Btu/(h ft2 F)); the coded row is applied at every wind speed and errs on the high-load side there. |
| Swinbank (1963) — Sky Temperature | T_sky_K = 0.0552 × T_amb_K^1.5 — clear-sky longwave radiation model (Q.J.R. Meteorol. Soc. 89; primary paper not held in ref). Applied to every outdoor hour as a clear sky (conservative on the heating side). |
| Stefan-Boltzmann Radiation | Q_rad = ε·σ·(T_pool⁴ − T_sky⁴) with ε = 0.95 for water (library value). |
| Design-Condition Sizing — pool-industry convention (not a cited clause) | Equipment sizing follows pool-industry practice (CIBSE / Astral methodology) — a convention of this tool, printed in no held document. Design heating ambient = mean temperature of the auto-detected coldest 3 months (detected from the fetched data by mean temperature, hemisphere-agnostic; up to three months, fewer on a period under six calendar months, and a period within one calendar month is refused). Design cooling ambient = mean of the hottest month (August 2024): the calendar month of the simulated period with the highest cooling gain at its mean conditions (mean air temperature, RH, wind and solar; summer set-point and make-up temperature), taken in the governing occupancy state (engineer ruling 29.09.2026 R3). Maintenance load q2 is evaluated at these mean conditions — zero solar for heating (worst-case overnight), that month's mean solar for cooling. The pool cover is not applied to the equipment size: the heating plant is sized on the uncovered load (it must hold set-point with the cover off); the cover changes the annual energy only (engineer ruling D25, 2026-09-22). |
| Open-Meteo Archive API | Hourly T, RH, wind speed and shortwave radiation for 2024-01-01 to 2024-12-31, requested with timezone=auto so every hour stamp is the SITE LOCAL clock (local time at the site (Asia/Dubai)); the cover window and the HP off-window are applied on that clock. Source of this run: Open-Meteo archive (live fetch) (data written 2026-10-20 10:07; lat 25.077, lon 55.309). |

# 2.  Design Inputs

| Parameter | Value |
| --- | --- |
| Location | Dubai |
| Simulation Period | 2024-01-01 to 2024-12-31 |
| Weather Data Source | Open-Meteo archive (live fetch) (data written 2026-10-20 10:07; lat 25.077, lon 55.309) |
| Time Basis (hourly stamps, schedules) | local time at the site (Asia/Dubai) |
| Pool Surface Area | 150.0 m² |
| Pool Average Depth | 1.4 m |
| Pool Volume | 210.0 m³ |
| Desired Water Temp — Winter | 26.0 °C |
| Desired Water Temp — Summer | 30.0 °C |
| Initial Water Temp — Winter | 10.0 °C |
| Initial Water Temp — Summer | 35.0 °C |
| Makeup Water Temp — Winter | 12.0 °C |
| Makeup Water Temp — Summer | 22.0 °C |
| Activity Factor (ASHRAE preset — occupancy switch outdoors) | 0.5 |
| Occupancy (Shah 2014) | Unoccupied — Eq. (7) only |
| Initial Heating Period | 72.0 h |
| Initial Cooling Period | 48.0 h |
| Pool Cover (winter) | No |
| Plot Type | Average Daily |

# 3.  Design Assumptions

Pool is outdoor, unenclosed. Open-Meteo 10 m wind is scaled by the library wind-sheltering factor (default 1.0 = fully exposed) to the near-pool wind before it feeds the evaporation and convection terms, correcting for the height/exposure gap vs. Shah's 0.3 m measurement basis. Full exposure is the higher load for HEATING only: more wind means more evaporation, which LOWERS the summer cooling duty (engineer ruling C068).

Heating design basis: unoccupied (Shah Eq. (7)); 10 m wind x sheltering 1 (library value); the ASHRAE calm-air evaporation floor (ruling D29); zero solar. Together these are high-load choices for the heating size; sheltering 1.0 LOWERS the summer cooling duty (more wind, more evaporation) (ruling C068). Hourly heating (peak, energy) acts only when the water would fall below the winter set-point 26.0 °C and hourly cooling only when it would rise above the summer set-point 30.0 °C, in every month; the water floats between them (engineer rulings 29.09.2026, heat to the winter set-point all year; cool only above the summer set-point); the heating and cooling sizes are unchanged by it (heating q2 at the winter set-point on the coldest-season means, cooling q2 at the summer set-point on the hottest-month means). Cooling design basis: hottest-month mean (engineer ruling 29.09.2026 R3) - August 2024, the calendar month of the simulated period with the highest cooling gain at its mean conditions (mean air temperature, RH, wind and solar; summer set-point and make-up temperature), taken in the governing occupancy state. Cooling design duty: pool unoccupied (Shah Eq. (7)): cooling q2 0.00 kW (August 2024). Cooling units are counted at the catalogue cooling capacity at its rating air temperature; the datasheets print less at hotter air (e.g. Inverter Max BYC-103TA1 58 kW at air 35 degC, 42 kW at 46 degC, datasheet p. 1) and no derate is applied.

Unoccupied pool: no opening hours apply (Eq. (7) on every hour).

Water surface temperature equals the desired (set-point) temperature at all times (steady-state heat balance per hour).

Solar absorptivity of water = 0.9 (library value; engineering value — open water absorbs approx. 85–95% of incident shortwave radiation).

Longwave emissivity of water surface = 0.95 (library value; open-water value).

Sky temperature computed by Swinbank (1963): T_sky_K = 0.0552·T_amb_K^1.5, applied to every hour as a clear sky (primary paper not held in ref; conservative on the heating side).

Pool cover reduces net heat loss by 60% during specified cover hours in the heating season (industry bubble-cover range 50–70%; not attributed to a specific ASHRAE clause).

Makeup water replaces evaporative losses at the specified seasonal makeup temperature and must be heated to the desired pool temperature.

Heating and cooling seasons are auto-detected as the coldest and hottest 3 months of the fetched weather (hemisphere-agnostic). Hourly heating acts only when the water would fall below the winter set-point and hourly cooling only when it would rise above the summer set-point, in every month; between the two set-points the water floats.

Equipment sizing = initial heat-up power (q1) + maintenance load at the mean design ambient (q2): heating at the coldest-season mean, cooling at the mean of the hottest month, August 2024 — the pool-industry convention this tool applies, not a cited clause. q1 is DIRECTED: a winter initial temperature above its set-point adds no heat-up power and a summer initial temperature below its set-point adds no cool-down power (engineer ruling D26, 2026-09-22).

The pool cover is not applied to the equipment size: the heating plant is sized on the uncovered load (it must hold set-point with the cover off); the cover changes the annual energy only (engineer ruling D25, 2026-09-22).

Outdoor evaporation: Shah 2014 Eq. (7), p. 8, floored by ASHRAE 2007 Ch. 4 Eq. 1 at zero wind (engineer extension; Shah p. 9 and Table 14 p. 13 take the largest of his own Eq. (1), (2) and (7)) (unoccupied outdoor pool). The ASHRAE activity factor is not applied outdoors (engineer ruling 19a-4, 2026-09-05); the preset only selects occupied / unoccupied.

Conduction through the pool shell and to the ground is NOT modelled (surface heat balance only). For an in-ground basin this is usually a few percent of the surface load; for an above-ground or poorly insulated shell add a conduction allowance to the heating side.

The occupancy multiplier is applied to the WHOLE water surface — this tool models a single basin of one type; a multi-feature pool should be run per feature area and the loads summed.

Hourly weather stamps are the site local clock (local time at the site (Asia/Dubai)); the cover window and the HP daily off-window are evaluated on that clock, so the schedules printed in this report are the ones the simulation applied.

Code compliance — ISPSC 2021 #303.1.3: outdoor heated pools require a vapor-retardant cover UNLESS more than 70% of the seasonal heating energy is from a heat pump or solar source. This design specifies heat-pump plant as the heating source; the exception applies only if that plant supplies more than 70% of the SEASONAL heating energy — verify the seasonal energy split (including any auxiliary/backup heat) before relying on the exemption. A cover remains beneficial for evaporation/energy control regardless.

# 4.  Step-by-Step Calculation

4.1  Saturation Vapour Pressure

Step 1: Arden Buck (1981) Equation

Formula: P_sat = 0.61121 × exp[(18.564 − T/254.4) × T/(255.57+T)] [kPa]

Substitution: Applied at pool surface temp T_w and ambient temp T_a each hour

Result: P_w, P_a [kPa] → converted to [Pa] for evaporation formula

Note: More accurate than Antoine equation near 0°C; separate formula for T < 0°C over ice.

4.2  Evaporation Loss

Step 2: Shah (2014) Eq. (7) — Wind-Driven Evaporation (unoccupied)

Formula: E0 = a × (u/b)^0.7 × max(P_w − P_a, 0) [kg/(h·m²), P in Pa]; E0 = max(E_wind, E_calm) Q_evap = E × A × L / 3600 [kW]

Substitution: a=5×10⁻⁵, b=0.15 m/s (ref. wind), A=150.0 m², L = 2501−2.36×T_w [kJ/kg] (T_w in °C — internal SI basis) Unoccupied pool: no occupancy multiplier; the ASHRAE activity factor is not applied outdoors

Result: E = 0.8352 kg/(h·m²) at the heating design condition -> Q_evap = 84.90 kW (72% of the surface losses)

Note: Method: Shah 2014 Eq. (7), p. 8, floored by ASHRAE 2007 Ch. 4 Eq. 1 at zero wind (engineer extension; Shah p. 9 and Table 14 p. 13 take the largest of his own Eq. (1), (2) and (7)) (unoccupied outdoor pool). Wind exponent 0.7 (Shah 2014, SE-14-001 Eq. (7), p. 8). At light wind the calm natural-convection value (ASHRAE 2007 Ch. 4 Eq. 1) floors the result - an engineer extension (ruling D29): Shah p. 9 / Table 14 take the largest of his own Eq. (1), (2), (7). Air wetter than the pool (P_a > P_w) floors evaporation at 0; that gain is not credited (disclosed under Warnings when it occurs).

4.3  Convective Heat Loss

Step 3: McAdams (1954) Forced Convection

Formula: h_cv = 5.68 + 3.94·u [W/(m²·°C), u in m/s] Q_conv = h_cv × A × (T_w − T_a) / 1000 [kW]

Substitution: A = 150.0 m²; u = hourly wind speed [m/s - the coefficients are SI]; at the heating design condition u = 3.65 m/s -> h_cv = 20.07 W/(m²·°C)

Result: Q_conv = 16.10 kW at the design condition (14% of the surface losses). Positive = heat loss (when T_pool > T_air).

Note: McAdams p. 207 Eq. 34 / Table XI; the coded pair is about 1 % above the printed conversion (disclosed in # 1). Jurges' data behind McAdams p. 207 Eq. 34 are for air parallel to a vertical plate; McAdams' Schack air-temperature correction and his low-velocity rule (take the larger of forced and natural convection, p. 210) are not applied; the coded pair is 5.68 + 3.94 u against the printed conversion 5.62 + 3.91 u. Table XI prints this linear row for velocities below 16 ft/s (4.88 m/s) only; above it McAdams prints h = 0.50 V'^0.78, which meets the linear row at 16 ft/s (both 4.35) and falls below it above (10.57 against 11.49 at 50 ft/s, Btu/(h ft2 F)); the coded row is applied at every wind speed and errs on the high-load side there.

4.4  Longwave Radiation Loss

Step 4: Stefan-Boltzmann + Swinbank Sky Temperature

Formula: T_sky_K = 0.0552 × T_amb_K^1.5 [Swinbank 1963] Q_rad = ε·σ·A·(T_w⁴ − T_sky⁴) / 1000 [kW]

Substitution: ε = 0.95 (water emissivity, library value), σ = 5.67e-08 W/(m²·K⁴)

Result: Q_rad = 16.46 kW at the design condition (14% of the surface losses).

Note: Clear-sky model applied to every hour (conservative on the heating side); the Swinbank paper is not held in ref.

4.5  Solar Gain

Step 5: Absorbed Shortwave Radiation

Formula: Q_solar = α × G × A / 1000 [kW]

Substitution: α = 0.9 (water absorptivity, library value), G = hourly irradiance [W/m²], A = 150.0 m²

Result: Solar gain reduces the net heating requirement. Applied to the net balance.

4.6  Makeup Water Heating

Step 6: Energy to Condition Makeup Water

Formula: Q_makeup = ṁ_evap × Cp × (T_w − T_makeup) / 3600 [kW]

Substitution: Cp = 4.186 kJ/(kg·°C); ṁ_evap = E × A [kg/h] T_makeup: winter = 12.0 °C, summer = 22.0 °C

Result: Makeup water penalty added to total heating load: Q_makeup = 2.04 kW at the heating design condition (inside q2).

4.7  Net Maintenance Load

Step 7: Total Hourly Net Load

Formula: Q_net = Q_evap + Q_conv + Q_rad − Q_solar + Q_makeup [kW]

Substitution: Positive Q_net = heating required; Negative = cooling (pool absorbs heat)

Result: Heating load = max(Q_net at the heating target, 0); Cooling load = max(−Q_net at the cooling target, 0)

Note: Hourly heating (peak, energy) acts only when the water would fall below the winter set-point 26.0 °C and hourly cooling only when it would rise above the summer set-point 30.0 °C, in every month; the water floats between them (engineer rulings 29.09.2026, heat to the winter set-point all year; cool only above the summer set-point).

4.8  Initial Heat-up / Cool-down Power

Step 8: Energy to Reach Set-Point Temperature

Formula: Q_init_heat = m·Cp·max(T_des − T_init, 0) / (3600·t); Q_init_cool = m·Cp·max(T_init − T_des, 0) / (3600·t) [kW]

Substitution: m = ρ·V = 998 × 210.0 kg, Cp = 4.186 kJ/(kg·°C) Heating: ΔT = max(26.0 °C − 10.0 °C, 0), t = 72.0 h Cooling: ΔT = max(35.0 °C − 30.0 °C, 0), t = 48.0 h

Result: Q_init_heat = 54.2 kW, Q_init_cool = 25.4 kW

Note: Directed (engineer ruling D26, 2026-09-22): a change against the season adds no power to that plant and is listed under Warnings.

4.9  Equipment Sizing

Step 9: Design-Condition Sizing (pool-industry convention — not a cited clause)

Formula: Q_size,heat = q1_heat + max(q2_heat, 0); Q_size,cool = q1_cool + max(−q2_cool, 0)

Substitution: Design heating ambient (mean of the coldest 3 months): 20.7 °C → q2 = 119.5 kW Design cooling ambient (mean of the hottest month, August 2024): 35.9 °C → q2 = 0.0 kW (the mean state of the hottest month, August 2024 is still a heating load of 0.2 kW; cooling maintenance = 0) Cooling q2 state: pool unoccupied (Shah Eq. (7)): cooling q2 0.00 kW (August 2024)

Result: Heating equipment: 173.7 kW (q1 heat-up 54.2 kW + q2 maintenance 119.5 kW) Cooling equipment: 25.4 kW (q1 pull-down, one-off 25.4 kW + q2 maintenance 0.0 kW) Implied summer water rise at this cooling size: up to 5.96 °C (at 22 Jul 2024 17:00); median of the daily maxima 0.66 °C; summer set-point 30.0 °C

Note: Sizing = q1 (initial heat-up / pull-down power, a one-off) + q2 (maintenance load at the design MEAN ambient - coldest season for heating, hottest month for cooling, engineer ruling 29.09.2026 R3 - per the methodology above); only q2 is a maintenance capacity (engineer ruling C114). Individual hours can exceed this mean-based figure — apply plant margin accordingly. Upper bound: the hottest-season hours are taken in time order with the plant held at the printed cooling size, any excess heat gain stored in the water and removed only by spare plant capacity; the pool's own self-regulation (a warmer pool loses more) is ignored. The figure depends strongly on the summer set-point - a lower set-point gives a larger rise. (engineer ruling C069) The pool cover is not applied to the equipment size: the heating plant is sized on the uncovered load (it must hold set-point with the cover off); the cover changes the annual energy only (engineer ruling D25, 2026-09-22).

⚠ Advisory

• Outdoor air was wetter than the pool surface in 717 of 8,784 hours (dP < 0, lowest -0.99 kPa): evaporation is floored at 0 on those hours and the condensation gain is not credited (Shah 2014 Eq. (7) p. 8 and ASHRAE 2007 Ch. 4 Eq. 1 p. 4.6 print no condensation case), so the heating load is overstated and the cooling load understated there (same floor as the indoor ruling D34, 2026-09-22).

• Ambient maximum 47.9 degC is >5 degC above the rated upper point (27 degC); above the rating point the COP is held at the rated value (not extrapolated) — verify against datasheet at high-T.

# 5.  Results

| Parameter | Value |
| --- | --- |
| Pool Volume | 210.0 m³ |
| Design Heating Ambient (mean of the coldest 3 months) | 20.7 °C |
| Design Cooling Ambient (mean of the hottest month, August 2024) | 35.9 °C |
| EQUIPMENT SIZING |  |
| Heating Equipment Size | 173.7 kW |
| └ Initial Heat-up Component | 54.2 kW |
| └ Maintenance at Design Temp | 119.5 kW |
| Cooling Equipment Size | 25.4 kW |
| └ q1 Pull-down (one-off initial cool-down) | 25.4 kW |
| └ q2 Maintenance at Design Temp | 0.0 kW (mean state still a heating load) (unoccupied pool governs) |
| └ Implied Summer Water Rise (upper bound, set-point dependent) | up to 5.96 °C (at 22 Jul 2024 17:00); median of the daily maxima 0.66 °C; summer set-point 30.0 °C |
| SIMULATION PEAKS |  |
| Peak Heating Load | 239.4 kW |
| └ Month of Peak | March 2024 |
| └ Heating Target (hourly heating, all months) | Winter set-point 26.0 °C (heating only below it) |
| Peak Cooling Load | 159.1 kW |
| └ Month of Peak | July 2024 |
| └ Cooling Target (hourly cooling, all months) | Summer set-point 30.0 °C (cooling only above it) |
| ANNUAL ENERGY |  |
| Heating Energy over the Simulated Period (366 days) | 379,031 kWh |
| Cooling Energy over the Simulated Period (366 days) | 46,479 kWh |
| Est. Annual Heating Energy (period / 1 whole calendar year) | 379,031 kWh |
| Est. Annual Cooling Energy (period / 1 whole calendar year) | 46,479 kWh |

Heat Loss Component Breakdown at Heating Design Condition

| Parameter | Value |
| --- | --- |
| Evaporation Loss | 84.9 kW |
| Convection Loss | 16.1 kW |
| Radiation Loss | 16.5 kW |
| Solar Gain (offset) | 0.0 kW |
| Net Loss (ex makeup) | 117.5 kW |
| Makeup Water Heat | 2.0 kW |
| Maintenance Load q2 (design) | 119.5 kW |

# 6.  Load Profile Chart

The chart below shows the simulated heating and cooling loads over the simulation period. Heating loads are highest in winter months when ambient temperature and humidity are lowest. Cooling loads (if any) occur when solar gain exceeds heat losses at high ambient temperatures.

# 7.  Equipment Schedule

Heat Pump Equipment Selection

| Parameter | Value |
| --- | --- |
| SELECTED EQUIPMENT |  |
| Manufacturer / Series | Astral Pool — i-Megaline Inver Chill |
| Model | INVER-250 |
| Quantity Selected | 1 unit |
| Inverter / Fixed Speed | Inverter (variable speed) |
| Refrigerant | R410A |
| Compressor Type | Scroll |
| Operating Ambient Range | 2.0 °C to 53.0 °C |
| HEATING PERFORMANCE (rated at A27°C / W26°C) |  |
| Rated Heating Capacity (max, per unit) | 250.00 kW |
| Heating Capacity Range (per unit) | 65.00 kW – 250.00 kW (inverter range) |
| COP at A27°C (rated, full load) | 10.37 |
| COP at A15°C (low-ambient, measured) | 7.78 |
| Heating Capacity at A15°C (fleet counted on this — ruling 19a-1) | 190.00 kW per unit (datasheet A15) |
| Electrical Input — Heating (rated, per unit) | 24.11 kW |
| COOLING PERFORMANCE (rated at A43°C / W32°C) |  |
| Rated Cooling Capacity (max, per unit) | 120.00 kW |
| Cooling Capacity Range (per unit) | 38.00 kW – 120.00 kW (inverter range) |
| EER at A43°C (rated, full load) | 5.48 |
| Electrical Input — Cooling (rated, per unit) | 21.90 kW |
| ELECTRICAL DATA |  |
| Rated Electrical Input (per unit) | — |
| Maximum Electrical Input (per unit) | 24.70 kW |
| Total Fleet Max. Electrical Input | 24.70 kW (1 × 24.70 kW) |
| PHYSICAL DATA |  |
| Net Dimensions (L × W × H) | 2260×1150×2130 mm |
| Net Weight (per unit) | — |
| Total Fleet Weight | — |
| SELECTION RESULT |  |
| Required Heating Capacity | 173.7 kW |
| Required Cooling Capacity | 25.4 kW |
| Installed Heating Capacity at the design ambient (A15 basis) | 190.00 kW (+9.4% above requirement; datasheet A15) |
| Installed Heating Capacity at rated conditions (nameplate) | 250.00 kW (1 × 250.00 kW) |
| Installed Cooling Capacity | 120.00 kW (+372.7% above requirement) |
| Governing Mode | Heating |

Energy & Operating Cost Analysis

| Parameter | Value |
| --- | --- |
| SEASONAL PERFORMANCE |  |
| Mean Seasonal COP (heating hours) | 9.02 (hourly-weighted, accounting for ambient temperature variation) |
| Mean Seasonal EER (cooling hours) | 5.51 (hourly-weighted, accounting for ambient temperature variation) |
| ANNUAL ELECTRICAL ENERGY |  |
| Heating — Electrical Energy | 42,013 kWh / year |
| Cooling — Electrical Energy | 8,431 kWh / year |
| Total Electrical Energy | 50,443 kWh / year |
| OPERATING COST |  |
| Electricity Tariff | 0.3800 AED / kWh |
| Estimated Annual Electricity Cost | 19,168 AED / year |

Note: Mean seasonal COP/EER are calculated by dividing total thermal output by total electrical input across all operating hours; COP and EER vary each hour with the ambient temperature. COP is linear between the catalogue rating point (A27) and A15 (measured), held at the higher rated value above the rating point, floored at 1.0, with the ambient clamped to the unit's operating range 2-53 degC. Below 15 degC the COP is a linear extension of the A27 / A15 pair, not a printed datasheet value - the library holds no COP below A15 (overnight call 28.09 N5, recommended option, Hussein review). EER falls 0.04 per degC above A43 and rises 0.01 per degC below, floored at 0.5. These are library curves from the Astral datasheets, not an EN 14511 rating (EN 14511-2 Table 13 rates air-to-water units at 7 / 6 degC outdoor and 40 / 45 degC water). Electrical consumption = thermal load ÷ COP(Tₐₘᵇ) per hour.

# R.  Reference Standards

ASHRAE HVAC Applications — 2007 Ch. 4 (SI Eq. 1) / 2019 Ch. 6 (I-P Eq. 2) — Natatorium evaporation equation + activity-factor table (the engine uses the SI Eq. 1 form).

Shah, M.M. (2014) ASHRAE Trans. SE-14-001  (outdoor) — Outdoor wind-driven pool evaporation (Eq. (7), p. 8), floored by the ASHRAE 2007 Ch. 4 Eq. 1 calm value (engineer extension; Shah's Table 14 takes the largest of his Eq. (1), (2), (7)); occupied outdoor pools by Eq. (5), p. 4 (Table 14, p. 13), with (ρ_r − ρ_w) held at the Table 6 p. 7 verified limit (engineer extension, ruling R2-01).

Arden Buck (1981) — Saturation vapour pressure equation (over liquid water / over ice).

McAdams (1954) — Forced-convection coefficient for an open water surface.

Stefan-Boltzmann radiation; Swinbank (1963) sky temperature  (outdoor) — Longwave radiation loss; the clear-sky temperature model applies to outdoor pools.

CIBSE Guide G (2014) / BS 5385-4:2009 — Pool water/air set-points; heat-up-rate limits (0.25/0.5 °C·h⁻¹).

ISPSC 2021 #303.1.3 — Outdoor heated-pool cover requirement + >70% heat-pump exception.

Open-Meteo Archive API — Hourly historical weather data (T, RH, wind, shortwave radiation). Weather data by Open-Meteo.com (https://open-meteo.com/), licensed CC BY 4.0 (https://creativecommons.org/licenses/by/4.0/). Generated using Copernicus Climate Change Service information 2022. Values derived from the hourly data (percentiles, simulation frames) were computed by this tool.

Engineer of record: Hussein Ragab

Generated by the Swimming Pool Load Simulator — pool thermal-load analysis on the ASHRAE HVAC Applications 2007 Ch. 4 Eq. 1 (indoor) / Shah 2014 (outdoor) evaporation basis.