## Equipment Schedule
Swimming Pool Heat-Pump — Equipment Schedule
Run: PL-01 Podium Pool ¦ Outdoor pool ¦ working units: SI
Project: Marina Commercial Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: - ¦ By: Hussein Ragab ¦ Chkd: - ¦ Rev: P2 ¦ Date: 2026-10-20
1. Pool Data
Parameter | Value | Unit | Basis / Reference
Pool type | Outdoor
Surface area | 150 | m²
Average depth | 1.4 | m
Pool volume | 210 | m³
Activity factor | 0.5 |  | ASHRAE HVAC Applications 2007 Ch. 4 p. 4.6 — activity-factor table (indoor Eq. 1 multiplier; outdoors the preset only selects occupied / unoccupied).
Occupancy (Shah 2014) | Unoccupied |  | Shah 2014 Eq. (7), p. 8, floored by ASHRAE 2007 Ch. 4 Eq. 1 at zero wind (engineer extension; Shah p. 9 and Table 14 p. 13 take the largest of his own Eq. (1), (2) and (7)) (unoccupied outdoor pool). Calm floor: ASHRAE 2007 Ch. 4 Eq. 1 at zero wind (engineer extension, ruling D29).
Desired pool temperature — winter | 26 | °C | Set-points: CIBSE Guide G (2014) # 10.6.1 p. 10-14 (air at least 2 degC above the water, max 30 degC; RH 60-70 %) and Table 10.10 (conventional pool 28 degC).
Desired pool temperature — summer | 30 | °C | Set-points: CIBSE Guide G (2014) # 10.6.1 p. 10-14 (air at least 2 degC above the water, max 30 degC; RH 60-70 %) and Table 10.10 (conventional pool 28 degC).
Makeup water temperature — winter | 12 | °C | Makeup water replaces evaporative losses at the specified supply temperature.
Makeup water temperature — summer | 22 | °C | Makeup water replaces evaporative losses at the specified supply temperature.
Initial heat-up period | 72 | h | Heat-up rates (heating direction only): 0.25 °C·h⁻¹ refill limit - BS 5385-4:2009 # 7.3.2.11 p. 19, quoted in CIBSE Guide G (2014) # 10.6.2 pp. 10-14 to 10-15; 0.5 °C·h⁻¹ heat-exchanger sizing - CIBSE Guide G (2014) # 10.6.2 p. 10-15 (a boiler / heat-exchanger capability statement, not a heat-pump limit, ruling C113). q1 is directed (ruling D26).
Initial cool-down period | 48 | h | Heat-up rates (heating direction only): 0.25 °C·h⁻¹ refill limit - BS 5385-4:2009 # 7.3.2.11 p. 19, quoted in CIBSE Guide G (2014) # 10.6.2 pp. 10-14 to 10-15; 0.5 °C·h⁻¹ heat-exchanger sizing - CIBSE Guide G (2014) # 10.6.2 p. 10-15 (a boiler / heat-exchanger capability statement, not a heat-pump limit, ruling C113). q1 is directed (ruling D26).
Pool cover | No |  | ISPSC 2021 #303.1.3 — outdoor heated-pool cover requirement (>70% heat-pump exception).
2. Design Conditions
Parameter | Value | Unit | Basis / Reference
Location | Dubai / United Arab Emirates |  | Open-Meteo Archive API — hourly T, RH, wind speed and shortwave radiation, requested with timezone=auto (site local clock).
Simulation period | 2024-01-01 to 2024-12-31 |  | Open-Meteo Archive API — hourly T, RH, wind speed and shortwave radiation, requested with timezone=auto (site local clock).
Weather data source | Open-Meteo archive (live fetch) |  | data written 2026-10-20 10:07; lat 25.077, lon 55.309
Time basis (hourly stamps, cover + HP-off schedules) | local time at the site (Asia/Dubai) |  | Open-Meteo archive requested with timezone=auto; the cover window and the HP daily off-window are evaluated on this clock.
Design heating ambient (coldest-season mean) | 20.7 | °C | Design sizing by pool-industry convention (CIBSE / Astral methodology - not a cited clause): heating ambient = mean of the auto-detected coldest 3 months, zero solar; cooling ambient = mean of the hottest month (August 2024), that month's mean solar - hottest month = the calendar month of the simulated period with the highest cooling gain at its mean conditions (mean air temperature, RH, wind and solar; summer set-point and make-up temperature), taken in the governing occupancy state (engineer ruling 29.09.2026 R3). The pool cover is not applied to the equipment size: the heating plant is sized on the uncovered load (it must hold set-point with the cover off); the cover changes the annual energy only (engineer ruling D25, 2026-09-22). Heating design basis: unoccupied (Shah Eq. (7)); 10 m wind x sheltering 1 (library value); the ASHRAE calm-air evaporation floor (ruling D29); zero solar. Together these are high-load choices for the heating size; sheltering 1.0 LOWERS the summer cooling duty (more wind, more evaporation) (ruling C068). Hourly heating (peak, energy) acts only when the water would fall below the winter set-point 26.0 °C and hourly cooling only when it would rise above the summer set-point 30.0 °C, in every month; the water floats between them (engineer rulings 29.09.2026, heat to the winter set-point all year; cool only above the summer set-point); the heating and cooling sizes are unchanged by it (heating q2 at the winter set-point on the coldest-season means, cooling q2 at the summer set-point on the hottest-month means). Cooling design basis: hottest-month mean (engineer ruling 29.09.2026 R3) - August 2024, the calendar month of the simulated period with the highest cooling gain at its mean conditions (mean air temperature, RH, wind and solar; summer set-point and make-up temperature), taken in the governing occupancy state. Cooling design duty: pool unoccupied (Shah Eq. (7)): cooling q2 0.00 kW (August 2024). Cooling units are counted at the catalogue cooling capacity at its rating air temperature; the datasheets print less at hotter air (e.g. Inverter Max BYC-103TA1 58 kW at air 35 degC, 42 kW at 46 degC, datasheet p. 1) and no derate is applied.
Coldest hour recorded | 25 Jan 2024
Design cooling ambient (hottest-month mean) | 35.9 | °C | Design sizing by pool-industry convention (CIBSE / Astral methodology - not a cited clause): heating ambient = mean of the auto-detected coldest 3 months, zero solar; cooling ambient = mean of the hottest month (August 2024), that month's mean solar - hottest month = the calendar month of the simulated period with the highest cooling gain at its mean conditions (mean air temperature, RH, wind and solar; summer set-point and make-up temperature), taken in the governing occupancy state (engineer ruling 29.09.2026 R3). The pool cover is not applied to the equipment size: the heating plant is sized on the uncovered load (it must hold set-point with the cover off); the cover changes the annual energy only (engineer ruling D25, 2026-09-22).
Hottest hour recorded | 24 Jun 2024
3. Heat-Loss Breakdown at Design Condition
Parameter | Value | Unit | Basis / Reference
Evaporation loss | 84.9 | kW | Shah 2014 Eq. (7), p. 8, floored by ASHRAE 2007 Ch. 4 Eq. 1 at zero wind (engineer extension; Shah p. 9 and Table 14 p. 13 take the largest of his own Eq. (1), (2) and (7)) (unoccupied outdoor pool). Calm floor: ASHRAE 2007 Ch. 4 Eq. 1 at zero wind (engineer extension, ruling D29).
Convection loss | 16.1 | kW | McAdams (1954) — h_cv = 5.68 + 3.94·u [W/(m²·°C)] for forced convection from an open water surface (engine constants; coded pair about 1 % above the printed p. 207 conversion). Jurges' data behind McAdams p. 207 Eq. 34 are for air parallel to a vertical plate; McAdams' Schack air-temperature correction and his low-velocity rule (take the larger of forced and natural convection, p. 210) are not applied; the coded pair is 5.68 + 3.94 u against the printed conversion 5.62 + 3.91 u. Table XI prints this linear row for velocities below 16 ft/s (4.88 m/s) only; above it McAdams prints h = 0.50 V'^0.78, which meets the linear row at 16 ft/s (both 4.35) and falls below it above (10.57 against 11.49 at 50 ft/s, Btu/(h ft2 F)); the coded row is applied at every wind speed and errs on the high-load side there.
Radiation loss | 16.46 | kW | Stefan-Boltzmann Q_rad = ε·σ·(T_pool⁴ − T_sky⁴), ε = 0.95 for water (library value); Swinbank (1963) clear-sky temperature.
Solar gain (offset) | 0 | kW | Zero at the heating design condition (worst-case overnight).
Net loss (excluding makeup) | 117.46 | kW | Evaporation + convection + radiation − solar. The makeup-water heat and any conduction allowance follow as their own rows.
Makeup water heat | 2.04 | kW | Makeup water replaces evaporative losses at the specified supply temperature. At the heating design condition.
Maintenance load q2 (design) | 119.5 | kW | Net loss + makeup water heat + conduction allowance = the q2 the heating sizing uses.
4. Equipment Sizing
Parameter | Value | Unit | Basis / Reference
q1 — initial heat-up | 54.15 | kW | Heat-up rates (heating direction only): 0.25 °C·h⁻¹ refill limit - BS 5385-4:2009 # 7.3.2.11 p. 19, quoted in CIBSE Guide G (2014) # 10.6.2 pp. 10-14 to 10-15; 0.5 °C·h⁻¹ heat-exchanger sizing - CIBSE Guide G (2014) # 10.6.2 p. 10-15 (a boiler / heat-exchanger capability statement, not a heat-pump limit, ruling C113). q1 is directed (ruling D26).
q2 — maintenance at design ambient (heating) | 119.5 | kW | Design sizing by pool-industry convention (CIBSE / Astral methodology - not a cited clause): heating ambient = mean of the auto-detected coldest 3 months, zero solar; cooling ambient = mean of the hottest month (August 2024), that month's mean solar - hottest month = the calendar month of the simulated period with the highest cooling gain at its mean conditions (mean air temperature, RH, wind and solar; summer set-point and make-up temperature), taken in the governing occupancy state (engineer ruling 29.09.2026 R3). The pool cover is not applied to the equipment size: the heating plant is sized on the uncovered load (it must hold set-point with the cover off); the cover changes the annual energy only (engineer ruling D25, 2026-09-22).
Required heating capacity | 173.66 | kW | Q_sizing = q1 + q2.
q1 — pull-down (one-off initial cool-down) | 25.38 | kW | Heat-up rates (heating direction only): 0.25 °C·h⁻¹ refill limit - BS 5385-4:2009 # 7.3.2.11 p. 19, quoted in CIBSE Guide G (2014) # 10.6.2 pp. 10-14 to 10-15; 0.5 °C·h⁻¹ heat-exchanger sizing - CIBSE Guide G (2014) # 10.6.2 p. 10-15 (a boiler / heat-exchanger capability statement, not a heat-pump limit, ruling C113). q1 is directed (ruling D26). A one-off pull-down, not a maintenance capacity (engineer ruling C114).
q2 — maintenance at design ambient (cooling) | 0 | kW | Design sizing by pool-industry convention (CIBSE / Astral methodology - not a cited clause): heating ambient = mean of the auto-detected coldest 3 months, zero solar; cooling ambient = mean of the hottest month (August 2024), that month's mean solar - hottest month = the calendar month of the simulated period with the highest cooling gain at its mean conditions (mean air temperature, RH, wind and solar; summer set-point and make-up temperature), taken in the governing occupancy state (engineer ruling 29.09.2026 R3). The pool cover is not applied to the equipment size: the heating plant is sized on the uncovered load (it must hold set-point with the cover off); the cover changes the annual energy only (engineer ruling D25, 2026-09-22). Note: the mean state of the hottest month, August 2024 is still a heating load of 0.2 kW; cooling maintenance = 0. State: pool unoccupied (Shah Eq. (7)): cooling q2 0.00 kW (August 2024).
Required cooling capacity | 25.38 | kW | Q_sizing = q1 (one-off pull-down) + q2 (maintenance).
Implied summer water rise at this cooling size (maximum) | 5.96 | °C | At 22 Jul 2024 17:00. Summer set-point 30.0 °C. Upper bound: the hottest-season hours are taken in time order with the plant held at the printed cooling size, any excess heat gain stored in the water and removed only by spare plant capacity; the pool's own self-regulation (a warmer pool loses more) is ignored. The figure depends strongly on the summer set-point - a lower set-point gives a larger rise. (engineer ruling C069)
Implied summer water rise (median of the daily maxima) | 0.66 | °C | Same recursion; half the hottest-season days peak below this.
Peak heating load (simulated hour) | 239.44 | kW | Occurred: March 2024. Individual hours can exceed the mean-based sizing figure — apply plant margin accordingly. Hourly heating (peak, energy) acts only when the water would fall below the winter set-point 26.0 °C and hourly cooling only when it would rise above the summer set-point 30.0 °C, in every month; the water floats between them (engineer rulings 29.09.2026, heat to the winter set-point all year; cool only above the summer set-point).
Peak cooling load (simulated hour) | 159.13 | kW | Occurred: July 2024. Cooling acts only above the summer set-point 30.0 °C, in every month (see the peak heating row).
5. Selected Heat Pump
Parameter | Value | Unit | Basis / Reference
Manufacturer / series | Astral Pool — i-Megaline Inver Chill |  | Astral Pool catalogue nameplate data (tool heat-pump library).
Model | INVER-250 |  | Astral Pool catalogue nameplate data (tool heat-pump library).
Quantity selected | 1 | unit(s) | n = ceil(required capacity / unit capacity), heating and cooling each checked; the larger count governs.
Inverter / fixed speed | Inverter (variable speed) |  | Astral Pool catalogue nameplate data (tool heat-pump library).
Refrigerant | R410A |  | Astral Pool catalogue nameplate data (tool heat-pump library).
Compressor type | Scroll |  | Astral Pool catalogue nameplate data (tool heat-pump library).
Operating ambient range | 2 to 53 | °C | Astral Pool catalogue nameplate data (tool heat-pump library).
Rated heating capacity, per unit (A27°C / W26°C) | 250 | kW | Astral Pool catalogue nameplate data (tool heat-pump library).
Heating capacity range, per unit | 65.00 - 250.00 (inverter) | kW | Astral Pool catalogue nameplate data (tool heat-pump library).
COP at A27°C (rated, full load) | 10.37 |  | Astral Pool catalogue nameplate data (tool heat-pump library).
COP at A15°C (low ambient, measured) | 7.78 |  | COP is linear between the catalogue rating point (A27) and A15 (measured), held at the higher rated value above the rating point, floored at 1.0, with the ambient clamped to the unit's operating range 2-53 degC. Below 15 degC the COP is a linear extension of the A27 / A15 pair, not a printed datasheet value - the library holds no COP below A15 (overnight call 28.09 N5, recommended option, Hussein review). EER falls 0.04 per degC above A43 and rises 0.01 per degC below, floored at 0.5. These are library curves from the Astral datasheets, not an EN 14511 rating (EN 14511-2 Table 13 rates air-to-water units at 7 / 6 degC outdoor and 40 / 45 degC water). Electrical input = thermal load / COP(T_amb).
Heating capacity at A15°C, per unit (fleet basis) | 190 | kW | datasheet A15. The unit count and the installed margin are taken on this design-ambient figure (engineer ruling 19a-1, 2026-09-05).
Electrical input — heating, per unit | 24.11 | kW | COP is linear between the catalogue rating point (A27) and A15 (measured), held at the higher rated value above the rating point, floored at 1.0, with the ambient clamped to the unit's operating range 2-53 degC. Below 15 degC the COP is a linear extension of the A27 / A15 pair, not a printed datasheet value - the library holds no COP below A15 (overnight call 28.09 N5, recommended option, Hussein review). EER falls 0.04 per degC above A43 and rises 0.01 per degC below, floored at 0.5. These are library curves from the Astral datasheets, not an EN 14511 rating (EN 14511-2 Table 13 rates air-to-water units at 7 / 6 degC outdoor and 40 / 45 degC water). Electrical input = thermal load / COP(T_amb).
Rated cooling capacity, per unit (A43°C / W32°C) | 120 | kW | Astral Pool catalogue nameplate data (tool heat-pump library).
Cooling capacity range, per unit | 38.00 - 120.00 (inverter) | kW | Astral Pool catalogue nameplate data (tool heat-pump library).
EER at A43°C (rated, full load) | 5.48 |  | Astral Pool catalogue nameplate data (tool heat-pump library).
Electrical input — cooling, per unit | 21.9 | kW | COP is linear between the catalogue rating point (A27) and A15 (measured), held at the higher rated value above the rating point, floored at 1.0, with the ambient clamped to the unit's operating range 2-53 degC. Below 15 degC the COP is a linear extension of the A27 / A15 pair, not a printed datasheet value - the library holds no COP below A15 (overnight call 28.09 N5, recommended option, Hussein review). EER falls 0.04 per degC above A43 and rises 0.01 per degC below, floored at 0.5. These are library curves from the Astral datasheets, not an EN 14511 rating (EN 14511-2 Table 13 rates air-to-water units at 7 / 6 degC outdoor and 40 / 45 degC water). Electrical input = thermal load / COP(T_amb).
Rated electrical input, per unit | - |  | Astral Pool catalogue nameplate data (tool heat-pump library).
Maximum electrical input, per unit | 24.7 | kW | Astral Pool catalogue nameplate data (tool heat-pump library).
Total fleet maximum electrical input | 24.7 | kW | 1 × nameplate maximum.
Net dimensions (L × W × H) | 2260×1150×2130 | mm | Astral Pool catalogue nameplate data (tool heat-pump library).
Net weight, per unit | - |  | Astral Pool catalogue nameplate data (tool heat-pump library).
Total fleet weight | -
Required heating capacity | 173.7 | kW | Selection duty.
Required cooling capacity | 25.4 | kW | Selection duty.
Installed heating capacity at the design ambient | 190 | kW | +9.4% above requirement (datasheet A15).
Installed heating capacity at rated conditions (nameplate) | 250 | kW | 1 × rated capacity; not the selection basis.
Installed cooling capacity | 120 | kW | +372.7% above requirement.
Governing mode | Heating |  | The mode with the tighter margin sets the unit count (when the heating margin is withheld, or a mode has no duty, the larger unit count).
6. Energy & Operating Cost
Parameter | Value | Unit | Basis / Reference
Mean seasonal COP (heating hours) | 9.02 |  | COP is linear between the catalogue rating point (A27) and A15 (measured), held at the higher rated value above the rating point, floored at 1.0, with the ambient clamped to the unit's operating range 2-53 degC. Below 15 degC the COP is a linear extension of the A27 / A15 pair, not a printed datasheet value - the library holds no COP below A15 (overnight call 28.09 N5, recommended option, Hussein review). EER falls 0.04 per degC above A43 and rises 0.01 per degC below, floored at 0.5. These are library curves from the Astral datasheets, not an EN 14511 rating (EN 14511-2 Table 13 rates air-to-water units at 7 / 6 degC outdoor and 40 / 45 degC water). Electrical input = thermal load / COP(T_amb).
Mean seasonal EER (cooling hours) | 5.51 |  | COP is linear between the catalogue rating point (A27) and A15 (measured), held at the higher rated value above the rating point, floored at 1.0, with the ambient clamped to the unit's operating range 2-53 degC. Below 15 degC the COP is a linear extension of the A27 / A15 pair, not a printed datasheet value - the library holds no COP below A15 (overnight call 28.09 N5, recommended option, Hussein review). EER falls 0.04 per degC above A43 and rises 0.01 per degC below, floored at 0.5. These are library curves from the Astral datasheets, not an EN 14511 rating (EN 14511-2 Table 13 rates air-to-water units at 7 / 6 degC outdoor and 40 / 45 degC water). Electrical input = thermal load / COP(T_amb).
Annual electrical energy — heating | 42013 | kWh/year
Annual electrical energy — cooling | 8431 | kWh/year
Total annual electrical energy | 50443 | kWh/year
Electricity tariff | 0.38 | AED/kWh
Estimated annual electricity cost | 19168 | AED/year
Reference Standards
Reference | Application
ASHRAE HVAC Applications — 2007 Ch. 4 (SI Eq. 1) / 2019 Ch. 6 (I-P Eq. 2) | Natatorium evaporation equation + activity-factor table (the engine uses the SI Eq. 1 form).
Shah, M.M. (2014) ASHRAE Trans. SE-14-001 (outdoor) | Outdoor wind-driven pool evaporation (Eq. (7), p. 8), floored by the ASHRAE 2007 Ch. 4 Eq. 1 calm value (engineer extension; Shah's Table 14 takes the largest of his Eq. (1), (2), (7)); occupied outdoor pools by Eq. (5), p. 4 (Table 14, p. 13), with (ρ_r − ρ_w) held at the Table 6 p. 7 verified limit (engineer extension, ruling R2-01).
Arden Buck (1981) | Saturation vapour pressure equation (over liquid water / over ice).
McAdams (1954) | Forced-convection coefficient for an open water surface.
Stefan-Boltzmann radiation; Swinbank (1963) sky temperature (outdoor) | Longwave radiation loss; the clear-sky temperature model applies to outdoor pools.
CIBSE Guide G (2014) / BS 5385-4:2009 | Pool water/air set-points; heat-up-rate limits (0.25/0.5 °C·h⁻¹).
ISPSC 2021 #303.1.3 | Outdoor heated-pool cover requirement + >70% heat-pump exception.
Open-Meteo Archive API | Hourly historical weather data (T, RH, wind, shortwave radiation). Weather data by Open-Meteo.com (https://open-meteo.com/), licensed CC BY 4.0 (https://creativecommons.org/licenses/by/4.0/). Generated using Copernicus Climate Change Service information 2022. Values derived from the hourly data (percentiles, simulation frames) were computed by this tool.
Generated by the Swimming Pool Load Simulator (Tool 19a). Internal calc is SI; displayed magnitudes follow the unit system.

## Load Schedule
Monthly Pool Load Schedule
Run: PL-01 Podium Pool ¦ Per-month heating / cooling loads ¦ working units: SI
Month | Avg heating (kW) | Peak heating (kW) | Avg cooling (kW) | Peak cooling (kW)
Jan 2024 | 92.3 | 188.5 | 0.1 | 25
Feb 2024 | 109.9 | 237.8 | 0.1 | 30.7
Mar 2024 | 76.1 | 239.4 | 1 | 65.7
Apr 2024 | 55.1 | 152.5 | 1.6 | 68.1
May 2024 | 25.2 | 116.2 | 4.4 | 103.3
Jun 2024 | 10.6 | 134.6 | 9 | 108.4
Jul 2024 | 3.6 | 80.6 | 15.9 | 159.1
Aug 2024 | 1.5 | 63.4 | 16.2 | 121.9
Sep 2024 | 7 | 118.6 | 9.3 | 98.6
Oct 2024 | 17.1 | 87.3 | 3.4 | 75.9
Nov 2024 | 39 | 141.1 | 2.1 | 60.6
Dec 2024 | 82.7 | 183.3 | 0.2 | 26.4

## Hourly Data
Hourly Pool Load Data
Per-hour simulation frame ¦ working units: SI
Time (local, Asia/Dubai) | Ambient DB (°C) | Ambient RH (%) | Wind (m/s) | Solar (W/m²) | Heat Target (°C) | Cool Target (°C) | Makeup Water (°C) | Heating Load (kW) | Cooling Load (kW)
2024-01-01 | 21.5 | 78 | 1.41 | 0 | 26 | 30 | 12 | 57.2128 | 0
2024-01-01 01:00 | 21 | 79 | 1.62 | 0 | 26 | 30 | 12 | 63.6234 | 0
2024-01-01 02:00 | 19.6 | 85 | 2.18 | 0 | 26 | 30 | 12 | 79.4098 | 0
2024-01-01 03:00 | 19.2 | 88 | 2.33 | 0 | 26 | 30 | 12 | 82.8763 | 0
2024-01-01 04:00 | 19.4 | 88 | 2.02 | 0 | 26 | 30 | 12 | 75.4998 | 0
2024-01-01 05:00 | 20.5 | 81 | 3.41 | 0 | 26 | 30 | 12 | 97.6615 | 0
2024-01-01 06:00 | 19.4 | 85 | 2.3 | 0 | 26 | 30 | 12 | 83.1852 | 0
2024-01-01 07:00 | 21.9 | 79 | 0.5 | 0 | 26 | 30 | 12 | 37.4987 | 0
2024-01-01 08:00 | 20 | 88 | 2.38 | 44 | 26 | 30 | 12 | 71.7081 | 0
2024-01-01 09:00 | 22 | 78 | 2.53 | 210 | 26 | 30 | 12 | 45.0311 | 0
2024-01-01 10:00 | 24 | 70 | 2.47 | 394 | 26 | 30 | 12 | 11.5767 | 0
2024-01-01 11:00 | 25.5 | 66 | 2.72 | 542 | 26 | 30 | 12 | 0 | 0
2024-01-01 12:00 | 26.5 | 58 | 3.93 | 633 | 26 | 30 | 12 | 0 | 0
2024-01-01 13:00 | 26.7 | 56 | 5.28 | 659 | 26 | 30 | 12 | 6.5495 | 0
2024-01-01 14:00 | 26.5 | 58 | 6.14 | 616 | 26 | 30 | 12 | 19.6914 | 0
2024-01-01 15:00 | 26.2 | 59 | 6.39 | 509 | 26 | 30 | 12 | 38.5463 | 0
2024-01-01 16:00 | 25.5 | 63 | 6.56 | 348 | 26 | 30 | 12 | 62.5381 | 0
2024-01-01 17:00 | 24.4 | 67 | 5.54 | 160 | 26 | 30 | 12 | 83.185 | 0
2024-01-01 18:00 | 23.4 | 72 | 4 | 18 | 26 | 30 | 12 | 86.45 | 0
2024-01-01 19:00 | 23.2 | 74 | 4.16 | 0 | 26 | 30 | 12 | 90.1498 | 0
2024-01-01 20:00 | 22.8 | 75 | 4.3 | 0 | 26 | 30 | 12 | 94.9495 | 0
2024-01-01 21:00 | 22.6 | 76 | 4.78 | 0 | 26 | 30 | 12 | 102.0265 | 0
2024-01-01 22:00 | 22.3 | 76 | 4.78 | 0 | 26 | 30 | 12 | 105.6448 | 0
2024-01-01 23:00 | 22 | 76 | 4.54 | 0 | 26 | 30 | 12 | 105.847 | 0
2024-01-02 | 21.6 | 79 | 4.26 | 0 | 26 | 30 | 12 | 102.0311 | 0
2024-01-02 01:00 | 21.4 | 80 | 4.3 | 0 | 26 | 30 | 12 | 103.4469 | 0
2024-01-02 02:00 | 21.2 | 82 | 4.3 | 0 | 26 | 30 | 12 | 102.9344 | 0
2024-01-02 03:00 | 21.1 | 83 | 4.2 | 0 | 26 | 30 | 12 | 101.2636 | 0
2024-01-02 04:00 | 21 | 83 | 4.3 | 0 | 26 | 30 | 12 | 103.8296 | 0
2024-01-02 05:00 | 21.1 | 82 | 4.1 | 0 | 26 | 30 | 12 | 101.1408 | 0
2024-01-02 06:00 | 21.2 | 81 | 4.2 | 0 | 26 | 30 | 12 | 102.8454 | 0
2024-01-02 07:00 | 20.9 | 79 | 3.91 | 0 | 26 | 30 | 12 | 104.2253 | 0
2024-01-02 08:00 | 21.8 | 74 | 3.51 | 41 | 26 | 30 | 12 | 89.6628 | 0
2024-01-02 09:00 | 23.7 | 65 | 4.56 | 207 | 26 | 30 | 12 | 76.3466 | 0
2024-01-02 10:00 | 24.6 | 60 | 5.73 | 388 | 26 | 30 | 12 | 66.359 | 0
2024-01-02 11:00 | 25.2 | 57 | 5.82 | 541 | 26 | 30 | 12 | 45.5934 | 0
2024-01-02 12:00 | 25.5 | 55 | 5.88 | 634 | 26 | 30 | 12 | 34.3922 | 0
2024-01-02 13:00 | 25.7 | 53 | 5.94 | 661 | 26 | 30 | 12 | 33.487 | 0
2024-01-02 14:00 | 25.5 | 52 | 6.19 | 607 | 26 | 30 | 12 | 48.9113 | 0
2024-01-02 15:00 | 25.3 | 53 | 6.09 | 502 | 26 | 30 | 12 | 61.984 | 0
2024-01-02 16:00 | 24.8 | 54 | 5.91 | 340 | 26 | 30 | 12 | 85.3786 | 0
2024-01-02 17:00 | 24 | 54 | 5.95 | 163 | 26 | 30 | 12 | 119.5858 | 0
2024-01-02 18:00 | 22.9 | 60 | 4.92 | 20 | 26 | 30 | 12 | 124.1802 | 0
2024-01-02 19:00 | 22.2 | 64 | 4.3 | 0 | 26 | 30 | 12 | 117.7073 | 0
2024-01-02 20:00 | 21.6 | 68 | 3.61 | 0 | 26 | 30 | 12 | 106.1856 | 0
2024-01-02 21:00 | 20.8 | 73 | 3.08 | 0 | 26 | 30 | 12 | 97.9112 | 0
2024-01-02 22:00 | 20.1 | 77 | 2.71 | 0 | 26 | 30 | 12 | 92.6558 | 0
2024-01-02 23:00 | 19.3 | 80 | 2.55 | 0 | 26 | 30 | 12 | 92.9882 | 0
2024-01-03 | 18.8 | 82 | 2.61 | 0 | 26 | 30 | 12 | 96.3234 | 0
2024-01-03 01:00 | 18.6 | 83 | 2.78 | 0 | 26 | 30 | 12 | 100.5112 | 0
2024-01-03 02:00 | 18.3 | 85 | 3.2 | 0 | 26 | 30 | 12 | 109.6428 | 0
2024-01-03 03:00 | 18.1 | 85 | 3.45 | 0 | 26 | 30 | 12 | 116.3635 | 0
2024-01-03 04:00 | 18 | 85 | 3.61 | 0 | 26 | 30 | 12 | 120.4424 | 0
2024-01-03 05:00 | 17.7 | 81 | 3.58 | 0 | 26 | 30 | 12 | 126.4797 | 0
2024-01-03 06:00 | 17.2 | 83 | 4.08 | 0 | 26 | 30 | 12 | 139.5591 | 0
2024-01-03 07:00 | 16.8 | 85 | 4.33 | 0 | 26 | 30 | 12 | 146.6031 | 0
2024-01-03 08:00 | 17.5 | 81 | 4.14 | 43 | 26 | 30 | 12 | 134.2007 | 0
2024-01-03 09:00 | 20 | 70 | 3.69 | 207 | 26 | 30 | 12 | 91.849 | 0
2024-01-03 10:00 | 22.6 | 60 | 3.97 | 399 | 26 | 30 | 12 | 60.01 | 0
2024-01-03 11:00 | 24.7 | 50 | 4.42 | 523 | 26 | 30 | 12 | 46.5984 | 0
2024-01-03 12:00 | 25.4 | 46 | 5.92 | 598 | 26 | 30 | 12 | 60.9482 | 0
2024-01-03 13:00 | 25.6 | 45 | 6.22 | 570 | 26 | 30 | 12 | 69.2627 | 0
2024-01-03 14:00 | 25.6 | 44 | 6.55 | 534 | 26 | 30 | 12 | 81.5057 | 0
2024-01-03 15:00 | 25.1 | 49 | 5.99 | 468 | 26 | 30 | 12 | 76.4547 | 0
2024-01-03 16:00 | 24.6 | 52 | 5.56 | 352 | 26 | 30 | 12 | 85.1344 | 0
2024-01-03 17:00 | 23.8 | 56 | 4.53 | 165 | 26 | 30 | 12 | 95.4914 | 0
2024-01-03 18:00 | 22.7 | 63 | 3.64 | 21 | 26 | 30 | 12 | 100.2577 | 0
2024-01-03 19:00 | 22.1 | 67 | 3.18 | 0 | 26 | 30 | 12 | 95.3863 | 0
2024-01-03 20:00 | 21.5 | 70 | 3.06 | 0 | 26 | 30 | 12 | 94.9065 | 0
2024-01-03 21:00 | 20.9 | 74 | 3.29 | 0 | 26 | 30 | 12 | 99.7598 | 0
2024-01-03 22:00 | 20.9 | 71 | 3.31 | 0 | 26 | 30 | 12 | 103.4805 | 0
2024-01-03 23:00 | 21.1 | 72 | 4.24 | 0 | 26 | 30 | 12 | 116.6969 | 0
2024-01-04 | 21.2 | 73 | 4.9 | 0 | 26 | 30 | 12 | 124.9441 | 0
2024-01-04 01:00 | 21 | 73 | 4.78 | 0 | 26 | 30 | 12 | 125.2882 | 0
2024-01-04 02:00 | 20.7 | 74 | 4.36 | 0 | 26 | 30 | 12 | 120.1954 | 0
2024-01-04 03:00 | 20.6 | 76 | 4.3 | 0 | 26 | 30 | 12 | 117.5783 | 0
2024-01-04 04:00 | 20 | 81 | 5 | 0 | 26 | 30 | 12 | 128.8806 | 0
2024-01-04 05:00 | 21.3 | 71 | 4.4 | 0 | 26 | 30 | 12 | 118.6544 | 0
2024-01-04 06:00 | 21.3 | 71 | 4.9 | 0 | 26 | 30 | 12 | 126.8208 | 0
2024-01-04 07:00 | 21.2 | 71 | 4.72 | 0 | 26 | 30 | 12 | 125.0096 | 0
2024-01-04 08:00 | 21.5 | 68 | 5.11 | 40 | 26 | 30 | 12 | 127.1827 | 0
2024-01-04 09:00 | 23.2 | 58 | 7.12 | 199 | 26 | 30 | 12 | 134.0814 | 0
2024-01-04 10:00 | 23.7 | 56 | 8.27 | 371 | 26 | 30 | 12 | 124.7617 | 0
2024-01-04 11:00 | 24.1 | 54 | 8.61 | 517 | 26 | 30 | 12 | 108.7445 | 0
2024-01-04 12:00 | 24.3 | 53 | 9.02 | 614 | 26 | 30 | 12 | 100.7623 | 0
2024-01-04 13:00 | 24.3 | 52 | 9.11 | 637 | 26 | 30 | 12 | 101.6678 | 0
2024-01-04 14:00 | 24.3 | 51 | 9.27 | 619 | 26 | 30 | 12 | 109.1092 | 0
2024-01-04 15:00 | 24 | 51 | 9.18 | 495 | 26 | 30 | 12 | 129.3663 | 0
2024-01-04 16:00 | 23.6 | 51 | 9.08 | 336 | 26 | 30 | 12 | 155.6415 | 0
2024-01-04 17:00 | 23.1 | 52 | 8.76 | 142 | 26 | 30 | 12 | 182.0535 | 0
2024-01-04 18:00 | 22.2 | 56 | 6.99 | 21 | 26 | 30 | 12 | 173.7322 | 0
2024-01-04 19:00 | 22 | 56 | 6.32 | 0 | 26 | 30 | 12 | 167.7583 | 0
2024-01-04 20:00 | 22 | 58 | 6.99 | 0 | 26 | 30 | 12 | 175.1059 | 0
2024-01-04 21:00 | 21.5 | 61 | 6.51 | 0 | 26 | 30 | 12 | 167.7747 | 0
2024-01-04 22:00 | 20.9 | 65 | 5.95 | 0 | 26 | 30 | 12 | 158.6121 | 0
2024-01-04 23:00 | 20.6 | 67 | 5.47 | 0 | 26 | 30 | 12 | 150.5845 | 0
2024-01-05 | 20.3 | 68 | 4.95 | 0 | 26 | 30 | 12 | 143.1488 | 0
2024-01-05 01:00 | 19.8 | 71 | 4.18 | 0 | 26 | 30 | 12 | 129.9404 | 0
2024-01-05 02:00 | 19.5 | 73 | 3.22 | 0 | 26 | 30 | 12 | 111.5019 | 0
2024-01-05 03:00 | 19.2 | 73 | 3.1 | 0 | 26 | 30 | 12 | 111.4682 | 0
2024-01-05 04:00 | 18.7 | 75 | 2.8 | 0 | 26 | 30 | 12 | 107.0872 | 0
2024-01-05 05:00 | 17.6 | 82 | 2.68 | 0 | 26 | 30 | 12 | 106.8729 | 0
2024-01-05 06:00 | 17.1 | 83 | 3.31 | 0 | 26 | 30 | 12 | 123.9903 | 0
2024-01-05 07:00 | 16.1 | 86 | 3.9 | 0 | 26 | 30 | 12 | 143.0804 | 0
2024-01-05 08:00 | 16.5 | 83 | 3.71 | 43 | 26 | 30 | 12 | 132.2226 | 0
2024-01-05 09:00 | 19.1 | 70 | 3.32 | 213 | 26 | 30 | 12 | 91.1553 | 0
2024-01-05 10:00 | 22 | 58 | 3.1 | 400 | 26 | 30 | 12 | 51.1252 | 0
2024-01-05 11:00 | 23.6 | 51 | 1.92 | 553 | 26 | 30 | 12 | 1.7616 | 0
2024-01-05 12:00 | 24.5 | 45 | 1.8 | 649 | 26 | 30 | 12 | 0 | 0
2024-01-05 13:00 | 25.2 | 42 | 2.24 | 678 | 26 | 30 | 12 | 0 | 0
2024-01-05 14:00 | 25.4 | 42 | 3.05 | 635 | 26 | 30 | 12 | 13.1542 | 0
2024-01-05 15:00 | 25.2 | 44 | 3.91 | 526 | 26 | 30 | 12 | 42.846 | 0
2024-01-05 16:00 | 24.5 | 47 | 4.36 | 340 | 26 | 30 | 12 | 77.2941 | 0
2024-01-05 17:00 | 23.6 | 55 | 5.01 | 115 | 26 | 30 | 12 | 113.8674 | 0
2024-01-05 18:00 | 22.7 | 60 | 4.88 | 23 | 26 | 30 | 12 | 125.2803 | 0
2024-01-05 19:00 | 22.2 | 62 | 3.83 | 0 | 26 | 30 | 12 | 112.3459 | 0
2024-01-05 20:00 | 21.7 | 64 | 3.67 | 0 | 26 | 30 | 12 | 111.3808 | 0
2024-01-05 21:00 | 20.9 | 67 | 3.3 | 0 | 26 | 30 | 12 | 107.7744 | 0
2024-01-05 22:00 | 19.9 | 72 | 2.61 | 0 | 26 | 30 | 12 | 96.7147 | 0
2024-01-05 23:00 | 18.8 | 82 | 2.06 | 0 | 26 | 30 | 12 | 84.6972 | 0
2024-01-06 | 18.2 | 86 | 2.27 | 0 | 26 | 30 | 12 | 90.4751 | 0
2024-01-06 01:00 | 17.7 | 86 | 2.69 | 0 | 26 | 30 | 12 | 103.1697 | 0
2024-01-06 02:00 | 17 | 85 | 3.03 | 0 | 26 | 30 | 12 | 116.909 | 0
2024-01-06 03:00 | 16.1 | 88 | 3.1 | 0 | 26 | 30 | 12 | 123.2958 | 0
2024-01-06 04:00 | 15.4 | 90 | 3.1 | 0 | 26 | 30 | 12 | 127.3505 | 0
2024-01-06 05:00 | 15.9 | 88 | 2.94 | 0 | 26 | 30 | 12 | 121.1478 | 0
2024-01-06 06:00 | 15.7 | 90 | 3.23 | 0 | 26 | 30 | 12 | 127.9621 | 0
2024-01-06 07:00 | 15.4 | 90 | 3.37 | 0 | 26 | 30 | 12 | 133.7069 | 0
2024-01-06 08:00 | 16.3 | 88 | 3.11 | 43 | 26 | 30 | 12 | 116.1019 | 0
2024-01-06 09:00 | 19.3 | 75 | 2.82 | 211 | 26 | 30 | 12 | 74.4504 | 0
2024-01-06 10:00 | 22.3 | 65 | 2.92 | 398 | 26 | 30 | 12 | 37.6294 | 0
2024-01-06 11:00 | 24.1 | 57 | 3.45 | 550 | 26 | 30 | 12 | 21.3368 | 0
2024-01-06 12:00 | 24.9 | 52 | 3.92 | 620 | 26 | 30 | 12 | 20.0112 | 0
2024-01-06 13:00 | 25.1 | 49 | 4.47 | 653 | 26 | 30 | 12 | 27.7401 | 0
2024-01-06 14:00 | 25 | 49 | 5.02 | 611 | 26 | 30 | 12 | 43.2876 | 0
2024-01-06 15:00 | 24.5 | 50 | 5.34 | 501 | 26 | 30 | 12 | 66.665 | 0
2024-01-06 16:00 | 24.1 | 52 | 5.55 | 359 | 26 | 30 | 12 | 89.7208 | 0
2024-01-06 17:00 | 23.4 | 54 | 5.69 | 170 | 26 | 30 | 12 | 121.5874 | 0
2024-01-06 18:00 | 22.4 | 60 | 4.65 | 24 | 26 | 30 | 12 | 124.4251 | 0
2024-01-06 19:00 | 21.7 | 63 | 3.61 | 0 | 26 | 30 | 12 | 111.5285 | 0
2024-01-06 20:00 | 21.1 | 65 | 3.51 | 0 | 26 | 30 | 12 | 112.4321 | 0
2024-01-06 21:00 | 20.4 | 66 | 3.34 | 0 | 26 | 30 | 12 | 113.8448 | 0
2024-01-06 22:00 | 19.6 | 71 | 3.06 | 0 | 26 | 30 | 12 | 109.3772 | 0
2024-01-06 23:00 | 18.9 | 74 | 2.86 | 0 | 26 | 30 | 12 | 107.7609 | 0
2024-01-07 | 18.2 | 76 | 2.91 | 0 | 26 | 30 | 12 | 112.4507 | 0
2024-01-07 01:00 | 17.6 | 79 | 3.04 | 0 | 26 | 30 | 12 | 117.424 | 0
2024-01-07 02:00 | 17.3 | 80 | 3.28 | 0 | 26 | 30 | 12 | 124.328 | 0
2024-01-07 03:00 | 16.8 | 83 | 3.41 | 0 | 26 | 30 | 12 | 128.7335 | 0
2024-01-07 04:00 | 16.6 | 84 | 3.49 | 0 | 26 | 30 | 12 | 131.3357 | 0
2024-01-07 05:00 | 16.7 | 81 | 3.81 | 0 | 26 | 30 | 12 | 140.357 | 0
2024-01-07 06:00 | 16 | 83 | 4.11 | 0 | 26 | 30 | 12 | 151.543 | 0
2024-01-07 07:00 | 15.4 | 86 | 4.4 | 0 | 26 | 30 | 12 | 160.8987 | 0
2024-01-07 08:00 | 16.1 | 82 | 4.2 | 42 | 26 | 30 | 12 | 147.9385 | 0
2024-01-07 09:00 | 18.7 | 71 | 4 | 200 | 26 | 30 | 12 | 109.7109 | 0
2024-01-07 10:00 | 21.4 | 61 | 4.24 | 396 | 26 | 30 | 12 | 75.2595 | 0
2024-01-07 11:00 | 22.9 | 52 | 3.47 | 558 | 26 | 30 | 12 | 37.47 | 0
2024-01-07 12:00 | 23.7 | 46 | 3 | 656 | 26 | 30 | 12 | 16.1817 | 0
2024-01-07 13:00 | 24.3 | 42 | 2.64 | 686 | 26 | 30 | 12 | 5.0579 | 0
2024-01-07 14:00 | 24.6 | 42 | 2.33 | 641 | 26 | 30 | 12 | 2.2505 | 0
2024-01-07 15:00 | 24.5 | 44 | 2.33 | 521 | 26 | 30 | 12 | 16.8704 | 0
2024-01-07 16:00 | 24.1 | 45 | 2.66 | 363 | 26 | 30 | 12 | 46.8897 | 0
2024-01-07 17:00 | 23 | 52 | 3.55 | 179 | 26 | 30 | 12 | 89.4048 | 0
2024-01-07 18:00 | 22.1 | 55 | 2.48 | 25 | 26 | 30 | 12 | 91.0999 | 0
2024-01-07 19:00 | 21 | 59 | 1.89 | 0 | 26 | 30 | 12 | 84.0554 | 0
2024-01-07 20:00 | 21.1 | 58 | 0.91 | 0 | 26 | 30 | 12 | 57.9492 | 0
2024-01-07 21:00 | 20.7 | 59 | 1 | 0 | 26 | 30 | 12 | 61.793 | 0
2024-01-07 22:00 | 20.6 | 59 | 0.67 | 0 | 26 | 30 | 12 | 51.8893 | 0
2024-01-07 23:00 | 17.7 | 71 | 2.24 | 0 | 26 | 30 | 12 | 103.8032 | 0
2024-01-08 | 16.9 | 75 | 2.72 | 0 | 26 | 30 | 12 | 118.3026 | 0
2024-01-08 01:00 | 15.8 | 81 | 2.35 | 0 | 26 | 30 | 12 | 112.0459 | 0
2024-01-08 02:00 | 15.1 | 85 | 2.01 | 0 | 26 | 30 | 12 | 104.8403 | 0
2024-01-08 03:00 | 14.8 | 86 | 1.79 | 0 | 26 | 30 | 12 | 99.8425 | 0
2024-01-08 04:00 | 14.6 | 87 | 2.59 | 0 | 26 | 30 | 12 | 122.5434 | 0
2024-01-08 05:00 | 14.4 | 86 | 2.88 | 0 | 26 | 30 | 12 | 132.2752 | 0
2024-01-08 06:00 | 13.6 | 89 | 2.64 | 0 | 26 | 30 | 12 | 129.4698 | 0
2024-01-08 07:00 | 13.2 | 91 | 2.56 | 0 | 26 | 30 | 12 | 128.7482 | 0
2024-01-08 08:00 | 14.7 | 84 | 2.16 | 42 | 26 | 30 | 12 | 106.306 | 0
2024-01-08 09:00 | 18.1 | 69 | 1.24 | 212 | 26 | 30 | 12 | 46.8554 | 0
2024-01-08 10:00 | 21.5 | 57 | 1.41 | 402 | 26 | 30 | 12 | 16.3939 | 0
2024-01-08 11:00 | 24.1 | 48 | 3.16 | 557 | 26 | 30 | 12 | 27.3408 | 0
2024-01-08 12:00 | 25.8 | 37 | 3.74 | 656 | 26 | 30 | 12 | 28.6567 | 0
2024-01-08 13:00 | 27.2 | 29 | 3.23 | 686 | 26 | 30 | 12 | 17.0371 | 0
2024-01-08 14:00 | 27.9 | 23 | 3.8 | 645 | 26 | 30 | 12 | 40.7643 | 0
2024-01-08 15:00 | 27.6 | 23 | 3.32 | 540 | 26 | 30 | 12 | 46.0762 | 0
2024-01-08 16:00 | 27.1 | 24 | 3.45 | 377 | 26 | 30 | 12 | 72.5387 | 0
2024-01-08 17:00 | 25.2 | 47 | 5.54 | 180 | 26 | 30 | 12 | 111.5586 | 0
2024-01-08 18:00 | 23.7 | 58 | 5.4 | 26 | 26 | 30 | 12 | 125.4387 | 0
2024-01-08 19:00 | 22.8 | 58 | 4.59 | 0 | 26 | 30 | 12 | 125.6874 | 0
2024-01-08 20:00 | 21.9 | 60 | 3.92 | 0 | 26 | 30 | 12 | 119.4264 | 0
2024-01-08 21:00 | 20.7 | 60 | 3.58 | 0 | 26 | 30 | 12 | 123.1092 | 0
2024-01-08 22:00 | 19.3 | 57 | 3.4 | 0 | 26 | 30 | 12 | 133.4223 | 0
2024-01-08 23:00 | 18 | 58 | 3 | 0 | 26 | 30 | 12 | 131.7459 | 0
2024-01-09 | 16.9 | 62 | 2.77 | 0 | 26 | 30 | 12 | 129.5745 | 0
2024-01-09 01:00 | 16.2 | 62 | 2.88 | 0 | 26 | 30 | 12 | 137.1385 | 0
2024-01-09 02:00 | 15.5 | 60 | 2.8 | 0 | 26 | 30 | 12 | 140.7199 | 0
2024-01-09 03:00 | 14.7 | 61 | 2.7 | 0 | 26 | 30 | 12 | 141.8621 | 0
2024-01-09 04:00 | 13.9 | 62 | 2.51 | 0 | 26 | 30 | 12 | 139.9105 | 0
2024-01-09 05:00 | 13.2 | 70 | 1.84 | 0 | 26 | 30 | 12 | 117.3849 | 0
2024-01-09 06:00 | 13 | 67 | 1.46 | 0 | 26 | 30 | 12 | 106.1825 | 0
2024-01-09 07:00 | 12.2 | 68 | 2.18 | 0 | 26 | 30 | 12 | 134.9251 | 0
2024-01-09 08:00 | 13.7 | 57 | 2.42 | 44 | 26 | 30 | 12 | 135.0355 | 0
2024-01-09 09:00 | 16.9 | 46 | 1.53 | 220 | 26 | 30 | 12 | 71.8126 | 0
2024-01-09 10:00 | 21 | 35 | 0.92 | 415 | 26 | 30 | 12 | 13.2224 | 0
2024-01-09 11:00 | 23.5 | 30 | 0.28 | 572 | 26 | 30 | 12 | 0 | 7.0337
2024-01-09 12:00 | 24.8 | 33 | 2.26 | 671 | 26 | 30 | 12 | 5.1956 | 0
2024-01-09 13:00 | 25.4 | 32 | 3.3 | 701 | 26 | 30 | 12 | 23.8875 | 0
2024-01-09 14:00 | 25.5 | 34 | 4.16 | 658 | 26 | 30 | 12 | 44.2772 | 0
2024-01-09 15:00 | 25.1 | 37 | 4.89 | 547 | 26 | 30 | 12 | 71.6294 | 0
2024-01-09 16:00 | 24.3 | 42 | 4.96 | 381 | 26 | 30 | 12 | 93.4121 | 0
2024-01-09 17:00 | 23.3 | 52 | 4.55 | 187 | 26 | 30 | 12 | 104.4042 | 0
2024-01-09 18:00 | 22.1 | 58 | 3.55 | 28 | 26 | 30 | 12 | 109.4561 | 0
2024-01-09 19:00 | 21.3 | 61 | 3.45 | 0 | 26 | 30 | 12 | 114.293 | 0
2024-01-09 20:00 | 20.7 | 63 | 3.41 | 0 | 26 | 30 | 12 | 116.1362 | 0
2024-01-09 21:00 | 20 | 66 | 3.28 | 0 | 26 | 30 | 12 | 115.8712 | 0
2024-01-09 22:00 | 19.1 | 71 | 2.97 | 0 | 26 | 30 | 12 | 111.3619 | 0
2024-01-09 23:00 | 18.2 | 75 | 2.56 | 0 | 26 | 30 | 12 | 105.3181 | 0
2024-01-10 | 17.7 | 77 | 2.33 | 0 | 26 | 30 | 12 | 101.7886 | 0
2024-01-10 01:00 | 18.5 | 72 | 1.61 | 0 | 26 | 30 | 12 | 82.1852 | 0
2024-01-10 02:00 | 19.5 | 68 | 0.94 | 0 | 26 | 30 | 12 | 60.9681 | 0
2024-01-10 03:00 | 15.4 | 84 | 2.33 | 0 | 26 | 30 | 12 | 112.2148 | 0
2024-01-10 04:00 | 14.6 | 88 | 3.2 | 0 | 26 | 30 | 12 | 137.6058 | 0
2024-01-10 05:00 | 13.6 | 91 | 2.69 | 0 | 26 | 30 | 12 | 129.6255 | 0
2024-01-10 06:00 | 13.2 | 91 | 2.72 | 0 | 26 | 30 | 12 | 133.2153 | 0
2024-01-10 07:00 | 12.6 | 91 | 2.7 | 0 | 26 | 30 | 12 | 136.739 | 0
2024-01-10 08:00 | 13.4 | 88 | 2.42 | 43 | 26 | 30 | 12 | 119.3741 | 0
2024-01-10 09:00 | 16.8 | 72 | 1.43 | 217 | 26 | 30 | 12 | 56.5095 | 0
2024-01-10 10:00 | 20.4 | 59 | 1 | 411 | 26 | 30 | 12 | 7.5544 | 0
2024-01-10 11:00 | 22.3 | 49 | 1.2 | 570 | 26 | 30 | 12 | 0 | 0
2024-01-10 12:00 | 23.3 | 44 | 2.1 | 671 | 26 | 30 | 12 | 0 | 0
2024-01-10 13:00 | 23.9 | 42 | 2.42 | 702 | 26 | 30 | 12 | 0.3355 | 0
2024-01-10 14:00 | 24.1 | 43 | 2.92 | 660 | 26 | 30 | 12 | 14.867 | 0
2024-01-10 15:00 | 23.9 | 45 | 3.72 | 550 | 26 | 30 | 12 | 45.1761 | 0
2024-01-10 16:00 | 23.2 | 46 | 4.41 | 385 | 26 | 30 | 12 | 85.5642 | 0
2024-01-10 17:00 | 22.4 | 48 | 4.38 | 192 | 26 | 30 | 12 | 115.0232 | 0
2024-01-10 18:00 | 21.2 | 56 | 3.5 | 29 | 26 | 30 | 12 | 118.1555 | 0
2024-01-10 19:00 | 20.2 | 62 | 2.88 | 0 | 26 | 30 | 12 | 109.7167 | 0
2024-01-10 20:00 | 19 | 70 | 2.25 | 0 | 26 | 30 | 12 | 96.5212 | 0
2024-01-10 21:00 | 18.5 | 74 | 1.78 | 0 | 26 | 30 | 12 | 85.3346 | 0
2024-01-10 22:00 | 20.1 | 68 | 0.85 | 0 | 26 | 30 | 12 | 55.8739 | 0
2024-01-10 23:00 | 19.5 | 70 | 0.5 | 0 | 26 | 30 | 12 | 49.3081 | 0
2024-01-11 | 16.8 | 81 | 1.7 | 0 | 26 | 30 | 12 | 88.8129 | 0
2024-01-11 01:00 | 15.4 | 86 | 2.87 | 0 | 26 | 30 | 12 | 124.7136 | 0
2024-01-11 02:00 | 14.6 | 89 | 3.05 | 0 | 26 | 30 | 12 | 133.1 | 0
2024-01-11 03:00 | 13.6 | 92 | 2.77 | 0 | 26 | 30 | 12 | 131.17 | 0
2024-01-11 04:00 | 12.7 | 94 | 2.77 | 0 | 26 | 30 | 12 | 136.2908 | 0
2024-01-11 05:00 | 13.5 | 92 | 2.75 | 0 | 26 | 30 | 12 | 131.338 | 0
2024-01-11 06:00 | 12.9 | 94 | 3.04 | 0 | 26 | 30 | 12 | 142.2745 | 0
2024-01-11 07:00 | 12.8 | 93 | 3.42 | 0 | 26 | 30 | 12 | 153.9166 | 0
2024-01-11 08:00 | 13.7 | 89 | 3.45 | 41 | 26 | 30 | 12 | 144.8424 | 0
2024-01-11 09:00 | 16.6 | 74 | 3.13 | 205 | 26 | 30 | 12 | 103.77 | 0
2024-01-11 10:00 | 19.8 | 62 | 2.9 | 404 | 26 | 30 | 12 | 58.5261 | 0
2024-01-11 11:00 | 21.4 | 57 | 2.46 | 569 | 26 | 30 | 12 | 19.9116 | 0
2024-01-11 12:00 | 22.5 | 49 | 2.14 | 671 | 26 | 30 | 12 | 0 | 0
2024-01-11 13:00 | 23.5 | 43 | 2.18 | 704 | 26 | 30 | 12 | 0 | 0
2024-01-11 14:00 | 24 | 42 | 2.83 | 663 | 26 | 30 | 12 | 14.3793 | 0
2024-01-11 15:00 | 23.3 | 52 | 3.97 | 552 | 26 | 30 | 12 | 44.5265 | 0
2024-01-11 16:00 | 22.3 | 56 | 4.74 | 385 | 26 | 30 | 12 | 84.5606 | 0
2024-01-11 17:00 | 21.6 | 58 | 3.94 | 191 | 26 | 30 | 12 | 99.3854 | 0
2024-01-11 18:00 | 20.9 | 64 | 3.09 | 30 | 26 | 30 | 12 | 102.8233 | 0
2024-01-11 19:00 | 20 | 68 | 2.39 | 0 | 26 | 30 | 12 | 94.7216 | 0
2024-01-11 20:00 | 18.7 | 71 | 1.7 | 0 | 26 | 30 | 12 | 84.0316 | 0
2024-01-11 21:00 | 19.8 | 65 | 0.76 | 0 | 26 | 30 | 12 | 55.5155 | 0
2024-01-11 22:00 | 19.1 | 67 | 0.85 | 0 | 26 | 30 | 12 | 60.2723 | 0
2024-01-11 23:00 | 16 | 84 | 2.47 | 0 | 26 | 30 | 12 | 111.8338 | 0
2024-01-12 | 15 | 90 | 2.82 | 0 | 26 | 30 | 12 | 123.6161 | 0
2024-01-12 01:00 | 13.9 | 94 | 2.51 | 0 | 26 | 30 | 12 | 120.9045 | 0
2024-01-12 02:00 | 13.1 | 95 | 2.51 | 0 | 26 | 30 | 12 | 125.7411 | 0
2024-01-12 03:00 | 12.2 | 96 | 2.75 | 0 | 26 | 30 | 12 | 138.0432 | 0
2024-01-12 04:00 | 11.5 | 97 | 2.87 | 0 | 26 | 30 | 12 | 145.7881 | 0
2024-01-12 05:00 | 12.4 | 94 | 2.95 | 0 | 26 | 30 | 12 | 143.446 | 0
2024-01-12 06:00 | 12.4 | 93 | 3.27 | 0 | 26 | 30 | 12 | 152.9533 | 0
2024-01-12 07:00 | 11.8 | 94 | 3.18 | 0 | 26 | 30 | 12 | 154.2968 | 0
2024-01-12 08:00 | 12.4 | 91 | 3.09 | 44 | 26 | 30 | 12 | 143.2745 | 0
2024-01-12 09:00 | 15.5 | 76 | 2.5 | 221 | 26 | 30 | 12 | 91.4172 | 0
2024-01-12 10:00 | 19.1 | 60 | 2.72 | 417 | 26 | 30 | 12 | 59.1684 | 0
2024-01-12 11:00 | 21.6 | 43 | 3.09 | 576 | 26 | 30 | 12 | 46.9785 | 0
2024-01-12 12:00 | 22.8 | 37 | 3.44 | 677 | 26 | 30 | 12 | 41.0227 | 0
2024-01-12 13:00 | 23.8 | 33 | 3.96 | 710 | 26 | 30 | 12 | 47.3839 | 0
2024-01-12 14:00 | 24 | 33 | 4.53 | 669 | 26 | 30 | 12 | 64.2156 | 0
2024-01-12 15:00 | 23.7 | 35 | 4.71 | 558 | 26 | 30 | 12 | 82.1496 | 0
2024-01-12 16:00 | 23.2 | 36 | 4.66 | 394 | 26 | 30 | 12 | 105.6482 | 0
2024-01-12 17:00 | 22.5 | 39 | 4.27 | 198 | 26 | 30 | 12 | 124.4089 | 0
2024-01-12 18:00 | 20.8 | 54 | 2.95 | 32 | 26 | 30 | 12 | 110.7243 | 0
2024-01-12 19:00 | 19.5 | 64 | 2.37 | 0 | 26 | 30 | 12 | 100.889 | 0
2024-01-12 20:00 | 19 | 67 | 1.63 | 0 | 26 | 30 | 12 | 83.0153 | 0
2024-01-12 21:00 | 20.4 | 59 | 0.36 | 0 | 26 | 30 | 12 | 49.2959 | 0
2024-01-12 22:00 | 17.6 | 72 | 1.79 | 0 | 26 | 30 | 12 | 91.8996 | 0
2024-01-12 23:00 | 16.2 | 78 | 3 | 0 | 26 | 30 | 12 | 127.9995 | 0
2024-01-13 | 15.1 | 84 | 3.12 | 0 | 26 | 30 | 12 | 134.6974 | 0
2024-01-13 01:00 | 14 | 88 | 3.04 | 0 | 26 | 30 | 12 | 138.0597 | 0
2024-01-13 02:00 | 13.1 | 92 | 3.18 | 0 | 26 | 30 | 12 | 145.8457 | 0
2024-01-13 03:00 | 12.4 | 92 | 3.26 | 0 | 26 | 30 | 12 | 153.3246 | 0
2024-01-13 04:00 | 11.8 | 92 | 3.12 | 0 | 26 | 30 | 12 | 153.794 | 0
2024-01-13 05:00 | 13.2 | 85 | 3.2 | 0 | 26 | 30 | 12 | 150.3262 | 0
2024-01-13 06:00 | 12.8 | 83 | 3.16 | 0 | 26 | 30 | 12 | 153.414 | 0
2024-01-13 07:00 | 12.3 | 80 | 3.19 | 0 | 26 | 30 | 12 | 159.7179 | 0
2024-01-13 08:00 | 13.1 | 71 | 3.16 | 42 | 26 | 30 | 12 | 153.5494 | 0
2024-01-13 09:00 | 16.8 | 53 | 2.58 | 213 | 26 | 30 | 12 | 102.7643 | 0
2024-01-13 10:00 | 20.6 | 41 | 1.7 | 405 | 26 | 30 | 12 | 39.2554 | 0
2024-01-13 11:00 | 23.1 | 32 | 1.51 | 563 | 26 | 30 | 12 | 7.4458 | 0
2024-01-13 12:00 | 24.4 | 28 | 1.8 | 663 | 26 | 30 | 12 | 0.4712 | 0
2024-01-13 13:00 | 25.2 | 27 | 2.61 | 697 | 26 | 30 | 12 | 15.5698 | 0
2024-01-13 14:00 | 25.5 | 27 | 3.23 | 659 | 26 | 30 | 12 | 34.5875 | 0
2024-01-13 15:00 | 25.2 | 29 | 3.74 | 553 | 26 | 30 | 12 | 59.8493 | 0
2024-01-13 16:00 | 24.5 | 32 | 3.75 | 390 | 26 | 30 | 12 | 82.2868 | 0
2024-01-13 17:00 | 23.7 | 36 | 3.56 | 195 | 26 | 30 | 12 | 104.037 | 0
2024-01-13 18:00 | 21.7 | 48 | 2.44 | 32 | 26 | 30 | 12 | 98.5425 | 0
2024-01-13 19:00 | 20.4 | 60 | 2.2 | 0 | 26 | 30 | 12 | 94.3693 | 0
2024-01-13 20:00 | 19.4 | 68 | 2.06 | 0 | 26 | 30 | 12 | 90.9419 | 0
2024-01-13 21:00 | 19.6 | 67 | 1.46 | 0 | 26 | 30 | 12 | 75.3945 | 0
2024-01-13 22:00 | 19.8 | 65 | 1.33 | 0 | 26 | 30 | 12 | 72.0651 | 0
2024-01-13 23:00 | 19.3 | 68 | 1.36 | 0 | 26 | 30 | 12 | 73.6713 | 0
2024-01-14 | 17.7 | 76 | 1.68 | 0 | 26 | 30 | 12 | 86.0771 | 0
2024-01-14 01:00 | 15.9 | 81 | 3.2 | 0 | 26 | 30 | 12 | 132.8303 | 0
2024-01-14 02:00 | 14.3 | 84 | 3 | 0 | 26 | 30 | 12 | 137.5446 | 0
2024-01-14 03:00 | 13.4 | 86 | 2.69 | 0 | 26 | 30 | 12 | 134.0257 | 0
2024-01-14 04:00 | 12.8 | 86 | 2.7 | 0 | 26 | 30 | 12 | 138.2969 | 0
2024-01-14 05:00 | 13 | 86 | 2.75 | 0 | 26 | 30 | 12 | 138.4151 | 0
2024-01-14 06:00 | 12.4 | 88 | 2.78 | 0 | 26 | 30 | 12 | 142.1273 | 0
2024-01-14 07:00 | 12.2 | 88 | 2.97 | 0 | 26 | 30 | 12 | 149.0291 | 0
2024-01-14 08:00 | 13.6 | 79 | 2.8 | 42 | 26 | 30 | 12 | 134.4792 | 0
2024-01-14 09:00 | 17.6 | 60 | 2.19 | 214 | 26 | 30 | 12 | 81.7671 | 0
2024-01-14 10:00 | 21.8 | 44 | 1.99 | 408 | 26 | 30 | 12 | 39.0968 | 0
2024-01-14 11:00 | 24.5 | 32 | 2 | 568 | 26 | 30 | 12 | 14.7733 | 0
2024-01-14 12:00 | 26.2 | 26 | 1.7 | 670 | 26 | 30 | 12 | 0 | 0
2024-01-14 13:00 | 27.2 | 23 | 2.3 | 704 | 26 | 30 | 12 | 1.0234 | 0
2024-01-14 14:00 | 27.6 | 24 | 3.05 | 666 | 26 | 30 | 12 | 21.1501 | 0
2024-01-14 15:00 | 27.2 | 27 | 3.58 | 559 | 26 | 30 | 12 | 45.1097 | 0
2024-01-14 16:00 | 26.3 | 29 | 4.03 | 396 | 26 | 30 | 12 | 79.634 | 0
2024-01-14 17:00 | 25.1 | 35 | 3.47 | 201 | 26 | 30 | 12 | 92.7807 | 0
2024-01-14 18:00 | 22.7 | 54 | 2.48 | 34 | 26 | 30 | 12 | 86.8927 | 0
2024-01-14 19:00 | 21.2 | 70 | 2.22 | 0 | 26 | 30 | 12 | 81.1995 | 0
2024-01-14 20:00 | 20.3 | 76 | 1.66 | 0 | 26 | 30 | 12 | 70.7001 | 0
2024-01-14 21:00 | 21.7 | 68 | 0.89 | 0 | 26 | 30 | 12 | 50.2415 | 0
2024-01-14 22:00 | 19.5 | 75 | 1.5 | 0 | 26 | 30 | 12 | 72.2298 | 0
2024-01-14 23:00 | 18.6 | 75 | 1.6 | 0 | 26 | 30 | 12 | 79.6307 | 0
2024-01-15 | 17.8 | 74 | 1.71 | 0 | 26 | 30 | 12 | 87.473 | 0
2024-01-15 01:00 | 16.2 | 76 | 2.52 | 0 | 26 | 30 | 12 | 117.2263 | 0
2024-01-15 02:00 | 15.8 | 68 | 2.9 | 0 | 26 | 30 | 12 | 135.824 | 0
2024-01-15 03:00 | 15.1 | 64 | 3.12 | 0 | 26 | 30 | 12 | 149.6457 | 0
2024-01-15 04:00 | 14.4 | 63 | 3.06 | 0 | 26 | 30 | 12 | 153.202 | 0
2024-01-15 05:00 | 13.4 | 69 | 2.75 | 0 | 26 | 30 | 12 | 146.1375 | 0
2024-01-15 06:00 | 13 | 68 | 2.8 | 0 | 26 | 30 | 12 | 150.7325 | 0
2024-01-15 07:00 | 12.8 | 64 | 3.09 | 0 | 26 | 30 | 12 | 163.5571 | 0
2024-01-15 08:00 | 13.8 | 56 | 2.77 | 43 | 26 | 30 | 12 | 146.7012 | 0
2024-01-15 09:00 | 17.5 | 44 | 1.96 | 219 | 26 | 30 | 12 | 85.0748 | 0
2024-01-15 10:00 | 22.4 | 31 | 2 | 415 | 26 | 30 | 12 | 46.4678 | 0
2024-01-15 11:00 | 25.9 | 22 | 1.9 | 577 | 26 | 30 | 12 | 14.1944 | 0
2024-01-15 12:00 | 27.6 | 19 | 1.89 | 680 | 26 | 30 | 12 | 0 | 0
2024-01-15 13:00 | 28.5 | 18 | 2.51 | 713 | 26 | 30 | 12 | 5.6297 | 0
2024-01-15 14:00 | 28.6 | 20 | 3.72 | 675 | 26 | 30 | 12 | 36.0552 | 0
2024-01-15 15:00 | 28.1 | 22 | 4.58 | 569 | 26 | 30 | 12 | 68.2356 | 0
2024-01-15 16:00 | 27.1 | 25 | 4.66 | 404 | 26 | 30 | 12 | 93.4124 | 0
2024-01-15 17:00 | 25.2 | 40 | 3.76 | 206 | 26 | 30 | 12 | 89.6513 | 0
2024-01-15 18:00 | 22.7 | 63 | 3 | 36 | 26 | 30 | 12 | 87.0115 | 0
2024-01-15 19:00 | 21.4 | 78 | 2.46 | 0 | 26 | 30 | 12 | 76.9889 | 0
2024-01-15 20:00 | 20.2 | 85 | 1.9 | 0 | 26 | 30 | 12 | 69.8972 | 0
2024-01-15 21:00 | 20.6 | 82 | 1.46 | 0 | 26 | 30 | 12 | 60.8912 | 0
2024-01-15 22:00 | 19.3 | 86 | 1.98 | 0 | 26 | 30 | 12 | 76.8342 | 0
2024-01-15 23:00 | 18 | 89 | 2.55 | 0 | 26 | 30 | 12 | 95.5603 | 0
2024-01-16 | 17.5 | 89 | 2.78 | 0 | 26 | 30 | 12 | 104.2467 | 0
2024-01-16 01:00 | 16.9 | 88 | 2.86 | 0 | 26 | 30 | 12 | 111.5124 | 0
2024-01-16 02:00 | 16.6 | 84 | 3.29 | 0 | 26 | 30 | 12 | 126.8406 | 0
2024-01-16 03:00 | 16.1 | 82 | 3.38 | 0 | 26 | 30 | 12 | 134.7302 | 0
2024-01-16 04:00 | 15.7 | 82 | 3.38 | 0 | 26 | 30 | 12 | 137.9782 | 0
2024-01-16 05:00 | 16.1 | 85 | 3.22 | 0 | 26 | 30 | 12 | 128.4882 | 0
2024-01-16 06:00 | 16.1 | 85 | 3.4 | 0 | 26 | 30 | 12 | 132.6632 | 0
2024-01-16 07:00 | 16 | 85 | 3.73 | 0 | 26 | 30 | 12 | 141.0772 | 0
2024-01-16 08:00 | 16.9 | 82 | 3.53 | 42 | 26 | 30 | 12 | 125.7789 | 0
2024-01-16 09:00 | 20.3 | 69 | 3 | 213 | 26 | 30 | 12 | 75.8231 | 0
2024-01-16 10:00 | 23.9 | 58 | 3 | 406 | 26 | 30 | 12 | 33.425 | 0
2024-01-16 11:00 | 26.3 | 51 | 4.3 | 564 | 26 | 30 | 12 | 21.5965 | 0
2024-01-16 12:00 | 27.3 | 47 | 5.48 | 664 | 26 | 30 | 12 | 21.5597 | 0
2024-01-16 13:00 | 27.5 | 46 | 5.92 | 696 | 26 | 30 | 12 | 22.8885 | 0
2024-01-16 14:00 | 27.3 | 48 | 6.46 | 658 | 26 | 30 | 12 | 32.0454 | 0
2024-01-16 15:00 | 27.1 | 48 | 6.61 | 553 | 26 | 30 | 12 | 50.6744 | 0
2024-01-16 16:00 | 26.3 | 52 | 6.74 | 392 | 26 | 30 | 12 | 74.4145 | 0
2024-01-16 17:00 | 25.3 | 59 | 6.06 | 198 | 26 | 30 | 12 | 89.2016 | 0
2024-01-16 18:00 | 24 | 70 | 4.71 | 35 | 26 | 30 | 12 | 89.5798 | 0
2024-01-16 19:00 | 23.2 | 77 | 4.5 | 0 | 26 | 30 | 12 | 89.6981 | 0
2024-01-16 20:00 | 22.7 | 83 | 4.43 | 0 | 26 | 30 | 12 | 85.5292 | 0
2024-01-16 21:00 | 22.1 | 91 | 4.18 | 0 | 26 | 30 | 12 | 78.2763 | 0
2024-01-16 22:00 | 21.8 | 93 | 4 | 0 | 26 | 30 | 12 | 77.1699 | 0
2024-01-16 23:00 | 21.6 | 93 | 4.24 | 0 | 26 | 30 | 12 | 82.2437 | 0
2024-01-17 | 21.5 | 92 | 4.41 | 0 | 26 | 30 | 12 | 86.8163 | 0
2024-01-17 01:00 | 21.4 | 91 | 4.6 | 0 | 26 | 30 | 12 | 91.7257 | 0
2024-01-17 02:00 | 21.7 | 88 | 5.16 | 0 | 26 | 30 | 12 | 98.929 | 0
2024-01-17 03:00 | 21.9 | 82 | 6.04 | 0 | 26 | 30 | 12 | 116.8191 | 0
2024-01-17 04:00 | 22 | 80 | 6.36 | 0 | 26 | 30 | 12 | 122.9504 | 0
2024-01-17 05:00 | 21.2 | 84 | 4.14 | 0 | 26 | 30 | 12 | 97.9546 | 0
2024-01-17 06:00 | 21.4 | 73 | 4.33 | 0 | 26 | 30 | 12 | 113.6541 | 0
2024-01-17 07:00 | 21.4 | 73 | 4.7 | 0 | 26 | 30 | 12 | 119.5187 | 0
2024-01-17 08:00 | 22.2 | 69 | 5.14 | 42 | 26 | 30 | 12 | 117.6183 | 0
2024-01-17 09:00 | 24.1 | 56 | 6.75 | 213 | 26 | 30 | 12 | 119.0387 | 0
2024-01-17 10:00 | 25.1 | 44 | 8.34 | 407 | 26 | 30 | 12 | 132.0223 | 0
2024-01-17 11:00 | 25.7 | 39 | 9.14 | 566 | 26 | 30 | 12 | 128.3956 | 0
2024-01-17 12:00 | 25.7 | 39 | 9.35 | 666 | 26 | 30 | 12 | 118.0049 | 0
2024-01-17 13:00 | 25.6 | 40 | 9.04 | 705 | 26 | 30 | 12 | 106.5567 | 0
2024-01-17 14:00 | 25.2 | 42 | 9.04 | 657 | 26 | 30 | 12 | 112.8899 | 0
2024-01-17 15:00 | 24.7 | 43 | 9.18 | 555 | 26 | 30 | 12 | 133.1752 | 0
2024-01-17 16:00 | 23.9 | 48 | 9.53 | 397 | 26 | 30 | 12 | 157.625 | 0
2024-01-17 17:00 | 23 | 55 | 9.02 | 205 | 26 | 30 | 12 | 171.3199 | 0
2024-01-17 18:00 | 21.9 | 63 | 7.94 | 38 | 26 | 30 | 12 | 175.7218 | 0
2024-01-17 19:00 | 21.5 | 65 | 7.2 | 0 | 26 | 30 | 12 | 171.1601 | 0
2024-01-17 20:00 | 21.2 | 68 | 6.52 | 0 | 26 | 30 | 12 | 158.8741 | 0
2024-01-17 21:00 | 20.8 | 70 | 6.17 | 0 | 26 | 30 | 12 | 154.9858 | 0
2024-01-17 22:00 | 20.6 | 68 | 5.97 | 0 | 26 | 30 | 12 | 157.5887 | 0
2024-01-17 23:00 | 20.2 | 66 | 5.39 | 0 | 26 | 30 | 12 | 155.2313 | 0
2024-01-18 | 19.6 | 69 | 4.71 | 0 | 26 | 30 | 12 | 144.6519 | 0
2024-01-18 01:00 | 19.1 | 72 | 3.95 | 0 | 26 | 30 | 12 | 130.8808 | 0
2024-01-18 02:00 | 18.5 | 75 | 3.4 | 0 | 26 | 30 | 12 | 121.6231 | 0
2024-01-18 03:00 | 17.8 | 79 | 3.14 | 0 | 26 | 30 | 12 | 118.0457 | 0
2024-01-18 04:00 | 17.3 | 82 | 3.01 | 0 | 26 | 30 | 12 | 116.5713 | 0
2024-01-18 05:00 | 17.9 | 78 | 2.75 | 0 | 26 | 30 | 12 | 109.4316 | 0
2024-01-18 06:00 | 17.4 | 80 | 2.64 | 0 | 26 | 30 | 12 | 108.9839 | 0
2024-01-18 07:00 | 17.1 | 81 | 3.08 | 0 | 26 | 30 | 12 | 120.5727 | 0
2024-01-18 08:00 | 17.5 | 79 | 3.4 | 39 | 26 | 30 | 12 | 120.9645 | 0
2024-01-18 09:00 | 19.6 | 71 | 3.4 | 194 | 26 | 30 | 12 | 90.2034 | 0
2024-01-18 10:00 | 22 | 60 | 3.23 | 386 | 26 | 30 | 12 | 53.2757 | 0
2024-01-18 11:00 | 23.4 | 52 | 2.24 | 567 | 26 | 30 | 12 | 7.2162 | 0
2024-01-18 12:00 | 24.3 | 49 | 3.79 | 678 | 26 | 30 | 12 | 19.9565 | 0
2024-01-18 13:00 | 24.4 | 49 | 5 | 709 | 26 | 30 | 12 | 35.9676 | 0
2024-01-18 14:00 | 24.2 | 51 | 5.89 | 669 | 26 | 30 | 12 | 54.1169 | 0
2024-01-18 15:00 | 23.9 | 51 | 5.44 | 557 | 26 | 30 | 12 | 65.3602 | 0
2024-01-18 16:00 | 23.4 | 54 | 4.39 | 371 | 26 | 30 | 12 | 72.5483 | 0
2024-01-18 17:00 | 23.1 | 58 | 4.27 | 201 | 26 | 30 | 12 | 90.0948 | 0
2024-01-18 18:00 | 22.3 | 63 | 3.37 | 38 | 26 | 30 | 12 | 96.7609 | 0
2024-01-18 19:00 | 21.8 | 66 | 3.67 | 0 | 26 | 30 | 12 | 107.9326 | 0
2024-01-18 20:00 | 21.2 | 68 | 4.09 | 0 | 26 | 30 | 12 | 118.4564 | 0
2024-01-18 21:00 | 20.6 | 72 | 3.64 | 0 | 26 | 30 | 12 | 111.0709 | 0
2024-01-18 22:00 | 19.8 | 76 | 2.92 | 0 | 26 | 30 | 12 | 100.0818 | 0
2024-01-18 23:00 | 19.3 | 79 | 2.94 | 0 | 26 | 30 | 12 | 101.6908 | 0
2024-01-19 | 18.9 | 81 | 2.92 | 0 | 26 | 30 | 12 | 102.7049 | 0
2024-01-19 01:00 | 18.3 | 84 | 2.5 | 0 | 26 | 30 | 12 | 96.1664 | 0
2024-01-19 02:00 | 18.1 | 85 | 2.8 | 0 | 26 | 30 | 12 | 103.1859 | 0
2024-01-19 03:00 | 18 | 86 | 2.81 | 0 | 26 | 30 | 12 | 103.3516 | 0
2024-01-19 04:00 | 18.1 | 85 | 2.83 | 0 | 26 | 30 | 12 | 103.8087 | 0
2024-01-19 05:00 | 18.5 | 83 | 1.61 | 0 | 26 | 30 | 12 | 75.7647 | 0
2024-01-19 06:00 | 18.1 | 85 | 1.77 | 0 | 26 | 30 | 12 | 80.6748 | 0
2024-01-19 07:00 | 17.4 | 87 | 2.11 | 0 | 26 | 30 | 12 | 91.7145 | 0
2024-01-19 08:00 | 18.4 | 85 | 2.42 | 40 | 26 | 30 | 12 | 87.5634 | 0
2024-01-19 09:00 | 20.8 | 73 | 2.28 | 200 | 26 | 30 | 12 | 55.5998 | 0
2024-01-19 10:00 | 22.9 | 62 | 2.79 | 383 | 26 | 30 | 12 | 35.9155 | 0
2024-01-19 11:00 | 24.1 | 55 | 5.07 | 553 | 26 | 30 | 12 | 50.2801 | 0
2024-01-19 12:00 | 24.4 | 53 | 5.88 | 658 | 26 | 30 | 12 | 48.96 | 0
2024-01-19 13:00 | 24.6 | 50 | 6.14 | 698 | 26 | 30 | 12 | 51.4625 | 0
2024-01-19 14:00 | 24.5 | 48 | 6.39 | 662 | 26 | 30 | 12 | 65.7824 | 0
2024-01-19 15:00 | 24.1 | 53 | 6.61 | 561 | 26 | 30 | 12 | 76.7059 | 0
2024-01-19 16:00 | 23.4 | 56 | 6.5 | 402 | 26 | 30 | 12 | 99.0277 | 0
2024-01-19 17:00 | 22.6 | 60 | 5.54 | 208 | 26 | 30 | 12 | 112.1978 | 0
2024-01-19 18:00 | 21.7 | 65 | 4.61 | 40 | 26 | 30 | 12 | 121.244 | 0
2024-01-19 19:00 | 21.1 | 70 | 4.06 | 0 | 26 | 30 | 12 | 116.2772 | 0
2024-01-19 20:00 | 20.5 | 74 | 3.71 | 0 | 26 | 30 | 12 | 110.9054 | 0
2024-01-19 21:00 | 19.7 | 78 | 3.1 | 0 | 26 | 30 | 12 | 102.4442 | 0
2024-01-19 22:00 | 18.9 | 82 | 2.75 | 0 | 26 | 30 | 12 | 98.3972 | 0
2024-01-19 23:00 | 17.9 | 87 | 2.47 | 0 | 26 | 30 | 12 | 96.1777 | 0
2024-01-20 | 17 | 89 | 2.22 | 0 | 26 | 30 | 12 | 95.6226 | 0
2024-01-20 01:00 | 16.5 | 90 | 1.98 | 0 | 26 | 30 | 12 | 92.6054 | 0
2024-01-20 02:00 | 16.1 | 91 | 2.37 | 0 | 26 | 30 | 12 | 104.0386 | 0
2024-01-20 03:00 | 15.7 | 91 | 2.6 | 0 | 26 | 30 | 12 | 112.398 | 0
2024-01-20 04:00 | 15.5 | 91 | 2.82 | 0 | 26 | 30 | 12 | 119.1602 | 0
2024-01-20 05:00 | 16.4 | 87 | 2.8 | 0 | 26 | 30 | 12 | 114.7891 | 0
2024-01-20 06:00 | 15.4 | 89 | 2.06 | 0 | 26 | 30 | 12 | 102.1251 | 0
2024-01-20 07:00 | 14.9 | 90 | 2.73 | 0 | 26 | 30 | 12 | 122.0932 | 0
2024-01-20 08:00 | 15 | 91 | 3 | 43 | 26 | 30 | 12 | 121.5407 | 0
2024-01-20 09:00 | 18.1 | 77 | 2.01 | 215 | 26 | 30 | 12 | 62.4422 | 0
2024-01-20 10:00 | 21 | 65 | 1.75 | 409 | 26 | 30 | 12 | 21.0442 | 0
2024-01-20 11:00 | 22.5 | 60 | 0.14 | 569 | 26 | 30 | 12 | 0 | 15.7582
2024-01-20 12:00 | 23.7 | 53 | 1.27 | 664 | 26 | 30 | 12 | 0 | 0
2024-01-20 13:00 | 24.6 | 50 | 2.19 | 703 | 26 | 30 | 12 | 0 | 0
2024-01-20 14:00 | 24.7 | 51 | 3.69 | 667 | 26 | 30 | 12 | 13.1593 | 0
2024-01-20 15:00 | 24.1 | 55 | 4.97 | 568 | 26 | 30 | 12 | 46.6934 | 0
2024-01-20 16:00 | 23.6 | 57 | 5.46 | 405 | 26 | 30 | 12 | 78.2268 | 0
2024-01-20 17:00 | 23 | 62 | 5.67 | 209 | 26 | 30 | 12 | 105.6741 | 0
2024-01-20 18:00 | 22.3 | 66 | 4.1 | 41 | 26 | 30 | 12 | 104.9555 | 0
2024-01-20 19:00 | 21.9 | 69 | 3.32 | 0 | 26 | 30 | 12 | 97.2002 | 0
2024-01-20 20:00 | 21.1 | 73 | 2.36 | 0 | 26 | 30 | 12 | 82.019 | 0
2024-01-20 21:00 | 20.3 | 77 | 2.19 | 0 | 26 | 30 | 12 | 80.9754 | 0
2024-01-20 22:00 | 19.6 | 81 | 2.08 | 0 | 26 | 30 | 12 | 80.4638 | 0
2024-01-20 23:00 | 19.6 | 81 | 1.36 | 0 | 26 | 30 | 12 | 64.9653 | 0
2024-01-21 | 18.8 | 85 | 1.52 | 0 | 26 | 30 | 12 | 70.8061 | 0
2024-01-21 01:00 | 17.8 | 90 | 2.48 | 0 | 26 | 30 | 12 | 94.8644 | 0
2024-01-21 02:00 | 17.5 | 93 | 2.7 | 0 | 26 | 30 | 12 | 99.4105 | 0
2024-01-21 03:00 | 17.4 | 94 | 2.83 | 0 | 26 | 30 | 12 | 102.0558 | 0
2024-01-21 04:00 | 17.3 | 94 | 2.86 | 0 | 26 | 30 | 12 | 103.4882 | 0
2024-01-21 05:00 | 17.1 | 93 | 2.83 | 0 | 26 | 30 | 12 | 105.3136 | 0
2024-01-21 06:00 | 16.9 | 92 | 3 | 0 | 26 | 30 | 12 | 111.327 | 0
2024-01-21 07:00 | 16.5 | 91 | 3.28 | 0 | 26 | 30 | 12 | 121.5128 | 0
2024-01-21 08:00 | 17.5 | 86 | 3.2 | 43 | 26 | 30 | 12 | 109.7894 | 0
2024-01-21 09:00 | 20.1 | 74 | 2.56 | 213 | 26 | 30 | 12 | 63.6636 | 0
2024-01-21 10:00 | 22.4 | 62 | 3.1 | 407 | 26 | 30 | 12 | 42.3645 | 0
2024-01-21 11:00 | 23.4 | 56 | 3.8 | 568 | 26 | 30 | 12 | 32.5606 | 0
2024-01-21 12:00 | 24 | 52 | 4.41 | 668 | 26 | 30 | 12 | 30.2452 | 0
2024-01-21 13:00 | 24.3 | 50 | 5.23 | 708 | 26 | 30 | 12 | 39.091 | 0
2024-01-21 14:00 | 24.2 | 51 | 5.89 | 673 | 26 | 30 | 12 | 53.5769 | 0
2024-01-21 15:00 | 24.2 | 51 | 5.71 | 569 | 26 | 30 | 12 | 64.7653 | 0
2024-01-21 16:00 | 23.7 | 53 | 6.04 | 409 | 26 | 30 | 12 | 93.4051 | 0
2024-01-21 17:00 | 23.1 | 54 | 5.53 | 215 | 26 | 30 | 12 | 116.256 | 0
2024-01-21 18:00 | 22.1 | 59 | 4.3 | 44 | 26 | 30 | 12 | 120.0257 | 0
2024-01-21 19:00 | 21.4 | 62 | 3.49 | 0 | 26 | 30 | 12 | 113.0526 | 0
2024-01-21 20:00 | 20.4 | 66 | 3.04 | 0 | 26 | 30 | 12 | 107.6678 | 0
2024-01-21 21:00 | 19.7 | 70 | 2.78 | 0 | 26 | 30 | 12 | 103.6248 | 0
2024-01-21 22:00 | 19.4 | 71 | 2.58 | 0 | 26 | 30 | 12 | 100.565 | 0
2024-01-21 23:00 | 18.8 | 74 | 2.24 | 0 | 26 | 30 | 12 | 94.5712 | 0
2024-01-22 | 18.8 | 75 | 2.64 | 0 | 26 | 30 | 12 | 102.825 | 0
2024-01-22 01:00 | 18 | 78 | 2.73 | 0 | 26 | 30 | 12 | 108.2366 | 0
2024-01-22 02:00 | 17.2 | 82 | 2.62 | 0 | 26 | 30 | 12 | 108.4414 | 0
2024-01-22 03:00 | 16.7 | 86 | 2.88 | 0 | 26 | 30 | 12 | 115.0953 | 0
2024-01-22 04:00 | 16 | 88 | 3.4 | 0 | 26 | 30 | 12 | 130.9756 | 0
2024-01-22 05:00 | 15 | 89 | 3.6 | 0 | 26 | 30 | 12 | 143.3295 | 0
2024-01-22 06:00 | 14.7 | 90 | 3.45 | 0 | 26 | 30 | 12 | 141.4597 | 0
2024-01-22 07:00 | 14.6 | 90 | 3.62 | 0 | 26 | 30 | 12 | 146.422 | 0
2024-01-22 08:00 | 15.4 | 84 | 3.45 | 44 | 26 | 30 | 12 | 134.5336 | 0
2024-01-22 09:00 | 18.2 | 71 | 3.14 | 218 | 26 | 30 | 12 | 92.6757 | 0
2024-01-22 10:00 | 21.4 | 59 | 2.92 | 416 | 26 | 30 | 12 | 48.6735 | 0
2024-01-22 11:00 | 23.3 | 55 | 2.56 | 580 | 26 | 30 | 12 | 9.691 | 0
2024-01-22 12:00 | 24.3 | 53 | 2.41 | 685 | 26 | 30 | 12 | 0 | 0
2024-01-22 13:00 | 25 | 51 | 3.23 | 722 | 26 | 30 | 12 | 0 | 0
2024-01-22 14:00 | 24.9 | 54 | 4.52 | 684 | 26 | 30 | 12 | 17.442 | 0
2024-01-22 15:00 | 24.4 | 56 | 5.37 | 577 | 26 | 30 | 12 | 46.2977 | 0
2024-01-22 16:00 | 23.9 | 58 | 5.39 | 414 | 26 | 30 | 12 | 70.5783 | 0
2024-01-22 17:00 | 23.5 | 63 | 5.25 | 218 | 26 | 30 | 12 | 90.4372 | 0
2024-01-22 18:00 | 22.7 | 67 | 3.81 | 45 | 26 | 30 | 12 | 94.3792 | 0
2024-01-22 19:00 | 22 | 70 | 3.13 | 0 | 26 | 30 | 12 | 91.8836 | 0
2024-01-22 20:00 | 21.1 | 74 | 2.38 | 0 | 26 | 30 | 12 | 81.5011 | 0
2024-01-22 21:00 | 20 | 79 | 1.99 | 0 | 26 | 30 | 12 | 77.421 | 0
2024-01-22 22:00 | 19.6 | 80 | 1.53 | 0 | 26 | 30 | 12 | 69.3813 | 0
2024-01-22 23:00 | 20 | 77 | 1.2 | 0 | 26 | 30 | 12 | 61.3046 | 0
2024-01-23 | 19 | 81 | 1.34 | 0 | 26 | 30 | 12 | 67.7061 | 0
2024-01-23 01:00 | 17.2 | 88 | 2 | 0 | 26 | 30 | 12 | 89.8259 | 0
2024-01-23 02:00 | 16.4 | 91 | 2.16 | 0 | 26 | 30 | 12 | 96.9811 | 0
2024-01-23 03:00 | 15.8 | 93 | 2.15 | 0 | 26 | 30 | 12 | 99.4984 | 0
2024-01-23 04:00 | 15.4 | 94 | 2.35 | 0 | 26 | 30 | 12 | 106.4947 | 0
2024-01-23 05:00 | 15.6 | 92 | 2 | 0 | 26 | 30 | 12 | 97.621 | 0
2024-01-23 06:00 | 14.9 | 94 | 2.26 | 0 | 26 | 30 | 12 | 107.6275 | 0
2024-01-23 07:00 | 14.5 | 95 | 2.34 | 0 | 26 | 30 | 12 | 111.7749 | 0
2024-01-23 08:00 | 16.1 | 93 | 2.68 | 44 | 26 | 30 | 12 | 103.9576 | 0
2024-01-23 09:00 | 18.5 | 81 | 2.15 | 220 | 26 | 30 | 12 | 59.694 | 0
2024-01-23 10:00 | 21.3 | 69 | 1.71 | 417 | 26 | 30 | 12 | 14.4192 | 0
2024-01-23 11:00 | 22.9 | 62 | 0.51 | 582 | 26 | 30 | 12 | 0 | 18.064
2024-01-23 12:00 | 24.2 | 55 | 0.81 | 689 | 26 | 30 | 12 | 0 | 25.0102
2024-01-23 13:00 | 25.3 | 49 | 2.25 | 726 | 26 | 30 | 12 | 0 | 0
2024-01-23 14:00 | 25.3 | 51 | 3.66 | 690 | 26 | 30 | 12 | 4.2767 | 0
2024-01-23 15:00 | 24.7 | 54 | 4.78 | 584 | 26 | 30 | 12 | 36.9872 | 0
2024-01-23 16:00 | 24 | 54 | 5 | 421 | 26 | 30 | 12 | 69.8996 | 0
2024-01-23 17:00 | 22.9 | 64 | 5.27 | 224 | 26 | 30 | 12 | 95.2384 | 0
2024-01-23 18:00 | 22 | 70 | 4.36 | 47 | 26 | 30 | 12 | 105.6705 | 0
2024-01-23 19:00 | 21.3 | 74 | 3.2 | 0 | 26 | 30 | 12 | 94.6457 | 0
2024-01-23 20:00 | 20.4 | 77 | 2.11 | 0 | 26 | 30 | 12 | 78.6862 | 0
2024-01-23 21:00 | 19.4 | 81 | 1.57 | 0 | 26 | 30 | 12 | 70.8235 | 0
2024-01-23 22:00 | 20.3 | 76 | 0.91 | 0 | 26 | 30 | 12 | 53.2508 | 0
2024-01-23 23:00 | 18.6 | 84 | 1.33 | 0 | 26 | 30 | 12 | 68.0146 | 0
2024-01-24 | 17.3 | 90 | 2.84 | 0 | 26 | 30 | 12 | 106.3039 | 0
2024-01-24 01:00 | 16 | 96 | 2.86 | 0 | 26 | 30 | 12 | 112.5313 | 0
2024-01-24 02:00 | 15.4 | 97 | 2.71 | 0 | 26 | 30 | 12 | 113.1139 | 0
2024-01-24 03:00 | 14.8 | 97 | 2.41 | 0 | 26 | 30 | 12 | 110.2937 | 0
2024-01-24 04:00 | 14.2 | 98 | 2.42 | 0 | 26 | 30 | 12 | 114.1175 | 0
2024-01-24 05:00 | 14.3 | 98 | 2.1 | 0 | 26 | 30 | 12 | 105.1321 | 0
2024-01-24 06:00 | 13.7 | 100 | 2.26 | 0 | 26 | 30 | 12 | 112.1808 | 0
2024-01-24 07:00 | 13.1 | 100 | 2.34 | 0 | 26 | 30 | 12 | 118.3035 | 0
2024-01-24 08:00 | 13.1 | 99 | 1.9 | 39 | 26 | 30 | 12 | 101.1886 | 0
2024-01-24 09:00 | 14.8 | 97 | 2.21 | 169 | 26 | 30 | 12 | 82.4565 | 0
2024-01-24 10:00 | 17.3 | 91 | 1.75 | 334 | 26 | 30 | 12 | 36.4594 | 0
2024-01-24 11:00 | 21.2 | 65 | 2.11 | 579 | 26 | 30 | 12 | 4.9733 | 0
2024-01-24 12:00 | 23.6 | 45 | 2.77 | 702 | 26 | 30 | 12 | 6.8696 | 0
2024-01-24 13:00 | 25.1 | 33 | 3.61 | 742 | 26 | 30 | 12 | 25.8535 | 0
2024-01-24 14:00 | 25.9 | 28 | 3.85 | 707 | 26 | 30 | 12 | 38.3342 | 0
2024-01-24 15:00 | 25.5 | 36 | 4.5 | 602 | 26 | 30 | 12 | 55.0464 | 0
2024-01-24 16:00 | 23.6 | 56 | 5.54 | 433 | 26 | 30 | 12 | 77.5786 | 0
2024-01-24 17:00 | 22.5 | 45 | 5.06 | 231 | 26 | 30 | 12 | 127.3326 | 0
2024-01-24 18:00 | 20.9 | 64 | 3.42 | 50 | 26 | 30 | 12 | 106.7861 | 0
2024-01-24 19:00 | 19.5 | 76 | 2.43 | 0 | 26 | 30 | 12 | 92.3867 | 0
2024-01-24 20:00 | 18 | 85 | 1.81 | 0 | 26 | 30 | 12 | 82.2143 | 0
2024-01-24 21:00 | 19.3 | 78 | 0.9 | 0 | 26 | 30 | 12 | 56.5216 | 0
2024-01-24 22:00 | 17.9 | 83 | 1.22 | 0 | 26 | 30 | 12 | 69.3103 | 0
2024-01-24 23:00 | 15.5 | 90 | 2.59 | 0 | 26 | 30 | 12 | 114.2782 | 0
2024-01-25 | 14.9 | 89 | 3.45 | 0 | 26 | 30 | 12 | 140.5819 | 0
2024-01-25 01:00 | 13.2 | 90 | 2.97 | 0 | 26 | 30 | 12 | 140.721 | 0
2024-01-25 02:00 | 12.2 | 86 | 2.78 | 0 | 26 | 30 | 12 | 144.6037 | 0
2024-01-25 03:00 | 11.6 | 77 | 2.94 | 0 | 26 | 30 | 12 | 158.5219 | 0
2024-01-25 04:00 | 11 | 74 | 3.09 | 0 | 26 | 30 | 12 | 168.8068 | 0
2024-01-25 05:00 | 11.9 | 72 | 2.73 | 0 | 26 | 30 | 12 | 152.7907 | 0
2024-01-25 06:00 | 11.2 | 76 | 2.52 | 0 | 26 | 30 | 12 | 147.8779 | 0
2024-01-25 07:00 | 11.1 | 75 | 2.69 | 0 | 26 | 30 | 12 | 154.5966 | 0
2024-01-25 08:00 | 12.4 | 68 | 2.77 | 44 | 26 | 30 | 12 | 147.4341 | 0
2024-01-25 09:00 | 16.5 | 52 | 2.55 | 215 | 26 | 30 | 12 | 104.019 | 0
2024-01-25 10:00 | 21.1 | 38 | 2.62 | 416 | 26 | 30 | 12 | 64.5391 | 0
2024-01-25 11:00 | 24.5 | 25 | 3.76 | 585 | 26 | 30 | 12 | 66.8726 | 0
2024-01-25 12:00 | 26.2 | 19 | 3.82 | 696 | 26 | 30 | 12 | 52.4159 | 0
2024-01-25 13:00 | 27.2 | 18 | 3.7 | 737 | 26 | 30 | 12 | 39.6029 | 0
2024-01-25 14:00 | 27.5 | 18 | 3.91 | 671 | 26 | 30 | 12 | 51.7416 | 0
2024-01-25 15:00 | 27.2 | 22 | 4.03 | 545 | 26 | 30 | 12 | 65.9733 | 0
2024-01-25 16:00 | 26.5 | 28 | 4.37 | 426 | 26 | 30 | 12 | 83.0809 | 0
2024-01-25 17:00 | 24.7 | 36 | 4.66 | 220 | 26 | 30 | 12 | 116.5984 | 0
2024-01-25 18:00 | 22.9 | 47 | 3.54 | 44 | 26 | 30 | 12 | 114.8929 | 0
2024-01-25 19:00 | 21.7 | 61 | 3.09 | 0 | 26 | 30 | 12 | 103.8626 | 0
2024-01-25 20:00 | 20.5 | 69 | 2.33 | 0 | 26 | 30 | 12 | 89.1476 | 0
2024-01-25 21:00 | 19.4 | 76 | 2 | 0 | 26 | 30 | 12 | 83.7381 | 0
2024-01-25 22:00 | 21.3 | 66 | 0.41 | 0 | 26 | 30 | 12 | 44.0623 | 0
2024-01-25 23:00 | 18 | 81 | 2.2 | 0 | 26 | 30 | 12 | 93.8734 | 0
2024-01-26 | 17.6 | 77 | 3.3 | 0 | 26 | 30 | 12 | 125.0189 | 0
2024-01-26 01:00 | 16.3 | 80 | 2.92 | 0 | 26 | 30 | 12 | 123.7348 | 0
2024-01-26 02:00 | 15.7 | 77 | 3.11 | 0 | 26 | 30 | 12 | 135.2568 | 0
2024-01-26 03:00 | 15.1 | 73 | 3.18 | 0 | 26 | 30 | 12 | 144.5385 | 0
2024-01-26 04:00 | 14.6 | 68 | 3.26 | 0 | 26 | 30 | 12 | 154.0381 | 0
2024-01-26 05:00 | 14.8 | 67 | 3.32 | 0 | 26 | 30 | 12 | 155.0875 | 0
2024-01-26 06:00 | 15 | 59 | 3.44 | 0 | 26 | 30 | 12 | 163.3628 | 0
2024-01-26 07:00 | 14.9 | 53 | 3.71 | 0 | 26 | 30 | 12 | 176.7944 | 0
2024-01-26 08:00 | 15.8 | 45 | 3.76 | 44 | 26 | 30 | 12 | 173.2222 | 0
2024-01-26 09:00 | 19.5 | 34 | 3.58 | 221 | 26 | 30 | 12 | 131.2953 | 0
2024-01-26 10:00 | 23.6 | 25 | 2.79 | 419 | 26 | 30 | 12 | 68.9828 | 0
2024-01-26 11:00 | 26.7 | 20 | 3.7 | 587 | 26 | 30 | 12 | 59.4036 | 0
2024-01-26 12:00 | 28.2 | 16 | 3.67 | 687 | 26 | 30 | 12 | 43.3146 | 0
2024-01-26 13:00 | 29.1 | 14 | 3.72 | 729 | 26 | 30 | 12 | 37.4522 | 0
2024-01-26 14:00 | 29.7 | 13 | 4.39 | 701 | 26 | 30 | 12 | 55.3997 | 0
2024-01-26 15:00 | 29.8 | 14 | 4.97 | 533 | 26 | 30 | 12 | 87.7504 | 0
2024-01-26 16:00 | 29.4 | 15 | 3.84 | 408 | 26 | 30 | 12 | 79.825 | 0
2024-01-26 17:00 | 26.9 | 31 | 2.86 | 216 | 26 | 30 | 12 | 71.2492 | 0
2024-01-26 18:00 | 23.8 | 43 | 2.92 | 52 | 26 | 30 | 12 | 98.9916 | 0
2024-01-26 19:00 | 22.1 | 48 | 2.66 | 0 | 26 | 30 | 12 | 105.6828 | 0
2024-01-26 20:00 | 20.9 | 65 | 1.9 | 0 | 26 | 30 | 12 | 80.3089 | 0
2024-01-26 21:00 | 20.5 | 65 | 3.44 | 0 | 26 | 30 | 12 | 116.1536 | 0
2024-01-26 22:00 | 19.6 | 60 | 3.57 | 0 | 26 | 30 | 12 | 131.8442 | 0
2024-01-26 23:00 | 18.8 | 54 | 3.61 | 0 | 26 | 30 | 12 | 145.3896 | 0
2024-01-27 | 18 | 50 | 3.2 | 0 | 26 | 30 | 12 | 144.2499 | 0
2024-01-27 01:00 | 17.4 | 54 | 3.22 | 0 | 26 | 30 | 12 | 145.1772 | 0
2024-01-27 02:00 | 17 | 57 | 3.47 | 0 | 26 | 30 | 12 | 151.988 | 0
2024-01-27 03:00 | 17.1 | 41 | 3.94 | 0 | 26 | 30 | 12 | 179.5645 | 0
2024-01-27 04:00 | 17.4 | 42 | 4.03 | 0 | 26 | 30 | 12 | 179.0496 | 0
2024-01-27 05:00 | 18.8 | 50 | 4.43 | 0 | 26 | 30 | 12 | 169.985 | 0
2024-01-27 06:00 | 19.2 | 52 | 5.03 | 0 | 26 | 30 | 12 | 178.0349 | 0
2024-01-27 07:00 | 19.4 | 55 | 5.5 | 0 | 26 | 30 | 12 | 182.2512 | 0
2024-01-27 08:00 | 20.5 | 57 | 6.79 | 30 | 26 | 30 | 12 | 188.4834 | 0
2024-01-27 09:00 | 21.9 | 56 | 7.16 | 149 | 26 | 30 | 12 | 163.1984 | 0
2024-01-27 10:00 | 23.7 | 53 | 8.43 | 336 | 26 | 30 | 12 | 139.385 | 0
2024-01-27 11:00 | 25.7 | 47 | 9.24 | 568 | 26 | 30 | 12 | 105.0035 | 0
2024-01-27 12:00 | 27 | 43 | 8.7 | 670 | 26 | 30 | 12 | 76.6678 | 0
2024-01-27 13:00 | 27.9 | 41 | 8 | 700 | 26 | 30 | 12 | 57.0549 | 0
2024-01-27 14:00 | 28.5 | 38 | 6.95 | 677 | 26 | 30 | 12 | 48.046 | 0
2024-01-27 15:00 | 28.8 | 36 | 6.01 | 568 | 26 | 30 | 12 | 52.2674 | 0
2024-01-27 16:00 | 28.6 | 36 | 5.86 | 338 | 26 | 30 | 12 | 83.4269 | 0
2024-01-27 17:00 | 28 | 37 | 4.7 | 148 | 26 | 30 | 12 | 95.4039 | 0
2024-01-27 18:00 | 26.4 | 44 | 2.79 | 41 | 26 | 30 | 12 | 78.3735 | 0
2024-01-27 19:00 | 23.9 | 69 | 2.48 | 0 | 26 | 30 | 12 | 66.8119 | 0
2024-01-27 20:00 | 23 | 75 | 2.4 | 0 | 26 | 30 | 12 | 66.3883 | 0
2024-01-27 21:00 | 23.2 | 72 | 1.34 | 0 | 26 | 30 | 12 | 50.178 | 0
2024-01-27 22:00 | 22 | 78 | 1.55 | 0 | 26 | 30 | 12 | 56.8733 | 0
2024-01-27 23:00 | 21.9 | 75 | 2.52 | 0 | 26 | 30 | 12 | 76.9841 | 0
2024-01-28 | 21.2 | 78 | 3.04 | 0 | 26 | 30 | 12 | 88.4235 | 0
2024-01-28 01:00 | 20.9 | 77 | 3.64 | 0 | 26 | 30 | 12 | 102.2981 | 0
2024-01-28 02:00 | 20.5 | 73 | 4.1 | 0 | 26 | 30 | 12 | 119.0652 | 0
2024-01-28 03:00 | 20.3 | 67 | 1.94 | 0 | 26 | 30 | 12 | 83.3469 | 0
2024-01-28 04:00 | 19.8 | 75 | 2.82 | 0 | 26 | 30 | 12 | 99.0426 | 0
2024-01-28 05:00 | 19.6 | 77 | 2.21 | 0 | 26 | 30 | 12 | 86.2295 | 0
2024-01-28 06:00 | 18.9 | 79 | 2.59 | 0 | 26 | 30 | 12 | 97.6558 | 0
2024-01-28 07:00 | 19 | 82 | 3.01 | 0 | 26 | 30 | 12 | 102.7429 | 0
2024-01-28 08:00 | 20.9 | 86 | 3 | 41 | 26 | 30 | 12 | 76.4491 | 0
2024-01-28 09:00 | 23.1 | 73 | 2.77 | 202 | 26 | 30 | 12 | 45.9771 | 0
2024-01-28 10:00 | 24.4 | 61 | 5.08 | 394 | 26 | 30 | 12 | 57.3595 | 0
2024-01-28 11:00 | 24.8 | 50 | 5.32 | 505 | 26 | 30 | 12 | 62.5287 | 0
2024-01-28 12:00 | 24.9 | 47 | 5.83 | 608 | 26 | 30 | 12 | 61.7151 | 0
2024-01-28 13:00 | 25 | 44 | 6.48 | 719 | 26 | 30 | 12 | 62.5893 | 0
2024-01-28 14:00 | 24.7 | 43 | 7.22 | 685 | 26 | 30 | 12 | 85.0872 | 0
2024-01-28 15:00 | 24.3 | 43 | 7.13 | 570 | 26 | 30 | 12 | 104.0614 | 0
2024-01-28 16:00 | 23.8 | 45 | 6.65 | 406 | 26 | 30 | 12 | 119.526 | 0
2024-01-28 17:00 | 23 | 49 | 5.98 | 225 | 26 | 30 | 12 | 133.2152 | 0
2024-01-28 18:00 | 22.1 | 55 | 5.07 | 53 | 26 | 30 | 12 | 139.0381 | 0
2024-01-28 19:00 | 21.6 | 58 | 4.12 | 0 | 26 | 30 | 12 | 128.677 | 0
2024-01-28 20:00 | 21 | 59 | 3.5 | 0 | 26 | 30 | 12 | 120.1439 | 0
2024-01-28 21:00 | 20.4 | 59 | 3.6 | 0 | 26 | 30 | 12 | 127.1626 | 0
2024-01-28 22:00 | 19.9 | 61 | 3.8 | 0 | 26 | 30 | 12 | 133.3083 | 0
2024-01-28 23:00 | 19.5 | 66 | 3.91 | 0 | 26 | 30 | 12 | 133.3113 | 0
2024-01-29 | 19.3 | 66 | 4.04 | 0 | 26 | 30 | 12 | 137.8211 | 0
2024-01-29 01:00 | 19 | 67 | 4.14 | 0 | 26 | 30 | 12 | 141.4792 | 0
2024-01-29 02:00 | 18.4 | 69 | 3.8 | 0 | 26 | 30 | 12 | 137.2571 | 0
2024-01-29 03:00 | 18 | 72 | 3.71 | 0 | 26 | 30 | 12 | 135.6035 | 0
2024-01-29 04:00 | 17.8 | 71 | 3.85 | 0 | 26 | 30 | 12 | 141.4679 | 0
2024-01-29 05:00 | 18.1 | 75 | 4.03 | 0 | 26 | 30 | 12 | 138.4641 | 0
2024-01-29 06:00 | 18 | 73 | 4.14 | 0 | 26 | 30 | 12 | 143.9 | 0
2024-01-29 07:00 | 18 | 72 | 4.2 | 0 | 26 | 30 | 12 | 146.2875 | 0
2024-01-29 08:00 | 19.2 | 66 | 4.41 | 48 | 26 | 30 | 12 | 139.9784 | 0
2024-01-29 09:00 | 21.7 | 50 | 4.96 | 229 | 26 | 30 | 12 | 125.116 | 0
2024-01-29 10:00 | 22.8 | 44 | 6.06 | 432 | 26 | 30 | 12 | 118.5465 | 0
2024-01-29 11:00 | 23.4 | 42 | 6.14 | 601 | 26 | 30 | 12 | 94.8167 | 0
2024-01-29 12:00 | 23.9 | 39 | 6.51 | 709 | 26 | 30 | 12 | 88.027 | 0
2024-01-29 13:00 | 24 | 39 | 6.22 | 713 | 26 | 30 | 12 | 81.0326 | 0
2024-01-29 14:00 | 23.8 | 39 | 6.48 | 531 | 26 | 30 | 12 | 112.5769 | 0
2024-01-29 15:00 | 24 | 40 | 7.4 | 562 | 26 | 30 | 12 | 120.4964 | 0
2024-01-29 16:00 | 23.5 | 44 | 7.02 | 417 | 26 | 30 | 12 | 130.1985 | 0
2024-01-29 17:00 | 22.8 | 50 | 5.21 | 163 | 26 | 30 | 12 | 127.9738 | 0
2024-01-29 18:00 | 22.2 | 53 | 4.41 | 40 | 26 | 30 | 12 | 130.4939 | 0
2024-01-29 19:00 | 21.6 | 57 | 3.52 | 0 | 26 | 30 | 12 | 118.0432 | 0
2024-01-29 20:00 | 21 | 61 | 3.44 | 0 | 26 | 30 | 12 | 116.5713 | 0
2024-01-29 21:00 | 20.5 | 64 | 3.47 | 0 | 26 | 30 | 12 | 117.8927 | 0
2024-01-29 22:00 | 20.2 | 66 | 3.26 | 0 | 26 | 30 | 12 | 113.8358 | 0
2024-01-29 23:00 | 19.7 | 69 | 3.05 | 0 | 26 | 30 | 12 | 110.341 | 0
2024-01-30 | 18.9 | 73 | 2.88 | 0 | 26 | 30 | 12 | 109.0939 | 0
2024-01-30 01:00 | 18.1 | 77 | 3.2 | 0 | 26 | 30 | 12 | 118.7348 | 0
2024-01-30 02:00 | 17.6 | 80 | 3.06 | 0 | 26 | 30 | 12 | 117.0074 | 0
2024-01-30 03:00 | 17.1 | 81 | 3.13 | 0 | 26 | 30 | 12 | 121.7078 | 0
2024-01-30 04:00 | 16.7 | 84 | 3.2 | 0 | 26 | 30 | 12 | 123.9829 | 0
2024-01-30 05:00 | 16.4 | 81 | 2.82 | 0 | 26 | 30 | 12 | 119.7939 | 0
2024-01-30 06:00 | 16 | 85 | 2.71 | 0 | 26 | 30 | 12 | 117.0851 | 0
2024-01-30 07:00 | 15.7 | 87 | 3 | 0 | 26 | 30 | 12 | 124.8789 | 0
2024-01-30 08:00 | 16.6 | 83 | 2.6 | 40 | 26 | 30 | 12 | 106.1428 | 0
2024-01-30 09:00 | 19.6 | 70 | 2.5 | 197 | 26 | 30 | 12 | 71.6377 | 0
2024-01-30 10:00 | 21.8 | 63 | 2.45 | 290 | 26 | 30 | 12 | 48.9427 | 0
2024-01-30 11:00 | 23.6 | 58 | 1.79 | 456 | 26 | 30 | 12 | 5.8669 | 0
2024-01-30 12:00 | 25 | 52 | 2.73 | 666 | 26 | 30 | 12 | 0 | 0
2024-01-30 13:00 | 25.4 | 51 | 3.84 | 655 | 26 | 30 | 12 | 11.0214 | 0
2024-01-30 14:00 | 25.9 | 44 | 3.55 | 621 | 26 | 30 | 12 | 17.6771 | 0
2024-01-30 15:00 | 26.7 | 35 | 3.16 | 551 | 26 | 30 | 12 | 27.7397 | 0
2024-01-30 16:00 | 26.1 | 37 | 3.68 | 335 | 26 | 30 | 12 | 68.49 | 0
2024-01-30 17:00 | 25.9 | 42 | 3.5 | 233 | 26 | 30 | 12 | 72.3182 | 0
2024-01-30 18:00 | 24.2 | 58 | 2.94 | 55 | 26 | 30 | 12 | 77.3627 | 0
2024-01-30 19:00 | 23.1 | 71 | 1.72 | 0 | 26 | 30 | 12 | 58.312 | 0
2024-01-30 20:00 | 22.1 | 79 | 1.12 | 0 | 26 | 30 | 12 | 47.7146 | 0
2024-01-30 21:00 | 22.3 | 78 | 0.57 | 0 | 26 | 30 | 12 | 36.4568 | 0
2024-01-30 22:00 | 21.3 | 83 | 0.91 | 0 | 26 | 30 | 12 | 45.5008 | 0
2024-01-30 23:00 | 19.8 | 87 | 1.53 | 0 | 26 | 30 | 12 | 63.958 | 0
2024-01-31 | 19.2 | 83 | 1.97 | 0 | 26 | 30 | 12 | 79.4157 | 0
2024-01-31 01:00 | 18.7 | 76 | 2.48 | 0 | 26 | 30 | 12 | 99.1702 | 0
2024-01-31 02:00 | 17.9 | 73 | 2.27 | 0 | 26 | 30 | 12 | 101.8804 | 0
2024-01-31 03:00 | 17.4 | 68 | 2.55 | 0 | 26 | 30 | 12 | 115.8972 | 0
2024-01-31 04:00 | 16.6 | 66 | 2.12 | 0 | 26 | 30 | 12 | 110.3913 | 0
2024-01-31 05:00 | 17.5 | 65 | 2.44 | 0 | 26 | 30 | 12 | 114.5902 | 0
2024-01-31 06:00 | 17.6 | 62 | 2.28 | 0 | 26 | 30 | 12 | 111.7906 | 0
2024-01-31 07:00 | 17.8 | 60 | 2.31 | 0 | 26 | 30 | 12 | 112.868 | 0
2024-01-31 08:00 | 19.4 | 53 | 2.25 | 42 | 26 | 30 | 12 | 101.5163 | 0
2024-01-31 09:00 | 21.8 | 46 | 1.25 | 161 | 26 | 30 | 12 | 49.8626 | 0
2024-01-31 10:00 | 24.3 | 36 | 0.71 | 282 | 26 | 30 | 12 | 11.8893 | 0
2024-01-31 11:00 | 25.3 | 34 | 0.82 | 289 | 26 | 30 | 12 | 12.3319 | 0
2024-01-31 12:00 | 26.2 | 35 | 2.51 | 366 | 26 | 30 | 12 | 42.0551 | 0
2024-01-31 13:00 | 26.6 | 40 | 4.57 | 558 | 26 | 30 | 12 | 44.8307 | 0
2024-01-31 14:00 | 27.1 | 36 | 2.53 | 537 | 26 | 30 | 12 | 12.5415 | 0
2024-01-31 15:00 | 27.3 | 37 | 1.43 | 327 | 26 | 30 | 12 | 14.1071 | 0
2024-01-31 16:00 | 27.1 | 38 | 2.2 | 210 | 26 | 30 | 12 | 47.1968 | 0
2024-01-31 17:00 | 27.1 | 43 | 3.57 | 224 | 26 | 30 | 12 | 63.3294 | 0
2024-01-31 18:00 | 25.8 | 51 | 1.99 | 54 | 26 | 30 | 12 | 57.2856 | 0
2024-01-31 19:00 | 25.3 | 56 | 1.39 | 0 | 26 | 30 | 12 | 51.3392 | 0
2024-01-31 20:00 | 24.4 | 62 | 0.76 | 0 | 26 | 30 | 12 | 38.4992 | 0
2024-01-31 21:00 | 24 | 66 | 2.01 | 0 | 26 | 30 | 12 | 61.72 | 0
2024-01-31 22:00 | 24 | 63 | 1.92 | 0 | 26 | 30 | 12 | 62.9824 | 0
2024-01-31 23:00 | 23.2 | 60 | 3.71 | 0 | 26 | 30 | 12 | 103.8202 | 0
2024-02-01 | 22.9 | 64 | 3.04 | 0 | 26 | 30 | 12 | 89.7554 | 0
2024-02-01 01:00 | 22.8 | 69 | 1.7 | 0 | 26 | 30 | 12 | 61.4338 | 0
2024-02-01 02:00 | 22.9 | 64 | 2.1 | 0 | 26 | 30 | 12 | 72.6699 | 0
2024-02-01 03:00 | 21.3 | 72 | 3.86 | 0 | 26 | 30 | 12 | 108.2885 | 0
2024-02-01 04:00 | 20.9 | 75 | 2.06 | 0 | 26 | 30 | 12 | 75.8867 | 0
2024-02-01 05:00 | 20.9 | 77 | 2.9 | 0 | 26 | 30 | 12 | 89.6591 | 0
2024-02-01 06:00 | 20 | 82 | 3.92 | 0 | 26 | 30 | 12 | 109.926 | 0
2024-02-01 07:00 | 19.8 | 81 | 4.44 | 0 | 26 | 30 | 12 | 121.9892 | 0
2024-02-01 08:00 | 20.3 | 81 | 5.03 | 27 | 26 | 30 | 12 | 122.1165 | 0
2024-02-01 09:00 | 22 | 69 | 4.64 | 191 | 26 | 30 | 12 | 92.1172 | 0
2024-02-01 10:00 | 23.9 | 60 | 5.19 | 376 | 26 | 30 | 12 | 69.0327 | 0
2024-02-01 11:00 | 25 | 56 | 5.97 | 485 | 26 | 30 | 12 | 59.8284 | 0
2024-02-01 12:00 | 26 | 53 | 6.08 | 583 | 26 | 30 | 12 | 42.0166 | 0
2024-02-01 13:00 | 26.6 | 50 | 6.21 | 604 | 26 | 30 | 12 | 40.2954 | 0
2024-02-01 14:00 | 27.3 | 49 | 5.56 | 511 | 26 | 30 | 12 | 38.5072 | 0
2024-02-01 15:00 | 28.6 | 44 | 3.85 | 532 | 26 | 30 | 12 | 10.8434 | 0
2024-02-01 16:00 | 28.2 | 49 | 6.14 | 421 | 26 | 30 | 12 | 45.9028 | 0
2024-02-01 17:00 | 27.8 | 49 | 6.3 | 222 | 26 | 30 | 12 | 79.802 | 0
2024-02-01 18:00 | 25 | 63 | 6.33 | 59 | 26 | 30 | 12 | 106.2597 | 0
2024-02-01 19:00 | 23.6 | 71 | 7.72 | 0 | 26 | 30 | 12 | 132.6968 | 0
2024-02-01 20:00 | 22.4 | 77 | 7.84 | 0 | 26 | 30 | 12 | 140.3664 | 0
2024-02-01 21:00 | 21.9 | 78 | 7.84 | 0 | 26 | 30 | 12 | 146.6272 | 0
2024-02-01 22:00 | 21.9 | 77 | 7.16 | 0 | 26 | 30 | 12 | 140.3241 | 0
2024-02-01 23:00 | 21.8 | 76 | 6.58 | 0 | 26 | 30 | 12 | 136.3288 | 0
2024-02-02 | 22 | 74 | 5.69 | 0 | 26 | 30 | 12 | 125.1869 | 0
2024-02-02 01:00 | 21.9 | 71 | 4.72 | 0 | 26 | 30 | 12 | 117.2077 | 0
2024-02-02 02:00 | 22.7 | 58 | 3.47 | 0 | 26 | 30 | 12 | 106.6393 | 0
2024-02-02 03:00 | 22.8 | 49 | 3.71 | 0 | 26 | 30 | 12 | 122.466 | 0
2024-02-02 04:00 | 23 | 47 | 4.65 | 0 | 26 | 30 | 12 | 142.4563 | 0
2024-02-02 05:00 | 22.4 | 65 | 5.39 | 0 | 26 | 30 | 12 | 131.4796 | 0
2024-02-02 06:00 | 23.2 | 56 | 4.4 | 0 | 26 | 30 | 12 | 121.5873 | 0
2024-02-02 07:00 | 23.3 | 50 | 4.8 | 0 | 26 | 30 | 12 | 137.4727 | 0
2024-02-02 08:00 | 23 | 51 | 5.19 | 33 | 26 | 30 | 12 | 141.3674 | 0
2024-02-02 09:00 | 24 | 53 | 4.74 | 149 | 26 | 30 | 12 | 104.1627 | 0
2024-02-02 10:00 | 24.9 | 58 | 5.02 | 234 | 26 | 30 | 12 | 78.0107 | 0
2024-02-02 11:00 | 27 | 43 | 4.98 | 421 | 26 | 30 | 12 | 59.7012 | 0
2024-02-02 12:00 | 27.1 | 42 | 5.77 | 591 | 26 | 30 | 12 | 49.5405 | 0
2024-02-02 13:00 | 24.2 | 60 | 10.03 | 656 | 26 | 30 | 12 | 89.3576 | 0
2024-02-02 14:00 | 24 | 51 | 9.46 | 583 | 26 | 30 | 12 | 121.4426 | 0
2024-02-02 15:00 | 22.7 | 49 | 8.94 | 521 | 26 | 30 | 12 | 147.2277 | 0
2024-02-02 16:00 | 22.6 | 48 | 9.5 | 358 | 26 | 30 | 12 | 182.4006 | 0
2024-02-02 17:00 | 22.1 | 47 | 8.08 | 166 | 26 | 30 | 12 | 193.5741 | 0
2024-02-02 18:00 | 21.3 | 50 | 7.24 | 43 | 26 | 30 | 12 | 198.6271 | 0
2024-02-02 19:00 | 20.2 | 55 | 6.66 | 0 | 26 | 30 | 12 | 197.2109 | 0
2024-02-02 20:00 | 19.3 | 61 | 5.82 | 0 | 26 | 30 | 12 | 181.0441 | 0
2024-02-02 21:00 | 19.3 | 63 | 5.12 | 0 | 26 | 30 | 12 | 163.9733 | 0
2024-02-02 22:00 | 19.3 | 65 | 5.68 | 0 | 26 | 30 | 12 | 172.2845 | 0
2024-02-02 23:00 | 18.8 | 67 | 5.71 | 0 | 26 | 30 | 12 | 175.5483 | 0
2024-02-03 | 18.1 | 68 | 6.22 | 0 | 26 | 30 | 12 | 192.3208 | 0
2024-02-03 01:00 | 17.7 | 70 | 6.32 | 0 | 26 | 30 | 12 | 196.1588 | 0
2024-02-03 02:00 | 17.5 | 71 | 6.32 | 0 | 26 | 30 | 12 | 197.1046 | 0
2024-02-03 03:00 | 17.5 | 70 | 6.36 | 0 | 26 | 30 | 12 | 199.353 | 0
2024-02-03 04:00 | 17.5 | 69 | 6.38 | 0 | 26 | 30 | 12 | 201.2 | 0
2024-02-03 05:00 | 18.2 | 64 | 6.39 | 0 | 26 | 30 | 12 | 200.5531 | 0
2024-02-03 06:00 | 18 | 63 | 6.45 | 0 | 26 | 30 | 12 | 205.611 | 0
2024-02-03 07:00 | 18 | 62 | 6.39 | 0 | 26 | 30 | 12 | 205.8385 | 0
2024-02-03 08:00 | 18.7 | 59 | 6.51 | 40 | 26 | 30 | 12 | 199.546 | 0
2024-02-03 09:00 | 19.4 | 57 | 7.46 | 138 | 26 | 30 | 12 | 200.3558 | 0
2024-02-03 10:00 | 19.6 | 55 | 7.81 | 175 | 26 | 30 | 12 | 203.319 | 0
2024-02-03 11:00 | 19.7 | 54 | 7.94 | 178 | 26 | 30 | 12 | 206.0498 | 0
2024-02-03 12:00 | 20.4 | 50 | 8.93 | 448 | 26 | 30 | 12 | 187.2784 | 0
2024-02-03 13:00 | 20.5 | 48 | 8.88 | 490 | 26 | 30 | 12 | 183.6594 | 0
2024-02-03 14:00 | 20.6 | 50 | 8.73 | 433 | 26 | 30 | 12 | 182.8166 | 0
2024-02-03 15:00 | 21.1 | 46 | 8.83 | 577 | 26 | 30 | 12 | 167.3158 | 0
2024-02-03 16:00 | 20.8 | 46 | 8.76 | 415 | 26 | 30 | 12 | 191.8678 | 0
2024-02-03 17:00 | 20.1 | 52 | 7.26 | 219 | 26 | 30 | 12 | 185.9923 | 0
2024-02-03 18:00 | 19.6 | 54 | 6.81 | 50 | 26 | 30 | 12 | 202.1718 | 0
2024-02-03 19:00 | 19.6 | 54 | 6.45 | 0 | 26 | 30 | 12 | 201.583 | 0
2024-02-03 20:00 | 19.5 | 56 | 6.57 | 0 | 26 | 30 | 12 | 201.8447 | 0
2024-02-03 21:00 | 19.3 | 57 | 6.45 | 0 | 26 | 30 | 12 | 200.0572 | 0
2024-02-03 22:00 | 18.6 | 59 | 6.2 | 0 | 26 | 30 | 12 | 199.6011 | 0
2024-02-03 23:00 | 18.3 | 62 | 5.87 | 0 | 26 | 30 | 12 | 191.5092 | 0
2024-02-04 | 18 | 64 | 5.73 | 0 | 26 | 30 | 12 | 188.9608 | 0
2024-02-04 01:00 | 17.9 | 65 | 5.64 | 0 | 26 | 30 | 12 | 186.7428 | 0
2024-02-04 02:00 | 17.7 | 65 | 5.66 | 0 | 26 | 30 | 12 | 189.3002 | 0
2024-02-04 03:00 | 17.6 | 63 | 5.57 | 0 | 26 | 30 | 12 | 191.0293 | 0
2024-02-04 04:00 | 17.4 | 63 | 5.63 | 0 | 26 | 30 | 12 | 194.4272 | 0
2024-02-04 05:00 | 18.8 | 60 | 6.16 | 0 | 26 | 30 | 12 | 195.0317 | 0
2024-02-04 06:00 | 18 | 62 | 5.92 | 0 | 26 | 30 | 12 | 195.8159 | 0
2024-02-04 07:00 | 17.9 | 61 | 6.01 | 0 | 26 | 30 | 12 | 200.25 | 0
2024-02-04 08:00 | 18.6 | 57 | 5.91 | 53 | 26 | 30 | 12 | 189.2252 | 0
2024-02-04 09:00 | 20 | 49 | 7.24 | 238 | 26 | 30 | 12 | 189.7433 | 0
2024-02-04 10:00 | 20.8 | 46 | 7.68 | 443 | 26 | 30 | 12 | 167.1508 | 0
2024-02-04 11:00 | 21.2 | 45 | 7.91 | 613 | 26 | 30 | 12 | 145.8658 | 0
2024-02-04 12:00 | 21.5 | 44 | 8.51 | 720 | 26 | 30 | 12 | 141.242 | 0
2024-02-04 13:00 | 21.6 | 43 | 8.73 | 760 | 26 | 30 | 12 | 140.955 | 0
2024-02-04 14:00 | 21.6 | 42 | 8.7 | 729 | 26 | 30 | 12 | 146.8804 | 0
2024-02-04 15:00 | 21.4 | 41 | 8.63 | 625 | 26 | 30 | 12 | 164.4151 | 0
2024-02-04 16:00 | 21.1 | 40 | 8.41 | 462 | 26 | 30 | 12 | 188.0254 | 0
2024-02-04 17:00 | 20.4 | 43 | 7.79 | 259 | 26 | 30 | 12 | 204.948 | 0
2024-02-04 18:00 | 19.6 | 44 | 6.49 | 68 | 26 | 30 | 12 | 209.8104 | 0
2024-02-04 19:00 | 19 | 45 | 5.64 | 0 | 26 | 30 | 12 | 203.7904 | 0
2024-02-04 20:00 | 18.5 | 46 | 5.41 | 0 | 26 | 30 | 12 | 201.4322 | 0
2024-02-04 21:00 | 18.3 | 50 | 5.2 | 0 | 26 | 30 | 12 | 192.8288 | 0
2024-02-04 22:00 | 18 | 54 | 5 | 0 | 26 | 30 | 12 | 185.6356 | 0
2024-02-04 23:00 | 17.9 | 58 | 5.12 | 0 | 26 | 30 | 12 | 184.3415 | 0
2024-02-05 | 17.7 | 62 | 5.04 | 0 | 26 | 30 | 12 | 179.417 | 0
2024-02-05 01:00 | 17.4 | 65 | 4.61 | 0 | 26 | 30 | 12 | 168.8308 | 0
2024-02-05 02:00 | 17.1 | 68 | 4.4 | 0 | 26 | 30 | 12 | 163.3778 | 0
2024-02-05 03:00 | 16.9 | 70 | 4.32 | 0 | 26 | 30 | 12 | 161.1911 | 0
2024-02-05 04:00 | 16.8 | 72 | 4.42 | 0 | 26 | 30 | 12 | 162.2939 | 0
2024-02-05 05:00 | 16.9 | 67 | 4.16 | 0 | 26 | 30 | 12 | 160.535 | 0
2024-02-05 06:00 | 17.2 | 68 | 4.61 | 0 | 26 | 30 | 12 | 167.2919 | 0
2024-02-05 07:00 | 17.4 | 65 | 4.7 | 0 | 26 | 30 | 12 | 170.9029 | 0
2024-02-05 08:00 | 18.8 | 59 | 5.04 | 54 | 26 | 30 | 12 | 165.3704 | 0
2024-02-05 09:00 | 21 | 49 | 5.97 | 237 | 26 | 30 | 12 | 153.0372 | 0
2024-02-05 10:00 | 22 | 46 | 7.59 | 440 | 26 | 30 | 12 | 151.1808 | 0
2024-02-05 11:00 | 22.7 | 42 | 8.15 | 610 | 26 | 30 | 12 | 138.6738 | 0
2024-02-05 12:00 | 23.2 | 41 | 8.41 | 712 | 26 | 30 | 12 | 125.5385 | 0
2024-02-05 13:00 | 23.4 | 40 | 8.59 | 749 | 26 | 30 | 12 | 123.6025 | 0
2024-02-05 14:00 | 23.4 | 41 | 8.36 | 721 | 26 | 30 | 12 | 120.8487 | 0
2024-02-05 15:00 | 23.1 | 41 | 8.1 | 611 | 26 | 30 | 12 | 134.9559 | 0
2024-02-05 16:00 | 22.8 | 40 | 7.78 | 436 | 26 | 30 | 12 | 158.7835 | 0
2024-02-05 17:00 | 21.9 | 49 | 7.15 | 245 | 26 | 30 | 12 | 164.3859 | 0
2024-02-05 18:00 | 21 | 52 | 5.8 | 64 | 26 | 30 | 12 | 167.9316 | 0
2024-02-05 19:00 | 20.4 | 55 | 5.32 | 0 | 26 | 30 | 12 | 168.4023 | 0
2024-02-05 20:00 | 19.9 | 57 | 4.93 | 0 | 26 | 30 | 12 | 162.3916 | 0
2024-02-05 21:00 | 19.4 | 59 | 4.49 | 0 | 26 | 30 | 12 | 155.0437 | 0
2024-02-05 22:00 | 18.9 | 60 | 4.3 | 0 | 26 | 30 | 12 | 154.1071 | 0
2024-02-05 23:00 | 18.6 | 61 | 4.3 | 0 | 26 | 30 | 12 | 155.5702 | 0
2024-02-06 | 18.5 | 64 | 4.44 | 0 | 26 | 30 | 12 | 156.0588 | 0
2024-02-06 01:00 | 18.3 | 67 | 4.32 | 0 | 26 | 30 | 12 | 151.7586 | 0
2024-02-06 02:00 | 18.1 | 70 | 4.22 | 0 | 26 | 30 | 12 | 148.0189 | 0
2024-02-06 03:00 | 17.9 | 72 | 4.1 | 0 | 26 | 30 | 12 | 145.045 | 0
2024-02-06 04:00 | 17.8 | 73 | 4.2 | 0 | 26 | 30 | 12 | 147.0463 | 0
2024-02-06 05:00 | 18.1 | 70 | 4.1 | 0 | 26 | 30 | 12 | 145.4062 | 0
2024-02-06 06:00 | 17.9 | 71 | 3.91 | 0 | 26 | 30 | 12 | 141.9339 | 0
2024-02-06 07:00 | 18 | 69 | 4.1 | 0 | 26 | 30 | 12 | 147.3966 | 0
2024-02-06 08:00 | 19.6 | 62 | 4.71 | 52 | 26 | 30 | 12 | 146.909 | 0
2024-02-06 09:00 | 21.8 | 52 | 6.07 | 235 | 26 | 30 | 12 | 141.287 | 0
2024-02-06 10:00 | 22.5 | 47 | 7.8 | 435 | 26 | 30 | 12 | 147.1107 | 0
2024-02-06 11:00 | 23.2 | 41 | 8.5 | 592 | 26 | 30 | 12 | 143.3194 | 0
2024-02-06 12:00 | 23.6 | 38 | 9.12 | 710 | 26 | 30 | 12 | 140.6868 | 0
2024-02-06 13:00 | 23.6 | 36 | 9.35 | 766 | 26 | 30 | 12 | 142.5835 | 0
2024-02-06 14:00 | 23.6 | 34 | 9.3 | 735 | 26 | 30 | 12 | 151.3344 | 0
2024-02-06 15:00 | 23.3 | 35 | 9.17 | 632 | 26 | 30 | 12 | 164.066 | 0
2024-02-06 16:00 | 22.6 | 39 | 9.31 | 467 | 26 | 30 | 12 | 187.6816 | 0
2024-02-06 17:00 | 22.1 | 43 | 8.14 | 262 | 26 | 30 | 12 | 190.7496 | 0
2024-02-06 18:00 | 21.2 | 44 | 6.82 | 70 | 26 | 30 | 12 | 199.6204 | 0
2024-02-06 19:00 | 20.5 | 47 | 6.26 | 0 | 26 | 30 | 12 | 199.6614 | 0
2024-02-06 20:00 | 19.8 | 52 | 5.63 | 0 | 26 | 30 | 12 | 185.4753 | 0
2024-02-06 21:00 | 19.3 | 56 | 5.71 | 0 | 26 | 30 | 12 | 186.2662 | 0
2024-02-06 22:00 | 19.1 | 56 | 6.43 | 0 | 26 | 30 | 12 | 203.512 | 0
2024-02-06 23:00 | 18.9 | 55 | 6.53 | 0 | 26 | 30 | 12 | 209.4367 | 0
2024-02-07 | 18.6 | 58 | 6.14 | 0 | 26 | 30 | 12 | 199.8355 | 0
2024-02-07 01:00 | 18.3 | 59 | 5.68 | 0 | 26 | 30 | 12 | 191.6475 | 0
2024-02-07 02:00 | 18.1 | 61 | 5.49 | 0 | 26 | 30 | 12 | 186.7993 | 0
2024-02-07 03:00 | 18.1 | 62 | 5.58 | 0 | 26 | 30 | 12 | 187.4121 | 0
2024-02-07 04:00 | 17.9 | 64 | 4.71 | 0 | 26 | 30 | 12 | 167.6341 | 0
2024-02-07 05:00 | 17.4 | 65 | 3.54 | 0 | 26 | 30 | 12 | 143.3915 | 0
2024-02-07 06:00 | 16.8 | 68 | 3.5 | 0 | 26 | 30 | 12 | 144.2808 | 0
2024-02-07 07:00 | 16.6 | 68 | 3.34 | 0 | 26 | 30 | 12 | 141.7758 | 0
2024-02-07 08:00 | 17.5 | 64 | 2.7 | 55 | 26 | 30 | 12 | 114.8118 | 0
2024-02-07 09:00 | 20.2 | 53 | 2.9 | 236 | 26 | 30 | 12 | 87.12 | 0
2024-02-07 10:00 | 22 | 45 | 5.42 | 444 | 26 | 30 | 12 | 110.6428 | 0
2024-02-07 11:00 | 22.4 | 44 | 6.63 | 549 | 26 | 30 | 12 | 117.9444 | 0
2024-02-07 12:00 | 22.9 | 42 | 7.06 | 730 | 26 | 30 | 12 | 100.0813 | 0
2024-02-07 13:00 | 22.9 | 42 | 7.09 | 643 | 26 | 30 | 12 | 112.3832 | 0
2024-02-07 14:00 | 23.2 | 42 | 6.96 | 715 | 26 | 30 | 12 | 96.8074 | 0
2024-02-07 15:00 | 23 | 43 | 7.04 | 641 | 26 | 30 | 12 | 108.4098 | 0
2024-02-07 16:00 | 22.4 | 45 | 7.05 | 460 | 26 | 30 | 12 | 135.8024 | 0
2024-02-07 17:00 | 22.1 | 48 | 6.7 | 264 | 26 | 30 | 12 | 153.1889 | 0
2024-02-07 18:00 | 21.1 | 52 | 5.53 | 74 | 26 | 30 | 12 | 160.1908 | 0
2024-02-07 19:00 | 20.4 | 54 | 4.78 | 0 | 26 | 30 | 12 | 158.6874 | 0
2024-02-07 20:00 | 19.9 | 55 | 4.71 | 0 | 26 | 30 | 12 | 160.4549 | 0
2024-02-07 21:00 | 19.6 | 53 | 4.63 | 0 | 26 | 30 | 12 | 164.0629 | 0
2024-02-07 22:00 | 19.4 | 53 | 5 | 0 | 26 | 30 | 12 | 174.1566 | 0
2024-02-07 23:00 | 19 | 56 | 4.8 | 0 | 26 | 30 | 12 | 169.3855 | 0
2024-02-08 | 18.6 | 59 | 4.64 | 0 | 26 | 30 | 12 | 165.6503 | 0
2024-02-08 01:00 | 18.2 | 61 | 4.57 | 0 | 26 | 30 | 12 | 165.2716 | 0
2024-02-08 02:00 | 17.9 | 63 | 4.24 | 0 | 26 | 30 | 12 | 158.0433 | 0
2024-02-08 03:00 | 17.7 | 64 | 4.06 | 0 | 26 | 30 | 12 | 154.4641 | 0
2024-02-08 04:00 | 17.2 | 66 | 3.35 | 0 | 26 | 30 | 12 | 139.2921 | 0
2024-02-08 05:00 | 15.9 | 71 | 2.55 | 0 | 26 | 30 | 12 | 123.4131 | 0
2024-02-08 06:00 | 15.7 | 72 | 2.82 | 0 | 26 | 30 | 12 | 131.3872 | 0
2024-02-08 07:00 | 15.3 | 73 | 3.32 | 0 | 26 | 30 | 12 | 146.8109 | 0
2024-02-08 08:00 | 16.1 | 69 | 3.71 | 52 | 26 | 30 | 12 | 147.1135 | 0
2024-02-08 09:00 | 18.9 | 58 | 3.73 | 210 | 26 | 30 | 12 | 114.9222 | 0
2024-02-08 10:00 | 20.9 | 52 | 4.28 | 263 | 26 | 30 | 12 | 110.7954 | 0
2024-02-08 11:00 | 22.4 | 45 | 4.94 | 494 | 26 | 30 | 12 | 90.331 | 0
2024-02-08 12:00 | 22.5 | 45 | 5.57 | 470 | 26 | 30 | 12 | 105.1935 | 0
2024-02-08 13:00 | 22.7 | 45 | 6.2 | 571 | 26 | 30 | 12 | 101.568 | 0
2024-02-08 14:00 | 22.9 | 43 | 6.17 | 686 | 26 | 30 | 12 | 87.2318 | 0
2024-02-08 15:00 | 22.7 | 42 | 5.98 | 611 | 26 | 30 | 12 | 97.6933 | 0
2024-02-08 16:00 | 22.3 | 43 | 6.23 | 453 | 26 | 30 | 12 | 126.1944 | 0
2024-02-08 17:00 | 21.9 | 45 | 5.7 | 231 | 26 | 30 | 12 | 146.0603 | 0
2024-02-08 18:00 | 21.2 | 50 | 4.98 | 63 | 26 | 30 | 12 | 152.6894 | 0
2024-02-08 19:00 | 20.4 | 53 | 3.48 | 0 | 26 | 30 | 12 | 131.3268 | 0
2024-02-08 20:00 | 19.7 | 56 | 2.62 | 0 | 26 | 30 | 12 | 112.5462 | 0
2024-02-08 21:00 | 19.1 | 59 | 2.53 | 0 | 26 | 30 | 12 | 111.5401 | 0
2024-02-08 22:00 | 18.8 | 61 | 3.04 | 0 | 26 | 30 | 12 | 124.4947 | 0
2024-02-08 23:00 | 18.4 | 64 | 3.31 | 0 | 26 | 30 | 12 | 131.1013 | 0
2024-02-09 | 18.2 | 64 | 3.73 | 0 | 26 | 30 | 12 | 142.5695 | 0
2024-02-09 01:00 | 18 | 66 | 3.61 | 0 | 26 | 30 | 12 | 139.3561 | 0
2024-02-09 02:00 | 17.1 | 70 | 3.01 | 0 | 26 | 30 | 12 | 128.0857 | 0
2024-02-09 03:00 | 16.5 | 73 | 2.89 | 0 | 26 | 30 | 12 | 126.9439 | 0
2024-02-09 04:00 | 16.3 | 74 | 2.72 | 0 | 26 | 30 | 12 | 123.2014 | 0
2024-02-09 05:00 | 15.1 | 80 | 2.81 | 0 | 26 | 30 | 12 | 129.5713 | 0
2024-02-09 06:00 | 14.7 | 81 | 3.1 | 0 | 26 | 30 | 12 | 139.3892 | 0
2024-02-09 07:00 | 14.3 | 83 | 3.42 | 0 | 26 | 30 | 12 | 149.3171 | 0
2024-02-09 08:00 | 15.2 | 79 | 3.49 | 55 | 26 | 30 | 12 | 139.73 | 0
2024-02-09 09:00 | 17.8 | 67 | 3.45 | 221 | 26 | 30 | 12 | 106.3618 | 0
2024-02-09 10:00 | 20.6 | 56 | 3.06 | 445 | 26 | 30 | 12 | 56.8619 | 0
2024-02-09 11:00 | 22.2 | 48 | 3.03 | 607 | 26 | 30 | 12 | 31.6443 | 0
2024-02-09 12:00 | 23 | 44 | 4.31 | 702 | 26 | 30 | 12 | 45.6008 | 0
2024-02-09 13:00 | 23.1 | 44 | 5.2 | 760 | 26 | 30 | 12 | 54.6868 | 0
2024-02-09 14:00 | 23 | 44 | 5.54 | 735 | 26 | 30 | 12 | 65.6277 | 0
2024-02-09 15:00 | 22.7 | 46 | 5.69 | 633 | 26 | 30 | 12 | 81.6641 | 0
2024-02-09 16:00 | 22 | 50 | 5.73 | 475 | 26 | 30 | 12 | 103.9079 | 0
2024-02-09 17:00 | 21.4 | 52 | 5.41 | 272 | 26 | 30 | 12 | 128.0111 | 0
2024-02-09 18:00 | 20.4 | 57 | 5.05 | 77 | 26 | 30 | 12 | 149.5593 | 0
2024-02-09 19:00 | 19.6 | 60 | 3.8 | 0 | 26 | 30 | 12 | 136.9761 | 0
2024-02-09 20:00 | 18.8 | 63 | 2.83 | 0 | 26 | 30 | 12 | 117.5757 | 0
2024-02-09 21:00 | 17.6 | 69 | 2.12 | 0 | 26 | 30 | 12 | 102.6442 | 0
2024-02-09 22:00 | 16.6 | 75 | 2 | 0 | 26 | 30 | 12 | 101.4919 | 0
2024-02-09 23:00 | 16 | 78 | 2.22 | 0 | 26 | 30 | 12 | 109.2164 | 0
2024-02-10 | 15.6 | 80 | 2.55 | 0 | 26 | 30 | 12 | 119.2837 | 0
2024-02-10 01:00 | 15.1 | 83 | 2.57 | 0 | 26 | 30 | 12 | 121.1905 | 0
2024-02-10 02:00 | 14.6 | 84 | 2.91 | 0 | 26 | 30 | 12 | 132.9913 | 0
2024-02-10 03:00 | 13.8 | 87 | 3.1 | 0 | 26 | 30 | 12 | 141.8205 | 0
2024-02-10 04:00 | 13 | 92 | 3.03 | 0 | 26 | 30 | 12 | 142.5393 | 0
2024-02-10 05:00 | 12.9 | 92 | 2.77 | 0 | 26 | 30 | 12 | 136.0838 | 0
2024-02-10 06:00 | 12.4 | 94 | 2.94 | 0 | 26 | 30 | 12 | 143.166 | 0
2024-02-10 07:00 | 12 | 94 | 2.94 | 0 | 26 | 30 | 12 | 146.0117 | 0
2024-02-10 08:00 | 13.2 | 88 | 2.66 | 62 | 26 | 30 | 12 | 124.9501 | 0
2024-02-10 09:00 | 16.6 | 73 | 2.38 | 252 | 26 | 30 | 12 | 78.9799 | 0
2024-02-10 10:00 | 19.4 | 62 | 2.06 | 461 | 26 | 30 | 12 | 33.109 | 0
2024-02-10 11:00 | 20.7 | 56 | 0.51 | 638 | 26 | 30 | 12 | 0 | 15.8639
2024-02-10 12:00 | 21.8 | 49 | 0.63 | 754 | 26 | 30 | 12 | 0 | 30.6504
2024-02-10 13:00 | 22.8 | 44 | 1.57 | 794 | 26 | 30 | 12 | 0 | 0
2024-02-10 14:00 | 23.2 | 44 | 2.7 | 763 | 26 | 30 | 12 | 0.8174 | 0
2024-02-10 15:00 | 22.8 | 49 | 3.89 | 655 | 26 | 30 | 12 | 37.7002 | 0
2024-02-10 16:00 | 22 | 51 | 4.19 | 486 | 26 | 30 | 12 | 70.6137 | 0
2024-02-10 17:00 | 21.7 | 51 | 3.74 | 280 | 26 | 30 | 12 | 91.5493 | 0
2024-02-10 18:00 | 20.6 | 58 | 3.68 | 80 | 26 | 30 | 12 | 117.6073 | 0
2024-02-10 19:00 | 19.8 | 61 | 2.47 | 0 | 26 | 30 | 12 | 103.8578 | 0
2024-02-10 20:00 | 18.9 | 66 | 1.9 | 0 | 26 | 30 | 12 | 91.2966 | 0
2024-02-10 21:00 | 17.8 | 72 | 1.66 | 0 | 26 | 30 | 12 | 87.2825 | 0
2024-02-10 22:00 | 17 | 76 | 1.92 | 0 | 26 | 30 | 12 | 96.4053 | 0
2024-02-10 23:00 | 16.6 | 76 | 2.34 | 0 | 26 | 30 | 12 | 109.9171 | 0
2024-02-11 | 15.8 | 80 | 1.98 | 0 | 26 | 30 | 12 | 102.6832 | 0
2024-02-11 01:00 | 15.4 | 83 | 2.05 | 0 | 26 | 30 | 12 | 105.2699 | 0
2024-02-11 02:00 | 16.3 | 81 | 2.69 | 0 | 26 | 30 | 12 | 117.3277 | 0
2024-02-11 03:00 | 15.3 | 88 | 2.48 | 0 | 26 | 30 | 12 | 114.2451 | 0
2024-02-11 04:00 | 14.7 | 91 | 2.34 | 0 | 26 | 30 | 12 | 112.8064 | 0
2024-02-11 05:00 | 16.4 | 83 | 1.92 | 0 | 26 | 30 | 12 | 95.8097 | 0
2024-02-11 06:00 | 16.5 | 84 | 2.77 | 0 | 26 | 30 | 12 | 115.5919 | 0
2024-02-11 07:00 | 17.4 | 86 | 3.07 | 0 | 26 | 30 | 12 | 113.6847 | 0
2024-02-11 08:00 | 17.5 | 89 | 1.33 | 14 | 26 | 30 | 12 | 69.4497 | 0
2024-02-11 09:00 | 17.5 | 87 | 2.11 | 29 | 26 | 30 | 12 | 87.1335 | 0
2024-02-11 10:00 | 18.7 | 83 | 2.58 | 151 | 26 | 30 | 12 | 75.2542 | 0
2024-02-11 11:00 | 18.6 | 70 | 4.6 | 90 | 26 | 30 | 12 | 139.1244 | 0
2024-02-11 12:00 | 18.3 | 64 | 3.28 | 147 | 26 | 30 | 12 | 111.2984 | 0
2024-02-11 13:00 | 18.5 | 66 | 1.1 | 139 | 26 | 30 | 12 | 52.1116 | 0
2024-02-11 14:00 | 19.2 | 62 | 2.44 | 251 | 26 | 30 | 12 | 72.2791 | 0
2024-02-11 15:00 | 19.6 | 61 | 2.63 | 276 | 26 | 30 | 12 | 71.7751 | 0
2024-02-11 16:00 | 19.1 | 66 | 1.61 | 176 | 26 | 30 | 12 | 58.8003 | 0
2024-02-11 17:00 | 19.7 | 71 | 2.5 | 188 | 26 | 30 | 12 | 71.296 | 0
2024-02-11 18:00 | 18.8 | 77 | 2.96 | 67 | 26 | 30 | 12 | 98.9233 | 0
2024-02-11 19:00 | 17.8 | 82 | 3.41 | 0 | 26 | 30 | 12 | 121.0762 | 0
2024-02-11 20:00 | 17.2 | 84 | 4.39 | 0 | 26 | 30 | 12 | 144.8767 | 0
2024-02-11 21:00 | 16.8 | 87 | 4.53 | 0 | 26 | 30 | 12 | 148.5808 | 0
2024-02-11 22:00 | 16.6 | 87 | 3.89 | 0 | 26 | 30 | 12 | 137.2768 | 0
2024-02-11 23:00 | 16.6 | 87 | 4.08 | 0 | 26 | 30 | 12 | 141.2971 | 0
2024-02-12 | 17.2 | 90 | 4.22 | 0 | 26 | 30 | 12 | 135.0734 | 0
2024-02-12 01:00 | 17.8 | 92 | 4.55 | 0 | 26 | 30 | 12 | 132.5729 | 0
2024-02-12 02:00 | 18 | 91 | 4.39 | 0 | 26 | 30 | 12 | 128.661 | 0
2024-02-12 03:00 | 17.9 | 91 | 4.5 | 0 | 26 | 30 | 12 | 131.7234 | 0
2024-02-12 04:00 | 17.5 | 91 | 4.88 | 0 | 26 | 30 | 12 | 143.0945 | 0
2024-02-12 05:00 | 18.1 | 90 | 4.71 | 0 | 26 | 30 | 12 | 134.3781 | 0
2024-02-12 06:00 | 18.7 | 86 | 5.2 | 0 | 26 | 30 | 12 | 140.8734 | 0
2024-02-12 07:00 | 18.5 | 87 | 4.78 | 0 | 26 | 30 | 12 | 134.7176 | 0
2024-02-12 08:00 | 18.4 | 93 | 2.25 | 13 | 26 | 30 | 12 | 81.747 | 0
2024-02-12 09:00 | 18.6 | 91 | 2.92 | 15 | 26 | 30 | 12 | 94.1959 | 0
2024-02-12 10:00 | 18.8 | 90 | 4.34 | 22 | 26 | 30 | 12 | 117.197 | 0
2024-02-12 11:00 | 18.8 | 88 | 6.82 | 78 | 26 | 30 | 12 | 152.2294 | 0
2024-02-12 12:00 | 19.1 | 87 | 9.53 | 137 | 26 | 30 | 12 | 181.0903 | 0
2024-02-12 13:00 | 21.1 | 80 | 9.02 | 677 | 26 | 30 | 12 | 79.4571 | 0
2024-02-12 14:00 | 20.6 | 81 | 6.8 | 268 | 26 | 30 | 12 | 111.559 | 0
2024-02-12 15:00 | 21.1 | 77 | 7.74 | 330 | 26 | 30 | 12 | 116.1187 | 0
2024-02-12 16:00 | 19.7 | 84 | 8.15 | 422 | 26 | 30 | 12 | 118.4441 | 0
2024-02-12 17:00 | 20.5 | 82 | 5.07 | 153 | 26 | 30 | 12 | 101.8181 | 0
2024-02-12 18:00 | 19 | 87 | 4.19 | 19 | 26 | 30 | 12 | 116.4413 | 0
2024-02-12 19:00 | 17.6 | 93 | 1.9 | 0 | 26 | 30 | 12 | 81.846 | 0
2024-02-12 20:00 | 17.6 | 92 | 2.08 | 0 | 26 | 30 | 12 | 86.3997 | 0
2024-02-12 21:00 | 17.1 | 93 | 2.95 | 0 | 26 | 30 | 12 | 107.8028 | 0
2024-02-12 22:00 | 17.5 | 91 | 4.2 | 0 | 26 | 30 | 12 | 130.5193 | 0
2024-02-12 23:00 | 16.8 | 94 | 1.14 | 0 | 26 | 30 | 12 | 67.8245 | 0
2024-02-13 | 17.6 | 90 | 0.54 | 0 | 26 | 30 | 12 | 50.4244 | 0
2024-02-13 01:00 | 16.4 | 95 | 2.41 | 0 | 26 | 30 | 12 | 100.1534 | 0
2024-02-13 02:00 | 16.7 | 92 | 3.85 | 0 | 26 | 30 | 12 | 130.6956 | 0
2024-02-13 03:00 | 17 | 90 | 5.46 | 0 | 26 | 30 | 12 | 160.9242 | 0
2024-02-13 04:00 | 17.2 | 89 | 4.05 | 0 | 26 | 30 | 12 | 132.7789 | 0
2024-02-13 05:00 | 17.6 | 91 | 3.31 | 0 | 26 | 30 | 12 | 112.4538 | 0
2024-02-13 06:00 | 17.9 | 90 | 3.88 | 0 | 26 | 30 | 12 | 121.4992 | 0
2024-02-13 07:00 | 17.8 | 89 | 3.59 | 0 | 26 | 30 | 12 | 117.9673 | 0
2024-02-13 08:00 | 18.4 | 88 | 3 | 60 | 26 | 30 | 12 | 94.026 | 0
2024-02-13 09:00 | 19.8 | 82 | 5.15 | 241 | 26 | 30 | 12 | 99.7253 | 0
2024-02-13 10:00 | 21 | 79 | 5.79 | 448 | 26 | 30 | 12 | 70.812 | 0
2024-02-13 11:00 | 22.5 | 72 | 6.79 | 612 | 26 | 30 | 12 | 54.0583 | 0
2024-02-13 12:00 | 23.5 | 68 | 6.91 | 690 | 26 | 30 | 12 | 38.6099 | 0
2024-02-13 13:00 | 24 | 66 | 7.08 | 742 | 26 | 30 | 12 | 30.5844 | 0
2024-02-13 14:00 | 24.2 | 66 | 7.08 | 716 | 26 | 30 | 12 | 31.0402 | 0
2024-02-13 15:00 | 24.3 | 66 | 6.96 | 602 | 26 | 30 | 12 | 43.5279 | 0
2024-02-13 16:00 | 23.9 | 66 | 6.46 | 451 | 26 | 30 | 12 | 63.8759 | 0
2024-02-13 17:00 | 23 | 74 | 3.61 | 238 | 26 | 30 | 12 | 52.8022 | 0
2024-02-13 18:00 | 21.6 | 81 | 3.19 | 79 | 26 | 30 | 12 | 73.1614 | 0
2024-02-13 19:00 | 20.4 | 85 | 3.16 | 1 | 26 | 30 | 12 | 90.0111 | 0
2024-02-13 20:00 | 19.7 | 87 | 3.67 | 0 | 26 | 30 | 12 | 103.0342 | 0
2024-02-13 21:00 | 19.2 | 88 | 4.04 | 0 | 26 | 30 | 12 | 113.1765 | 0
2024-02-13 22:00 | 18.7 | 90 | 3.65 | 0 | 26 | 30 | 12 | 109.3943 | 0
2024-02-13 23:00 | 18.4 | 92 | 3.41 | 0 | 26 | 30 | 12 | 106.005 | 0
2024-02-14 | 18.2 | 92 | 3.31 | 0 | 26 | 30 | 12 | 106.0568 | 0
2024-02-14 01:00 | 17.9 | 93 | 3.11 | 0 | 26 | 30 | 12 | 104.1056 | 0
2024-02-14 02:00 | 17.9 | 92 | 3.35 | 0 | 26 | 30 | 12 | 109.5695 | 0
2024-02-14 03:00 | 17.9 | 93 | 3.42 | 0 | 26 | 30 | 12 | 109.9367 | 0
2024-02-14 04:00 | 17.8 | 94 | 3.61 | 0 | 26 | 30 | 12 | 113.439 | 0
2024-02-14 05:00 | 18.7 | 93 | 4.27 | 0 | 26 | 30 | 12 | 116.5779 | 0
2024-02-14 06:00 | 18.5 | 93 | 3.93 | 0 | 26 | 30 | 12 | 113.0613 | 0
2024-02-14 07:00 | 18.3 | 94 | 3.45 | 0 | 26 | 30 | 12 | 105.7095 | 0
2024-02-14 08:00 | 19.2 | 91 | 3.1 | 66 | 26 | 30 | 12 | 85.1955 | 0
2024-02-14 09:00 | 21.4 | 83 | 4.96 | 251 | 26 | 30 | 12 | 74.3308 | 0
2024-02-14 10:00 | 23 | 79 | 5.18 | 452 | 26 | 30 | 12 | 35.7663 | 0
2024-02-14 11:00 | 24.4 | 73 | 5.76 | 621 | 26 | 30 | 12 | 11.2536 | 0
2024-02-14 12:00 | 25.3 | 67 | 5.55 | 732 | 26 | 30 | 12 | 0 | 0
2024-02-14 13:00 | 25.7 | 65 | 4.54 | 711 | 26 | 30 | 12 | 0 | 0
2024-02-14 14:00 | 25.2 | 66 | 5.08 | 671 | 26 | 30 | 12 | 0.6278 | 0
2024-02-14 15:00 | 25 | 69 | 4.62 | 525 | 26 | 30 | 12 | 12.1305 | 0
2024-02-14 16:00 | 24.3 | 71 | 4.6 | 379 | 26 | 30 | 12 | 36.5071 | 0
2024-02-14 17:00 | 24 | 73 | 4.49 | 227 | 26 | 30 | 12 | 55.9334 | 0
2024-02-14 18:00 | 22.1 | 82 | 4.43 | 77 | 26 | 30 | 12 | 83.8719 | 0
2024-02-14 19:00 | 21.4 | 86 | 4.54 | 1 | 26 | 30 | 12 | 98.0991 | 0
2024-02-14 20:00 | 20.9 | 88 | 4.8 | 0 | 26 | 30 | 12 | 104.906 | 0
2024-02-14 21:00 | 20.2 | 90 | 4.72 | 0 | 26 | 30 | 12 | 109.6773 | 0
2024-02-14 22:00 | 19.9 | 91 | 4.88 | 0 | 26 | 30 | 12 | 114.2818 | 0
2024-02-14 23:00 | 19.8 | 92 | 4.83 | 0 | 26 | 30 | 12 | 113.4429 | 0
2024-02-15 | 19.6 | 92 | 4.75 | 0 | 26 | 30 | 12 | 114.7572 | 0
2024-02-15 01:00 | 19.4 | 92 | 4.46 | 0 | 26 | 30 | 12 | 112.8153 | 0
2024-02-15 02:00 | 19 | 92 | 3.8 | 0 | 26 | 30 | 12 | 106.7675 | 0
2024-02-15 03:00 | 18.5 | 92 | 3.31 | 0 | 26 | 30 | 12 | 103.2723 | 0
2024-02-15 04:00 | 17.9 | 93 | 2.94 | 0 | 26 | 30 | 12 | 100.8529 | 0
2024-02-15 05:00 | 18.4 | 93 | 2.66 | 0 | 26 | 30 | 12 | 91.3462 | 0
2024-02-15 06:00 | 18.1 | 92 | 2.88 | 0 | 26 | 30 | 12 | 98.8567 | 0
2024-02-15 07:00 | 17.7 | 89 | 3.04 | 0 | 26 | 30 | 12 | 107.9743 | 0
2024-02-15 08:00 | 19 | 81 | 3.02 | 69 | 26 | 30 | 12 | 94.5586 | 0
2024-02-15 09:00 | 21.4 | 75 | 2.61 | 259 | 26 | 30 | 12 | 47.5139 | 0
2024-02-15 10:00 | 23.7 | 74 | 2.97 | 465 | 26 | 30 | 12 | 6.7999 | 0
2024-02-15 11:00 | 25.6 | 70 | 4.22 | 635 | 26 | 30 | 12 | 0 | 0
2024-02-15 12:00 | 26.7 | 64 | 4.66 | 745 | 26 | 30 | 12 | 0 | 0
2024-02-15 13:00 | 27.4 | 57 | 4.08 | 785 | 26 | 30 | 12 | 0 | 0
2024-02-15 14:00 | 27.9 | 52 | 3.03 | 742 | 26 | 30 | 12 | 0 | 0
2024-02-15 15:00 | 27.9 | 50 | 1.9 | 642 | 26 | 30 | 12 | 0 | 0
2024-02-15 16:00 | 27.6 | 50 | 0.81 | 480 | 26 | 30 | 12 | 0 | 8.1355
2024-02-15 17:00 | 25.9 | 73 | 2.86 | 276 | 26 | 30 | 12 | 11.8358 | 0
2024-02-15 18:00 | 23.1 | 88 | 4.2 | 82 | 26 | 30 | 12 | 59.4916 | 0
2024-02-15 19:00 | 21.9 | 87 | 3.83 | 1 | 26 | 30 | 12 | 81.9321 | 0
2024-02-15 20:00 | 21.5 | 89 | 4.03 | 0 | 26 | 30 | 12 | 86.4127 | 0
2024-02-15 21:00 | 21.1 | 90 | 3.7 | 0 | 26 | 30 | 12 | 85.3694 | 0
2024-02-15 22:00 | 20.6 | 91 | 3.71 | 0 | 26 | 30 | 12 | 89.6791 | 0
2024-02-15 23:00 | 20.3 | 92 | 4.1 | 0 | 26 | 30 | 12 | 97.1919 | 0
2024-02-16 | 20 | 93 | 4.47 | 0 | 26 | 30 | 12 | 104.5747 | 0
2024-02-16 01:00 | 19.9 | 93 | 4.49 | 0 | 26 | 30 | 12 | 106.0564 | 0
2024-02-16 02:00 | 19.6 | 92 | 4.33 | 0 | 26 | 30 | 12 | 108.5345 | 0
2024-02-16 03:00 | 19.3 | 92 | 4.49 | 0 | 26 | 30 | 12 | 114.4411 | 0
2024-02-16 04:00 | 19 | 92 | 4.27 | 0 | 26 | 30 | 12 | 114.412 | 0
2024-02-16 05:00 | 19.8 | 92 | 3.94 | 0 | 26 | 30 | 12 | 100.4597 | 0
2024-02-16 06:00 | 19.7 | 92 | 3.94 | 0 | 26 | 30 | 12 | 101.5487 | 0
2024-02-16 07:00 | 19.4 | 90 | 3.88 | 0 | 26 | 30 | 12 | 106.138 | 0
2024-02-16 08:00 | 20.5 | 83 | 3.61 | 67 | 26 | 30 | 12 | 89.5974 | 0
2024-02-16 09:00 | 22.2 | 77 | 3.32 | 257 | 26 | 30 | 12 | 50.0967 | 0
2024-02-16 10:00 | 24.1 | 72 | 4.95 | 459 | 26 | 30 | 12 | 30.391 | 0
2024-02-16 11:00 | 25.5 | 71 | 5.77 | 629 | 26 | 30 | 12 | 0 | 0
2024-02-16 12:00 | 26.8 | 66 | 6.01 | 741 | 26 | 30 | 12 | 0 | 0
2024-02-16 13:00 | 27.6 | 62 | 5.81 | 783 | 26 | 30 | 12 | 0 | 0
2024-02-16 14:00 | 28.2 | 58 | 4.74 | 750 | 26 | 30 | 12 | 0 | 0
2024-02-16 15:00 | 28.5 | 56 | 3.77 | 644 | 26 | 30 | 12 | 0 | 0
2024-02-16 16:00 | 28.4 | 56 | 2.21 | 478 | 26 | 30 | 12 | 0 | 0
2024-02-16 17:00 | 25.7 | 79 | 3.67 | 276 | 26 | 30 | 12 | 11.6431 | 0
2024-02-16 18:00 | 23.5 | 86 | 3.2 | 84 | 26 | 30 | 12 | 47.7414 | 0
2024-02-16 19:00 | 22.5 | 89 | 2.41 | 1 | 26 | 30 | 12 | 56.4685 | 0
2024-02-16 20:00 | 22.1 | 90 | 3.2 | 0 | 26 | 30 | 12 | 68.6165 | 0
2024-02-16 21:00 | 21.9 | 88 | 3.71 | 0 | 26 | 30 | 12 | 79.2926 | 0
2024-02-16 22:00 | 21.6 | 88 | 3.83 | 0 | 26 | 30 | 12 | 84.0933 | 0
2024-02-16 23:00 | 21.4 | 88 | 3.91 | 0 | 26 | 30 | 12 | 87.3428 | 0
2024-02-17 | 21.3 | 88 | 3.81 | 0 | 26 | 30 | 12 | 87.1417 | 0
2024-02-17 01:00 | 21.1 | 88 | 3.83 | 0 | 26 | 30 | 12 | 89.5944 | 0
2024-02-17 02:00 | 20.7 | 88 | 3.74 | 0 | 26 | 30 | 12 | 92.6375 | 0
2024-02-17 03:00 | 20.4 | 89 | 3.77 | 0 | 26 | 30 | 12 | 95.0534 | 0
2024-02-17 04:00 | 20.1 | 90 | 3.67 | 0 | 26 | 30 | 12 | 95.5474 | 0
2024-02-17 05:00 | 21.2 | 88 | 3.72 | 0 | 26 | 30 | 12 | 87.0261 | 0
2024-02-17 06:00 | 20.9 | 89 | 3.82 | 0 | 26 | 30 | 12 | 90.3884 | 0
2024-02-17 07:00 | 20.8 | 86 | 5 | 0 | 26 | 30 | 12 | 111.799 | 0
2024-02-17 08:00 | 21.5 | 74 | 6.51 | 70 | 26 | 30 | 12 | 134.0288 | 0
2024-02-17 09:00 | 22.5 | 69 | 5.95 | 259 | 26 | 30 | 12 | 96.2965 | 0
2024-02-17 10:00 | 23.9 | 63 | 6.81 | 463 | 26 | 30 | 12 | 73.213 | 0
2024-02-17 11:00 | 25.2 | 59 | 7.2 | 630 | 26 | 30 | 12 | 45.8226 | 0
2024-02-17 12:00 | 26.3 | 57 | 7.03 | 741 | 26 | 30 | 12 | 17.6256 | 0
2024-02-17 13:00 | 27.2 | 55 | 6.65 | 782 | 26 | 30 | 12 | 0.2246 | 0
2024-02-17 14:00 | 27.8 | 54 | 6.18 | 748 | 26 | 30 | 12 | 0 | 0
2024-02-17 15:00 | 28.1 | 53 | 5.51 | 645 | 26 | 30 | 12 | 0.2504 | 0
2024-02-17 16:00 | 28 | 55 | 4.74 | 483 | 26 | 30 | 12 | 11.0908 | 0
2024-02-17 17:00 | 27.4 | 57 | 2.97 | 284 | 26 | 30 | 12 | 21.3284 | 0
2024-02-17 18:00 | 24.9 | 71 | 2.69 | 88 | 26 | 30 | 12 | 47.1263 | 0
2024-02-17 19:00 | 23.2 | 77 | 2.69 | 1 | 26 | 30 | 12 | 66.6148 | 0
2024-02-17 20:00 | 22.3 | 79 | 3.01 | 0 | 26 | 30 | 12 | 76.9847 | 0
2024-02-17 21:00 | 21.1 | 82 | 3.14 | 0 | 26 | 30 | 12 | 86.5944 | 0
2024-02-17 22:00 | 20.5 | 83 | 3.29 | 0 | 26 | 30 | 12 | 93.4746 | 0
2024-02-17 23:00 | 20.1 | 82 | 3.72 | 0 | 26 | 30 | 12 | 105.5708 | 0
2024-02-18 | 19.9 | 79 | 3.98 | 0 | 26 | 30 | 12 | 115.5573 | 0
2024-02-18 01:00 | 19.7 | 77 | 4.1 | 0 | 26 | 30 | 12 | 122.1088 | 0
2024-02-18 02:00 | 19.5 | 77 | 4.23 | 0 | 26 | 30 | 12 | 126.4902 | 0
2024-02-18 03:00 | 19.3 | 76 | 3.91 | 0 | 26 | 30 | 12 | 123.6616 | 0
2024-02-18 04:00 | 18.9 | 77 | 3.89 | 0 | 26 | 30 | 12 | 125.9436 | 0
2024-02-18 05:00 | 19.7 | 75 | 3.67 | 0 | 26 | 30 | 12 | 116.4725 | 0
2024-02-18 06:00 | 19.1 | 80 | 3.93 | 0 | 26 | 30 | 12 | 121.4225 | 0
2024-02-18 07:00 | 19 | 84 | 3.75 | 0 | 26 | 30 | 12 | 114.6495 | 0
2024-02-18 08:00 | 20.3 | 84 | 3.38 | 73 | 26 | 30 | 12 | 85.8851 | 0
2024-02-18 09:00 | 22.8 | 87 | 3.2 | 262 | 26 | 30 | 12 | 29.6944 | 0
2024-02-18 10:00 | 24.1 | 77 | 6.81 | 459 | 26 | 30 | 12 | 39.2586 | 0
2024-02-18 11:00 | 24.3 | 66 | 8.05 | 631 | 26 | 30 | 12 | 51.8158 | 0
2024-02-18 12:00 | 24.6 | 53 | 8.86 | 753 | 26 | 30 | 12 | 75.0598 | 0
2024-02-18 13:00 | 24.3 | 52 | 9.05 | 801 | 26 | 30 | 12 | 78.7093 | 0
2024-02-18 14:00 | 23.7 | 51 | 8.95 | 772 | 26 | 30 | 12 | 93.3286 | 0
2024-02-18 15:00 | 23 | 50 | 8.53 | 668 | 26 | 30 | 12 | 113.9377 | 0
2024-02-18 16:00 | 22.5 | 49 | 8.43 | 501 | 26 | 30 | 12 | 144.36 | 0
2024-02-18 17:00 | 22 | 50 | 8.12 | 292 | 26 | 30 | 12 | 171.8408 | 0
2024-02-18 18:00 | 20.8 | 56 | 6.7 | 92 | 26 | 30 | 12 | 176.6146 | 0
2024-02-18 19:00 | 19.9 | 61 | 6.7 | 1 | 26 | 30 | 12 | 191.0035 | 0
2024-02-18 20:00 | 19.6 | 64 | 6.9 | 0 | 26 | 30 | 12 | 193.4277 | 0
2024-02-18 21:00 | 19.3 | 67 | 7.02 | 0 | 26 | 30 | 12 | 194.3377 | 0
2024-02-18 22:00 | 18.9 | 69 | 7.2 | 0 | 26 | 30 | 12 | 199.5095 | 0
2024-02-18 23:00 | 18.7 | 71 | 7.4 | 0 | 26 | 30 | 12 | 202.4482 | 0
2024-02-19 | 18.5 | 71 | 7.5 | 0 | 26 | 30 | 12 | 207.0376 | 0
2024-02-19 01:00 | 18.5 | 70 | 7.3 | 0 | 26 | 30 | 12 | 205.0427 | 0
2024-02-19 02:00 | 18.3 | 70 | 7.4 | 0 | 26 | 30 | 12 | 209.6155 | 0
2024-02-19 03:00 | 18.2 | 71 | 7.2 | 0 | 26 | 30 | 12 | 205.5348 | 0
2024-02-19 04:00 | 18 | 71 | 6.91 | 0 | 26 | 30 | 12 | 202.6156 | 0
2024-02-19 05:00 | 18.3 | 73 | 6.51 | 0 | 26 | 30 | 12 | 188.0426 | 0
2024-02-19 06:00 | 18.1 | 75 | 6.02 | 0 | 26 | 30 | 12 | 178.2438 | 0
2024-02-19 07:00 | 18.1 | 75 | 5.92 | 0 | 26 | 30 | 12 | 176.3257 | 0
2024-02-19 08:00 | 19.1 | 73 | 5.26 | 80 | 26 | 30 | 12 | 144.2207 | 0
2024-02-19 09:00 | 20.7 | 65 | 6.32 | 272 | 26 | 30 | 12 | 130.7065 | 0
2024-02-19 10:00 | 21.6 | 62 | 6.81 | 481 | 26 | 30 | 12 | 104.5845 | 0
2024-02-19 11:00 | 22.2 | 60 | 7.62 | 662 | 26 | 30 | 12 | 88.7879 | 0
2024-02-19 12:00 | 22.6 | 58 | 7.83 | 779 | 26 | 30 | 12 | 74.8823 | 0
2024-02-19 13:00 | 22.8 | 56 | 8.03 | 826 | 26 | 30 | 12 | 73.2798 | 0
2024-02-19 14:00 | 22.8 | 56 | 8.05 | 793 | 26 | 30 | 12 | 78.0385 | 0
2024-02-19 15:00 | 22.6 | 55 | 7.98 | 686 | 26 | 30 | 12 | 96.6171 | 0
2024-02-19 16:00 | 22.2 | 57 | 7.67 | 516 | 26 | 30 | 12 | 115.8292 | 0
2024-02-19 17:00 | 21.5 | 62 | 6.97 | 304 | 26 | 30 | 12 | 132.4111 | 0
2024-02-19 18:00 | 20.5 | 67 | 6.23 | 97 | 26 | 30 | 12 | 151.8531 | 0
2024-02-19 19:00 | 19.8 | 70 | 5.52 | 2 | 26 | 30 | 12 | 155.8596 | 0
2024-02-19 20:00 | 19.3 | 71 | 4.82 | 0 | 26 | 30 | 12 | 147.2343 | 0
2024-02-19 21:00 | 18.6 | 74 | 4.1 | 0 | 26 | 30 | 12 | 136.333 | 0
2024-02-19 22:00 | 18 | 78 | 3.72 | 0 | 26 | 30 | 12 | 129.7252 | 0
2024-02-19 23:00 | 17.5 | 81 | 3.61 | 0 | 26 | 30 | 12 | 128.8868 | 0
2024-02-20 | 16.9 | 84 | 3.4 | 0 | 26 | 30 | 12 | 126.7738 | 0
2024-02-20 01:00 | 16.5 | 87 | 3.61 | 0 | 26 | 30 | 12 | 132.1645 | 0
2024-02-20 02:00 | 16 | 88 | 3.94 | 0 | 26 | 30 | 12 | 143.0252 | 0
2024-02-20 03:00 | 15.7 | 88 | 4.08 | 0 | 26 | 30 | 12 | 148.9372 | 0
2024-02-20 04:00 | 15.6 | 89 | 3.91 | 0 | 26 | 30 | 12 | 145.1516 | 0
2024-02-20 05:00 | 15.6 | 89 | 3.92 | 0 | 26 | 30 | 12 | 145.376 | 0
2024-02-20 06:00 | 15.4 | 90 | 3.88 | 0 | 26 | 30 | 12 | 145.4193 | 0
2024-02-20 07:00 | 15.1 | 91 | 3.73 | 0 | 26 | 30 | 12 | 143.8344 | 0
2024-02-20 08:00 | 16.2 | 88 | 3.51 | 80 | 26 | 30 | 12 | 120.9228 | 0
2024-02-20 09:00 | 18.9 | 79 | 3.4 | 276 | 26 | 30 | 12 | 76.9258 | 0
2024-02-20 10:00 | 21.4 | 70 | 3.78 | 482 | 26 | 30 | 12 | 43.4372 | 0
2024-02-20 11:00 | 23 | 62 | 5.11 | 651 | 26 | 30 | 12 | 37.4864 | 0
2024-02-20 12:00 | 23.6 | 59 | 5.45 | 766 | 26 | 30 | 12 | 25.5875 | 0
2024-02-20 13:00 | 24 | 55 | 5.75 | 809 | 26 | 30 | 12 | 27.3126 | 0
2024-02-20 14:00 | 24.1 | 55 | 6.29 | 773 | 26 | 30 | 12 | 39.0017 | 0
2024-02-20 15:00 | 24 | 54 | 6.48 | 663 | 26 | 30 | 12 | 60.0854 | 0
2024-02-20 16:00 | 23.7 | 53 | 6.2 | 503 | 26 | 30 | 12 | 83.2427 | 0
2024-02-20 17:00 | 22.8 | 58 | 5.31 | 297 | 26 | 30 | 12 | 97.6897 | 0
2024-02-20 18:00 | 21.5 | 67 | 4.31 | 94 | 26 | 30 | 12 | 107.9815 | 0
2024-02-20 19:00 | 20.5 | 74 | 4.08 | 2 | 26 | 30 | 12 | 117.1744 | 0
2024-02-20 20:00 | 20 | 78 | 4 | 0 | 26 | 30 | 12 | 116.108 | 0
2024-02-20 21:00 | 19.5 | 82 | 3.81 | 0 | 26 | 30 | 12 | 113.0504 | 0
2024-02-20 22:00 | 19 | 84 | 3.76 | 0 | 26 | 30 | 12 | 114.831 | 0
2024-02-20 23:00 | 18.8 | 84 | 4.05 | 0 | 26 | 30 | 12 | 122.086 | 0
2024-02-21 | 18.7 | 83 | 4.36 | 0 | 26 | 30 | 12 | 129.9191 | 0
2024-02-21 01:00 | 18.8 | 82 | 4.7 | 0 | 26 | 30 | 12 | 136.2057 | 0
2024-02-21 02:00 | 18.8 | 82 | 5.02 | 0 | 26 | 30 | 12 | 141.8999 | 0
2024-02-21 03:00 | 18.8 | 80 | 5.35 | 0 | 26 | 30 | 12 | 150.443 | 0
2024-02-21 04:00 | 18.8 | 81 | 5.94 | 0 | 26 | 30 | 12 | 159.3178 | 0
2024-02-21 05:00 | 19.1 | 80 | 6.05 | 0 | 26 | 30 | 12 | 158.8181 | 0
2024-02-21 06:00 | 18.9 | 81 | 6 | 0 | 26 | 30 | 12 | 159.0537 | 0
2024-02-21 07:00 | 18.6 | 76 | 5.66 | 1 | 26 | 30 | 12 | 163.9016 | 0
2024-02-21 08:00 | 19.6 | 70 | 5.51 | 84 | 26 | 30 | 12 | 146.9181 | 0
2024-02-21 09:00 | 21.2 | 62 | 6.94 | 288 | 26 | 30 | 12 | 138.0757 | 0
2024-02-21 10:00 | 22.1 | 58 | 7.55 | 501 | 26 | 30 | 12 | 115.1676 | 0
2024-02-21 11:00 | 22.9 | 53 | 8.02 | 675 | 26 | 30 | 12 | 99.1203 | 0
2024-02-21 12:00 | 23.4 | 51 | 7.98 | 788 | 26 | 30 | 12 | 80.9606 | 0
2024-02-21 13:00 | 23.6 | 50 | 7.98 | 829 | 26 | 30 | 12 | 75.057 | 0
2024-02-21 14:00 | 23.6 | 50 | 7.98 | 793 | 26 | 30 | 12 | 79.917 | 0
2024-02-21 15:00 | 23.4 | 51 | 8.1 | 686 | 26 | 30 | 12 | 96.5868 | 0
2024-02-21 16:00 | 23.1 | 50 | 8.09 | 517 | 26 | 30 | 12 | 125.8813 | 0
2024-02-21 17:00 | 22.7 | 52 | 7.43 | 308 | 26 | 30 | 12 | 144.2025 | 0
2024-02-21 18:00 | 21.6 | 58 | 6.95 | 100 | 26 | 30 | 12 | 166.159 | 0
2024-02-21 19:00 | 20.7 | 64 | 5.66 | 2 | 26 | 30 | 12 | 157.2883 | 0
2024-02-21 20:00 | 20.1 | 69 | 4.65 | 0 | 26 | 30 | 12 | 138.3572 | 0
2024-02-21 21:00 | 19.8 | 72 | 4.54 | 0 | 26 | 30 | 12 | 135.432 | 0
2024-02-21 22:00 | 19.5 | 74 | 4.18 | 0 | 26 | 30 | 12 | 129.2105 | 0
2024-02-21 23:00 | 18.9 | 77 | 3.57 | 0 | 26 | 30 | 12 | 119.6196 | 0
2024-02-22 | 18 | 83 | 3 | 0 | 26 | 30 | 12 | 109.8838 | 0
2024-02-22 01:00 | 17.4 | 87 | 2.86 | 0 | 26 | 30 | 12 | 108.3587 | 0
2024-02-22 02:00 | 17 | 89 | 2.88 | 0 | 26 | 30 | 12 | 110.3646 | 0
2024-02-22 03:00 | 16.7 | 92 | 2.82 | 0 | 26 | 30 | 12 | 109.097 | 0
2024-02-22 04:00 | 16.1 | 92 | 2.5 | 0 | 26 | 30 | 12 | 106.4388 | 0
2024-02-22 05:00 | 16.2 | 91 | 2.98 | 0 | 26 | 30 | 12 | 117.4065 | 0
2024-02-22 06:00 | 16.2 | 91 | 2.95 | 0 | 26 | 30 | 12 | 116.7309 | 0
2024-02-22 07:00 | 15.9 | 91 | 2.73 | 1 | 26 | 30 | 12 | 113.8668 | 0
2024-02-22 08:00 | 18.1 | 82 | 2.25 | 83 | 26 | 30 | 12 | 82.4216 | 0
2024-02-22 09:00 | 20.7 | 69 | 1.49 | 285 | 26 | 30 | 12 | 30.6644 | 0
2024-02-22 10:00 | 22.6 | 58 | 1.63 | 498 | 26 | 30 | 12 | 2.4216 | 0
2024-02-22 11:00 | 23.5 | 54 | 2.45 | 673 | 26 | 30 | 12 | 0 | 0
2024-02-22 12:00 | 24.1 | 52 | 3.08 | 788 | 26 | 30 | 12 | 0 | 0
2024-02-22 13:00 | 24.4 | 50 | 3.88 | 830 | 26 | 30 | 12 | 0 | 0
2024-02-22 14:00 | 24.3 | 48 | 4.36 | 797 | 26 | 30 | 12 | 15.7692 | 0
2024-02-22 15:00 | 24.1 | 48 | 4.84 | 692 | 26 | 30 | 12 | 40.3556 | 0
2024-02-22 16:00 | 23.3 | 51 | 5.16 | 525 | 26 | 30 | 12 | 71.3055 | 0
2024-02-22 17:00 | 22.5 | 58 | 5.52 | 310 | 26 | 30 | 12 | 102.8047 | 0
2024-02-22 18:00 | 21.4 | 64 | 5.41 | 102 | 26 | 30 | 12 | 131.3797 | 0
2024-02-22 19:00 | 20.7 | 65 | 4.6 | 2 | 26 | 30 | 12 | 136.5074 | 0
2024-02-22 20:00 | 20.1 | 67 | 4.14 | 0 | 26 | 30 | 12 | 131.2577 | 0
2024-02-22 21:00 | 19.2 | 72 | 3.32 | 0 | 26 | 30 | 12 | 117.0686 | 0
2024-02-22 22:00 | 18 | 79 | 2.53 | 0 | 26 | 30 | 12 | 102.9104 | 0
2024-02-22 23:00 | 17.1 | 84 | 1.93 | 0 | 26 | 30 | 12 | 91.235 | 0
2024-02-23 | 16.4 | 87 | 2.22 | 0 | 26 | 30 | 12 | 100.9672 | 0
2024-02-23 01:00 | 16 | 87 | 2.86 | 0 | 26 | 30 | 12 | 119.2365 | 0
2024-02-23 02:00 | 15 | 90 | 3.3 | 0 | 26 | 30 | 12 | 135.3604 | 0
2024-02-23 03:00 | 14 | 94 | 3.6 | 0 | 26 | 30 | 12 | 147.9208 | 0
2024-02-23 04:00 | 13.7 | 95 | 3.5 | 0 | 26 | 30 | 12 | 147.2318 | 0
2024-02-23 05:00 | 14.1 | 95 | 2.9 | 0 | 26 | 30 | 12 | 128.9688 | 0
2024-02-23 06:00 | 13.7 | 96 | 2.79 | 0 | 26 | 30 | 12 | 128.4674 | 0
2024-02-23 07:00 | 13.5 | 95 | 2.98 | 1 | 26 | 30 | 12 | 135.4141 | 0
2024-02-23 08:00 | 15.4 | 86 | 2.93 | 86 | 26 | 30 | 12 | 114.5925 | 0
2024-02-23 09:00 | 18.6 | 73 | 3.03 | 286 | 26 | 30 | 12 | 76.0901 | 0
2024-02-23 10:00 | 20.9 | 68 | 2.92 | 497 | 26 | 30 | 12 | 32.1647 | 0
2024-02-23 11:00 | 22.4 | 64 | 2.05 | 671 | 26 | 30 | 12 | 0 | 0
2024-02-23 12:00 | 23.9 | 57 | 2.6 | 785 | 26 | 30 | 12 | 0 | 0
2024-02-23 13:00 | 24.8 | 52 | 3.77 | 826 | 26 | 30 | 12 | 0 | 0
2024-02-23 14:00 | 25.1 | 51 | 4.1 | 791 | 26 | 30 | 12 | 0 | 0
2024-02-23 15:00 | 24.8 | 53 | 4.81 | 683 | 26 | 30 | 12 | 24.8559 | 0
2024-02-23 16:00 | 24.1 | 55 | 4.35 | 514 | 26 | 30 | 12 | 44.0957 | 0
2024-02-23 17:00 | 23.2 | 62 | 4.59 | 306 | 26 | 30 | 12 | 73.7994 | 0
2024-02-23 18:00 | 21.9 | 72 | 3.71 | 101 | 26 | 30 | 12 | 86.3297 | 0
2024-02-23 19:00 | 20.9 | 80 | 2.5 | 2 | 26 | 30 | 12 | 79.4618 | 0
2024-02-23 20:00 | 20 | 86 | 2.25 | 0 | 26 | 30 | 12 | 76.9951 | 0
2024-02-23 21:00 | 19.1 | 92 | 2.16 | 0 | 26 | 30 | 12 | 77.3594 | 0
2024-02-23 22:00 | 18.3 | 94 | 2.19 | 0 | 26 | 30 | 12 | 82.3403 | 0
2024-02-23 23:00 | 17.8 | 96 | 2.42 | 0 | 26 | 30 | 12 | 89.1527 | 0
2024-02-24 | 17.3 | 97 | 2.61 | 0 | 26 | 30 | 12 | 96.0988 | 0
2024-02-24 01:00 | 16.7 | 98 | 2.96 | 0 | 26 | 30 | 12 | 107.3366 | 0
2024-02-24 02:00 | 16.3 | 99 | 3.21 | 0 | 26 | 30 | 12 | 115.1085 | 0
2024-02-24 03:00 | 16 | 100 | 3.32 | 0 | 26 | 30 | 12 | 119.2316 | 0
2024-02-24 04:00 | 15.9 | 100 | 3.67 | 0 | 26 | 30 | 12 | 127.3621 | 0
2024-02-24 05:00 | 16.1 | 99 | 3.3 | 0 | 26 | 30 | 12 | 118.747 | 0
2024-02-24 06:00 | 15.6 | 99 | 3.2 | 0 | 26 | 30 | 12 | 121.0179 | 0
2024-02-24 07:00 | 15.5 | 99 | 3.1 | 1 | 26 | 30 | 12 | 119.5467 | 0
2024-02-24 08:00 | 16.2 | 99 | 3.2 | 60 | 26 | 30 | 12 | 107.6858 | 0
2024-02-24 09:00 | 17.8 | 93 | 3.41 | 190 | 26 | 30 | 12 | 85.036 | 0
2024-02-24 10:00 | 21.8 | 68 | 3.77 | 466 | 26 | 30 | 12 | 44.1919 | 0
2024-02-24 11:00 | 24.8 | 51 | 3.52 | 663 | 26 | 30 | 12 | 9.8962 | 0
2024-02-24 12:00 | 26.8 | 41 | 3.64 | 775 | 26 | 30 | 12 | 0 | 0
2024-02-24 13:00 | 28 | 34 | 4.23 | 816 | 26 | 30 | 12 | 3.7946 | 0
2024-02-24 14:00 | 28.1 | 33 | 4.37 | 782 | 26 | 30 | 12 | 12.0267 | 0
2024-02-24 15:00 | 27.7 | 33 | 4.54 | 676 | 26 | 30 | 12 | 32.7686 | 0
2024-02-24 16:00 | 26.8 | 39 | 5.06 | 509 | 26 | 30 | 12 | 59.7076 | 0
2024-02-24 17:00 | 25.6 | 49 | 4.52 | 302 | 26 | 30 | 12 | 70.9854 | 0
2024-02-24 18:00 | 24 | 57 | 3.63 | 100 | 26 | 30 | 12 | 85.9845 | 0
2024-02-24 19:00 | 22.6 | 64 | 3.31 | 3 | 26 | 30 | 12 | 96.5893 | 0
2024-02-24 20:00 | 21.6 | 68 | 2.78 | 0 | 26 | 30 | 12 | 91.0693 | 0
2024-02-24 21:00 | 20.6 | 72 | 2.5 | 0 | 26 | 30 | 12 | 89.3161 | 0
2024-02-24 22:00 | 19.7 | 77 | 2.27 | 0 | 26 | 30 | 12 | 86.7986 | 0
2024-02-24 23:00 | 19 | 80 | 2.42 | 0 | 26 | 30 | 12 | 92.5193 | 0
2024-02-25 | 18.1 | 85 | 2.26 | 0 | 26 | 30 | 12 | 91.6868 | 0
2024-02-25 01:00 | 18 | 86 | 2.72 | 0 | 26 | 30 | 12 | 101.4789 | 0
2024-02-25 02:00 | 17.6 | 86 | 2.63 | 0 | 26 | 30 | 12 | 102.6362 | 0
2024-02-25 03:00 | 17.3 | 84 | 2.73 | 0 | 26 | 30 | 12 | 108.6755 | 0
2024-02-25 04:00 | 16.7 | 83 | 2.82 | 0 | 26 | 30 | 12 | 116.0392 | 0
2024-02-25 05:00 | 17.1 | 86 | 1.65 | 0 | 26 | 30 | 12 | 83.1002 | 0
2024-02-25 06:00 | 17.1 | 83 | 1.84 | 0 | 26 | 30 | 12 | 89.5847 | 0
2024-02-25 07:00 | 16.9 | 81 | 2.06 | 1 | 26 | 30 | 12 | 97.4405 | 0
2024-02-25 08:00 | 18.5 | 71 | 1.92 | 78 | 26 | 30 | 12 | 80.2642 | 0
2024-02-25 09:00 | 20.7 | 61 | 1.62 | 130 | 26 | 30 | 12 | 59.999 | 0
2024-02-25 10:00 | 22.9 | 50 | 2 | 241 | 26 | 30 | 12 | 50.6789 | 0
2024-02-25 11:00 | 25.4 | 37 | 2.45 | 431 | 26 | 30 | 12 | 34.2637 | 0
2024-02-25 12:00 | 27.4 | 31 | 1.3 | 678 | 26 | 30 | 12 | 0 | 0.7065
2024-02-25 13:00 | 27.5 | 32 | 1.08 | 374 | 26 | 30 | 12 | 1.9035 | 0
2024-02-25 14:00 | 28.4 | 30 | 2.21 | 385 | 26 | 30 | 12 | 26.448 | 0
2024-02-25 15:00 | 29.2 | 29 | 2.18 | 362 | 26 | 30 | 12 | 25.7705 | 0
2024-02-25 16:00 | 30 | 29 | 3.5 | 386 | 26 | 30 | 12 | 43.2789 | 0
2024-02-25 17:00 | 27.1 | 34 | 4.97 | 67 | 26 | 30 | 12 | 125.7854 | 0
2024-02-25 18:00 | 25.6 | 39 | 6.3 | 75 | 26 | 30 | 12 | 151.3328 | 0
2024-02-25 19:00 | 23.6 | 67 | 7.2 | 2 | 26 | 30 | 12 | 135.7416 | 0
2024-02-25 20:00 | 22.7 | 72 | 5.55 | 0 | 26 | 30 | 12 | 117.6925 | 0
2024-02-25 21:00 | 22.2 | 77 | 6.8 | 0 | 26 | 30 | 12 | 131.184 | 0
2024-02-25 22:00 | 22.1 | 75 | 2.81 | 0 | 26 | 30 | 12 | 80.1371 | 0
2024-02-25 23:00 | 21.7 | 71 | 2.79 | 0 | 26 | 30 | 12 | 87.3376 | 0
2024-02-26 | 21 | 84 | 3.91 | 0 | 26 | 30 | 12 | 96.8533 | 0
2024-02-26 01:00 | 20.8 | 85 | 4.21 | 0 | 26 | 30 | 12 | 102.106 | 0
2024-02-26 02:00 | 20.5 | 82 | 5.11 | 0 | 26 | 30 | 12 | 123.0704 | 0
2024-02-26 03:00 | 20.1 | 91 | 5.3 | 0 | 26 | 30 | 12 | 117.5614 | 0
2024-02-26 04:00 | 20 | 91 | 5.2 | 0 | 26 | 30 | 12 | 117.505 | 0
2024-02-26 05:00 | 20.6 | 90 | 4.5 | 0 | 26 | 30 | 12 | 101.7738 | 0
2024-02-26 06:00 | 20.3 | 89 | 5 | 0 | 26 | 30 | 12 | 113.7511 | 0
2024-02-26 07:00 | 19.8 | 90 | 4.8 | 1 | 26 | 30 | 12 | 115.5991 | 0
2024-02-26 08:00 | 20.7 | 82 | 5.52 | 86 | 26 | 30 | 12 | 114.9082 | 0
2024-02-26 09:00 | 21.7 | 72 | 5.76 | 260 | 26 | 30 | 12 | 98.4806 | 0
2024-02-26 10:00 | 22.5 | 66 | 5.7 | 484 | 26 | 30 | 12 | 67.834 | 0
2024-02-26 11:00 | 23.1 | 61 | 6.4 | 635 | 26 | 30 | 12 | 59.6495 | 0
2024-02-26 12:00 | 23.4 | 59 | 7.1 | 703 | 26 | 30 | 12 | 60.7505 | 0
2024-02-26 13:00 | 23.5 | 56 | 7.4 | 727 | 26 | 30 | 12 | 67.239 | 0
2024-02-26 14:00 | 23.3 | 54 | 7.81 | 678 | 26 | 30 | 12 | 87.4438 | 0
2024-02-26 15:00 | 22.6 | 56 | 8.51 | 526 | 26 | 30 | 12 | 124.0439 | 0
2024-02-26 16:00 | 22 | 59 | 8.36 | 386 | 26 | 30 | 12 | 142.6326 | 0
2024-02-26 17:00 | 22 | 57 | 7.98 | 298 | 26 | 30 | 12 | 153.0456 | 0
2024-02-26 18:00 | 21 | 59 | 6.46 | 106 | 26 | 30 | 12 | 162.4892 | 0
2024-02-26 19:00 | 20.3 | 62 | 5.02 | 3 | 26 | 30 | 12 | 152.6982 | 0
2024-02-26 20:00 | 20.2 | 62 | 4.8 | 0 | 26 | 30 | 12 | 149.8275 | 0
2024-02-26 21:00 | 20.2 | 62 | 4.4 | 0 | 26 | 30 | 12 | 141.8661 | 0
2024-02-26 22:00 | 19.9 | 64 | 4.1 | 0 | 26 | 30 | 12 | 136.025 | 0
2024-02-26 23:00 | 19.6 | 65 | 3.98 | 0 | 26 | 30 | 12 | 135.0489 | 0
2024-02-27 | 19.1 | 68 | 3.67 | 0 | 26 | 30 | 12 | 129.493 | 0
2024-02-27 01:00 | 18.9 | 69 | 3.51 | 0 | 26 | 30 | 12 | 126.6809 | 0
2024-02-27 02:00 | 18.4 | 71 | 3.11 | 0 | 26 | 30 | 12 | 119.8756 | 0
2024-02-27 03:00 | 17.7 | 75 | 2.72 | 0 | 26 | 30 | 12 | 112.6262 | 0
2024-02-27 04:00 | 17.3 | 78 | 2.31 | 0 | 26 | 30 | 12 | 103.2414 | 0
2024-02-27 05:00 | 17.6 | 76 | 1.75 | 0 | 26 | 30 | 12 | 88.4758 | 0
2024-02-27 06:00 | 17.1 | 78 | 2.16 | 0 | 26 | 30 | 12 | 100.7826 | 0
2024-02-27 07:00 | 16.6 | 81 | 2.33 | 2 | 26 | 30 | 12 | 106.0332 | 0
2024-02-27 08:00 | 18.5 | 72 | 1.66 | 97 | 26 | 30 | 12 | 70.3964 | 0
2024-02-27 09:00 | 20.7 | 62 | 1.08 | 303 | 26 | 30 | 12 | 21.7091 | 0
2024-02-27 10:00 | 22.2 | 52 | 2.46 | 514 | 26 | 30 | 12 | 26.9403 | 0
2024-02-27 11:00 | 22.9 | 49 | 3.35 | 686 | 26 | 30 | 12 | 21.6246 | 0
2024-02-27 12:00 | 23.4 | 47 | 4.02 | 798 | 26 | 30 | 12 | 18.8366 | 0
2024-02-27 13:00 | 23.7 | 46 | 4.79 | 843 | 26 | 30 | 12 | 26.4388 | 0
2024-02-27 14:00 | 23.8 | 45 | 5.05 | 809 | 26 | 30 | 12 | 36.66 | 0
2024-02-27 15:00 | 23.5 | 43 | 5.1 | 705 | 26 | 30 | 12 | 58.1121 | 0
2024-02-27 16:00 | 23 | 45 | 4.76 | 538 | 26 | 30 | 12 | 75.2503 | 0
2024-02-27 17:00 | 22.4 | 50 | 4.39 | 323 | 26 | 30 | 12 | 94.5444 | 0
2024-02-27 18:00 | 21.5 | 54 | 3.47 | 111 | 26 | 30 | 12 | 106.4558 | 0
2024-02-27 19:00 | 20.4 | 60 | 2.36 | 3 | 26 | 30 | 12 | 97.7987 | 0
2024-02-27 20:00 | 19.4 | 65 | 2.14 | 0 | 26 | 30 | 12 | 95.1255 | 0
2024-02-27 21:00 | 18.5 | 67 | 2.42 | 0 | 26 | 30 | 12 | 106.2026 | 0
2024-02-27 22:00 | 17.5 | 72 | 1.99 | 0 | 26 | 30 | 12 | 97.8243 | 0
2024-02-27 23:00 | 17.9 | 69 | 1.46 | 0 | 26 | 30 | 12 | 82.8259 | 0
2024-02-28 | 17.9 | 68 | 1.22 | 0 | 26 | 30 | 12 | 76.2538 | 0
2024-02-28 01:00 | 18.3 | 65 | 0.73 | 0 | 26 | 30 | 12 | 60.0433 | 0
2024-02-28 02:00 | 17.6 | 68 | 0.94 | 0 | 26 | 30 | 12 | 68.7004 | 0
2024-02-28 03:00 | 15.3 | 78 | 1.5 | 0 | 26 | 30 | 12 | 92.4228 | 0
2024-02-28 04:00 | 14.1 | 84 | 1.98 | 0 | 26 | 30 | 12 | 110.319 | 0
2024-02-28 05:00 | 15.3 | 77 | 2.62 | 0 | 26 | 30 | 12 | 125.1629 | 0
2024-02-28 06:00 | 14.7 | 82 | 2.8 | 0 | 26 | 30 | 12 | 130.7259 | 0
2024-02-28 07:00 | 14.6 | 84 | 2.55 | 2 | 26 | 30 | 12 | 123.0953 | 0
2024-02-28 08:00 | 16.1 | 78 | 1.22 | 97 | 26 | 30 | 12 | 66.9205 | 0
2024-02-28 09:00 | 18.5 | 68 | 0.32 | 304 | 26 | 30 | 12 | 11.4701 | 0
2024-02-28 10:00 | 20.7 | 61 | 0.95 | 516 | 26 | 30 | 12 | 0 | 0
2024-02-28 11:00 | 22.5 | 56 | 2.56 | 689 | 26 | 30 | 12 | 0 | 0
2024-02-28 12:00 | 23.5 | 55 | 4.06 | 806 | 26 | 30 | 12 | 5.5565 | 0
2024-02-28 13:00 | 24 | 52 | 4.81 | 847 | 26 | 30 | 12 | 12.8468 | 0
2024-02-28 14:00 | 23.9 | 52 | 5.52 | 811 | 26 | 30 | 12 | 30.4642 | 0
2024-02-28 15:00 | 23.7 | 51 | 5.05 | 699 | 26 | 30 | 12 | 41.7546 | 0
2024-02-28 16:00 | 23.6 | 54 | 4.25 | 525 | 26 | 30 | 12 | 47.4014 | 0
2024-02-28 17:00 | 23.4 | 55 | 4.1 | 308 | 26 | 30 | 12 | 74.4194 | 0
2024-02-28 18:00 | 22.5 | 59 | 3.7 | 103 | 26 | 30 | 12 | 97.4022 | 0
2024-02-28 19:00 | 22.1 | 61 | 3.55 | 3 | 26 | 30 | 12 | 109.0268 | 0
2024-02-28 20:00 | 21 | 69 | 2.63 | 0 | 26 | 30 | 12 | 91.7493 | 0
2024-02-28 21:00 | 20.3 | 76 | 2.28 | 0 | 26 | 30 | 12 | 83.5965 | 0
2024-02-28 22:00 | 19.8 | 80 | 2.16 | 0 | 26 | 30 | 12 | 81.4767 | 0
2024-02-28 23:00 | 20.2 | 79 | 1.84 | 0 | 26 | 30 | 12 | 73.0433 | 0
2024-02-29 | 19 | 87 | 1.4 | 0 | 26 | 30 | 12 | 65.8652 | 0
2024-02-29 01:00 | 18.7 | 88 | 1.43 | 0 | 26 | 30 | 12 | 67.6755 | 0
2024-02-29 02:00 | 18.5 | 90 | 1.77 | 0 | 26 | 30 | 12 | 75.1044 | 0
2024-02-29 03:00 | 19.5 | 85 | 2.75 | 0 | 26 | 30 | 12 | 90.9036 | 0
2024-02-29 04:00 | 19.7 | 83 | 3.72 | 0 | 26 | 30 | 12 | 108.3764 | 0
2024-02-29 05:00 | 20.2 | 83 | 4.12 | 0 | 26 | 30 | 12 | 109.8834 | 0
2024-02-29 06:00 | 19 | 87 | 1.51 | 0 | 26 | 30 | 12 | 68.2801 | 0
2024-02-29 07:00 | 19.6 | 81 | 2.58 | 2 | 26 | 30 | 12 | 90.1672 | 0
2024-02-29 08:00 | 21.4 | 65 | 2.7 | 80 | 26 | 30 | 12 | 83.2941 | 0
2024-02-29 09:00 | 22.9 | 54 | 5.3 | 273 | 26 | 30 | 12 | 106.6962 | 0
2024-02-29 10:00 | 22.9 | 55 | 6.24 | 342 | 26 | 30 | 12 | 111.2937 | 0
2024-02-29 11:00 | 23.7 | 50 | 6.69 | 643 | 26 | 30 | 12 | 78.5064 | 0
2024-02-29 12:00 | 24.1 | 47 | 7.61 | 776 | 26 | 30 | 12 | 76.9662 | 0
2024-02-29 13:00 | 24.2 | 44 | 8.55 | 842 | 26 | 30 | 12 | 89.1315 | 0
2024-02-29 14:00 | 23.8 | 45 | 9.32 | 808 | 26 | 30 | 12 | 108.8518 | 0
2024-02-29 15:00 | 23.1 | 45 | 9.96 | 702 | 26 | 30 | 12 | 143.8904 | 0
2024-02-29 16:00 | 22.5 | 45 | 9.71 | 534 | 26 | 30 | 12 | 171.4713 | 0
2024-02-29 17:00 | 21.8 | 45 | 8.99 | 322 | 26 | 30 | 12 | 197.4928 | 0
2024-02-29 18:00 | 20.6 | 51 | 8.67 | 112 | 26 | 30 | 12 | 222.8728 | 0
2024-02-29 19:00 | 19.8 | 55 | 7.84 | 4 | 26 | 30 | 12 | 224.3945 | 0
2024-02-29 20:00 | 19.3 | 59 | 7.41 | 0 | 26 | 30 | 12 | 215.6909 | 0
2024-02-29 21:00 | 18.8 | 57 | 7.58 | 0 | 26 | 30 | 12 | 228.9228 | 0
2024-02-29 22:00 | 18.3 | 59 | 7.88 | 0 | 26 | 30 | 12 | 237.8468 | 0
2024-02-29 23:00 | 18 | 62 | 7.68 | 0 | 26 | 30 | 12 | 232.5154 | 0
2024-03-01 | 17.9 | 61 | 7.73 | 0 | 26 | 30 | 17 | 235.0553 | 0
2024-03-01 01:00 | 17.6 | 64 | 7.69 | 0 | 26 | 30 | 17 | 233.1402 | 0
2024-03-01 02:00 | 17.4 | 65 | 7.76 | 0 | 26 | 30 | 17 | 235.5306 | 0
2024-03-01 03:00 | 17.4 | 64 | 7.87 | 0 | 26 | 30 | 17 | 239.405 | 0
2024-03-01 04:00 | 17.3 | 63 | 7.73 | 0 | 26 | 30 | 17 | 239.4373 | 0
2024-03-01 05:00 | 17.6 | 59 | 6.83 | 0 | 26 | 30 | 17 | 222.9742 | 0
2024-03-01 06:00 | 17.3 | 59 | 6.29 | 0 | 26 | 30 | 17 | 214.4113 | 0
2024-03-01 07:00 | 17.1 | 60 | 5.68 | 3 | 26 | 30 | 17 | 200.8978 | 0
2024-03-01 08:00 | 18.6 | 52 | 5.99 | 105 | 26 | 30 | 17 | 190.0059 | 0
2024-03-01 09:00 | 19.7 | 46 | 6.71 | 318 | 26 | 30 | 17 | 175.0426 | 0
2024-03-01 10:00 | 20.5 | 44 | 6.76 | 540 | 26 | 30 | 17 | 141.0904 | 0
2024-03-01 11:00 | 21.3 | 43 | 7 | 713 | 26 | 30 | 17 | 115.8107 | 0
2024-03-01 12:00 | 21.8 | 41 | 6.08 | 794 | 26 | 30 | 17 | 84.6343 | 0
2024-03-01 13:00 | 22.2 | 36 | 6.26 | 785 | 26 | 30 | 17 | 94.8789 | 0
2024-03-01 14:00 | 22.4 | 35 | 3.9 | 787 | 26 | 30 | 17 | 41.6946 | 0
2024-03-01 15:00 | 22.1 | 40 | 6.1 | 599 | 26 | 30 | 17 | 110.204 | 0
2024-03-01 16:00 | 21.3 | 40 | 7.8 | 496 | 26 | 30 | 17 | 167.159 | 0
2024-03-01 17:00 | 21.2 | 35 | 6.21 | 329 | 26 | 30 | 17 | 166.6625 | 0
2024-03-01 18:00 | 20.1 | 38 | 5.94 | 116 | 26 | 30 | 17 | 194.3502 | 0
2024-03-01 19:00 | 19.1 | 41 | 4.3 | 4 | 26 | 30 | 17 | 173.5799 | 0
2024-03-01 20:00 | 18.3 | 43 | 2.56 | 0 | 26 | 30 | 17 | 129.3514 | 0
2024-03-01 21:00 | 17.1 | 47 | 2.13 | 0 | 26 | 30 | 17 | 119.4902 | 0
2024-03-01 22:00 | 16.1 | 51 | 1.87 | 0 | 26 | 30 | 17 | 113.4521 | 0
2024-03-01 23:00 | 15.3 | 52 | 2 | 0 | 26 | 30 | 17 | 121.0191 | 0
2024-03-02 | 14.7 | 51 | 2.77 | 0 | 26 | 30 | 17 | 149.8554 | 0
2024-03-02 01:00 | 14 | 51 | 3.18 | 0 | 26 | 30 | 17 | 166.8913 | 0
2024-03-02 02:00 | 13.4 | 51 | 2.55 | 0 | 26 | 30 | 17 | 149.5719 | 0
2024-03-02 03:00 | 13.6 | 53 | 1.62 | 0 | 26 | 30 | 17 | 114.6774 | 0
2024-03-02 04:00 | 13 | 52 | 3.18 | 0 | 26 | 30 | 17 | 172.0885 | 0
2024-03-02 05:00 | 13.9 | 55 | 2.68 | 0 | 26 | 30 | 17 | 148.8362 | 0
2024-03-02 06:00 | 13.3 | 56 | 2.65 | 0 | 26 | 30 | 17 | 150.5383 | 0
2024-03-02 07:00 | 12.5 | 52 | 3.85 | 3 | 26 | 30 | 17 | 196.2708 | 0
2024-03-02 08:00 | 14.8 | 41 | 3.16 | 102 | 26 | 30 | 17 | 155.0529 | 0
2024-03-02 09:00 | 18.2 | 34 | 2.75 | 320 | 26 | 30 | 17 | 99.7674 | 0
2024-03-02 10:00 | 20.6 | 38 | 4.11 | 539 | 26 | 30 | 17 | 89.2526 | 0
2024-03-02 11:00 | 21.8 | 34 | 3.67 | 706 | 26 | 30 | 17 | 52.3931 | 0
2024-03-02 12:00 | 22.6 | 31 | 2.62 | 805 | 26 | 30 | 17 | 9.9876 | 0
2024-03-02 13:00 | 23.1 | 29 | 1.52 | 795 | 26 | 30 | 17 | 0 | 0
2024-03-02 14:00 | 23.5 | 27 | 0.1 | 790 | 26 | 30 | 17 | 0 | 36.3576
2024-03-02 15:00 | 23.9 | 26 | 2.27 | 669 | 26 | 30 | 17 | 17.0128 | 0
2024-03-02 16:00 | 22.3 | 39 | 6.45 | 522 | 26 | 30 | 17 | 127.5873 | 0
2024-03-02 17:00 | 21.5 | 37 | 6.87 | 318 | 26 | 30 | 17 | 175.8787 | 0
2024-03-02 18:00 | 20.6 | 38 | 5.54 | 117 | 26 | 30 | 17 | 180.4905 | 0
2024-03-02 19:00 | 20 | 42 | 4.5 | 5 | 26 | 30 | 17 | 170.3071 | 0
2024-03-02 20:00 | 19.4 | 42 | 4.02 | 0 | 26 | 30 | 17 | 163.5665 | 0
2024-03-02 21:00 | 18.4 | 43 | 3.55 | 0 | 26 | 30 | 17 | 156.9625 | 0
2024-03-02 22:00 | 17.2 | 43 | 3.67 | 0 | 26 | 30 | 17 | 168.1872 | 0
2024-03-02 23:00 | 16.3 | 47 | 3.35 | 0 | 26 | 30 | 17 | 161.1263 | 0
2024-03-03 | 15.6 | 59 | 3.51 | 0 | 26 | 30 | 17 | 160.2956 | 0
2024-03-03 01:00 | 14.8 | 63 | 3.16 | 0 | 26 | 30 | 17 | 152.6863 | 0
2024-03-03 02:00 | 14.1 | 66 | 3.01 | 0 | 26 | 30 | 17 | 150.7425 | 0
2024-03-03 03:00 | 13.3 | 69 | 2.89 | 0 | 26 | 30 | 17 | 150.2544 | 0
2024-03-03 04:00 | 12.5 | 72 | 2.65 | 0 | 26 | 30 | 17 | 145.9102 | 0
2024-03-03 05:00 | 12.1 | 73 | 2.4 | 0 | 26 | 30 | 17 | 139.6464 | 0
2024-03-03 06:00 | 11.9 | 73 | 2.72 | 0 | 26 | 30 | 17 | 151.1389 | 0
2024-03-03 07:00 | 11.8 | 73 | 3.11 | 4 | 26 | 30 | 17 | 163.5368 | 0
2024-03-03 08:00 | 14.1 | 61 | 2.62 | 115 | 26 | 30 | 17 | 126.5819 | 0
2024-03-03 09:00 | 17.6 | 49 | 2.3 | 333 | 26 | 30 | 17 | 75.892 | 0
2024-03-03 10:00 | 20.2 | 36 | 3.54 | 555 | 26 | 30 | 17 | 77.4576 | 0
2024-03-03 11:00 | 21.9 | 27 | 2.98 | 735 | 26 | 30 | 17 | 37.631 | 0
2024-03-03 12:00 | 23 | 23 | 1.03 | 852 | 26 | 30 | 17 | 0 | 15.4219
2024-03-03 13:00 | 23.8 | 20 | 0.32 | 891 | 26 | 30 | 17 | 0 | 47.1485
2024-03-03 14:00 | 24.4 | 18 | 0.5 | 854 | 26 | 30 | 17 | 0 | 42.2699
2024-03-03 15:00 | 24.4 | 21 | 2.7 | 741 | 26 | 30 | 17 | 22.6904 | 0
2024-03-03 16:00 | 23.2 | 35 | 5.01 | 563 | 26 | 30 | 17 | 90.947 | 0
2024-03-03 17:00 | 22.2 | 36 | 5.15 | 340 | 26 | 30 | 17 | 130.9243 | 0
2024-03-03 18:00 | 21 | 44 | 5.36 | 121 | 26 | 30 | 17 | 162.9118 | 0
2024-03-03 19:00 | 19.9 | 46 | 3.91 | 5 | 26 | 30 | 17 | 151.7902 | 0
2024-03-03 20:00 | 19 | 50 | 2.7 | 0 | 26 | 30 | 17 | 123.5342 | 0
2024-03-03 21:00 | 18 | 54 | 2.75 | 0 | 26 | 30 | 17 | 127.684 | 0
2024-03-03 22:00 | 17 | 56 | 2.86 | 0 | 26 | 30 | 17 | 135.3494 | 0
2024-03-03 23:00 | 16.3 | 57 | 2.61 | 0 | 26 | 30 | 17 | 131.6946 | 0
2024-03-04 | 15.9 | 57 | 3.19 | 0 | 26 | 30 | 17 | 150.9 | 0
2024-03-04 01:00 | 15.2 | 62 | 3.27 | 0 | 26 | 30 | 17 | 153.9101 | 0
2024-03-04 02:00 | 14.6 | 70 | 3.3 | 0 | 26 | 30 | 17 | 152.8272 | 0
2024-03-04 03:00 | 14.4 | 75 | 3.58 | 0 | 26 | 30 | 17 | 158.0884 | 0
2024-03-04 04:00 | 14.2 | 74 | 3.81 | 0 | 26 | 30 | 17 | 166.5687 | 0
2024-03-04 05:00 | 14.9 | 74 | 3.9 | 0 | 26 | 30 | 17 | 163.3373 | 0
2024-03-04 06:00 | 15.1 | 74 | 3.89 | 0 | 26 | 30 | 17 | 161.4527 | 0
2024-03-04 07:00 | 15.8 | 70 | 3.41 | 3 | 26 | 30 | 17 | 146.6518 | 0
2024-03-04 08:00 | 17.2 | 58 | 3.25 | 93 | 26 | 30 | 17 | 130.431 | 0
2024-03-04 09:00 | 20.6 | 37 | 3.92 | 289 | 26 | 30 | 17 | 119.4612 | 0
2024-03-04 10:00 | 23.3 | 53 | 6.18 | 529 | 26 | 30 | 17 | 83.1472 | 0
2024-03-04 11:00 | 25.6 | 43 | 7.18 | 706 | 26 | 30 | 17 | 69.0395 | 0
2024-03-04 12:00 | 27.2 | 36 | 6.8 | 795 | 26 | 30 | 17 | 50.1768 | 0
2024-03-04 13:00 | 28.2 | 33 | 5.89 | 853 | 26 | 30 | 17 | 25.3126 | 0
2024-03-04 14:00 | 28.8 | 31 | 5.29 | 720 | 26 | 30 | 17 | 32.8915 | 0
2024-03-04 15:00 | 29 | 27 | 4.3 | 384 | 26 | 30 | 17 | 68.8681 | 0
2024-03-04 16:00 | 27.3 | 40 | 3.36 | 408 | 26 | 30 | 17 | 37.6461 | 0
2024-03-04 17:00 | 26.8 | 38 | 1.04 | 117 | 26 | 30 | 17 | 33.5919 | 0
2024-03-04 18:00 | 25.4 | 46 | 4.18 | 107 | 26 | 30 | 17 | 98.2163 | 0
2024-03-04 19:00 | 24 | 50 | 5.91 | 4 | 26 | 30 | 17 | 147.5022 | 0
2024-03-04 20:00 | 23.1 | 57 | 6.11 | 0 | 26 | 30 | 17 | 147.9703 | 0
2024-03-04 21:00 | 22.5 | 61 | 5.14 | 0 | 26 | 30 | 17 | 132.3064 | 0
2024-03-04 22:00 | 21.7 | 63 | 5.6 | 0 | 26 | 30 | 17 | 145.5993 | 0
2024-03-04 23:00 | 21.1 | 67 | 6.26 | 0 | 26 | 30 | 17 | 156.8265 | 0
2024-03-05 | 20.5 | 69 | 6.43 | 0 | 26 | 30 | 17 | 163.8456 | 0
2024-03-05 01:00 | 20.6 | 70 | 6.45 | 0 | 26 | 30 | 17 | 161.1293 | 0
2024-03-05 02:00 | 19.9 | 72 | 6.02 | 0 | 26 | 30 | 17 | 159.6389 | 0
2024-03-05 03:00 | 19.6 | 77 | 5.81 | 0 | 26 | 30 | 17 | 152.0704 | 0
2024-03-05 04:00 | 19.3 | 79 | 5.28 | 0 | 26 | 30 | 17 | 143.8387 | 0
2024-03-05 05:00 | 19.9 | 82 | 4.2 | 0 | 26 | 30 | 17 | 114.9827 | 0
2024-03-05 06:00 | 19.9 | 80 | 3.26 | 0 | 26 | 30 | 17 | 101.0771 | 0
2024-03-05 07:00 | 20.2 | 80 | 3.96 | 4 | 26 | 30 | 17 | 109.7954 | 0
2024-03-05 08:00 | 20.9 | 77 | 5.81 | 95 | 26 | 30 | 17 | 122.5953 | 0
2024-03-05 09:00 | 22.9 | 71 | 6.1 | 257 | 26 | 30 | 17 | 88.5578 | 0
2024-03-05 10:00 | 22.6 | 74 | 4.3 | 376 | 26 | 30 | 17 | 47.327 | 0
2024-03-05 11:00 | 23.4 | 70 | 6.36 | 365 | 26 | 30 | 17 | 72.1791 | 0
2024-03-05 12:00 | 22.5 | 74 | 6.26 | 369 | 26 | 30 | 17 | 75.2936 | 0
2024-03-05 13:00 | 23.2 | 73 | 5 | 406 | 26 | 30 | 17 | 47.004 | 0
2024-03-05 14:00 | 23.2 | 73 | 4.26 | 527 | 26 | 30 | 17 | 21.2501 | 0
2024-03-05 15:00 | 24.3 | 70 | 3.96 | 588 | 26 | 30 | 17 | 1.8255 | 0
2024-03-05 16:00 | 24.7 | 70 | 4.3 | 397 | 26 | 30 | 17 | 27.1305 | 0
2024-03-05 17:00 | 21.6 | 79 | 6 | 285 | 26 | 30 | 17 | 86.7391 | 0
2024-03-05 18:00 | 20.7 | 83 | 5.9 | 98 | 26 | 30 | 17 | 116.2688 | 0
2024-03-05 19:00 | 20 | 86 | 2.64 | 5 | 26 | 30 | 17 | 82.8061 | 0
2024-03-05 20:00 | 19.5 | 90 | 2.4 | 0 | 26 | 30 | 17 | 79.849 | 0
2024-03-05 21:00 | 19 | 92 | 2.77 | 0 | 26 | 30 | 17 | 88.7511 | 0
2024-03-05 22:00 | 18.7 | 94 | 2.68 | 0 | 26 | 30 | 17 | 87.9617 | 0
2024-03-05 23:00 | 18.6 | 96 | 2.9 | 0 | 26 | 30 | 17 | 90.9657 | 0
2024-03-06 | 18.6 | 95 | 2.95 | 0 | 26 | 30 | 17 | 92.7187 | 0
2024-03-06 01:00 | 17.7 | 96 | 2.18 | 0 | 26 | 30 | 17 | 84.6992 | 0
2024-03-06 02:00 | 17.2 | 96 | 2.12 | 0 | 26 | 30 | 17 | 86.9937 | 0
2024-03-06 03:00 | 17.1 | 96 | 2.76 | 0 | 26 | 30 | 17 | 101.0136 | 0
2024-03-06 04:00 | 16.7 | 97 | 2.86 | 0 | 26 | 30 | 17 | 105.5492 | 0
2024-03-06 05:00 | 17.4 | 88 | 1.77 | 0 | 26 | 30 | 17 | 82.7489 | 0
2024-03-06 06:00 | 17.4 | 88 | 1.56 | 0 | 26 | 30 | 17 | 77.7176 | 0
2024-03-06 07:00 | 16.8 | 90 | 2.75 | 5 | 26 | 30 | 17 | 107.0892 | 0
2024-03-06 08:00 | 17.6 | 92 | 2.77 | 115 | 26 | 30 | 17 | 84.7911 | 0
2024-03-06 09:00 | 20.1 | 83 | 2.73 | 320 | 26 | 30 | 17 | 43.7737 | 0
2024-03-06 10:00 | 22.1 | 62 | 3.57 | 551 | 26 | 30 | 17 | 33.4598 | 0
2024-03-06 11:00 | 23 | 54 | 4.5 | 728 | 26 | 30 | 17 | 29.3047 | 0
2024-03-06 12:00 | 23.2 | 53 | 5.15 | 843 | 26 | 30 | 17 | 24.7566 | 0
2024-03-06 13:00 | 22.9 | 57 | 5.39 | 883 | 26 | 30 | 17 | 19.6015 | 0
2024-03-06 14:00 | 22.8 | 57 | 5.32 | 845 | 26 | 30 | 17 | 24.6874 | 0
2024-03-06 15:00 | 22.5 | 58 | 5.11 | 734 | 26 | 30 | 17 | 37.7167 | 0
2024-03-06 16:00 | 22.1 | 58 | 4.7 | 561 | 26 | 30 | 17 | 58.0894 | 0
2024-03-06 17:00 | 21.8 | 57 | 4.03 | 341 | 26 | 30 | 17 | 79.6307 | 0
2024-03-06 18:00 | 20.5 | 70 | 2.66 | 123 | 26 | 30 | 17 | 77.9862 | 0
2024-03-06 19:00 | 19 | 79 | 2.51 | 5 | 26 | 30 | 17 | 94.0429 | 0
2024-03-06 20:00 | 18.5 | 83 | 2.41 | 0 | 26 | 30 | 17 | 93.0826 | 0
2024-03-06 21:00 | 17.7 | 87 | 1.93 | 0 | 26 | 30 | 17 | 85.2033 | 0
2024-03-06 22:00 | 18.3 | 86 | 1.89 | 0 | 26 | 30 | 17 | 81.1214 | 0
2024-03-06 23:00 | 17 | 89 | 2.62 | 0 | 26 | 30 | 17 | 104.1317 | 0
2024-03-07 | 15.8 | 93 | 2.9 | 0 | 26 | 30 | 17 | 116.6687 | 0
2024-03-07 01:00 | 15.1 | 95 | 3.01 | 0 | 26 | 30 | 17 | 123.2799 | 0
2024-03-07 02:00 | 14.6 | 96 | 2.75 | 0 | 26 | 30 | 17 | 120.208 | 0
2024-03-07 03:00 | 14.7 | 95 | 2.75 | 0 | 26 | 30 | 17 | 120.1241 | 0
2024-03-07 04:00 | 16 | 91 | 2.45 | 0 | 26 | 30 | 17 | 106.1247 | 0
2024-03-07 05:00 | 16.9 | 87 | 2.02 | 0 | 26 | 30 | 17 | 92.3951 | 0
2024-03-07 06:00 | 15.9 | 91 | 2.1 | 0 | 26 | 30 | 17 | 98.333 | 0
2024-03-07 07:00 | 15.9 | 91 | 2.31 | 5 | 26 | 30 | 17 | 102.7914 | 0
2024-03-07 08:00 | 17.7 | 84 | 2.11 | 109 | 26 | 30 | 17 | 76.5464 | 0
2024-03-07 09:00 | 19.9 | 76 | 2.09 | 333 | 26 | 30 | 17 | 37.0371 | 0
2024-03-07 10:00 | 21.6 | 66 | 1.66 | 549 | 26 | 30 | 17 | 0 | 0
2024-03-07 11:00 | 22.8 | 59 | 1.36 | 713 | 26 | 30 | 17 | 0 | 3.3631
2024-03-07 12:00 | 23.8 | 55 | 2.18 | 819 | 26 | 30 | 17 | 0 | 0
2024-03-07 13:00 | 24.1 | 56 | 2.94 | 850 | 26 | 30 | 17 | 0 | 0
2024-03-07 14:00 | 23.9 | 58 | 3.68 | 802 | 26 | 30 | 17 | 0 | 0
2024-03-07 15:00 | 23.7 | 56 | 3.64 | 708 | 26 | 30 | 17 | 7.4819 | 0
2024-03-07 16:00 | 23 | 56 | 3.34 | 395 | 26 | 30 | 17 | 50.2678 | 0
2024-03-07 17:00 | 22.7 | 63 | 2.83 | 295 | 26 | 30 | 17 | 48.4086 | 0
2024-03-07 18:00 | 21.5 | 75 | 2.97 | 119 | 26 | 30 | 17 | 71.308 | 0
2024-03-07 19:00 | 19.9 | 86 | 2.02 | 6 | 26 | 30 | 17 | 72.3004 | 0
2024-03-07 20:00 | 19 | 89 | 1.5 | 0 | 26 | 30 | 17 | 66.6089 | 0
2024-03-07 21:00 | 18.4 | 90 | 2.27 | 0 | 26 | 30 | 17 | 85.6794 | 0
2024-03-07 22:00 | 17.8 | 91 | 2.69 | 0 | 26 | 30 | 17 | 97.9034 | 0
2024-03-07 23:00 | 17 | 92 | 2.61 | 0 | 26 | 30 | 17 | 101.6957 | 0
2024-03-08 | 16.6 | 91 | 2.92 | 0 | 26 | 30 | 17 | 112.2863 | 0
2024-03-08 01:00 | 16.3 | 92 | 2.02 | 0 | 26 | 30 | 17 | 93.2196 | 0
2024-03-08 02:00 | 15.6 | 94 | 1.87 | 0 | 26 | 30 | 17 | 92.7722 | 0
2024-03-08 03:00 | 15.9 | 93 | 1.71 | 0 | 26 | 30 | 17 | 87.448 | 0
2024-03-08 04:00 | 16.2 | 91 | 2.72 | 0 | 26 | 30 | 17 | 110.9394 | 0
2024-03-08 05:00 | 18.1 | 81 | 2.57 | 0 | 26 | 30 | 17 | 100.9817 | 0
2024-03-08 06:00 | 18.6 | 81 | 1.4 | 0 | 26 | 30 | 17 | 70.949 | 0
2024-03-08 07:00 | 18.6 | 77 | 2.39 | 3 | 26 | 30 | 17 | 96.143 | 0
2024-03-08 08:00 | 19 | 75 | 2.91 | 36 | 26 | 30 | 17 | 101.7045 | 0
2024-03-08 09:00 | 20.9 | 79 | 3.67 | 103 | 26 | 30 | 17 | 85.9031 | 0
2024-03-08 10:00 | 22.6 | 70 | 3.98 | 164 | 26 | 30 | 17 | 77.1251 | 0
2024-03-08 11:00 | 25.8 | 57 | 5.3 | 341 | 26 | 30 | 17 | 57.7997 | 0
2024-03-08 12:00 | 28.7 | 57 | 5.93 | 649 | 26 | 30 | 17 | 0 | 0
2024-03-08 13:00 | 30.5 | 45 | 5.1 | 784 | 26 | 30 | 17 | 0 | 0
2024-03-08 14:00 | 31.3 | 40 | 3.63 | 770 | 26 | 30 | 17 | 0 | 0
2024-03-08 15:00 | 31.2 | 38 | 1.4 | 647 | 26 | 30 | 17 | 0 | 18.5273
2024-03-08 16:00 | 30.4 | 40 | 1.04 | 523 | 26 | 30 | 17 | 0 | 11.3084
2024-03-08 17:00 | 28.1 | 53 | 4.57 | 329 | 26 | 30 | 17 | 32.7196 | 0
2024-03-08 18:00 | 26.8 | 59 | 2.69 | 119 | 26 | 30 | 17 | 41.9856 | 0
2024-03-08 19:00 | 25 | 71 | 3.41 | 6 | 26 | 30 | 17 | 65.2025 | 0
2024-03-08 20:00 | 24 | 78 | 5.03 | 0 | 26 | 30 | 17 | 83.1143 | 0
2024-03-08 21:00 | 23.1 | 81 | 6.36 | 0 | 26 | 30 | 17 | 103.6121 | 0
2024-03-08 22:00 | 23 | 78 | 4.88 | 0 | 26 | 30 | 17 | 94.4419 | 0
2024-03-08 23:00 | 22.2 | 82 | 4.76 | 0 | 26 | 30 | 17 | 96.5971 | 0
2024-03-09 | 21.4 | 87 | 4.14 | 0 | 26 | 30 | 17 | 91.1421 | 0
2024-03-09 01:00 | 21.1 | 87 | 3.64 | 0 | 26 | 30 | 17 | 87.7362 | 0
2024-03-09 02:00 | 21.2 | 85 | 2.64 | 0 | 26 | 30 | 17 | 74.441 | 0
2024-03-09 03:00 | 21.5 | 82 | 0.2 | 0 | 26 | 30 | 17 | 37.0507 | 0
2024-03-09 04:00 | 20.8 | 84 | 2.89 | 0 | 26 | 30 | 17 | 82.7726 | 0
2024-03-09 05:00 | 19.8 | 88 | 3.24 | 0 | 26 | 30 | 17 | 93.4083 | 0
2024-03-09 06:00 | 19.9 | 90 | 4.02 | 0 | 26 | 30 | 17 | 102.4082 | 0
2024-03-09 07:00 | 20 | 90 | 3.54 | 2 | 26 | 30 | 17 | 93.8227 | 0
2024-03-09 08:00 | 20 | 92 | 4.12 | 29 | 26 | 30 | 17 | 96.4291 | 0
2024-03-09 09:00 | 20.1 | 90 | 5.02 | 41 | 26 | 30 | 17 | 108.9734 | 0
2024-03-09 10:00 | 20.6 | 89 | 4.05 | 61 | 26 | 30 | 17 | 88.1306 | 0
2024-03-09 11:00 | 21.2 | 89 | 6.35 | 166 | 26 | 30 | 17 | 95.2365 | 0
2024-03-09 12:00 | 21.2 | 86 | 4.18 | 88 | 26 | 30 | 17 | 83.4081 | 0
2024-03-09 13:00 | 22.4 | 84 | 5.12 | 257 | 26 | 30 | 17 | 60.3291 | 0
2024-03-09 14:00 | 24.3 | 77 | 5.08 | 626 | 26 | 30 | 17 | 0 | 0
2024-03-09 15:00 | 23.6 | 78 | 5.03 | 186 | 26 | 30 | 17 | 63.2881 | 0
2024-03-09 16:00 | 24.2 | 77 | 4.34 | 187 | 26 | 30 | 17 | 50.1523 | 0
2024-03-09 17:00 | 20.4 | 80 | 5.8 | 83 | 26 | 30 | 17 | 125.7565 | 0
2024-03-09 18:00 | 19.8 | 83 | 4.84 | 35 | 26 | 30 | 17 | 120.4526 | 0
2024-03-09 19:00 | 19.7 | 85 | 4.68 | 6 | 26 | 30 | 17 | 120.3135 | 0
2024-03-09 20:00 | 19.7 | 87 | 4.33 | 0 | 26 | 30 | 17 | 113.0404 | 0
2024-03-09 21:00 | 19.6 | 84 | 5 | 0 | 26 | 30 | 17 | 128.7239 | 0
2024-03-09 22:00 | 18.9 | 85 | 3.51 | 0 | 26 | 30 | 17 | 109.5608 | 0
2024-03-09 23:00 | 18.4 | 87 | 3.07 | 0 | 26 | 30 | 17 | 103.8373 | 0
2024-03-10 | 18.2 | 89 | 2.91 | 0 | 26 | 30 | 17 | 100.6595 | 0
2024-03-10 01:00 | 17.9 | 91 | 2.61 | 0 | 26 | 30 | 17 | 95.5088 | 0
2024-03-10 02:00 | 17.6 | 92 | 2.44 | 0 | 26 | 30 | 17 | 93.5783 | 0
2024-03-10 03:00 | 17.2 | 92 | 2.47 | 0 | 26 | 30 | 17 | 97.1911 | 0
2024-03-10 04:00 | 17.1 | 90 | 2.95 | 0 | 26 | 30 | 17 | 109.6886 | 0
2024-03-10 05:00 | 16.8 | 93 | 2.1 | 0 | 26 | 30 | 17 | 91.1975 | 0
2024-03-10 06:00 | 16.3 | 94 | 2.1 | 0 | 26 | 30 | 17 | 93.9197 | 0
2024-03-10 07:00 | 16.3 | 93 | 2.62 | 7 | 26 | 30 | 17 | 105.5457 | 0
2024-03-10 08:00 | 18.1 | 88 | 2.43 | 130 | 26 | 30 | 17 | 75.0722 | 0
2024-03-10 09:00 | 20 | 84 | 1.77 | 345 | 26 | 30 | 17 | 22.5075 | 0
2024-03-10 10:00 | 21.7 | 81 | 2.06 | 558 | 26 | 30 | 17 | 0 | 0
2024-03-10 11:00 | 22.8 | 75 | 2.38 | 731 | 26 | 30 | 17 | 0 | 0
2024-03-10 12:00 | 23.5 | 73 | 2.6 | 843 | 26 | 30 | 17 | 0 | 0
2024-03-10 13:00 | 23.8 | 74 | 3.42 | 880 | 26 | 30 | 17 | 0 | 0
2024-03-10 14:00 | 23.5 | 74 | 4.2 | 841 | 26 | 30 | 17 | 0 | 0
2024-03-10 15:00 | 23.3 | 72 | 4.29 | 730 | 26 | 30 | 17 | 0 | 0
2024-03-10 16:00 | 22.9 | 74 | 3.81 | 559 | 26 | 30 | 17 | 12.6997 | 0
2024-03-10 17:00 | 22.3 | 77 | 3.45 | 343 | 26 | 30 | 17 | 38.9088 | 0
2024-03-10 18:00 | 21 | 87 | 1.88 | 127 | 26 | 30 | 17 | 45.0855 | 0
2024-03-10 19:00 | 19.6 | 90 | 1.27 | 7 | 26 | 30 | 17 | 56.9339 | 0
2024-03-10 20:00 | 19.9 | 89 | 0.5 | 0 | 26 | 30 | 17 | 41.7326 | 0
2024-03-10 21:00 | 18.4 | 94 | 1.2 | 0 | 26 | 30 | 17 | 60.8686 | 0
2024-03-10 22:00 | 16.8 | 98 | 2.01 | 0 | 26 | 30 | 17 | 86.107 | 0
2024-03-10 23:00 | 16.6 | 98 | 2.51 | 0 | 26 | 30 | 17 | 98.2973 | 0
2024-03-11 | 15.7 | 100 | 2.56 | 0 | 26 | 30 | 17 | 104.8468 | 0
2024-03-11 01:00 | 14.9 | 100 | 2.33 | 0 | 26 | 30 | 17 | 105.3089 | 0
2024-03-11 02:00 | 14.1 | 100 | 1.62 | 0 | 26 | 30 | 17 | 91.9506 | 0
2024-03-11 03:00 | 13.4 | 100 | 1.7 | 0 | 26 | 30 | 17 | 98.0885 | 0
2024-03-11 04:00 | 12.6 | 100 | 1.56 | 0 | 26 | 30 | 17 | 98.2315 | 0
2024-03-11 05:00 | 14 | 99 | 1.56 | 0 | 26 | 30 | 17 | 91.2478 | 0
2024-03-11 06:00 | 14.5 | 100 | 1.63 | 0 | 26 | 30 | 17 | 89.991 | 0
2024-03-11 07:00 | 14.5 | 98 | 1.7 | 7 | 26 | 30 | 17 | 91.8551 | 0
2024-03-11 08:00 | 15.4 | 98 | 1.75 | 98 | 26 | 30 | 17 | 75.6354 | 0
2024-03-11 09:00 | 17.6 | 98 | 1.88 | 236 | 26 | 30 | 17 | 46.1186 | 0
2024-03-11 10:00 | 20.7 | 89 | 1.57 | 487 | 26 | 30 | 17 | 0 | 0
2024-03-11 11:00 | 24.3 | 62 | 1.21 | 749 | 26 | 30 | 17 | 0 | 23.2159
2024-03-11 12:00 | 26.5 | 45 | 1.52 | 864 | 26 | 30 | 17 | 0 | 26.2512
2024-03-11 13:00 | 27.8 | 33 | 1.7 | 901 | 26 | 30 | 17 | 0 | 19.7823
2024-03-11 14:00 | 28.4 | 29 | 1.4 | 861 | 26 | 30 | 17 | 0 | 24.5427
2024-03-11 15:00 | 27.8 | 38 | 1.78 | 744 | 26 | 30 | 17 | 0 | 1.1579
2024-03-11 16:00 | 26.2 | 60 | 2.28 | 564 | 26 | 30 | 17 | 0 | 0
2024-03-11 17:00 | 24.3 | 65 | 2.35 | 348 | 26 | 30 | 17 | 18.7019 | 0
2024-03-11 18:00 | 21.9 | 83 | 2.1 | 129 | 26 | 30 | 17 | 45.0344 | 0
2024-03-11 19:00 | 19.7 | 89 | 2.34 | 7 | 26 | 30 | 17 | 77.1083 | 0
2024-03-11 20:00 | 18.9 | 88 | 2.56 | 0 | 26 | 30 | 17 | 89.112 | 0
2024-03-11 21:00 | 18.5 | 88 | 3.2 | 0 | 26 | 30 | 17 | 104.5198 | 0
2024-03-11 22:00 | 18.2 | 87 | 3.67 | 0 | 26 | 30 | 17 | 117.08 | 0
2024-03-11 23:00 | 18 | 87 | 4.25 | 0 | 26 | 30 | 17 | 129.9121 | 0
2024-03-12 | 18 | 80 | 4.7 | 0 | 26 | 30 | 17 | 146.4816 | 0
2024-03-12 01:00 | 17.9 | 72 | 4.81 | 0 | 26 | 30 | 17 | 159.2711 | 0
2024-03-12 02:00 | 18.3 | 68 | 5.32 | 0 | 26 | 30 | 17 | 170.7138 | 0
2024-03-12 03:00 | 19.1 | 67 | 6.31 | 0 | 26 | 30 | 17 | 182.5471 | 0
2024-03-12 04:00 | 19 | 69 | 6.15 | 0 | 26 | 30 | 17 | 177.6579 | 0
2024-03-12 05:00 | 20.4 | 67 | 5.98 | 0 | 26 | 30 | 17 | 160.857 | 0
2024-03-12 06:00 | 20.2 | 75 | 6.35 | 0 | 26 | 30 | 17 | 156.2815 | 0
2024-03-12 07:00 | 22.1 | 69 | 6.31 | 9 | 26 | 30 | 17 | 139.5963 | 0
2024-03-12 08:00 | 22 | 77 | 5.66 | 117 | 26 | 30 | 17 | 103.0012 | 0
2024-03-12 09:00 | 23.2 | 78 | 4.74 | 320 | 26 | 30 | 17 | 47.12 | 0
2024-03-12 10:00 | 24 | 59 | 6.66 | 569 | 26 | 30 | 17 | 63.4083 | 0
2024-03-12 11:00 | 23.8 | 69 | 7.03 | 760 | 26 | 30 | 17 | 22.924 | 0
2024-03-12 12:00 | 23.9 | 63 | 7.89 | 879 | 26 | 30 | 17 | 29.5402 | 0
2024-03-12 13:00 | 23.9 | 64 | 8.02 | 924 | 26 | 30 | 17 | 22.5662 | 0
2024-03-12 14:00 | 23.9 | 60 | 7.7 | 875 | 26 | 30 | 17 | 34.9887 | 0
2024-03-12 15:00 | 23.5 | 62 | 7.12 | 753 | 26 | 30 | 17 | 45.1196 | 0
2024-03-12 16:00 | 22.7 | 66 | 7.23 | 576 | 26 | 30 | 17 | 73.4103 | 0
2024-03-12 17:00 | 22.2 | 69 | 6.52 | 355 | 26 | 30 | 17 | 94.4894 | 0
2024-03-12 18:00 | 20.7 | 73 | 6.07 | 135 | 26 | 30 | 17 | 130.4163 | 0
2024-03-12 19:00 | 19.6 | 72 | 5.97 | 8 | 26 | 30 | 17 | 161.4099 | 0
2024-03-12 20:00 | 19.2 | 73 | 5.36 | 0 | 26 | 30 | 17 | 154.8185 | 0
2024-03-12 21:00 | 18.6 | 79 | 4.08 | 0 | 26 | 30 | 17 | 129.5603 | 0
2024-03-12 22:00 | 17.3 | 87 | 2.52 | 0 | 26 | 30 | 17 | 101.1763 | 0
2024-03-12 23:00 | 16.7 | 88 | 2.42 | 0 | 26 | 30 | 17 | 102.5086 | 0
2024-03-13 | 16.6 | 89 | 3.08 | 0 | 26 | 30 | 17 | 117.3694 | 0
2024-03-13 01:00 | 15.6 | 91 | 3.52 | 0 | 26 | 30 | 17 | 133.9251 | 0
2024-03-13 02:00 | 14.8 | 94 | 3.6 | 0 | 26 | 30 | 17 | 140.2698 | 0
2024-03-13 03:00 | 14.8 | 95 | 3.24 | 0 | 26 | 30 | 17 | 131.1005 | 0
2024-03-13 04:00 | 14.6 | 95 | 2.66 | 0 | 26 | 30 | 17 | 118.6354 | 0
2024-03-13 05:00 | 15.7 | 93 | 2.42 | 0 | 26 | 30 | 17 | 106.2168 | 0
2024-03-13 06:00 | 15.1 | 96 | 3.04 | 0 | 26 | 30 | 17 | 123.2534 | 0
2024-03-13 07:00 | 15.5 | 94 | 2.91 | 10 | 26 | 30 | 17 | 117.172 | 0
2024-03-13 08:00 | 17.3 | 89 | 2.14 | 141 | 26 | 30 | 17 | 72.2677 | 0
2024-03-13 09:00 | 19.7 | 84 | 1.49 | 360 | 26 | 30 | 17 | 16.6226 | 0
2024-03-13 10:00 | 21.4 | 78 | 0.64 | 577 | 26 | 30 | 17 | 0 | 15.8234
2024-03-13 11:00 | 23.3 | 71 | 2.1 | 752 | 26 | 30 | 17 | 0 | 0
2024-03-13 12:00 | 24.5 | 68 | 2.75 | 863 | 26 | 30 | 17 | 0 | 1.4254
2024-03-13 13:00 | 26.8 | 51 | 3.42 | 894 | 26 | 30 | 17 | 0 | 0
2024-03-13 14:00 | 27.3 | 46 | 5.3 | 854 | 26 | 30 | 17 | 0 | 0
2024-03-13 15:00 | 27.1 | 44 | 5.76 | 742 | 26 | 30 | 17 | 23.2125 | 0
2024-03-13 16:00 | 26.6 | 45 | 5.63 | 570 | 26 | 30 | 17 | 47.9877 | 0
2024-03-13 17:00 | 25.2 | 65 | 3.18 | 349 | 26 | 30 | 17 | 22.8031 | 0
2024-03-13 18:00 | 23 | 79 | 2.56 | 132 | 26 | 30 | 17 | 46.3292 | 0
2024-03-13 19:00 | 20.6 | 87 | 2.55 | 8 | 26 | 30 | 17 | 75.0761 | 0
2024-03-13 20:00 | 19.4 | 91 | 2.45 | 0 | 26 | 30 | 17 | 80.6981 | 0
2024-03-13 21:00 | 18.7 | 94 | 2.6 | 0 | 26 | 30 | 17 | 86.5287 | 0
2024-03-13 22:00 | 18.5 | 97 | 2.72 | 0 | 26 | 30 | 17 | 87.8398 | 0
2024-03-13 23:00 | 17.9 | 96 | 2.64 | 0 | 26 | 30 | 17 | 92.1705 | 0
2024-03-14 | 16.8 | 93 | 2.38 | 0 | 26 | 30 | 17 | 97.4638 | 0
2024-03-14 01:00 | 16 | 87 | 2.8 | 0 | 26 | 30 | 17 | 117.205 | 0
2024-03-14 02:00 | 15.1 | 86 | 2.6 | 0 | 26 | 30 | 17 | 119.4054 | 0
2024-03-14 03:00 | 15.1 | 85 | 3.18 | 0 | 26 | 30 | 17 | 134.7453 | 0
2024-03-14 04:00 | 14.9 | 84 | 3.49 | 0 | 26 | 30 | 17 | 144.7715 | 0
2024-03-14 05:00 | 18.1 | 99 | 3.63 | 0 | 26 | 30 | 17 | 105.2994 | 0
2024-03-14 06:00 | 17.3 | 92 | 3.01 | 0 | 26 | 30 | 17 | 107.6348 | 0
2024-03-14 07:00 | 16.7 | 94 | 3.21 | 10 | 26 | 30 | 17 | 113.8271 | 0
2024-03-14 08:00 | 18.8 | 90 | 2.82 | 144 | 26 | 30 | 17 | 73.6401 | 0
2024-03-14 09:00 | 21.1 | 84 | 2.47 | 365 | 26 | 30 | 17 | 24.275 | 0
2024-03-14 10:00 | 23.6 | 74 | 2.72 | 583 | 26 | 30 | 17 | 0 | 0
2024-03-14 11:00 | 26.2 | 49 | 3.61 | 759 | 26 | 30 | 17 | 0 | 0
2024-03-14 12:00 | 27.7 | 40 | 4.22 | 873 | 26 | 30 | 17 | 0 | 0
2024-03-14 13:00 | 28.1 | 40 | 3.54 | 906 | 26 | 30 | 17 | 0 | 0
2024-03-14 14:00 | 28.2 | 40 | 3.22 | 859 | 26 | 30 | 17 | 0 | 0
2024-03-14 15:00 | 28.3 | 39 | 2.34 | 741 | 26 | 30 | 17 | 0 | 0
2024-03-14 16:00 | 27.6 | 41 | 1.87 | 564 | 26 | 30 | 17 | 0 | 0
2024-03-14 17:00 | 25.5 | 67 | 2.83 | 347 | 26 | 30 | 17 | 13.3009 | 0
2024-03-14 18:00 | 22.7 | 81 | 2.79 | 131 | 26 | 30 | 17 | 49.9885 | 0
2024-03-14 19:00 | 21.1 | 89 | 2.97 | 8 | 26 | 30 | 17 | 75.0622 | 0
2024-03-14 20:00 | 20.1 | 93 | 2.22 | 0 | 26 | 30 | 17 | 69.7189 | 0
2024-03-14 21:00 | 21.2 | 91 | 0.5 | 0 | 26 | 30 | 17 | 35.9397 | 0
2024-03-14 22:00 | 20.6 | 94 | 0.7 | 0 | 26 | 30 | 17 | 39.7452 | 0
2024-03-14 23:00 | 18 | 98 | 2 | 0 | 26 | 30 | 17 | 77.6568 | 0
2024-03-15 | 17.9 | 99 | 2.82 | 0 | 26 | 30 | 17 | 93.0857 | 0
2024-03-15 01:00 | 17.3 | 98 | 2.85 | 0 | 26 | 30 | 17 | 99.5682 | 0
2024-03-15 02:00 | 17 | 94 | 2.82 | 0 | 26 | 30 | 17 | 104.6044 | 0
2024-03-15 03:00 | 16.6 | 92 | 2.8 | 0 | 26 | 30 | 17 | 108.9025 | 0
2024-03-15 04:00 | 16.4 | 91 | 2.96 | 0 | 26 | 30 | 17 | 114.7654 | 0
2024-03-15 05:00 | 17.2 | 92 | 3 | 0 | 26 | 30 | 17 | 108.2688 | 0
2024-03-15 06:00 | 17.2 | 87 | 3.22 | 0 | 26 | 30 | 17 | 117.0664 | 0
2024-03-15 07:00 | 17.4 | 81 | 3.1 | 11 | 26 | 30 | 17 | 116.5097 | 0
2024-03-15 08:00 | 19.5 | 74 | 2.51 | 145 | 26 | 30 | 17 | 75.6611 | 0
2024-03-15 09:00 | 22.3 | 67 | 2.21 | 360 | 26 | 30 | 17 | 27.0454 | 0
2024-03-15 10:00 | 25 | 60 | 1.97 | 575 | 26 | 30 | 17 | 0 | 0
2024-03-15 11:00 | 27.2 | 55 | 2.66 | 745 | 26 | 30 | 17 | 0 | 0
2024-03-15 12:00 | 28.1 | 53 | 3.65 | 848 | 26 | 30 | 17 | 0 | 0
2024-03-15 13:00 | 28 | 58 | 4.79 | 885 | 26 | 30 | 17 | 0 | 0
2024-03-15 14:00 | 26.2 | 61 | 7.16 | 827 | 26 | 30 | 17 | 0 | 0
2024-03-15 15:00 | 25 | 67 | 5.48 | 425 | 26 | 30 | 17 | 38.1177 | 0
2024-03-15 16:00 | 24.4 | 68 | 4.15 | 239 | 26 | 30 | 17 | 53.3478 | 0
2024-03-15 17:00 | 24.2 | 68 | 3.68 | 141 | 26 | 30 | 17 | 62.6873 | 0
2024-03-15 18:00 | 23 | 78 | 1.79 | 125 | 26 | 30 | 17 | 37.2145 | 0
2024-03-15 19:00 | 23 | 72 | 0.81 | 8 | 26 | 30 | 17 | 39.5106 | 0
2024-03-15 20:00 | 21.4 | 80 | 1.24 | 0 | 26 | 30 | 17 | 52.9558 | 0
2024-03-15 21:00 | 19.7 | 86 | 2.38 | 0 | 26 | 30 | 17 | 81.2184 | 0
2024-03-15 22:00 | 19.5 | 85 | 3 | 0 | 26 | 30 | 17 | 94.9479 | 0
2024-03-15 23:00 | 18.6 | 88 | 2.4 | 0 | 26 | 30 | 17 | 88.299 | 0
2024-03-16 | 17.9 | 90 | 1.51 | 0 | 26 | 30 | 17 | 72.6349 | 0
2024-03-16 01:00 | 17.6 | 90 | 2.62 | 0 | 26 | 30 | 17 | 98.8156 | 0
2024-03-16 02:00 | 17.4 | 90 | 2.65 | 0 | 26 | 30 | 17 | 100.9846 | 0
2024-03-16 03:00 | 17.3 | 89 | 2.81 | 0 | 26 | 30 | 17 | 105.9262 | 0
2024-03-16 04:00 | 16.9 | 90 | 2.22 | 0 | 26 | 30 | 17 | 95.1764 | 0
2024-03-16 05:00 | 17.7 | 90 | 2.1 | 0 | 26 | 30 | 17 | 87.0537 | 0
2024-03-16 06:00 | 17.8 | 88 | 2.42 | 0 | 26 | 30 | 17 | 94.6174 | 0
2024-03-16 07:00 | 18.3 | 84 | 2.77 | 12 | 26 | 30 | 17 | 99.6679 | 0
2024-03-16 08:00 | 20.6 | 75 | 3.66 | 144 | 26 | 30 | 17 | 87.8215 | 0
2024-03-16 09:00 | 23.7 | 70 | 2.86 | 358 | 26 | 30 | 17 | 24.1406 | 0
2024-03-16 10:00 | 25.9 | 59 | 2.96 | 563 | 26 | 30 | 17 | 0 | 0
2024-03-16 11:00 | 28 | 57 | 3.26 | 733 | 26 | 30 | 17 | 0 | 0
2024-03-16 12:00 | 29.7 | 52 | 3.53 | 842 | 26 | 30 | 17 | 0 | 4.4398
2024-03-16 13:00 | 30.6 | 50 | 3.3 | 875 | 26 | 30 | 17 | 0 | 18.2285
2024-03-16 14:00 | 30.8 | 52 | 2.94 | 833 | 26 | 30 | 17 | 0 | 25.0884
2024-03-16 15:00 | 29.7 | 62 | 3.86 | 718 | 26 | 30 | 17 | 0 | 2.288
2024-03-16 16:00 | 28 | 66 | 3.89 | 546 | 26 | 30 | 17 | 0 | 0
2024-03-16 17:00 | 27.2 | 67 | 3.58 | 337 | 26 | 30 | 17 | 5.4934 | 0
2024-03-16 18:00 | 25.1 | 75 | 3.3 | 127 | 26 | 30 | 17 | 40.9262 | 0
2024-03-16 19:00 | 23.3 | 81 | 2.55 | 8 | 26 | 30 | 17 | 58.2491 | 0
2024-03-16 20:00 | 22.4 | 82 | 2.48 | 0 | 26 | 30 | 17 | 64.9943 | 0
2024-03-16 21:00 | 21.9 | 81 | 3.01 | 0 | 26 | 30 | 17 | 77.9454 | 0
2024-03-16 22:00 | 21.5 | 82 | 3.31 | 0 | 26 | 30 | 17 | 84.9285 | 0
2024-03-16 23:00 | 21.1 | 81 | 3.75 | 0 | 26 | 30 | 17 | 96.63 | 0
2024-03-17 | 21.3 | 77 | 3.9 | 0 | 26 | 30 | 17 | 101.9118 | 0
2024-03-17 01:00 | 20.9 | 78 | 3.42 | 0 | 26 | 30 | 17 | 96.9072 | 0
2024-03-17 02:00 | 20.4 | 80 | 3.23 | 0 | 26 | 30 | 17 | 96.0846 | 0
2024-03-17 03:00 | 20.2 | 79 | 3.29 | 0 | 26 | 30 | 17 | 99.9836 | 0
2024-03-17 04:00 | 19.9 | 78 | 3.22 | 0 | 26 | 30 | 17 | 102.4089 | 0
2024-03-17 05:00 | 19.8 | 82 | 2.78 | 0 | 26 | 30 | 17 | 91.2497 | 0
2024-03-17 06:00 | 19.6 | 82 | 2.97 | 0 | 26 | 30 | 17 | 96.4063 | 0
2024-03-17 07:00 | 19.8 | 82 | 2.76 | 13 | 26 | 30 | 17 | 89.1265 | 0
2024-03-17 08:00 | 22.3 | 76 | 1.92 | 148 | 26 | 30 | 17 | 42.6249 | 0
2024-03-17 09:00 | 26 | 66 | 1.9 | 359 | 26 | 30 | 17 | 0 | 0
2024-03-17 10:00 | 28.1 | 54 | 3.83 | 561 | 26 | 30 | 17 | 0 | 0
2024-03-17 11:00 | 30 | 46 | 3.73 | 739 | 26 | 30 | 17 | 0 | 0
2024-03-17 12:00 | 31.2 | 43 | 4.24 | 845 | 26 | 30 | 17 | 0 | 0
2024-03-17 13:00 | 31.6 | 42 | 3.42 | 880 | 26 | 30 | 17 | 0 | 9.4171
2024-03-17 14:00 | 31.3 | 49 | 2.62 | 836 | 26 | 30 | 17 | 0 | 30.6567
2024-03-17 15:00 | 30.3 | 57 | 3.08 | 723 | 26 | 30 | 17 | 0 | 12.2004
2024-03-17 16:00 | 29.1 | 59 | 3.18 | 547 | 26 | 30 | 17 | 0 | 0
2024-03-17 17:00 | 27.9 | 60 | 2.83 | 339 | 26 | 30 | 17 | 2.9386 | 0
2024-03-17 18:00 | 25.9 | 72 | 1.79 | 118 | 26 | 30 | 17 | 23.2846 | 0
2024-03-17 19:00 | 24.1 | 80 | 1.94 | 8 | 26 | 30 | 17 | 45.4136 | 0
2024-03-17 20:00 | 23.8 | 80 | 2.6 | 0 | 26 | 30 | 17 | 56.6594 | 0
2024-03-17 21:00 | 23.5 | 82 | 3.09 | 0 | 26 | 30 | 17 | 62.6368 | 0
2024-03-17 22:00 | 23.3 | 83 | 3.32 | 0 | 26 | 30 | 17 | 65.9231 | 0
2024-03-17 23:00 | 22.4 | 86 | 2.21 | 0 | 26 | 30 | 17 | 57.4925 | 0
2024-03-18 | 22.1 | 87 | 1.73 | 0 | 26 | 30 | 17 | 52.2665 | 0
2024-03-18 01:00 | 22.5 | 82 | 1.2 | 0 | 26 | 30 | 17 | 45.005 | 0
2024-03-18 02:00 | 23.3 | 75 | 0.63 | 0 | 26 | 30 | 17 | 34.2351 | 0
2024-03-18 03:00 | 21.5 | 82 | 1.48 | 0 | 26 | 30 | 17 | 55.6493 | 0
2024-03-18 04:00 | 20.3 | 87 | 2.51 | 0 | 26 | 30 | 17 | 77.9435 | 0
2024-03-18 05:00 | 20.3 | 89 | 2.56 | 0 | 26 | 30 | 17 | 76.9855 | 0
2024-03-18 06:00 | 19.5 | 92 | 2.55 | 0 | 26 | 30 | 17 | 80.7848 | 0
2024-03-18 07:00 | 19.3 | 93 | 2.33 | 14 | 26 | 30 | 17 | 75.8783 | 0
2024-03-18 08:00 | 21.4 | 85 | 1.9 | 157 | 26 | 30 | 17 | 40.0918 | 0
2024-03-18 09:00 | 24.7 | 71 | 1.68 | 380 | 26 | 30 | 17 | 0 | 0
2024-03-18 10:00 | 27 | 56 | 1.77 | 598 | 26 | 30 | 17 | 0 | 0
2024-03-18 11:00 | 28.7 | 50 | 2.28 | 771 | 26 | 30 | 17 | 0 | 10.5986
2024-03-18 12:00 | 29.7 | 47 | 1.91 | 878 | 26 | 30 | 17 | 0 | 37.4211
2024-03-18 13:00 | 30 | 48 | 3.04 | 910 | 26 | 30 | 17 | 0 | 18.9619
2024-03-18 14:00 | 28.9 | 52 | 5.05 | 864 | 26 | 30 | 17 | 0 | 0
2024-03-18 15:00 | 27.9 | 49 | 5.06 | 749 | 26 | 30 | 17 | 0 | 0
2024-03-18 16:00 | 26.6 | 60 | 5.26 | 573 | 26 | 30 | 17 | 9.7469 | 0
2024-03-18 17:00 | 25 | 68 | 5.61 | 306 | 26 | 30 | 17 | 53.5101 | 0
2024-03-18 18:00 | 23.7 | 79 | 3.61 | 98 | 26 | 30 | 17 | 57.0718 | 0
2024-03-18 19:00 | 22.2 | 87 | 1.94 | 9 | 26 | 30 | 17 | 53.2969 | 0
2024-03-18 20:00 | 21.7 | 88 | 1.12 | 0 | 26 | 30 | 17 | 44.6413 | 0
2024-03-18 21:00 | 22.2 | 84 | 0.45 | 0 | 26 | 30 | 17 | 34.2589 | 0
2024-03-18 22:00 | 20.8 | 90 | 1.25 | 0 | 26 | 30 | 17 | 50.7886 | 0
2024-03-18 23:00 | 19.6 | 93 | 2.53 | 0 | 26 | 30 | 17 | 78.778 | 0
2024-03-19 | 19.2 | 93 | 2.86 | 0 | 26 | 30 | 17 | 87.6938 | 0
2024-03-19 01:00 | 18.4 | 94 | 2.31 | 0 | 26 | 30 | 17 | 83.5166 | 0
2024-03-19 02:00 | 19.3 | 88 | 1.02 | 0 | 26 | 30 | 17 | 55.0056 | 0
2024-03-19 03:00 | 19.4 | 86 | 0.41 | 0 | 26 | 30 | 17 | 44.2126 | 0
2024-03-19 04:00 | 19.7 | 84 | 0.5 | 0 | 26 | 30 | 17 | 44.0574 | 0
2024-03-19 05:00 | 19 | 82 | 1.1 | 0 | 26 | 30 | 17 | 61.057 | 0
2024-03-19 06:00 | 18.5 | 86 | 1.21 | 0 | 26 | 30 | 17 | 64.3518 | 0
2024-03-19 07:00 | 18.5 | 89 | 1.39 | 15 | 26 | 30 | 17 | 65.03 | 0
2024-03-19 08:00 | 20.8 | 77 | 1.82 | 150 | 26 | 30 | 17 | 49.6298 | 0
2024-03-19 09:00 | 23 | 69 | 1.34 | 356 | 26 | 30 | 17 | 4.9896 | 0
2024-03-19 10:00 | 25.6 | 61 | 1.55 | 523 | 26 | 30 | 17 | 0 | 0
2024-03-19 11:00 | 28.1 | 51 | 0.92 | 679 | 26 | 30 | 17 | 0 | 34.3794
2024-03-19 12:00 | 29.7 | 46 | 0.63 | 776 | 26 | 30 | 17 | 0 | 61.168
2024-03-19 13:00 | 31.1 | 42 | 0.89 | 853 | 26 | 30 | 17 | 0 | 65.7049
2024-03-19 14:00 | 31.6 | 44 | 2.05 | 789 | 26 | 30 | 17 | 0 | 30.7063
2024-03-19 15:00 | 31.5 | 47 | 3.07 | 639 | 26 | 30 | 17 | 0 | 0
2024-03-19 16:00 | 31.2 | 47 | 3.32 | 528 | 26 | 30 | 17 | 0 | 0
2024-03-19 17:00 | 28.5 | 56 | 4.52 | 339 | 26 | 30 | 17 | 19.8003 | 0
2024-03-19 18:00 | 26.7 | 69 | 3.42 | 129 | 26 | 30 | 17 | 34.2509 | 0
2024-03-19 19:00 | 24.9 | 77 | 4.01 | 9 | 26 | 30 | 17 | 62.6841 | 0
2024-03-19 20:00 | 24.5 | 79 | 3.62 | 0 | 26 | 30 | 17 | 61.727 | 0
2024-03-19 21:00 | 24.4 | 76 | 3.32 | 0 | 26 | 30 | 17 | 64.011 | 0
2024-03-19 22:00 | 24.1 | 76 | 3.12 | 0 | 26 | 30 | 17 | 64.7383 | 0
2024-03-19 23:00 | 23.7 | 77 | 2.9 | 0 | 26 | 30 | 17 | 64.6272 | 0
2024-03-20 | 23.4 | 79 | 2.72 | 0 | 26 | 30 | 17 | 62.7695 | 0
2024-03-20 01:00 | 23.2 | 79 | 2.59 | 0 | 26 | 30 | 17 | 62.8484 | 0
2024-03-20 02:00 | 23.1 | 76 | 3.16 | 0 | 26 | 30 | 17 | 74.7685 | 0
2024-03-20 03:00 | 23.1 | 75 | 3.01 | 0 | 26 | 30 | 17 | 73.9318 | 0
2024-03-20 04:00 | 22.3 | 80 | 2.38 | 0 | 26 | 30 | 17 | 66.3233 | 0
2024-03-20 05:00 | 23.6 | 71 | 4.5 | 0 | 26 | 30 | 17 | 94.0977 | 0
2024-03-20 06:00 | 24.1 | 68 | 5.6 | 0 | 26 | 30 | 17 | 106.7509 | 0
2024-03-20 07:00 | 25.1 | 55 | 8.16 | 16 | 26 | 30 | 17 | 151.0594 | 0
2024-03-20 08:00 | 26.7 | 40 | 8.88 | 147 | 26 | 30 | 17 | 162.1411 | 0
2024-03-20 09:00 | 28.9 | 36 | 8.54 | 372 | 26 | 30 | 17 | 108.8861 | 0
2024-03-20 10:00 | 30.9 | 34 | 8.56 | 572 | 26 | 30 | 17 | 60.5462 | 0
2024-03-20 11:00 | 32 | 34 | 8.54 | 667 | 26 | 30 | 17 | 31.1712 | 0
2024-03-20 12:00 | 32.7 | 34 | 7.52 | 718 | 26 | 30 | 17 | 5.1624 | 0
2024-03-20 13:00 | 29.4 | 53 | 6.42 | 463 | 26 | 30 | 17 | 13.9461 | 0
2024-03-20 14:00 | 29.7 | 49 | 6.22 | 824 | 26 | 30 | 17 | 0 | 0
2024-03-20 15:00 | 29.4 | 49 | 5.44 | 542 | 26 | 30 | 17 | 6.3893 | 0
2024-03-20 16:00 | 28.8 | 52 | 3.57 | 318 | 26 | 30 | 17 | 18.4398 | 0
2024-03-20 17:00 | 28.9 | 52 | 2.64 | 311 | 26 | 30 | 17 | 8.3397 | 0
2024-03-20 18:00 | 27.1 | 64 | 2.73 | 121 | 26 | 30 | 17 | 32.6389 | 0
2024-03-20 19:00 | 25 | 78 | 1.66 | 9 | 26 | 30 | 17 | 37.3652 | 0
2024-03-20 20:00 | 24.1 | 85 | 1.08 | 0 | 26 | 30 | 17 | 32.4412 | 0
2024-03-20 21:00 | 23.2 | 89 | 1.5 | 0 | 26 | 30 | 17 | 40.2546 | 0
2024-03-20 22:00 | 22.7 | 92 | 1.9 | 0 | 26 | 30 | 17 | 46.0609 | 0
2024-03-20 23:00 | 22.5 | 92 | 2.45 | 0 | 26 | 30 | 17 | 53.8106 | 0
2024-03-21 | 22.3 | 90 | 2.72 | 0 | 26 | 30 | 17 | 60.7309 | 0
2024-03-21 01:00 | 22.2 | 90 | 2.98 | 0 | 26 | 30 | 17 | 64.7066 | 0
2024-03-21 02:00 | 22 | 91 | 2.75 | 0 | 26 | 30 | 17 | 62.8163 | 0
2024-03-21 03:00 | 21.3 | 92 | 2.33 | 0 | 26 | 30 | 17 | 62.6027 | 0
2024-03-21 04:00 | 21.2 | 93 | 2.5 | 0 | 26 | 30 | 17 | 64.8381 | 0
2024-03-21 05:00 | 21.6 | 94 | 2.18 | 0 | 26 | 30 | 17 | 56.4059 | 0
2024-03-21 06:00 | 21.3 | 94 | 2.28 | 0 | 26 | 30 | 17 | 60.16 | 0
2024-03-21 07:00 | 21.8 | 94 | 2.42 | 17 | 26 | 30 | 17 | 55.3866 | 0
2024-03-21 08:00 | 23.6 | 87 | 2.47 | 161 | 26 | 30 | 17 | 27.6373 | 0
2024-03-21 09:00 | 24.8 | 77 | 3.41 | 377 | 26 | 30 | 17 | 8.496 | 0
2024-03-21 10:00 | 25.8 | 65 | 4.3 | 583 | 26 | 30 | 17 | 0 | 0
2024-03-21 11:00 | 26.4 | 60 | 5.19 | 753 | 26 | 30 | 17 | 0 | 0
2024-03-21 12:00 | 26.7 | 58 | 5 | 859 | 26 | 30 | 17 | 0 | 0
2024-03-21 13:00 | 27 | 54 | 5.58 | 893 | 26 | 30 | 17 | 0 | 0
2024-03-21 14:00 | 26.9 | 51 | 5.85 | 850 | 26 | 30 | 17 | 0 | 0
2024-03-21 15:00 | 26.6 | 53 | 5.82 | 732 | 26 | 30 | 17 | 10.1856 | 0
2024-03-21 16:00 | 26 | 55 | 5.57 | 566 | 26 | 30 | 17 | 32.5599 | 0
2024-03-21 17:00 | 24.7 | 62 | 5.08 | 355 | 26 | 30 | 17 | 56.4428 | 0
2024-03-21 18:00 | 23.3 | 73 | 4.43 | 141 | 26 | 30 | 17 | 74.4152 | 0
2024-03-21 19:00 | 22.3 | 80 | 3.41 | 10 | 26 | 30 | 17 | 79.5783 | 0
2024-03-21 20:00 | 21.4 | 83 | 3.07 | 0 | 26 | 30 | 17 | 81.2078 | 0
2024-03-21 21:00 | 20.5 | 87 | 2.87 | 0 | 26 | 30 | 17 | 82.106 | 0
2024-03-21 22:00 | 19.5 | 91 | 2.39 | 0 | 26 | 30 | 17 | 78.8597 | 0
2024-03-21 23:00 | 18.6 | 94 | 1.92 | 0 | 26 | 30 | 17 | 74.5748 | 0
2024-03-22 | 18.1 | 95 | 2.04 | 0 | 26 | 30 | 17 | 79.7267 | 0
2024-03-22 01:00 | 17.8 | 95 | 2.6 | 0 | 26 | 30 | 17 | 92.9872 | 0
2024-03-22 02:00 | 17.1 | 97 | 2.85 | 0 | 26 | 30 | 17 | 102.0382 | 0
2024-03-22 03:00 | 16.6 | 99 | 2.6 | 0 | 26 | 30 | 17 | 99.4781 | 0
2024-03-22 04:00 | 16.5 | 98 | 2.75 | 0 | 26 | 30 | 17 | 104.1326 | 0
2024-03-22 05:00 | 17.5 | 97 | 2.86 | 0 | 26 | 30 | 17 | 98.8793 | 0
2024-03-22 06:00 | 17.3 | 97 | 3.23 | 0 | 26 | 30 | 17 | 107.6914 | 0
2024-03-22 07:00 | 17.4 | 96 | 2.96 | 19 | 26 | 30 | 17 | 99.9127 | 0
2024-03-22 08:00 | 19.6 | 84 | 2.63 | 168 | 26 | 30 | 17 | 65.615 | 0
2024-03-22 09:00 | 22.4 | 71 | 2.59 | 389 | 26 | 30 | 17 | 25.3043 | 0
2024-03-22 10:00 | 24.6 | 60 | 3.01 | 600 | 26 | 30 | 17 | 0 | 0
2024-03-22 11:00 | 25.9 | 58 | 4.32 | 770 | 26 | 30 | 17 | 0 | 0
2024-03-22 12:00 | 26.3 | 60 | 5.7 | 875 | 26 | 30 | 17 | 0 | 0
2024-03-22 13:00 | 26.2 | 63 | 5.41 | 904 | 26 | 30 | 17 | 0 | 0
2024-03-22 14:00 | 26.4 | 61 | 4.74 | 857 | 26 | 30 | 17 | 0 | 0
2024-03-22 15:00 | 26.7 | 58 | 3.58 | 716 | 26 | 30 | 17 | 0 | 0
2024-03-22 16:00 | 26.4 | 61 | 3.54 | 533 | 26 | 30 | 17 | 0 | 0
2024-03-22 17:00 | 25.7 | 66 | 2.48 | 310 | 26 | 30 | 17 | 13.585 | 0
2024-03-22 18:00 | 24.7 | 70 | 2.05 | 130 | 26 | 30 | 17 | 35.5582 | 0
2024-03-22 19:00 | 23.2 | 85 | 1.21 | 10 | 26 | 30 | 17 | 37.9549 | 0
2024-03-22 20:00 | 22.4 | 88 | 1.03 | 0 | 26 | 30 | 17 | 39.4102 | 0
2024-03-22 21:00 | 21.9 | 88 | 1.33 | 0 | 26 | 30 | 17 | 46.8824 | 0
2024-03-22 22:00 | 21.1 | 88 | 1.72 | 0 | 26 | 30 | 17 | 58.1887 | 0
2024-03-22 23:00 | 20.9 | 87 | 1.71 | 0 | 26 | 30 | 17 | 60.0592 | 0
2024-03-23 | 20.8 | 86 | 1.3 | 0 | 26 | 30 | 17 | 53.9709 | 0
2024-03-23 01:00 | 20.4 | 88 | 1.3 | 0 | 26 | 30 | 17 | 55.0951 | 0
2024-03-23 02:00 | 21.3 | 91 | 3.33 | 0 | 26 | 30 | 17 | 76.837 | 0
2024-03-23 03:00 | 21.3 | 93 | 2.51 | 0 | 26 | 30 | 17 | 64.1047 | 0
2024-03-23 04:00 | 20.8 | 94 | 2.45 | 0 | 26 | 30 | 17 | 66.66 | 0
2024-03-23 05:00 | 22.7 | 93 | 2.61 | 0 | 26 | 30 | 17 | 52.6505 | 0
2024-03-23 06:00 | 22.8 | 92 | 3.99 | 0 | 26 | 30 | 17 | 66.0398 | 0
2024-03-23 07:00 | 23.3 | 88 | 2.9 | 9 | 26 | 30 | 17 | 54.1454 | 0
2024-03-23 08:00 | 24.5 | 79 | 1.55 | 97 | 26 | 30 | 17 | 26.7831 | 0
2024-03-23 09:00 | 24 | 78 | 4.2 | 50 | 26 | 30 | 17 | 67.983 | 0
2024-03-23 10:00 | 25.7 | 60 | 2.32 | 283 | 26 | 30 | 17 | 22.174 | 0
2024-03-23 11:00 | 27.3 | 55 | 2.25 | 570 | 26 | 30 | 17 | 0 | 0
2024-03-23 12:00 | 29.2 | 48 | 3.26 | 735 | 26 | 30 | 17 | 0 | 0
2024-03-23 13:00 | 30.7 | 40 | 3.89 | 762 | 26 | 30 | 17 | 0 | 0
2024-03-23 14:00 | 31.4 | 34 | 3.81 | 693 | 26 | 30 | 17 | 0 | 0
2024-03-23 15:00 | 31.8 | 33 | 2.73 | 669 | 26 | 30 | 17 | 0 | 0
2024-03-23 16:00 | 32.2 | 32 | 2.1 | 564 | 26 | 30 | 17 | 0 | 0
2024-03-23 17:00 | 32 | 32 | 1.17 | 349 | 26 | 30 | 17 | 0 | 0
2024-03-23 18:00 | 28.1 | 58 | 3.73 | 117 | 26 | 30 | 17 | 43.0107 | 0
2024-03-23 19:00 | 25.3 | 65 | 3.62 | 10 | 26 | 30 | 17 | 73.0858 | 0
2024-03-23 20:00 | 24.7 | 70 | 3.4 | 0 | 26 | 30 | 17 | 70.3349 | 0
2024-03-23 21:00 | 24.1 | 73 | 2.9 | 0 | 26 | 30 | 17 | 65.8587 | 0
2024-03-23 22:00 | 23.8 | 75 | 2.69 | 0 | 26 | 30 | 17 | 63.4347 | 0
2024-03-23 23:00 | 23.5 | 77 | 2.31 | 0 | 26 | 30 | 17 | 58.7464 | 0
2024-03-24 | 23.5 | 77 | 2.56 | 0 | 26 | 30 | 17 | 62.0707 | 0
2024-03-24 01:00 | 23.4 | 76 | 3.11 | 0 | 26 | 30 | 17 | 71.2871 | 0
2024-03-24 02:00 | 22.7 | 78 | 3.28 | 0 | 26 | 30 | 17 | 77.7294 | 0
2024-03-24 03:00 | 22.3 | 80 | 3.1 | 0 | 26 | 30 | 17 | 76.668 | 0
2024-03-24 04:00 | 21.9 | 80 | 3.26 | 0 | 26 | 30 | 17 | 82.7051 | 0
2024-03-24 05:00 | 23.7 | 77 | 0.81 | 0 | 26 | 30 | 17 | 35.0081 | 0
2024-03-24 06:00 | 23.5 | 84 | 4.31 | 0 | 26 | 30 | 17 | 72.4139 | 0
2024-03-24 07:00 | 23.7 | 81 | 4.03 | 15 | 26 | 30 | 17 | 69.8286 | 0
2024-03-24 08:00 | 25.4 | 71 | 3.02 | 163 | 26 | 30 | 17 | 35.8418 | 0
2024-03-24 09:00 | 27.3 | 56 | 4.46 | 329 | 26 | 30 | 17 | 34.3128 | 0
2024-03-24 10:00 | 28.3 | 48 | 4.48 | 301 | 26 | 30 | 17 | 44.0272 | 0
2024-03-24 11:00 | 30.7 | 39 | 4.94 | 663 | 26 | 30 | 17 | 0 | 0
2024-03-24 12:00 | 31.5 | 38 | 5.02 | 569 | 26 | 30 | 17 | 3.607 | 0
2024-03-24 13:00 | 31.9 | 38 | 3.42 | 432 | 26 | 30 | 17 | 1.0445 | 0
2024-03-24 14:00 | 33.4 | 32 | 2.38 | 524 | 26 | 30 | 17 | 0 | 0
2024-03-24 15:00 | 33.7 | 31 | 2.9 | 245 | 26 | 30 | 17 | 20.6345 | 0
2024-03-24 16:00 | 32.7 | 36 | 3.12 | 158 | 26 | 30 | 17 | 32.1716 | 0
2024-03-24 17:00 | 30.4 | 49 | 3.79 | 149 | 26 | 30 | 17 | 33.3681 | 0
2024-03-24 18:00 | 27.6 | 56 | 5.93 | 35 | 26 | 30 | 17 | 85.0711 | 0
2024-03-24 19:00 | 26.9 | 60 | 5.77 | 3 | 26 | 30 | 17 | 87.7383 | 0
2024-03-24 20:00 | 26.4 | 59 | 4.9 | 0 | 26 | 30 | 17 | 87.8522 | 0
2024-03-24 21:00 | 26 | 55 | 6.22 | 0 | 26 | 30 | 17 | 116.8439 | 0
2024-03-24 22:00 | 25.7 | 56 | 6.33 | 0 | 26 | 30 | 17 | 119.8188 | 0
2024-03-24 23:00 | 25.4 | 55 | 5.91 | 0 | 26 | 30 | 17 | 120.7358 | 0
2024-03-25 | 26.2 | 52 | 6.61 | 0 | 26 | 30 | 17 | 126.1302 | 0
2024-03-25 01:00 | 26.3 | 53 | 6.3 | 0 | 26 | 30 | 17 | 118.597 | 0
2024-03-25 02:00 | 26.2 | 54 | 7.43 | 0 | 26 | 30 | 17 | 130.565 | 0
2024-03-25 03:00 | 25.8 | 58 | 6.84 | 0 | 26 | 30 | 17 | 119.4926 | 0
2024-03-25 04:00 | 25.9 | 55 | 6.11 | 0 | 26 | 30 | 17 | 116.8376 | 0
2024-03-25 05:00 | 26.8 | 45 | 6.52 | 0 | 26 | 30 | 17 | 134.7962 | 0
2024-03-25 06:00 | 26.8 | 40 | 7.03 | 0 | 26 | 30 | 17 | 154.9491 | 0
2024-03-25 07:00 | 26.6 | 41 | 7.71 | 16 | 26 | 30 | 17 | 162.2156 | 0
2024-03-25 08:00 | 27.3 | 43 | 7.91 | 112 | 26 | 30 | 17 | 136.4192 | 0
2024-03-25 09:00 | 28.7 | 42 | 7.93 | 327 | 26 | 30 | 17 | 90.5904 | 0
2024-03-25 10:00 | 29.2 | 41 | 8.58 | 466 | 26 | 30 | 17 | 74.594 | 0
2024-03-25 11:00 | 28.5 | 49 | 7.26 | 399 | 26 | 30 | 17 | 54.9367 | 0
2024-03-25 12:00 | 30.2 | 48 | 7.72 | 846 | 26 | 30 | 17 | 0 | 0
2024-03-25 13:00 | 30.3 | 48 | 7.71 | 540 | 26 | 30 | 17 | 14.8713 | 0
2024-03-25 14:00 | 31.7 | 44 | 6.6 | 540 | 26 | 30 | 17 | 0 | 0
2024-03-25 15:00 | 32.1 | 41 | 6.18 | 392 | 26 | 30 | 17 | 21.2312 | 0
2024-03-25 16:00 | 33.2 | 36 | 5.36 | 477 | 26 | 30 | 17 | 5.8592 | 0
2024-03-25 17:00 | 28.4 | 58 | 2.25 | 140 | 26 | 30 | 17 | 22.5558 | 0
2024-03-25 18:00 | 28 | 60 | 2 | 61 | 26 | 30 | 17 | 31.0394 | 0
2024-03-25 19:00 | 27.1 | 65 | 2.34 | 4 | 26 | 30 | 17 | 43.1311 | 0
2024-03-25 20:00 | 27.3 | 66 | 0.58 | 0 | 26 | 30 | 17 | 21.0759 | 0
2024-03-25 21:00 | 26.6 | 68 | 2.12 | 0 | 26 | 30 | 17 | 41.7653 | 0
2024-03-25 22:00 | 25.5 | 79 | 0.92 | 0 | 26 | 30 | 17 | 26.5718 | 0
2024-03-25 23:00 | 26.9 | 63 | 0.22 | 0 | 26 | 30 | 17 | 24.3792 | 0
2024-03-26 | 25.1 | 72 | 5.35 | 0 | 26 | 30 | 17 | 82.7482 | 0
2024-03-26 01:00 | 24.1 | 84 | 6.93 | 0 | 26 | 30 | 17 | 85.7938 | 0
2024-03-26 02:00 | 23.1 | 82 | 8.22 | 0 | 26 | 30 | 17 | 119.3934 | 0
2024-03-26 03:00 | 22.5 | 84 | 6.9 | 0 | 26 | 30 | 17 | 112.5841 | 0
2024-03-26 04:00 | 22.4 | 84 | 5.39 | 0 | 26 | 30 | 17 | 98.0289 | 0
2024-03-26 05:00 | 23.2 | 75 | 5.36 | 0 | 26 | 30 | 17 | 102.6755 | 0
2024-03-26 06:00 | 22.7 | 76 | 5.96 | 0 | 26 | 30 | 17 | 114.7913 | 0
2024-03-26 07:00 | 22.5 | 76 | 5.09 | 13 | 26 | 30 | 17 | 104.8663 | 0
2024-03-26 08:00 | 23.3 | 76 | 5.35 | 100 | 26 | 30 | 17 | 85.9372 | 0
2024-03-26 09:00 | 24 | 69 | 5.67 | 265 | 26 | 30 | 17 | 71.1731 | 0
2024-03-26 10:00 | 24 | 66 | 6.45 | 335 | 26 | 30 | 17 | 77.1437 | 0
2024-03-26 11:00 | 24.6 | 60 | 6.71 | 435 | 26 | 30 | 17 | 71.6145 | 0
2024-03-26 12:00 | 25.8 | 49 | 7.35 | 780 | 26 | 30 | 17 | 43.3205 | 0
2024-03-26 13:00 | 25.9 | 48 | 7.71 | 872 | 26 | 30 | 17 | 36.8706 | 0
2024-03-26 14:00 | 25.7 | 47 | 7.86 | 841 | 26 | 30 | 17 | 48.6021 | 0
2024-03-26 15:00 | 25 | 54 | 7.69 | 685 | 26 | 30 | 17 | 59.0182 | 0
2024-03-26 16:00 | 24.5 | 55 | 7.98 | 596 | 26 | 30 | 17 | 79.6678 | 0
2024-03-26 17:00 | 23.3 | 59 | 8.1 | 280 | 26 | 30 | 17 | 132.1855 | 0
2024-03-26 18:00 | 22.3 | 65 | 8.45 | 97 | 26 | 30 | 17 | 163.1498 | 0
2024-03-26 19:00 | 21.7 | 71 | 7.73 | 7 | 26 | 30 | 17 | 161.5637 | 0
2024-03-26 20:00 | 21.5 | 73 | 6.96 | 0 | 26 | 30 | 17 | 150.7923 | 0
2024-03-26 21:00 | 21.3 | 72 | 6.51 | 0 | 26 | 30 | 17 | 149.0556 | 0
2024-03-26 22:00 | 21.1 | 74 | 6.89 | 0 | 26 | 30 | 17 | 153.7072 | 0
2024-03-26 23:00 | 20.9 | 75 | 6.84 | 0 | 26 | 30 | 17 | 154.005 | 0
2024-03-27 | 20.6 | 75 | 6.8 | 0 | 26 | 30 | 17 | 157.7073 | 0
2024-03-27 01:00 | 20.4 | 73 | 6.61 | 0 | 26 | 30 | 17 | 161.1238 | 0
2024-03-27 02:00 | 20.3 | 70 | 6.85 | 0 | 26 | 30 | 17 | 171.6417 | 0
2024-03-27 03:00 | 20 | 69 | 6.91 | 0 | 26 | 30 | 17 | 178.4664 | 0
2024-03-27 04:00 | 19.8 | 72 | 6.77 | 0 | 26 | 30 | 17 | 173.5909 | 0
2024-03-27 05:00 | 20.2 | 70 | 5.74 | 0 | 26 | 30 | 17 | 154.3326 | 0
2024-03-27 06:00 | 19.8 | 69 | 5.5 | 0 | 26 | 30 | 17 | 156.3048 | 0
2024-03-27 07:00 | 20.1 | 67 | 5.12 | 17 | 26 | 30 | 17 | 146.6586 | 0
2024-03-27 08:00 | 20.9 | 65 | 6.2 | 115 | 26 | 30 | 17 | 146.3159 | 0
2024-03-27 09:00 | 22.1 | 61 | 6.81 | 354 | 26 | 30 | 17 | 115.9637 | 0
2024-03-27 10:00 | 22.7 | 60 | 6.42 | 507 | 26 | 30 | 17 | 83.4273 | 0
2024-03-27 11:00 | 23.3 | 58 | 6.31 | 613 | 26 | 30 | 17 | 63.788 | 0
2024-03-27 12:00 | 24.1 | 55 | 7.32 | 810 | 26 | 30 | 17 | 47.6606 | 0
2024-03-27 13:00 | 24.4 | 50 | 8.17 | 867 | 26 | 30 | 17 | 60.0397 | 0
2024-03-27 14:00 | 24.3 | 50 | 8.55 | 790 | 26 | 30 | 17 | 77.311 | 0
2024-03-27 15:00 | 24.2 | 49 | 8.73 | 703 | 26 | 30 | 17 | 95.7964 | 0
2024-03-27 16:00 | 23.5 | 55 | 8.69 | 435 | 26 | 30 | 17 | 126.3432 | 0
2024-03-27 17:00 | 22.9 | 56 | 7.13 | 276 | 26 | 30 | 17 | 131.1332 | 0
2024-03-27 18:00 | 22 | 61 | 6.32 | 124 | 26 | 30 | 17 | 140.5355 | 0
2024-03-27 19:00 | 21 | 67 | 5 | 13 | 26 | 30 | 17 | 135.2684 | 0
2024-03-27 20:00 | 20.6 | 68 | 4.61 | 0 | 26 | 30 | 17 | 132.9896 | 0
2024-03-27 21:00 | 19.9 | 70 | 4.12 | 0 | 26 | 30 | 17 | 128.2885 | 0
2024-03-27 22:00 | 19.4 | 75 | 3.86 | 0 | 26 | 30 | 17 | 122.1878 | 0
2024-03-27 23:00 | 19.3 | 79 | 3.91 | 0 | 26 | 30 | 17 | 119.5551 | 0
2024-03-28 | 19.1 | 81 | 3.91 | 0 | 26 | 30 | 17 | 119.2512 | 0
2024-03-28 01:00 | 19.2 | 81 | 3.49 | 0 | 26 | 30 | 17 | 110.5521 | 0
2024-03-28 02:00 | 18.8 | 84 | 3.33 | 0 | 26 | 30 | 17 | 108.1313 | 0
2024-03-28 03:00 | 18.2 | 87 | 3.39 | 0 | 26 | 30 | 17 | 111.7531 | 0
2024-03-28 04:00 | 18 | 88 | 3.5 | 0 | 26 | 30 | 17 | 114.7271 | 0
2024-03-28 05:00 | 17.5 | 87 | 3.55 | 0 | 26 | 30 | 17 | 121.2375 | 0
2024-03-28 06:00 | 16.8 | 89 | 4.2 | 0 | 26 | 30 | 17 | 139.0396 | 0
2024-03-28 07:00 | 17.2 | 86 | 4.6 | 27 | 26 | 30 | 17 | 142.4308 | 0
2024-03-28 08:00 | 19.5 | 76 | 4.32 | 188 | 26 | 30 | 17 | 103.2381 | 0
2024-03-28 09:00 | 22.7 | 63 | 5.3 | 412 | 26 | 30 | 17 | 73.5503 | 0
2024-03-28 10:00 | 25 | 54 | 6.69 | 618 | 26 | 30 | 17 | 55.0144 | 0
2024-03-28 11:00 | 25.7 | 51 | 7.61 | 792 | 26 | 30 | 17 | 41.1844 | 0
2024-03-28 12:00 | 26.2 | 48 | 8.22 | 896 | 26 | 30 | 17 | 35.7386 | 0
2024-03-28 13:00 | 26.4 | 48 | 8.9 | 929 | 26 | 30 | 17 | 36.437 | 0
2024-03-28 14:00 | 26.3 | 47 | 9.04 | 885 | 26 | 30 | 17 | 48.7571 | 0
2024-03-28 15:00 | 26 | 47 | 9.43 | 769 | 26 | 30 | 17 | 74.0319 | 0
2024-03-28 16:00 | 25.5 | 48 | 9.85 | 589 | 26 | 30 | 17 | 108.6782 | 0
2024-03-28 17:00 | 24.4 | 52 | 8.83 | 369 | 26 | 30 | 17 | 131.107 | 0
2024-03-28 18:00 | 23.5 | 58 | 7.51 | 149 | 26 | 30 | 17 | 141.0719 | 0
2024-03-28 19:00 | 22.7 | 60 | 6.62 | 13 | 26 | 30 | 17 | 153.1584 | 0
2024-03-28 20:00 | 22.3 | 60 | 6.24 | 0 | 26 | 30 | 17 | 154.1246 | 0
2024-03-28 21:00 | 22 | 59 | 6.17 | 0 | 26 | 30 | 17 | 158.5372 | 0
2024-03-28 22:00 | 21.8 | 59 | 6.28 | 0 | 26 | 30 | 17 | 162.806 | 0
2024-03-28 23:00 | 21.6 | 61 | 6.28 | 0 | 26 | 30 | 17 | 161.6022 | 0
2024-03-29 | 21.3 | 64 | 6.02 | 0 | 26 | 30 | 17 | 155.6347 | 0
2024-03-29 01:00 | 21 | 69 | 5.79 | 0 | 26 | 30 | 17 | 147.0633 | 0
2024-03-29 02:00 | 20.9 | 70 | 5.73 | 0 | 26 | 30 | 17 | 145.6742 | 0
2024-03-29 03:00 | 20.8 | 70 | 6.04 | 0 | 26 | 30 | 17 | 151.9291 | 0
2024-03-29 04:00 | 20.7 | 70 | 6.43 | 0 | 26 | 30 | 17 | 159.4903 | 0
2024-03-29 05:00 | 20.4 | 75 | 4.88 | 0 | 26 | 30 | 17 | 130.03 | 0
2024-03-29 06:00 | 20.5 | 74 | 5.47 | 0 | 26 | 30 | 17 | 139.9921 | 0
2024-03-29 07:00 | 21.2 | 71 | 5.46 | 28 | 26 | 30 | 17 | 132.3114 | 0
2024-03-29 08:00 | 23.2 | 58 | 6.14 | 192 | 26 | 30 | 17 | 119.3163 | 0
2024-03-29 09:00 | 24.3 | 53 | 7.81 | 418 | 26 | 30 | 17 | 109.4086 | 0
2024-03-29 10:00 | 25.1 | 52 | 7.67 | 632 | 26 | 30 | 17 | 69.6106 | 0
2024-03-29 11:00 | 25.8 | 47 | 7.93 | 801 | 26 | 30 | 17 | 53.5167 | 0
2024-03-29 12:00 | 26.1 | 46 | 7.96 | 907 | 26 | 30 | 17 | 38.1023 | 0
2024-03-29 13:00 | 26.3 | 47 | 8.01 | 938 | 26 | 30 | 17 | 28.837 | 0
2024-03-29 14:00 | 26.1 | 50 | 8.1 | 889 | 26 | 30 | 17 | 30.9773 | 0
2024-03-29 15:00 | 25.7 | 52 | 7.76 | 770 | 26 | 30 | 17 | 43.3424 | 0
2024-03-29 16:00 | 25 | 55 | 7.48 | 585 | 26 | 30 | 17 | 67.297 | 0
2024-03-29 17:00 | 24.3 | 59 | 6.83 | 371 | 26 | 30 | 17 | 88.2626 | 0
2024-03-29 18:00 | 23.2 | 65 | 6.6 | 151 | 26 | 30 | 17 | 117.2499 | 0
2024-03-29 19:00 | 22.4 | 70 | 5.18 | 13 | 26 | 30 | 17 | 117.2979 | 0
2024-03-29 20:00 | 21.9 | 73 | 4.3 | 0 | 26 | 30 | 17 | 107.1672 | 0
2024-03-29 21:00 | 21.3 | 76 | 3.45 | 0 | 26 | 30 | 17 | 95.9753 | 0
2024-03-29 22:00 | 20.5 | 79 | 3.05 | 0 | 26 | 30 | 17 | 93.1311 | 0
2024-03-29 23:00 | 19.7 | 83 | 3.05 | 0 | 26 | 30 | 17 | 96.0445 | 0
2024-03-30 | 19 | 87 | 3.11 | 0 | 26 | 30 | 17 | 99.388 | 0
2024-03-30 01:00 | 18.2 | 90 | 2.91 | 0 | 26 | 30 | 17 | 99.7999 | 0
2024-03-30 02:00 | 17.5 | 92 | 3.14 | 0 | 26 | 30 | 17 | 108.5279 | 0
2024-03-30 03:00 | 16.9 | 95 | 3.32 | 0 | 26 | 30 | 17 | 114.792 | 0
2024-03-30 04:00 | 16.8 | 95 | 3.18 | 0 | 26 | 30 | 17 | 112.8568 | 0
2024-03-30 05:00 | 17.6 | 91 | 2.7 | 0 | 26 | 30 | 17 | 99.6883 | 0
2024-03-30 06:00 | 17.2 | 93 | 2.33 | 0 | 26 | 30 | 17 | 93.4875 | 0
2024-03-30 07:00 | 17.5 | 90 | 2.14 | 29 | 26 | 30 | 17 | 85.3732 | 0
2024-03-30 08:00 | 20.1 | 76 | 2.01 | 193 | 26 | 30 | 17 | 52.9439 | 0
2024-03-30 09:00 | 22.5 | 67 | 1.75 | 416 | 26 | 30 | 17 | 9.2983 | 0
2024-03-30 10:00 | 24.2 | 59 | 0.72 | 628 | 26 | 30 | 17 | 0 | 22.7704
2024-03-30 11:00 | 26 | 51 | 0.42 | 794 | 26 | 30 | 17 | 0 | 53.789
2024-03-30 12:00 | 27.8 | 44 | 1.71 | 895 | 26 | 30 | 17 | 0 | 30.2961
2024-03-30 13:00 | 28.7 | 42 | 2.2 | 922 | 26 | 30 | 17 | 0 | 22.3146
2024-03-30 14:00 | 28 | 52 | 6.51 | 867 | 26 | 30 | 17 | 0 | 0
2024-03-30 15:00 | 26.2 | 57 | 7.24 | 750 | 26 | 30 | 17 | 19.22 | 0
2024-03-30 16:00 | 25.8 | 62 | 6.3 | 518 | 26 | 30 | 17 | 34.1071 | 0
2024-03-30 17:00 | 25.9 | 56 | 3.76 | 153 | 26 | 30 | 17 | 64.0478 | 0
2024-03-30 18:00 | 25.2 | 64 | 3.54 | 80 | 26 | 30 | 17 | 65.1614 | 0
2024-03-30 19:00 | 24.2 | 73 | 3.4 | 12 | 26 | 30 | 17 | 69.4609 | 0
2024-03-30 20:00 | 23.3 | 80 | 3.48 | 0 | 26 | 30 | 17 | 71.6713 | 0
2024-03-30 21:00 | 22.7 | 81 | 3.06 | 0 | 26 | 30 | 17 | 71.2069 | 0
2024-03-30 22:00 | 22 | 87 | 2.73 | 0 | 26 | 30 | 17 | 66.7362 | 0
2024-03-30 23:00 | 21.7 | 94 | 3.42 | 0 | 26 | 30 | 17 | 70.2197 | 0
2024-03-31 | 21.6 | 95 | 3.36 | 0 | 26 | 30 | 17 | 69.4315 | 0
2024-03-31 01:00 | 21.4 | 95 | 3.08 | 0 | 26 | 30 | 17 | 68.2663 | 0
2024-03-31 02:00 | 21.3 | 95 | 3.08 | 0 | 26 | 30 | 17 | 69.2664 | 0
2024-03-31 03:00 | 21.1 | 96 | 1.89 | 0 | 26 | 30 | 17 | 54.8459 | 0
2024-03-31 04:00 | 21.4 | 96 | 0.85 | 0 | 26 | 30 | 17 | 37.8516 | 0
2024-03-31 05:00 | 21.2 | 96 | 0.9 | 0 | 26 | 30 | 17 | 39.6522 | 0
2024-03-31 06:00 | 21 | 98 | 0.92 | 0 | 26 | 30 | 17 | 40.0799 | 0
2024-03-31 07:00 | 21.1 | 97 | 2 | 17 | 26 | 30 | 17 | 53.2567 | 0
2024-03-31 08:00 | 22.5 | 90 | 2.2 | 141 | 26 | 30 | 17 | 33.8412 | 0
2024-03-31 09:00 | 23 | 85 | 2.19 | 106 | 26 | 30 | 17 | 39.0541 | 0
2024-03-31 10:00 | 24.1 | 73 | 3.26 | 178 | 26 | 30 | 17 | 46.3322 | 0
2024-03-31 11:00 | 26.4 | 54 | 3.53 | 417 | 26 | 30 | 17 | 23.8139 | 0
2024-03-31 12:00 | 28 | 45 | 4.02 | 548 | 26 | 30 | 17 | 13.9522 | 0
2024-03-31 13:00 | 28.7 | 42 | 4.83 | 647 | 26 | 30 | 17 | 10.7779 | 0
2024-03-31 14:00 | 27.9 | 53 | 5.53 | 579 | 26 | 30 | 17 | 11.1762 | 0
2024-03-31 15:00 | 26.9 | 57 | 5.98 | 513 | 26 | 30 | 17 | 28.0972 | 0
2024-03-31 16:00 | 26.2 | 53 | 6.79 | 381 | 26 | 30 | 17 | 74.3508 | 0
2024-03-31 17:00 | 24.6 | 63 | 5.7 | 317 | 26 | 30 | 17 | 68.6023 | 0
2024-03-31 18:00 | 23.8 | 62 | 4.26 | 134 | 26 | 30 | 17 | 84.9751 | 0
2024-03-31 19:00 | 22.8 | 70 | 2.91 | 13 | 26 | 30 | 17 | 79.1394 | 0
2024-03-31 20:00 | 22.4 | 72 | 2.24 | 0 | 26 | 30 | 17 | 70.8773 | 0
2024-03-31 21:00 | 21.9 | 74 | 2.15 | 0 | 26 | 30 | 17 | 71.0829 | 0
2024-03-31 22:00 | 20.8 | 79 | 2.16 | 0 | 26 | 30 | 17 | 74.8306 | 0
2024-03-31 23:00 | 20.3 | 82 | 2.33 | 0 | 26 | 30 | 17 | 79.1023 | 0
2024-04-01 | 19.2 | 88 | 2.45 | 0 | 26 | 30 | 17 | 84.7095 | 0
2024-04-01 01:00 | 18.5 | 89 | 2.5 | 0 | 26 | 30 | 17 | 90.25 | 0
2024-04-01 02:00 | 17.9 | 90 | 2.92 | 0 | 26 | 30 | 17 | 102.4975 | 0
2024-04-01 03:00 | 17.7 | 90 | 3.18 | 0 | 26 | 30 | 17 | 109.3335 | 0
2024-04-01 04:00 | 17.4 | 91 | 3.37 | 0 | 26 | 30 | 17 | 114.8443 | 0
2024-04-01 05:00 | 17.6 | 92 | 3.05 | 0 | 26 | 30 | 17 | 105.8912 | 0
2024-04-01 06:00 | 17.5 | 92 | 3.14 | 0 | 26 | 30 | 17 | 108.5279 | 0
2024-04-01 07:00 | 18.3 | 90 | 3.32 | 29 | 26 | 30 | 17 | 102.7527 | 0
2024-04-01 08:00 | 20.4 | 81 | 2.92 | 156 | 26 | 30 | 17 | 68.6518 | 0
2024-04-01 09:00 | 22.5 | 73 | 4.3 | 295 | 26 | 30 | 17 | 60.8407 | 0
2024-04-01 10:00 | 24.8 | 62 | 4.75 | 560 | 26 | 30 | 17 | 23.376 | 0
2024-04-01 11:00 | 26.1 | 53 | 5.09 | 593 | 26 | 30 | 17 | 25.8758 | 0
2024-04-01 12:00 | 27 | 42 | 5.71 | 610 | 26 | 30 | 17 | 46.1886 | 0
2024-04-01 13:00 | 27.2 | 38 | 6.66 | 694 | 26 | 30 | 17 | 56.3902 | 0
2024-04-01 14:00 | 27.5 | 37 | 6.91 | 862 | 26 | 30 | 17 | 36.4775 | 0
2024-04-01 15:00 | 27.1 | 40 | 6.6 | 717 | 26 | 30 | 17 | 48.3401 | 0
2024-04-01 16:00 | 26.5 | 43 | 5.82 | 585 | 26 | 30 | 17 | 54.4294 | 0
2024-04-01 17:00 | 25.6 | 45 | 4.96 | 361 | 26 | 30 | 17 | 76.735 | 0
2024-04-01 18:00 | 24.6 | 52 | 4.11 | 147 | 26 | 30 | 17 | 89.0187 | 0
2024-04-01 19:00 | 23.5 | 59 | 2.84 | 14 | 26 | 30 | 17 | 84.879 | 0
2024-04-01 20:00 | 22.8 | 64 | 2.88 | 0 | 26 | 30 | 17 | 87.2164 | 0
2024-04-01 21:00 | 22.3 | 67 | 2.76 | 0 | 26 | 30 | 17 | 85.7435 | 0
2024-04-01 22:00 | 21.2 | 70 | 2.77 | 0 | 26 | 30 | 17 | 91.4225 | 0
2024-04-01 23:00 | 20.5 | 70 | 3.31 | 0 | 26 | 30 | 17 | 107.395 | 0
2024-04-02 | 19.8 | 71 | 3.19 | 0 | 26 | 30 | 17 | 109.807 | 0
2024-04-02 01:00 | 19.2 | 73 | 3.24 | 0 | 26 | 30 | 17 | 113.7458 | 0
2024-04-02 02:00 | 18.8 | 75 | 3.35 | 0 | 26 | 30 | 17 | 117.3735 | 0
2024-04-02 03:00 | 18.4 | 79 | 3.4 | 0 | 26 | 30 | 17 | 117.8954 | 0
2024-04-02 04:00 | 18.1 | 82 | 3.4 | 0 | 26 | 30 | 17 | 117.6105 | 0
2024-04-02 05:00 | 18.9 | 77 | 3.53 | 0 | 26 | 30 | 17 | 118.1513 | 0
2024-04-02 06:00 | 18.5 | 78 | 3.67 | 0 | 26 | 30 | 17 | 123.4922 | 0
2024-04-02 07:00 | 19.5 | 73 | 3.57 | 30 | 26 | 30 | 17 | 113.8053 | 0
2024-04-02 08:00 | 21.6 | 65 | 3.01 | 178 | 26 | 30 | 17 | 74.0202 | 0
2024-04-02 09:00 | 24.6 | 53 | 3.5 | 415 | 26 | 30 | 17 | 41.1178 | 0
2024-04-02 10:00 | 26.9 | 44 | 4.59 | 618 | 26 | 30 | 17 | 25.3007 | 0
2024-04-02 11:00 | 27.9 | 35 | 6.33 | 711 | 26 | 30 | 17 | 49.1628 | 0
2024-04-02 12:00 | 27.8 | 34 | 6.42 | 706 | 26 | 30 | 17 | 54.9748 | 0
2024-04-02 13:00 | 28.5 | 31 | 6.3 | 912 | 26 | 30 | 17 | 25.8595 | 0
2024-04-02 14:00 | 28.7 | 29 | 6.41 | 882 | 26 | 30 | 17 | 35.073 | 0
2024-04-02 15:00 | 28.2 | 31 | 6.54 | 765 | 26 | 30 | 17 | 52.6498 | 0
2024-04-02 16:00 | 27.3 | 35 | 6.2 | 569 | 26 | 30 | 17 | 72.9277 | 0
2024-04-02 17:00 | 26.2 | 38 | 5.63 | 350 | 26 | 30 | 17 | 97.7251 | 0
2024-04-02 18:00 | 25.1 | 45 | 4.77 | 151 | 26 | 30 | 17 | 106.8874 | 0
2024-04-02 19:00 | 23.9 | 53 | 3.31 | 14 | 26 | 30 | 17 | 97.7377 | 0
2024-04-02 20:00 | 23.2 | 57 | 2.88 | 0 | 26 | 30 | 17 | 92.1357 | 0
2024-04-02 21:00 | 22.3 | 62 | 2.55 | 0 | 26 | 30 | 17 | 87.0057 | 0
2024-04-02 22:00 | 21.5 | 66 | 2.56 | 0 | 26 | 30 | 17 | 89.033 | 0
2024-04-02 23:00 | 20.8 | 69 | 3.14 | 0 | 26 | 30 | 17 | 102.7039 | 0
2024-04-03 | 19.9 | 71 | 3.06 | 0 | 26 | 30 | 17 | 106.3645 | 0
2024-04-03 01:00 | 19.2 | 69 | 2.77 | 0 | 26 | 30 | 17 | 107.3864 | 0
2024-04-03 02:00 | 18.5 | 70 | 2.69 | 0 | 26 | 30 | 17 | 109.6973 | 0
2024-04-03 03:00 | 18 | 73 | 2.64 | 0 | 26 | 30 | 17 | 109.5952 | 0
2024-04-03 04:00 | 17.2 | 78 | 2.12 | 0 | 26 | 30 | 17 | 98.6323 | 0
2024-04-03 05:00 | 18.5 | 67 | 2.42 | 0 | 26 | 30 | 17 | 105.6116 | 0
2024-04-03 06:00 | 18.3 | 65 | 2.73 | 0 | 26 | 30 | 17 | 116.1806 | 0
2024-04-03 07:00 | 18.9 | 59 | 2.75 | 33 | 26 | 30 | 17 | 113.2724 | 0
2024-04-03 08:00 | 22.2 | 44 | 2.6 | 179 | 26 | 30 | 17 | 82.8561 | 0
2024-04-03 09:00 | 25.1 | 35 | 3.04 | 307 | 26 | 30 | 17 | 68.1149 | 0
2024-04-03 10:00 | 27.6 | 28 | 3.12 | 632 | 26 | 30 | 17 | 20.0891 | 0
2024-04-03 11:00 | 29.5 | 22 | 3.1 | 814 | 26 | 30 | 17 | 0 | 0
2024-04-03 12:00 | 30.6 | 19 | 4.13 | 926 | 26 | 30 | 17 | 0 | 0
2024-04-03 13:00 | 31 | 19 | 5.1 | 957 | 26 | 30 | 17 | 9.5803 | 0
2024-04-03 14:00 | 31 | 18 | 5.54 | 910 | 26 | 30 | 17 | 26.6378 | 0
2024-04-03 15:00 | 30 | 21 | 5.92 | 746 | 26 | 30 | 17 | 55.4312 | 0
2024-04-03 16:00 | 28.5 | 31 | 6.04 | 577 | 26 | 30 | 17 | 67.0432 | 0
2024-04-03 17:00 | 27.5 | 34 | 5.07 | 351 | 26 | 30 | 17 | 84.3633 | 0
2024-04-03 18:00 | 25.9 | 41 | 4.78 | 147 | 26 | 30 | 17 | 107.5211 | 0
2024-04-03 19:00 | 24.5 | 51 | 3.63 | 14 | 26 | 30 | 17 | 101.2722 | 0
2024-04-03 20:00 | 23.9 | 61 | 3.52 | 0 | 26 | 30 | 17 | 92.2818 | 0
2024-04-03 21:00 | 23.4 | 62 | 3.28 | 0 | 26 | 30 | 17 | 91.4917 | 0
2024-04-03 22:00 | 23.1 | 64 | 2.68 | 0 | 26 | 30 | 17 | 81.355 | 0
2024-04-03 23:00 | 21.7 | 66 | 2.47 | 0 | 26 | 30 | 17 | 85.8139 | 0
2024-04-04 | 20.6 | 66 | 2.6 | 0 | 26 | 30 | 17 | 96.3272 | 0
2024-04-04 01:00 | 20 | 64 | 2.55 | 0 | 26 | 30 | 17 | 101.2063 | 0
2024-04-04 02:00 | 20.1 | 57 | 3.28 | 0 | 26 | 30 | 17 | 123.8491 | 0
2024-04-04 03:00 | 19 | 56 | 2.82 | 0 | 26 | 30 | 17 | 121.4564 | 0
2024-04-04 04:00 | 18.3 | 59 | 2.06 | 0 | 26 | 30 | 17 | 103.1689 | 0
2024-04-04 05:00 | 20 | 58 | 1.17 | 0 | 26 | 30 | 17 | 69.9556 | 0
2024-04-04 06:00 | 19.6 | 54 | 3.31 | 0 | 26 | 30 | 17 | 131.3441 | 0
2024-04-04 07:00 | 19.9 | 50 | 3.06 | 35 | 26 | 30 | 17 | 122.4295 | 0
2024-04-04 08:00 | 23 | 38 | 2.28 | 169 | 26 | 30 | 17 | 77.4332 | 0
2024-04-04 09:00 | 26.6 | 25 | 4 | 434 | 26 | 30 | 17 | 77.7958 | 0
2024-04-04 10:00 | 28.7 | 20 | 5.63 | 651 | 26 | 30 | 17 | 76.8593 | 0
2024-04-04 11:00 | 29.9 | 18 | 5.84 | 819 | 26 | 30 | 17 | 53.5485 | 0
2024-04-04 12:00 | 30.4 | 17 | 6.54 | 923 | 26 | 30 | 17 | 50.8801 | 0
2024-04-04 13:00 | 30.4 | 17 | 6.94 | 952 | 26 | 30 | 17 | 53.9961 | 0
2024-04-04 14:00 | 30.4 | 18 | 6.97 | 905 | 26 | 30 | 17 | 57.5706 | 0
2024-04-04 15:00 | 30.1 | 17 | 6.86 | 788 | 26 | 30 | 17 | 77.5034 | 0
2024-04-04 16:00 | 29.4 | 20 | 6.69 | 611 | 26 | 30 | 17 | 95.5844 | 0
2024-04-04 17:00 | 27.8 | 32 | 5.43 | 386 | 26 | 30 | 17 | 87.4275 | 0
2024-04-04 18:00 | 25.7 | 47 | 4.77 | 162 | 26 | 30 | 17 | 95.6936 | 0
2024-04-04 19:00 | 23.7 | 64 | 3.31 | 16 | 26 | 30 | 17 | 84.5722 | 0
2024-04-04 20:00 | 22.7 | 71 | 2.79 | 0 | 26 | 30 | 17 | 78.6916 | 0
2024-04-04 21:00 | 21.3 | 76 | 2.18 | 0 | 26 | 30 | 17 | 74.1527 | 0
2024-04-04 22:00 | 20.3 | 79 | 1.84 | 0 | 26 | 30 | 17 | 72.0294 | 0
2024-04-04 23:00 | 19.5 | 81 | 2.08 | 0 | 26 | 30 | 17 | 80.7248 | 0
2024-04-05 | 18.6 | 85 | 2.16 | 0 | 26 | 30 | 17 | 85.6238 | 0
2024-04-05 01:00 | 18.2 | 85 | 2.45 | 0 | 26 | 30 | 17 | 94.5775 | 0
2024-04-05 02:00 | 18.3 | 81 | 3.41 | 0 | 26 | 30 | 17 | 117.0287 | 0
2024-04-05 03:00 | 17.4 | 81 | 3.31 | 0 | 26 | 30 | 17 | 122.5991 | 0
2024-04-05 04:00 | 16.8 | 82 | 3.21 | 0 | 26 | 30 | 17 | 124.4224 | 0
2024-04-05 05:00 | 17.2 | 81 | 3 | 0 | 26 | 30 | 17 | 117.338 | 0
2024-04-05 06:00 | 16.8 | 82 | 3.2 | 0 | 26 | 30 | 17 | 124.1957 | 0
2024-04-05 07:00 | 17.7 | 76 | 2.91 | 41 | 26 | 30 | 17 | 110.0789 | 0
2024-04-05 08:00 | 21.1 | 59 | 2.22 | 221 | 26 | 30 | 17 | 60.9548 | 0
2024-04-05 09:00 | 24.5 | 46 | 2.28 | 452 | 26 | 30 | 17 | 22.3454 | 0
2024-04-05 10:00 | 26.8 | 38 | 2.52 | 667 | 26 | 30 | 17 | 0 | 0
2024-04-05 11:00 | 28.6 | 31 | 3.91 | 835 | 26 | 30 | 17 | 0 | 0
2024-04-05 12:00 | 29.3 | 28 | 5.47 | 938 | 26 | 30 | 17 | 9.2361 | 0
2024-04-05 13:00 | 29.3 | 28 | 6.39 | 968 | 26 | 30 | 17 | 19.7232 | 0
2024-04-05 14:00 | 29.1 | 27 | 6.89 | 919 | 26 | 30 | 17 | 39.1682 | 0
2024-04-05 15:00 | 28.7 | 30 | 6.71 | 798 | 26 | 30 | 17 | 48.1913 | 0
2024-04-05 16:00 | 28 | 34 | 6.36 | 615 | 26 | 30 | 17 | 64.1387 | 0
2024-04-05 17:00 | 26.4 | 47 | 4.96 | 388 | 26 | 30 | 17 | 60.8105 | 0
2024-04-05 18:00 | 24.8 | 57 | 4.27 | 162 | 26 | 30 | 17 | 79.2677 | 0
2024-04-05 19:00 | 23.3 | 68 | 2.9 | 16 | 26 | 30 | 17 | 76.6786 | 0
2024-04-05 20:00 | 22.3 | 74 | 2.33 | 0 | 26 | 30 | 17 | 71.2649 | 0
2024-04-05 21:00 | 21.4 | 78 | 2.41 | 0 | 26 | 30 | 17 | 75.7115 | 0
2024-04-05 22:00 | 20.6 | 81 | 2.73 | 0 | 26 | 30 | 17 | 84.7509 | 0
2024-04-05 23:00 | 19.8 | 83 | 2.82 | 0 | 26 | 30 | 17 | 91.0548 | 0
2024-04-06 | 19 | 83 | 2.82 | 0 | 26 | 30 | 17 | 97.586 | 0
2024-04-06 01:00 | 18.3 | 82 | 3.1 | 0 | 26 | 30 | 17 | 109.7945 | 0
2024-04-06 02:00 | 17.8 | 84 | 3.2 | 0 | 26 | 30 | 17 | 114.2286 | 0
2024-04-06 03:00 | 17.5 | 83 | 3.51 | 0 | 26 | 30 | 17 | 124.1822 | 0
2024-04-06 04:00 | 17.1 | 80 | 3.71 | 0 | 26 | 30 | 17 | 134.8073 | 0
2024-04-06 05:00 | 17.9 | 76 | 3.2 | 0 | 26 | 30 | 17 | 120.5974 | 0
2024-04-06 06:00 | 17.6 | 73 | 3.3 | 0 | 26 | 30 | 17 | 127.9469 | 0
2024-04-06 07:00 | 18.4 | 65 | 3.41 | 42 | 26 | 30 | 17 | 126.0468 | 0
2024-04-06 08:00 | 21.3 | 54 | 3.1 | 220 | 26 | 30 | 17 | 84.4602 | 0
2024-04-06 09:00 | 24.7 | 46 | 3.4 | 447 | 26 | 30 | 17 | 44.2443 | 0
2024-04-06 10:00 | 27.2 | 39 | 4.17 | 659 | 26 | 30 | 17 | 20.1193 | 0
2024-04-06 11:00 | 29 | 36 | 4.52 | 823 | 26 | 30 | 17 | 0 | 0
2024-04-06 12:00 | 29.6 | 34 | 5.76 | 924 | 26 | 30 | 17 | 0 | 0
2024-04-06 13:00 | 29.5 | 32 | 6.18 | 952 | 26 | 30 | 17 | 5.084 | 0
2024-04-06 14:00 | 29.4 | 30 | 6.28 | 906 | 26 | 30 | 17 | 19.5793 | 0
2024-04-06 15:00 | 28.9 | 31 | 5.97 | 787 | 26 | 30 | 17 | 33.4674 | 0
2024-04-06 16:00 | 28.3 | 35 | 5.28 | 605 | 26 | 30 | 17 | 43.3913 | 0
2024-04-06 17:00 | 26.7 | 43 | 4.96 | 384 | 26 | 30 | 17 | 66.5384 | 0
2024-04-06 18:00 | 25.4 | 53 | 4.52 | 161 | 26 | 30 | 17 | 83.9079 | 0
2024-04-06 19:00 | 23.8 | 65 | 3.26 | 17 | 26 | 30 | 17 | 81.4613 | 0
2024-04-06 20:00 | 22.7 | 73 | 2.24 | 0 | 26 | 30 | 17 | 67.7464 | 0
2024-04-06 21:00 | 21.5 | 80 | 1.7 | 0 | 26 | 30 | 17 | 60.969 | 0
2024-04-06 22:00 | 20.9 | 78 | 1.75 | 0 | 26 | 30 | 17 | 67.1495 | 0
2024-04-06 23:00 | 20.1 | 77 | 2.16 | 0 | 26 | 30 | 17 | 81.3182 | 0
2024-04-07 | 19.6 | 75 | 2.61 | 0 | 26 | 30 | 17 | 95.7482 | 0
2024-04-07 01:00 | 19 | 75 | 3.01 | 0 | 26 | 30 | 17 | 108.6654 | 0
2024-04-07 02:00 | 17.9 | 78 | 2.65 | 0 | 26 | 30 | 17 | 106.581 | 0
2024-04-07 03:00 | 17.3 | 77 | 2.85 | 0 | 26 | 30 | 17 | 116.3776 | 0
2024-04-07 04:00 | 16.9 | 73 | 3.09 | 0 | 26 | 30 | 17 | 128.3352 | 0
2024-04-07 05:00 | 17.9 | 72 | 2.69 | 0 | 26 | 30 | 17 | 112.2784 | 0
2024-04-07 06:00 | 17.4 | 70 | 2.97 | 0 | 26 | 30 | 17 | 124.2286 | 0
2024-04-07 07:00 | 18.3 | 63 | 2.7 | 41 | 26 | 30 | 17 | 111.5461 | 0
2024-04-07 08:00 | 22.1 | 48 | 2.14 | 217 | 26 | 30 | 17 | 63.1343 | 0
2024-04-07 09:00 | 26.1 | 34 | 1.78 | 442 | 26 | 30 | 17 | 15.4725 | 0
2024-04-07 10:00 | 28.7 | 25 | 0.58 | 649 | 26 | 30 | 17 | 0 | 30.0746
2024-04-07 11:00 | 30.3 | 24 | 1.93 | 841 | 26 | 30 | 17 | 0 | 5.1884
2024-04-07 12:00 | 30.9 | 27 | 3.76 | 929 | 26 | 30 | 17 | 0 | 0
2024-04-07 13:00 | 30.7 | 24 | 5.58 | 958 | 26 | 30 | 17 | 6.1606 | 0
2024-04-07 14:00 | 30.3 | 24 | 5.86 | 909 | 26 | 30 | 17 | 21.0048 | 0
2024-04-07 15:00 | 29.9 | 25 | 5.95 | 790 | 26 | 30 | 17 | 39.4562 | 0
2024-04-07 16:00 | 28.8 | 29 | 5.38 | 610 | 26 | 30 | 17 | 54.1863 | 0
2024-04-07 17:00 | 27.2 | 40 | 5.24 | 384 | 26 | 30 | 17 | 72.1771 | 0
2024-04-07 18:00 | 25.2 | 58 | 3.83 | 160 | 26 | 30 | 17 | 67.5904 | 0
2024-04-07 19:00 | 23.9 | 70 | 2.1 | 17 | 26 | 30 | 17 | 57.35 | 0
2024-04-07 20:00 | 22.6 | 82 | 1.1 | 0 | 26 | 30 | 17 | 42.7896 | 0
2024-04-07 21:00 | 21.9 | 84 | 1.32 | 0 | 26 | 30 | 17 | 49.2128 | 0
2024-04-07 22:00 | 21.2 | 86 | 1.5 | 0 | 26 | 30 | 17 | 55.2138 | 0
2024-04-07 23:00 | 20.4 | 87 | 1.8 | 0 | 26 | 30 | 17 | 64.9538 | 0
2024-04-08 | 21.2 | 80 | 1.1 | 0 | 26 | 30 | 17 | 51.1831 | 0
2024-04-08 01:00 | 19.7 | 89 | 2.28 | 0 | 26 | 30 | 17 | 76.9906 | 0
2024-04-08 02:00 | 19.1 | 97 | 2.06 | 0 | 26 | 30 | 17 | 71.56 | 0
2024-04-08 03:00 | 20.9 | 94 | 0.98 | 0 | 26 | 30 | 17 | 43.4525 | 0
2024-04-08 04:00 | 20.5 | 96 | 0.5 | 0 | 26 | 30 | 17 | 37.1096 | 0
2024-04-08 05:00 | 20.3 | 94 | 0.82 | 0 | 26 | 30 | 17 | 43.4537 | 0
2024-04-08 06:00 | 18.3 | 95 | 1.88 | 0 | 26 | 30 | 17 | 75.167 | 0
2024-04-08 07:00 | 19.5 | 84 | 2.73 | 44 | 26 | 30 | 17 | 85.0098 | 0
2024-04-08 08:00 | 22.8 | 61 | 1.89 | 221 | 26 | 30 | 17 | 41.5094 | 0
2024-04-08 09:00 | 26 | 44 | 1.1 | 440 | 26 | 30 | 17 | 0 | 0
2024-04-08 10:00 | 28.5 | 33 | 1.1 | 566 | 26 | 30 | 17 | 0 | 0.6382
2024-04-08 11:00 | 30.6 | 28 | 3.19 | 778 | 26 | 30 | 17 | 0 | 0
2024-04-08 12:00 | 31.3 | 25 | 3.22 | 698 | 26 | 30 | 17 | 0 | 0
2024-04-08 13:00 | 33.1 | 20 | 3.35 | 926 | 26 | 30 | 17 | 0 | 0
2024-04-08 14:00 | 32.7 | 20 | 1.43 | 448 | 26 | 30 | 17 | 0 | 0
2024-04-08 15:00 | 33.2 | 19 | 5.34 | 751 | 26 | 30 | 17 | 23.1269 | 0
2024-04-08 16:00 | 32.8 | 17 | 3.83 | 570 | 26 | 30 | 17 | 30.4739 | 0
2024-04-08 17:00 | 31.2 | 18 | 3.88 | 290 | 26 | 30 | 17 | 77.5489 | 0
2024-04-08 18:00 | 29.7 | 26 | 2.92 | 138 | 26 | 30 | 17 | 72.552 | 0
2024-04-08 19:00 | 27.9 | 37 | 2.25 | 15 | 26 | 30 | 17 | 70.4085 | 0
2024-04-08 20:00 | 26.5 | 48 | 1.84 | 0 | 26 | 30 | 17 | 60.1582 | 0
2024-04-08 21:00 | 25.8 | 53 | 2.24 | 0 | 26 | 30 | 17 | 66.4255 | 0
2024-04-08 22:00 | 25.4 | 54 | 2.4 | 0 | 26 | 30 | 17 | 70.8122 | 0
2024-04-08 23:00 | 24.6 | 58 | 2.02 | 0 | 26 | 30 | 17 | 65.2425 | 0
2024-04-09 | 23.8 | 63 | 1.99 | 0 | 26 | 30 | 17 | 65.1586 | 0
2024-04-09 01:00 | 23.7 | 66 | 1.3 | 0 | 26 | 30 | 17 | 50.5083 | 0
2024-04-09 02:00 | 25.1 | 56 | 0.45 | 0 | 26 | 30 | 17 | 34.292 | 0
2024-04-09 03:00 | 24.8 | 58 | 0.85 | 0 | 26 | 30 | 17 | 40.7223 | 0
2024-04-09 04:00 | 24.2 | 64 | 0.76 | 0 | 26 | 30 | 17 | 38.162 | 0
2024-04-09 05:00 | 22.9 | 71 | 1.66 | 0 | 26 | 30 | 17 | 58.1785 | 0
2024-04-09 06:00 | 23.5 | 71 | 2.39 | 0 | 26 | 30 | 17 | 66.0464 | 0
2024-04-09 07:00 | 24.3 | 69 | 2.14 | 14 | 26 | 30 | 17 | 56.4342 | 0
2024-04-09 08:00 | 26.2 | 60 | 1.97 | 136 | 26 | 30 | 17 | 33.3074 | 0
2024-04-09 09:00 | 27.5 | 53 | 2.6 | 208 | 26 | 30 | 17 | 31.4594 | 0
2024-04-09 10:00 | 29.1 | 45 | 3.31 | 368 | 26 | 30 | 17 | 18.8258 | 0
2024-04-09 11:00 | 29.7 | 42 | 3.18 | 407 | 26 | 30 | 17 | 12.2318 | 0
2024-04-09 12:00 | 29.7 | 42 | 2.79 | 398 | 26 | 30 | 17 | 8.1336 | 0
2024-04-09 13:00 | 30.9 | 38 | 3.2 | 646 | 26 | 30 | 17 | 0 | 0
2024-04-09 14:00 | 30.7 | 38 | 3.89 | 468 | 26 | 30 | 17 | 12.5087 | 0
2024-04-09 15:00 | 31 | 36 | 3.66 | 484 | 26 | 30 | 17 | 9.1313 | 0
2024-04-09 16:00 | 30.8 | 35 | 3.86 | 374 | 26 | 30 | 17 | 30.5933 | 0
2024-04-09 17:00 | 29 | 43 | 3.77 | 109 | 26 | 30 | 17 | 64.4826 | 0
2024-04-09 18:00 | 28.1 | 48 | 2.91 | 90 | 26 | 30 | 17 | 54.2885 | 0
2024-04-09 19:00 | 28 | 46 | 2.76 | 6 | 26 | 30 | 17 | 67.2932 | 0
2024-04-09 20:00 | 27.2 | 48 | 2.01 | 0 | 26 | 30 | 17 | 58.9354 | 0
2024-04-09 21:00 | 26.6 | 51 | 2.47 | 0 | 26 | 30 | 17 | 67.0509 | 0
2024-04-09 22:00 | 26.3 | 52 | 2.28 | 0 | 26 | 30 | 17 | 64.829 | 0
2024-04-09 23:00 | 25.8 | 56 | 1.92 | 0 | 26 | 30 | 17 | 57.7149 | 0
2024-04-10 | 25.9 | 56 | 2.47 | 0 | 26 | 30 | 17 | 65.9365 | 0
2024-04-10 01:00 | 25.7 | 58 | 3.19 | 0 | 26 | 30 | 17 | 75.5283 | 0
2024-04-10 02:00 | 25.4 | 57 | 2.97 | 0 | 26 | 30 | 17 | 76.2614 | 0
2024-04-10 03:00 | 24.7 | 60 | 2.04 | 0 | 26 | 30 | 17 | 62.9522 | 0
2024-04-10 04:00 | 24 | 71 | 2.02 | 0 | 26 | 30 | 17 | 56.759 | 0
2024-04-10 05:00 | 24.2 | 61 | 2.28 | 0 | 26 | 30 | 17 | 69.5054 | 0
2024-04-10 06:00 | 24.3 | 64 | 2.33 | 0 | 26 | 30 | 17 | 66.4384 | 0
2024-04-10 07:00 | 25 | 64 | 1.78 | 26 | 26 | 30 | 17 | 49.3115 | 0
2024-04-10 08:00 | 26.2 | 60 | 1.44 | 94 | 26 | 30 | 17 | 30.8964 | 0
2024-04-10 09:00 | 28.5 | 49 | 2.22 | 295 | 26 | 30 | 17 | 12.4625 | 0
2024-04-10 10:00 | 31.1 | 36 | 4.44 | 622 | 26 | 30 | 17 | 0 | 0
2024-04-10 11:00 | 32.6 | 30 | 5.42 | 800 | 26 | 30 | 17 | 0 | 0
2024-04-10 12:00 | 32.8 | 30 | 5.8 | 890 | 26 | 30 | 17 | 0 | 0
2024-04-10 13:00 | 32.7 | 32 | 5.68 | 909 | 26 | 30 | 17 | 0 | 0
2024-04-10 14:00 | 32.5 | 32 | 5.81 | 852 | 26 | 30 | 17 | 0 | 0
2024-04-10 15:00 | 31.8 | 34 | 5.82 | 732 | 26 | 30 | 17 | 0 | 0
2024-04-10 16:00 | 31.2 | 35 | 5.24 | 557 | 26 | 30 | 17 | 19.3068 | 0
2024-04-10 17:00 | 30.1 | 38 | 5.51 | 361 | 26 | 30 | 17 | 52.6682 | 0
2024-04-10 18:00 | 29 | 44 | 4.8 | 128 | 26 | 30 | 17 | 72.6386 | 0
2024-04-10 19:00 | 28.1 | 49 | 4.06 | 10 | 26 | 30 | 17 | 78.2786 | 0
2024-04-10 20:00 | 27.7 | 52 | 4.12 | 0 | 26 | 30 | 17 | 78.5236 | 0
2024-04-10 21:00 | 26.9 | 57 | 3.32 | 0 | 26 | 30 | 17 | 67.9308 | 0
2024-04-10 22:00 | 26.4 | 61 | 2.79 | 0 | 26 | 30 | 17 | 59.915 | 0
2024-04-10 23:00 | 25.2 | 68 | 2.7 | 0 | 26 | 30 | 17 | 59.8839 | 0
2024-04-11 | 24.8 | 74 | 1.9 | 0 | 26 | 30 | 17 | 46.4967 | 0
2024-04-11 01:00 | 24.8 | 73 | 2.67 | 0 | 26 | 30 | 17 | 56.8339 | 0
2024-04-11 02:00 | 24.4 | 73 | 2.28 | 0 | 26 | 30 | 17 | 55.3679 | 0
2024-04-11 03:00 | 24.5 | 73 | 2.41 | 0 | 26 | 30 | 17 | 56.2269 | 0
2024-04-11 04:00 | 23.8 | 79 | 1.55 | 0 | 26 | 30 | 17 | 44.4912 | 0
2024-04-11 05:00 | 23 | 68 | 2.9 | 0 | 26 | 30 | 17 | 81.3512 | 0
2024-04-11 06:00 | 23 | 67 | 3.62 | 0 | 26 | 30 | 17 | 93.9753 | 0
2024-04-11 07:00 | 24.1 | 61 | 3.64 | 47 | 26 | 30 | 17 | 85.9569 | 0
2024-04-11 08:00 | 26.9 | 51 | 3.62 | 223 | 26 | 30 | 17 | 51.6363 | 0
2024-04-11 09:00 | 29.6 | 42 | 4.16 | 421 | 26 | 30 | 17 | 23.7516 | 0
2024-04-11 10:00 | 32.2 | 34 | 4.12 | 637 | 26 | 30 | 17 | 0 | 0
2024-04-11 11:00 | 33.7 | 31 | 5.2 | 798 | 26 | 30 | 17 | 0 | 0
2024-04-11 12:00 | 34.3 | 31 | 6.6 | 899 | 26 | 30 | 17 | 0 | 0
2024-04-11 13:00 | 32.8 | 38 | 7.88 | 909 | 26 | 30 | 17 | 0 | 0
2024-04-11 14:00 | 31 | 50 | 7.75 | 820 | 26 | 30 | 17 | 0 | 0
2024-04-11 15:00 | 30.6 | 52 | 5.61 | 622 | 26 | 30 | 17 | 0 | 0
2024-04-11 16:00 | 30.3 | 52 | 4.52 | 443 | 26 | 30 | 17 | 0 | 0
2024-04-11 17:00 | 30.3 | 51 | 4.08 | 272 | 26 | 30 | 17 | 15.8186 | 0
2024-04-11 18:00 | 29 | 57 | 4.37 | 134 | 26 | 30 | 17 | 38.1767 | 0
2024-04-11 19:00 | 27.5 | 66 | 3.52 | 16 | 26 | 30 | 17 | 46.8447 | 0
2024-04-11 20:00 | 26.8 | 71 | 2.44 | 0 | 26 | 30 | 17 | 39.4964 | 0
2024-04-11 21:00 | 26.4 | 74 | 1.9 | 0 | 26 | 30 | 17 | 34.5827 | 0
2024-04-11 22:00 | 26 | 72 | 2.33 | 0 | 26 | 30 | 17 | 44.0827 | 0
2024-04-11 23:00 | 25.9 | 71 | 1.66 | 0 | 26 | 30 | 17 | 38.6969 | 0
2024-04-12 | 25.9 | 69 | 2.44 | 0 | 26 | 30 | 17 | 49.6721 | 0
2024-04-12 01:00 | 25.7 | 69 | 2.83 | 0 | 26 | 30 | 17 | 55.7095 | 0
2024-04-12 02:00 | 25.3 | 72 | 3 | 0 | 26 | 30 | 17 | 57.2201 | 0
2024-04-12 03:00 | 24.9 | 73 | 1.6 | 0 | 26 | 30 | 17 | 42.8597 | 0
2024-04-12 04:00 | 24.9 | 72 | 1.55 | 0 | 26 | 30 | 17 | 43.0284 | 0
2024-04-12 05:00 | 24.2 | 75 | 1.3 | 0 | 26 | 30 | 17 | 41.4366 | 0
2024-04-12 06:00 | 24.2 | 74 | 3.47 | 0 | 26 | 30 | 17 | 70.5128 | 0
2024-04-12 07:00 | 24.9 | 71 | 1.06 | 45 | 26 | 30 | 17 | 30.5089 | 0
2024-04-12 08:00 | 26.8 | 64 | 2.48 | 193 | 26 | 30 | 17 | 22.8529 | 0
2024-04-12 09:00 | 28.3 | 56 | 1.75 | 233 | 26 | 30 | 17 | 7.4097 | 0
2024-04-12 10:00 | 28.8 | 54 | 1.32 | 262 | 26 | 30 | 17 | 0 | 0
2024-04-12 11:00 | 30 | 46 | 4.9 | 588 | 26 | 30 | 17 | 0 | 0
2024-04-12 12:00 | 31.5 | 38 | 4.53 | 700 | 26 | 30 | 17 | 0 | 0
2024-04-12 13:00 | 30.3 | 45 | 6.07 | 571 | 26 | 30 | 17 | 7.5992 | 0
2024-04-12 14:00 | 31.6 | 38 | 5.26 | 772 | 26 | 30 | 17 | 0 | 0
2024-04-12 15:00 | 31.7 | 35 | 4.72 | 571 | 26 | 30 | 17 | 6.204 | 0
2024-04-12 16:00 | 31.8 | 33 | 4.06 | 527 | 26 | 30 | 17 | 8.3633 | 0
2024-04-12 17:00 | 30.5 | 41 | 5.81 | 359 | 26 | 30 | 17 | 43.0109 | 0
2024-04-12 18:00 | 28.2 | 55 | 4.95 | 128 | 26 | 30 | 17 | 57.9956 | 0
2024-04-12 19:00 | 27.2 | 60 | 4.82 | 14 | 26 | 30 | 17 | 73.4031 | 0
2024-04-12 20:00 | 26.7 | 59 | 3.26 | 0 | 26 | 30 | 17 | 65.9009 | 0
2024-04-12 21:00 | 26.4 | 60 | 1.62 | 0 | 26 | 30 | 17 | 45.1782 | 0
2024-04-12 22:00 | 25.8 | 60 | 2.24 | 0 | 26 | 30 | 17 | 58.4609 | 0
2024-04-12 23:00 | 25.5 | 60 | 2.45 | 0 | 26 | 30 | 17 | 63.8132 | 0
2024-04-13 | 25.2 | 62 | 2.4 | 0 | 26 | 30 | 17 | 63.0055 | 0
2024-04-13 01:00 | 24.6 | 64 | 2.51 | 0 | 26 | 30 | 17 | 66.9649 | 0
2024-04-13 02:00 | 24.3 | 65 | 2.6 | 0 | 26 | 30 | 17 | 69.5352 | 0
2024-04-13 03:00 | 24.1 | 67 | 3.04 | 0 | 26 | 30 | 17 | 75.2661 | 0
2024-04-13 04:00 | 23.9 | 67 | 3.18 | 0 | 26 | 30 | 17 | 79.063 | 0
2024-04-13 05:00 | 24.3 | 67 | 3.33 | 0 | 26 | 30 | 17 | 77.4935 | 0
2024-04-13 06:00 | 23.7 | 68 | 3.22 | 0 | 26 | 30 | 17 | 80.1555 | 0
2024-04-13 07:00 | 24.6 | 62 | 3 | 52 | 26 | 30 | 17 | 69.7652 | 0
2024-04-13 08:00 | 26.9 | 49 | 3.36 | 237 | 26 | 30 | 17 | 49.3241 | 0
2024-04-13 09:00 | 28.8 | 36 | 4.5 | 458 | 26 | 30 | 17 | 44.2399 | 0
2024-04-13 10:00 | 30.3 | 27 | 4.97 | 645 | 26 | 30 | 17 | 34.1516 | 0
2024-04-13 11:00 | 31.3 | 23 | 6.13 | 803 | 26 | 30 | 17 | 32.9396 | 0
2024-04-13 12:00 | 31.8 | 22 | 6.9 | 896 | 26 | 30 | 17 | 30.0043 | 0
2024-04-13 13:00 | 30.4 | 27 | 6.84 | 572 | 26 | 30 | 17 | 71.0621 | 0
2024-04-13 14:00 | 29.4 | 31 | 6.43 | 313 | 26 | 30 | 17 | 98.8982 | 0
2024-04-13 15:00 | 30 | 27 | 6.74 | 459 | 26 | 30 | 17 | 89.2615 | 0
2024-04-13 16:00 | 30.1 | 26 | 7.27 | 492 | 26 | 30 | 17 | 94.6702 | 0
2024-04-13 17:00 | 28.4 | 39 | 7.34 | 278 | 26 | 30 | 17 | 103.9434 | 0
2024-04-13 18:00 | 26.4 | 48 | 6.56 | 141 | 26 | 30 | 17 | 113.7999 | 0
2024-04-13 19:00 | 24.8 | 63 | 2.48 | 10 | 26 | 30 | 17 | 64.7621 | 0
2024-04-13 20:00 | 25.6 | 58 | 4.25 | 0 | 26 | 30 | 17 | 90.8773 | 0
2024-04-13 21:00 | 23.7 | 64 | 1.98 | 0 | 26 | 30 | 17 | 64.7141 | 0
2024-04-13 22:00 | 23.5 | 68 | 2.56 | 0 | 26 | 30 | 17 | 71.8702 | 0
2024-04-13 23:00 | 23.6 | 67 | 2.8 | 0 | 26 | 30 | 17 | 75.951 | 0
2024-04-14 | 23.3 | 71 | 1.53 | 0 | 26 | 30 | 17 | 53.4291 | 0
2024-04-14 01:00 | 23 | 70 | 2.82 | 0 | 26 | 30 | 17 | 77.7936 | 0
2024-04-14 02:00 | 22.8 | 72 | 3.24 | 0 | 26 | 30 | 17 | 83.6144 | 0
2024-04-14 03:00 | 22.5 | 73 | 3.32 | 0 | 26 | 30 | 17 | 86.3536 | 0
2024-04-14 04:00 | 22.2 | 75 | 2.79 | 0 | 26 | 30 | 17 | 78.5159 | 0
2024-04-14 05:00 | 23.5 | 72 | 2.82 | 0 | 26 | 30 | 17 | 71.263 | 0
2024-04-14 06:00 | 22.6 | 72 | 2.92 | 0 | 26 | 30 | 17 | 80.4779 | 0
2024-04-14 07:00 | 23.6 | 66 | 3.11 | 54 | 26 | 30 | 17 | 74.6619 | 0
2024-04-14 08:00 | 25.8 | 53 | 3.47 | 237 | 26 | 30 | 17 | 54.2324 | 0
2024-04-14 09:00 | 27.3 | 41 | 4.65 | 461 | 26 | 30 | 17 | 49.6183 | 0
2024-04-14 10:00 | 28.4 | 35 | 5.81 | 670 | 26 | 30 | 17 | 41.5423 | 0
2024-04-14 11:00 | 28.8 | 36 | 6.76 | 837 | 26 | 30 | 17 | 24.9457 | 0
2024-04-14 12:00 | 29.4 | 31 | 6.84 | 937 | 26 | 30 | 17 | 20.4583 | 0
2024-04-14 13:00 | 29.4 | 31 | 6.77 | 967 | 26 | 30 | 17 | 15.4266 | 0
2024-04-14 14:00 | 29 | 35 | 6.33 | 915 | 26 | 30 | 17 | 9.1859 | 0
2024-04-14 15:00 | 28.8 | 36 | 6.06 | 790 | 26 | 30 | 17 | 21.8664 | 0
2024-04-14 16:00 | 28.3 | 37 | 5.7 | 606 | 26 | 30 | 17 | 44.5417 | 0
2024-04-14 17:00 | 27.7 | 33 | 4.81 | 374 | 26 | 30 | 17 | 77.2037 | 0
2024-04-14 18:00 | 26.6 | 40 | 3.7 | 163 | 26 | 30 | 17 | 82.264 | 0
2024-04-14 19:00 | 24.7 | 55 | 2.62 | 19 | 26 | 30 | 17 | 75.9578 | 0
2024-04-14 20:00 | 23.6 | 62 | 2.52 | 0 | 26 | 30 | 17 | 76.9571 | 0
2024-04-14 21:00 | 22.7 | 64 | 2.84 | 0 | 26 | 30 | 17 | 87.2994 | 0
2024-04-14 22:00 | 21.8 | 70 | 2.42 | 0 | 26 | 30 | 17 | 80.3425 | 0
2024-04-14 23:00 | 20.9 | 73 | 2.15 | 0 | 26 | 30 | 17 | 78.8715 | 0
2024-04-15 | 20.3 | 70 | 2.33 | 0 | 26 | 30 | 17 | 89.1649 | 0
2024-04-15 01:00 | 19.6 | 71 | 2.12 | 0 | 26 | 30 | 17 | 88.376 | 0
2024-04-15 02:00 | 19.1 | 70 | 2.04 | 0 | 26 | 30 | 17 | 90.3594 | 0
2024-04-15 03:00 | 18.7 | 70 | 2.21 | 0 | 26 | 30 | 17 | 96.9475 | 0
2024-04-15 04:00 | 18.7 | 67 | 2.77 | 0 | 26 | 30 | 17 | 112.6979 | 0
2024-04-15 05:00 | 20.2 | 67 | 2.47 | 0 | 26 | 30 | 17 | 95.4337 | 0
2024-04-15 06:00 | 19.7 | 66 | 3.36 | 0 | 26 | 30 | 17 | 119.2878 | 0
2024-04-15 07:00 | 20.5 | 62 | 2.7 | 57 | 26 | 30 | 17 | 95.2351 | 0
2024-04-15 08:00 | 23.6 | 50 | 3.11 | 244 | 26 | 30 | 17 | 69.0966 | 0
2024-04-15 09:00 | 27.4 | 32 | 2.78 | 470 | 26 | 30 | 17 | 29.8628 | 0
2024-04-15 10:00 | 29.7 | 24 | 2.37 | 680 | 26 | 30 | 17 | 0 | 0
2024-04-15 11:00 | 31 | 41 | 2.8 | 837 | 26 | 30 | 17 | 0 | 10.2091
2024-04-15 12:00 | 33 | 42 | 3.64 | 915 | 26 | 30 | 17 | 0 | 23.2542
2024-04-15 13:00 | 34.1 | 34 | 2.44 | 927 | 26 | 30 | 17 | 0 | 40.997
2024-04-15 14:00 | 33.8 | 32 | 2.33 | 823 | 26 | 30 | 17 | 0 | 23.6813
2024-04-15 15:00 | 32.6 | 32 | 4.05 | 574 | 26 | 30 | 17 | 0 | 0
2024-04-15 16:00 | 32 | 36 | 5.83 | 505 | 26 | 30 | 17 | 20.5332 | 0
2024-04-15 17:00 | 26.2 | 65 | 5.01 | 326 | 26 | 30 | 17 | 35.184 | 0
2024-04-15 18:00 | 27.3 | 63 | 3.51 | 155 | 26 | 30 | 17 | 35.2357 | 0
2024-04-15 19:00 | 26.5 | 66 | 3.77 | 19 | 26 | 30 | 17 | 59.3769 | 0
2024-04-15 20:00 | 26.2 | 68 | 3.76 | 0 | 26 | 30 | 17 | 61.7185 | 0
2024-04-15 21:00 | 26.2 | 70 | 3.4 | 0 | 26 | 30 | 17 | 55.13 | 0
2024-04-15 22:00 | 26.2 | 70 | 3.64 | 0 | 26 | 30 | 17 | 57.3011 | 0
2024-04-15 23:00 | 25.9 | 70 | 4.11 | 0 | 26 | 30 | 17 | 64.932 | 0
2024-04-16 | 26 | 75 | 5 | 0 | 26 | 30 | 17 | 61.4389 | 0
2024-04-16 01:00 | 24.4 | 84 | 5.14 | 0 | 26 | 30 | 17 | 67.5278 | 0
2024-04-16 02:00 | 23.3 | 88 | 6.44 | 0 | 26 | 30 | 17 | 86.9215 | 0
2024-04-16 03:00 | 22.8 | 89 | 6.61 | 0 | 26 | 30 | 17 | 94.6512 | 0
2024-04-16 04:00 | 22.7 | 88 | 7.76 | 0 | 26 | 30 | 17 | 108.685 | 0
2024-04-16 05:00 | 23.1 | 86 | 1.6 | 0 | 26 | 30 | 17 | 44.4032 | 0
2024-04-16 06:00 | 21 | 91 | 4.12 | 0 | 26 | 30 | 17 | 90.1978 | 0
2024-04-16 07:00 | 21.9 | 87 | 4.07 | 21 | 26 | 30 | 17 | 81.6912 | 0
2024-04-16 08:00 | 23.3 | 83 | 4.77 | 163 | 26 | 30 | 17 | 59.0909 | 0
2024-04-16 09:00 | 25.8 | 73 | 5.02 | 450 | 26 | 30 | 17 | 7.6004 | 0
2024-04-16 10:00 | 26.2 | 70 | 5.3 | 510 | 26 | 30 | 17 | 2.4464 | 0
2024-04-16 11:00 | 23.8 | 76 | 5.05 | 129 | 26 | 30 | 17 | 72.1221 | 0
2024-04-16 12:00 | 25.2 | 74 | 6.41 | 758 | 26 | 30 | 17 | 0 | 0
2024-04-16 13:00 | 24.4 | 74 | 7.5 | 190 | 26 | 30 | 17 | 83.2322 | 0
2024-04-16 14:00 | 23.6 | 80 | 5.85 | 179 | 26 | 30 | 17 | 68.8193 | 0
2024-04-16 15:00 | 23.6 | 81 | 6.57 | 90 | 26 | 30 | 17 | 85.5906 | 0
2024-04-16 16:00 | 23.2 | 86 | 5.92 | 56 | 26 | 30 | 17 | 80.4751 | 0
2024-04-16 17:00 | 22.9 | 83 | 9.82 | 29 | 26 | 30 | 17 | 131.5306 | 0
2024-04-16 18:00 | 22.6 | 79 | 9.95 | 9 | 26 | 30 | 17 | 152.4568 | 0
2024-04-16 19:00 | 22.4 | 86 | 5.91 | 3 | 26 | 30 | 17 | 99.6514 | 0
2024-04-16 20:00 | 22.6 | 86 | 6.45 | 0 | 26 | 30 | 17 | 102.4237 | 0
2024-04-16 21:00 | 22.7 | 83 | 6.62 | 0 | 26 | 30 | 17 | 108.5138 | 0
2024-04-16 22:00 | 22.9 | 84 | 5.08 | 0 | 26 | 30 | 17 | 87.8803 | 0
2024-04-16 23:00 | 22.6 | 86 | 4.75 | 0 | 26 | 30 | 17 | 85.1165 | 0
2024-04-17 | 22.2 | 90 | 6.4 | 0 | 26 | 30 | 17 | 100.5926 | 0
2024-04-17 01:00 | 21.6 | 95 | 5.37 | 0 | 26 | 30 | 17 | 90.7529 | 0
2024-04-17 02:00 | 21.8 | 95 | 4.97 | 0 | 26 | 30 | 17 | 83.9167 | 0
2024-04-17 03:00 | 22.6 | 92 | 6.02 | 0 | 26 | 30 | 17 | 86.9053 | 0
2024-04-17 04:00 | 22.4 | 89 | 6.73 | 0 | 26 | 30 | 17 | 102.426 | 0
2024-04-17 05:00 | 20.7 | 93 | 3.55 | 0 | 26 | 30 | 17 | 83.6369 | 0
2024-04-17 06:00 | 21.1 | 90 | 3.64 | 0 | 26 | 30 | 17 | 84.1248 | 0
2024-04-17 07:00 | 21.7 | 88 | 3.8 | 39 | 26 | 30 | 17 | 76.8916 | 0
2024-04-17 08:00 | 22.6 | 83 | 4.03 | 109 | 26 | 30 | 17 | 66.8823 | 0
2024-04-17 09:00 | 23.3 | 80 | 4.61 | 417 | 26 | 30 | 17 | 28.0627 | 0
2024-04-17 10:00 | 24 | 78 | 4.79 | 658 | 26 | 30 | 17 | 0 | 0
2024-04-17 11:00 | 24.6 | 73 | 5.69 | 808 | 26 | 30 | 17 | 0 | 0
2024-04-17 12:00 | 25 | 71 | 5.87 | 874 | 26 | 30 | 17 | 0 | 0
2024-04-17 13:00 | 25.1 | 69 | 6.2 | 915 | 26 | 30 | 17 | 0 | 0
2024-04-17 14:00 | 25.3 | 68 | 6.56 | 826 | 26 | 30 | 17 | 0 | 0
2024-04-17 15:00 | 25.2 | 69 | 6.66 | 706 | 26 | 30 | 17 | 4.7458 | 0
2024-04-17 16:00 | 25 | 70 | 6.82 | 529 | 26 | 30 | 17 | 30.9104 | 0
2024-04-17 17:00 | 24.5 | 69 | 5.72 | 380 | 26 | 30 | 17 | 49.4589 | 0
2024-04-17 18:00 | 23.7 | 76 | 4.6 | 166 | 26 | 30 | 17 | 63.4753 | 0
2024-04-17 19:00 | 22.5 | 82 | 4.46 | 21 | 26 | 30 | 17 | 86.4784 | 0
2024-04-17 20:00 | 22.1 | 84 | 3.98 | 0 | 26 | 30 | 17 | 85.2468 | 0
2024-04-17 21:00 | 21.7 | 86 | 3.71 | 0 | 26 | 30 | 17 | 83.5703 | 0
2024-04-17 22:00 | 21.4 | 86 | 3.55 | 0 | 26 | 30 | 17 | 84.5954 | 0
2024-04-17 23:00 | 21 | 86 | 3.39 | 0 | 26 | 30 | 17 | 86.3757 | 0
2024-04-18 | 20.7 | 87 | 3.78 | 0 | 26 | 30 | 17 | 93.9108 | 0
2024-04-18 01:00 | 20.2 | 88 | 3.94 | 0 | 26 | 30 | 17 | 100.3717 | 0
2024-04-18 02:00 | 19.7 | 89 | 4.24 | 0 | 26 | 30 | 17 | 109.1657 | 0
2024-04-18 03:00 | 19.2 | 90 | 4.41 | 0 | 26 | 30 | 17 | 116.1978 | 0
2024-04-18 04:00 | 19 | 91 | 4.08 | 0 | 26 | 30 | 17 | 111.9004 | 0
2024-04-18 05:00 | 19.7 | 89 | 4.08 | 0 | 26 | 30 | 17 | 106.6938 | 0
2024-04-18 06:00 | 19.5 | 88 | 3.98 | 0 | 26 | 30 | 17 | 108.4244 | 0
2024-04-18 07:00 | 20.1 | 86 | 4.05 | 63 | 26 | 30 | 17 | 97.0366 | 0
2024-04-18 08:00 | 21.7 | 83 | 3.61 | 249 | 26 | 30 | 17 | 52.3829 | 0
2024-04-18 09:00 | 23.7 | 73 | 4.34 | 472 | 26 | 30 | 17 | 24.0299 | 0
2024-04-18 10:00 | 25.5 | 63 | 4.53 | 677 | 26 | 30 | 17 | 0 | 0
2024-04-18 11:00 | 26.8 | 57 | 4.61 | 835 | 26 | 30 | 17 | 0 | 0
2024-04-18 12:00 | 27.6 | 53 | 4.83 | 929 | 26 | 30 | 17 | 0 | 0
2024-04-18 13:00 | 28 | 49 | 5 | 951 | 26 | 30 | 17 | 0 | 0
2024-04-18 14:00 | 27.9 | 50 | 5.01 | 900 | 26 | 30 | 17 | 0 | 0
2024-04-18 15:00 | 27.5 | 53 | 4.73 | 779 | 26 | 30 | 17 | 0 | 0
2024-04-18 16:00 | 26.9 | 58 | 4.2 | 601 | 26 | 30 | 17 | 0 | 0
2024-04-18 17:00 | 26.5 | 58 | 2.59 | 388 | 26 | 30 | 17 | 8.1455 | 0
2024-04-18 18:00 | 24.9 | 78 | 1.39 | 170 | 26 | 30 | 17 | 13.214 | 0
2024-04-18 19:00 | 23.7 | 78 | 1.2 | 22 | 26 | 30 | 17 | 37.8011 | 0
2024-04-18 20:00 | 23.8 | 76 | 0.81 | 0 | 26 | 30 | 17 | 35.0377 | 0
2024-04-18 21:00 | 22 | 83 | 1.3 | 0 | 26 | 30 | 17 | 48.9139 | 0
2024-04-18 22:00 | 20.7 | 87 | 2.72 | 0 | 26 | 30 | 17 | 78.0099 | 0
2024-04-18 23:00 | 19.9 | 87 | 2.48 | 0 | 26 | 30 | 17 | 80.6222 | 0
2024-04-19 | 19.4 | 86 | 2.86 | 0 | 26 | 30 | 17 | 92.3469 | 0
2024-04-19 01:00 | 18.7 | 88 | 3 | 0 | 26 | 30 | 17 | 99.0369 | 0
2024-04-19 02:00 | 18.5 | 88 | 2.83 | 0 | 26 | 30 | 17 | 97.4893 | 0
2024-04-19 03:00 | 18 | 90 | 2.32 | 0 | 26 | 30 | 17 | 89.6036 | 0
2024-04-19 04:00 | 17.6 | 91 | 2.09 | 0 | 26 | 30 | 17 | 86.8562 | 0
2024-04-19 05:00 | 18.8 | 89 | 1.96 | 0 | 26 | 30 | 17 | 77.3524 | 0
2024-04-19 06:00 | 18.7 | 87 | 2.33 | 0 | 26 | 30 | 17 | 86.9292 | 0
2024-04-19 07:00 | 20 | 84 | 2.13 | 66 | 26 | 30 | 17 | 67.0664 | 0
2024-04-19 08:00 | 22.7 | 77 | 1.88 | 256 | 26 | 30 | 17 | 23.8133 | 0
2024-04-19 09:00 | 25.2 | 62 | 2.2 | 481 | 26 | 30 | 17 | 0 | 0
2024-04-19 10:00 | 26.8 | 54 | 2.38 | 688 | 26 | 30 | 17 | 0 | 0
2024-04-19 11:00 | 28 | 49 | 2.08 | 848 | 26 | 30 | 17 | 0 | 20.0385
2024-04-19 12:00 | 28.8 | 47 | 2.24 | 943 | 26 | 30 | 17 | 0 | 31.466
2024-04-19 13:00 | 29.2 | 45 | 2.21 | 965 | 26 | 30 | 17 | 0 | 35.2666
2024-04-19 14:00 | 29.1 | 49 | 3.01 | 912 | 26 | 30 | 17 | 0 | 13.8398
2024-04-19 15:00 | 28.1 | 57 | 4.5 | 787 | 26 | 30 | 17 | 0 | 0
2024-04-19 16:00 | 26.8 | 56 | 5.02 | 607 | 26 | 30 | 17 | 8.7161 | 0
2024-04-19 17:00 | 25.8 | 67 | 5.23 | 394 | 26 | 30 | 17 | 29.1866 | 0
2024-04-19 18:00 | 24.5 | 79 | 3.89 | 173 | 26 | 30 | 17 | 40.9197 | 0
2024-04-19 19:00 | 23 | 87 | 2.84 | 23 | 26 | 30 | 17 | 55.6894 | 0
2024-04-19 20:00 | 21.9 | 90 | 1.75 | 0 | 26 | 30 | 17 | 51.6703 | 0
2024-04-19 21:00 | 23 | 84 | 0.76 | 0 | 26 | 30 | 17 | 34.1026 | 0
2024-04-19 22:00 | 20.6 | 93 | 2.69 | 0 | 26 | 30 | 17 | 72.7235 | 0
2024-04-19 23:00 | 19.6 | 97 | 2.91 | 0 | 26 | 30 | 17 | 81.2244 | 0
2024-04-20 | 18.7 | 98 | 2.56 | 0 | 26 | 30 | 17 | 82.5649 | 0
2024-04-20 01:00 | 18.2 | 98 | 2.28 | 0 | 26 | 30 | 17 | 81.5352 | 0
2024-04-20 02:00 | 17.7 | 98 | 2.12 | 0 | 26 | 30 | 17 | 82.1485 | 0
2024-04-20 03:00 | 17.4 | 97 | 2.24 | 0 | 26 | 30 | 17 | 87.4089 | 0
2024-04-20 04:00 | 17.4 | 94 | 2.5 | 0 | 26 | 30 | 17 | 94.86 | 0
2024-04-20 05:00 | 18.7 | 89 | 1.84 | 0 | 26 | 30 | 17 | 75.5599 | 0
2024-04-20 06:00 | 18.6 | 85 | 1.93 | 0 | 26 | 30 | 17 | 80.7205 | 0
2024-04-20 07:00 | 20.3 | 77 | 1.84 | 69 | 26 | 30 | 17 | 64.136 | 0
2024-04-20 08:00 | 22.5 | 74 | 1.17 | 261 | 26 | 30 | 17 | 14.0095 | 0
2024-04-20 09:00 | 25 | 62 | 0.95 | 488 | 26 | 30 | 17 | 0 | 0.3075
2024-04-20 10:00 | 26.9 | 55 | 0.22 | 698 | 26 | 30 | 17 | 0 | 46.3738
2024-04-20 11:00 | 28.3 | 51 | 1.06 | 858 | 26 | 30 | 17 | 0 | 54.942
2024-04-20 12:00 | 29 | 51 | 2.41 | 952 | 26 | 30 | 17 | 0 | 35.5194
2024-04-20 13:00 | 28.3 | 56 | 4.28 | 971 | 26 | 30 | 17 | 0 | 0.4532
2024-04-20 14:00 | 27.6 | 54 | 4.03 | 917 | 26 | 30 | 17 | 0 | 0
2024-04-20 15:00 | 27.1 | 59 | 4.17 | 797 | 26 | 30 | 17 | 0 | 0
2024-04-20 16:00 | 26.3 | 66 | 4.46 | 615 | 26 | 30 | 17 | 0 | 0
2024-04-20 17:00 | 25.9 | 72 | 4.49 | 394 | 26 | 30 | 17 | 11.4597 | 0
2024-04-20 18:00 | 24.8 | 81 | 3.49 | 174 | 26 | 30 | 17 | 30.824 | 0
2024-04-20 19:00 | 23.3 | 87 | 2.97 | 23 | 26 | 30 | 17 | 54.144 | 0
2024-04-20 20:00 | 22.4 | 90 | 2.51 | 0 | 26 | 30 | 17 | 57.3748 | 0
2024-04-20 21:00 | 21.6 | 91 | 1.73 | 0 | 26 | 30 | 17 | 52.7455 | 0
2024-04-20 22:00 | 20.8 | 94 | 2.42 | 0 | 26 | 30 | 17 | 66.2382 | 0
2024-04-20 23:00 | 20.1 | 97 | 2.78 | 0 | 26 | 30 | 17 | 74.7357 | 0
2024-04-21 | 19.3 | 98 | 2.34 | 0 | 26 | 30 | 17 | 73.9908 | 0
2024-04-21 01:00 | 18.8 | 98 | 2.24 | 0 | 26 | 30 | 17 | 76.2278 | 0
2024-04-21 02:00 | 18.6 | 97 | 2.35 | 0 | 26 | 30 | 17 | 80.4737 | 0
2024-04-21 03:00 | 18.3 | 98 | 2.63 | 0 | 26 | 30 | 17 | 87.1085 | 0
2024-04-21 04:00 | 17.8 | 98 | 2.15 | 0 | 26 | 30 | 17 | 82.0208 | 0
2024-04-21 05:00 | 19.5 | 94 | 2.02 | 0 | 26 | 30 | 17 | 70.1009 | 0
2024-04-21 06:00 | 19.2 | 93 | 1.99 | 0 | 26 | 30 | 17 | 72.4184 | 0
2024-04-21 07:00 | 20.7 | 87 | 1.33 | 70 | 26 | 30 | 17 | 45.074 | 0
2024-04-21 08:00 | 22.6 | 82 | 1.02 | 261 | 26 | 30 | 17 | 6.2007 | 0
2024-04-21 09:00 | 25.2 | 72 | 0.86 | 486 | 26 | 30 | 17 | 0 | 9.7272
2024-04-21 10:00 | 27.4 | 63 | 1.34 | 691 | 26 | 30 | 17 | 0 | 29.4524
2024-04-21 11:00 | 29.1 | 55 | 1.53 | 849 | 26 | 30 | 17 | 0 | 48.6519
2024-04-21 12:00 | 30 | 53 | 2.31 | 942 | 26 | 30 | 17 | 0 | 47.1463
2024-04-21 13:00 | 30.1 | 57 | 3.08 | 961 | 26 | 30 | 17 | 0 | 42.3607
2024-04-21 14:00 | 29.9 | 59 | 3.9 | 905 | 26 | 30 | 17 | 0 | 22.8871
2024-04-21 15:00 | 29.3 | 54 | 4.25 | 782 | 26 | 30 | 17 | 0 | 0
2024-04-21 16:00 | 28.3 | 57 | 4.11 | 607 | 26 | 30 | 17 | 0 | 0
2024-04-21 17:00 | 27.4 | 63 | 3.29 | 393 | 26 | 30 | 17 | 0.0487 | 0
2024-04-21 18:00 | 25.7 | 76 | 2.71 | 174 | 26 | 30 | 17 | 21.8464 | 0
2024-04-21 19:00 | 23.6 | 87 | 2.41 | 23 | 26 | 30 | 17 | 45.6643 | 0
2024-04-21 20:00 | 22.5 | 92 | 1.84 | 0 | 26 | 30 | 17 | 46.8911 | 0
2024-04-21 21:00 | 22.1 | 92 | 2.42 | 0 | 26 | 30 | 17 | 56.9787 | 0
2024-04-21 22:00 | 21.5 | 93 | 2.82 | 0 | 26 | 30 | 17 | 66.2629 | 0
2024-04-21 23:00 | 20.8 | 92 | 2.42 | 0 | 26 | 30 | 17 | 68.0143 | 0
2024-04-22 | 20.3 | 92 | 2.26 | 0 | 26 | 30 | 17 | 69.6105 | 0
2024-04-22 01:00 | 20 | 91 | 2.39 | 0 | 26 | 30 | 17 | 74.9131 | 0
2024-04-22 02:00 | 19.4 | 90 | 2.02 | 0 | 26 | 30 | 17 | 73.6933 | 0
2024-04-22 03:00 | 19.3 | 88 | 2.43 | 0 | 26 | 30 | 17 | 83.5676 | 0
2024-04-22 04:00 | 18.9 | 88 | 2.38 | 0 | 26 | 30 | 17 | 85.662 | 0
2024-04-22 05:00 | 20.1 | 87 | 2.4 | 0 | 26 | 30 | 17 | 77.6609 | 0
2024-04-22 06:00 | 20 | 85 | 2.45 | 0 | 26 | 30 | 17 | 81.0157 | 0
2024-04-22 07:00 | 21.2 | 80 | 1.75 | 71 | 26 | 30 | 17 | 54.2171 | 0
2024-04-22 08:00 | 23.6 | 74 | 1.57 | 260 | 26 | 30 | 17 | 14.861 | 0
2024-04-22 09:00 | 26.6 | 64 | 2.1 | 481 | 26 | 30 | 17 | 0 | 0
2024-04-22 10:00 | 29.4 | 52 | 2.06 | 684 | 26 | 30 | 17 | 0 | 11.9807
2024-04-22 11:00 | 30.9 | 45 | 1.44 | 840 | 26 | 30 | 17 | 0 | 49.657
2024-04-22 12:00 | 32.2 | 40 | 1.28 | 932 | 26 | 30 | 17 | 0 | 68.0652
2024-04-22 13:00 | 32.9 | 38 | 1.84 | 952 | 26 | 30 | 17 | 0 | 57.435
2024-04-22 14:00 | 33.4 | 36 | 1.79 | 899 | 26 | 30 | 17 | 0 | 51.6607
2024-04-22 15:00 | 33.9 | 34 | 2.33 | 778 | 26 | 30 | 17 | 0 | 22.0215
2024-04-22 16:00 | 34.1 | 31 | 2.06 | 602 | 26 | 30 | 17 | 0 | 0.883
2024-04-22 17:00 | 31.5 | 50 | 3.3 | 387 | 26 | 30 | 17 | 0 | 0
2024-04-22 18:00 | 28.8 | 67 | 2.43 | 172 | 26 | 30 | 17 | 3.9065 | 0
2024-04-22 19:00 | 26.3 | 76 | 2.69 | 23 | 26 | 30 | 17 | 36.4133 | 0
2024-04-22 20:00 | 25.3 | 76 | 3.16 | 0 | 26 | 30 | 17 | 53.2832 | 0
2024-04-22 21:00 | 24.3 | 74 | 3.38 | 0 | 26 | 30 | 17 | 68.458 | 0
2024-04-22 22:00 | 23.8 | 74 | 3.61 | 0 | 26 | 30 | 17 | 76.2823 | 0
2024-04-22 23:00 | 23.3 | 73 | 4.06 | 0 | 26 | 30 | 17 | 88.6968 | 0
2024-04-23 | 23.1 | 67 | 5.07 | 0 | 26 | 30 | 17 | 114.2208 | 0
2024-04-23 01:00 | 22.9 | 67 | 4.97 | 0 | 26 | 30 | 17 | 115.142 | 0
2024-04-23 02:00 | 22.4 | 74 | 4.43 | 0 | 26 | 30 | 17 | 102.116 | 0
2024-04-23 03:00 | 22.2 | 75 | 4.43 | 0 | 26 | 30 | 17 | 102.8737 | 0
2024-04-23 04:00 | 21.6 | 78 | 3.81 | 0 | 26 | 30 | 17 | 96.1981 | 0
2024-04-23 05:00 | 23.4 | 73 | 2.92 | 0 | 26 | 30 | 17 | 72.3707 | 0
2024-04-23 06:00 | 22.8 | 74 | 5.28 | 0 | 26 | 30 | 17 | 108.6465 | 0
2024-04-23 07:00 | 24.3 | 56 | 5.24 | 61 | 26 | 30 | 17 | 114.3159 | 0
2024-04-23 08:00 | 26.3 | 54 | 4.98 | 253 | 26 | 30 | 17 | 66.0316 | 0
2024-04-23 09:00 | 28.7 | 51 | 5.47 | 437 | 26 | 30 | 17 | 24.5489 | 0
2024-04-23 10:00 | 30.8 | 47 | 4.61 | 650 | 26 | 30 | 17 | 0 | 0
2024-04-23 11:00 | 33.3 | 41 | 4.02 | 841 | 26 | 30 | 17 | 0 | 7.0772
2024-04-23 12:00 | 34.4 | 41 | 3.36 | 930 | 26 | 30 | 17 | 0 | 41.4292
2024-04-23 13:00 | 36.3 | 34 | 2.16 | 948 | 26 | 30 | 17 | 0 | 65.6984
2024-04-23 14:00 | 37.4 | 27 | 3.8 | 891 | 26 | 30 | 17 | 0 | 17.3561
2024-04-23 15:00 | 36 | 39 | 3.31 | 778 | 26 | 30 | 17 | 0 | 32.1755
2024-04-23 16:00 | 34.6 | 48 | 3.61 | 598 | 26 | 30 | 17 | 0 | 13.0427
2024-04-23 17:00 | 33.7 | 47 | 3.45 | 390 | 26 | 30 | 17 | 0 | 0
2024-04-23 18:00 | 27.8 | 66 | 5.63 | 174 | 26 | 30 | 17 | 36.4249 | 0
2024-04-23 19:00 | 26.1 | 75 | 4.18 | 24 | 26 | 30 | 17 | 51.0156 | 0
2024-04-23 20:00 | 25.4 | 81 | 3.44 | 0 | 26 | 30 | 17 | 47.2566 | 0
2024-04-23 21:00 | 24.9 | 86 | 3.52 | 0 | 26 | 30 | 17 | 46.0555 | 0
2024-04-23 22:00 | 24.5 | 87 | 3.42 | 0 | 26 | 30 | 17 | 48.4774 | 0
2024-04-23 23:00 | 24.1 | 90 | 3.32 | 0 | 26 | 30 | 17 | 48.0787 | 0
2024-04-24 | 23.6 | 90 | 3.69 | 0 | 26 | 30 | 17 | 56.7025 | 0
2024-04-24 01:00 | 23.2 | 92 | 3.94 | 0 | 26 | 30 | 17 | 60.7168 | 0
2024-04-24 02:00 | 23 | 91 | 3.98 | 0 | 26 | 30 | 17 | 64.9477 | 0
2024-04-24 03:00 | 22.5 | 89 | 3.78 | 0 | 26 | 30 | 17 | 71.6487 | 0
2024-04-24 04:00 | 21.7 | 89 | 3.76 | 0 | 26 | 30 | 17 | 80.3831 | 0
2024-04-24 05:00 | 21.9 | 91 | 3.94 | 0 | 26 | 30 | 17 | 77.609 | 0
2024-04-24 06:00 | 21.4 | 90 | 4.33 | 1 | 26 | 30 | 17 | 89.2925 | 0
2024-04-24 07:00 | 22.2 | 86 | 4.4 | 77 | 26 | 30 | 17 | 75.8832 | 0
2024-04-24 08:00 | 24.1 | 79 | 4.33 | 273 | 26 | 30 | 17 | 36.3802 | 0
2024-04-24 09:00 | 26.4 | 68 | 4.97 | 497 | 26 | 30 | 17 | 2.9928 | 0
2024-04-24 10:00 | 28.4 | 53 | 5.34 | 700 | 26 | 30 | 17 | 0 | 0
2024-04-24 11:00 | 29.5 | 43 | 5.8 | 854 | 26 | 30 | 17 | 0 | 0
2024-04-24 12:00 | 29.8 | 43 | 6.43 | 953 | 26 | 30 | 17 | 0 | 0
2024-04-24 13:00 | 29.9 | 41 | 6.79 | 974 | 26 | 30 | 17 | 0 | 0
2024-04-24 14:00 | 29.8 | 42 | 6.55 | 922 | 26 | 30 | 17 | 0 | 0
2024-04-24 15:00 | 29.6 | 45 | 6.32 | 801 | 26 | 30 | 17 | 0 | 0
2024-04-24 16:00 | 28.9 | 49 | 6.5 | 620 | 26 | 30 | 17 | 12.2152 | 0
2024-04-24 17:00 | 28 | 52 | 5.51 | 400 | 26 | 30 | 17 | 36.3002 | 0
2024-04-24 18:00 | 26.7 | 58 | 3.98 | 180 | 26 | 30 | 17 | 51.7416 | 0
2024-04-24 19:00 | 24.7 | 70 | 3.51 | 26 | 26 | 30 | 17 | 68.1329 | 0
2024-04-24 20:00 | 23.6 | 78 | 3.09 | 0 | 26 | 30 | 17 | 66.6484 | 0
2024-04-24 21:00 | 22.7 | 80 | 3.11 | 0 | 26 | 30 | 17 | 73.0412 | 0
2024-04-24 22:00 | 21.8 | 80 | 3 | 0 | 26 | 30 | 17 | 79.8052 | 0
2024-04-24 23:00 | 20.9 | 81 | 2.94 | 0 | 26 | 30 | 17 | 85.7548 | 0
2024-04-25 | 20 | 83 | 3.1 | 0 | 26 | 30 | 17 | 94.3053 | 0
2024-04-25 01:00 | 19.1 | 86 | 2.92 | 0 | 26 | 30 | 17 | 95.969 | 0
2024-04-25 02:00 | 18.6 | 86 | 3 | 0 | 26 | 30 | 17 | 101.6929 | 0
2024-04-25 03:00 | 18.2 | 82 | 3.28 | 0 | 26 | 30 | 17 | 114.3069 | 0
2024-04-25 04:00 | 18.1 | 73 | 4.02 | 0 | 26 | 30 | 17 | 139.61 | 0
2024-04-25 05:00 | 20.6 | 56 | 4.22 | 0 | 26 | 30 | 17 | 141.4503 | 0
2024-04-25 06:00 | 20.6 | 51 | 4.08 | 1 | 26 | 30 | 17 | 144.6961 | 0
2024-04-25 07:00 | 21.7 | 48 | 3.81 | 78 | 26 | 30 | 17 | 123.3267 | 0
2024-04-25 08:00 | 24.2 | 43 | 3.64 | 275 | 26 | 30 | 17 | 80.3947 | 0
2024-04-25 09:00 | 27.6 | 38 | 2.94 | 501 | 26 | 30 | 17 | 18.5473 | 0
2024-04-25 10:00 | 31.3 | 23 | 3.52 | 705 | 26 | 30 | 17 | 2.8273 | 0
2024-04-25 11:00 | 32.9 | 17 | 2.2 | 861 | 26 | 30 | 17 | 0 | 0.783
2024-04-25 12:00 | 32.5 | 21 | 4.02 | 954 | 26 | 30 | 17 | 0 | 0
2024-04-25 13:00 | 30.7 | 30 | 7 | 971 | 26 | 30 | 17 | 5.989 | 0
2024-04-25 14:00 | 32.3 | 24 | 5.54 | 919 | 26 | 30 | 17 | 0 | 0
2024-04-25 15:00 | 31.5 | 27 | 6.6 | 797 | 26 | 30 | 17 | 25.2162 | 0
2024-04-25 16:00 | 31.4 | 28 | 5.53 | 616 | 26 | 30 | 17 | 33.191 | 0
2024-04-25 17:00 | 31.7 | 25 | 4.88 | 400 | 26 | 30 | 17 | 58.722 | 0
2024-04-25 18:00 | 29.8 | 31 | 4.55 | 180 | 26 | 30 | 17 | 84.882 | 0
2024-04-25 19:00 | 27 | 48 | 4.44 | 26 | 26 | 30 | 17 | 94.1052 | 0
2024-04-25 20:00 | 25.6 | 49 | 4.38 | 0 | 26 | 30 | 17 | 108.7553 | 0
2024-04-25 21:00 | 24.6 | 52 | 3.97 | 0 | 26 | 30 | 17 | 106.5468 | 0
2024-04-25 22:00 | 23.9 | 51 | 3.92 | 0 | 26 | 30 | 17 | 113.5169 | 0
2024-04-25 23:00 | 22.9 | 48 | 3.42 | 0 | 26 | 30 | 17 | 116.2039 | 0
2024-04-26 | 22.7 | 58 | 3.3 | 0 | 26 | 30 | 17 | 102.7834 | 0
2024-04-26 01:00 | 22.8 | 63 | 3.67 | 0 | 26 | 30 | 17 | 102.0256 | 0
2024-04-26 02:00 | 22.1 | 64 | 3.49 | 0 | 26 | 30 | 17 | 103.896 | 0
2024-04-26 03:00 | 21.2 | 65 | 3.22 | 0 | 26 | 30 | 17 | 105.32 | 0
2024-04-26 04:00 | 20.8 | 64 | 3.3 | 0 | 26 | 30 | 17 | 111.2725 | 0
2024-04-26 05:00 | 21.7 | 59 | 3.3 | 0 | 26 | 30 | 17 | 109.677 | 0
2024-04-26 06:00 | 20.8 | 62 | 2.56 | 1 | 26 | 30 | 17 | 97.6204 | 0
2024-04-26 07:00 | 22.7 | 56 | 2.06 | 80 | 26 | 30 | 17 | 69.1139 | 0
2024-04-26 08:00 | 25.5 | 45 | 2.6 | 274 | 26 | 30 | 17 | 47.6509 | 0
2024-04-26 09:00 | 28.9 | 35 | 4.21 | 499 | 26 | 30 | 17 | 35.4959 | 0
2024-04-26 10:00 | 30.5 | 40 | 5.61 | 703 | 26 | 30 | 17 | 0 | 0
2024-04-26 11:00 | 31.5 | 41 | 6.22 | 854 | 26 | 30 | 17 | 0 | 0
2024-04-26 12:00 | 32.3 | 39 | 7 | 942 | 26 | 30 | 17 | 0 | 0
2024-04-26 13:00 | 32.2 | 39 | 8.12 | 960 | 26 | 30 | 17 | 0 | 0
2024-04-26 14:00 | 31.7 | 39 | 8.29 | 907 | 26 | 30 | 17 | 0 | 0
2024-04-26 15:00 | 31.2 | 41 | 7.79 | 789 | 26 | 30 | 17 | 0 | 0
2024-04-26 16:00 | 30.9 | 39 | 6.85 | 613 | 26 | 30 | 17 | 19.9342 | 0
2024-04-26 17:00 | 30.7 | 40 | 5.51 | 396 | 26 | 30 | 17 | 35.4567 | 0
2024-04-26 18:00 | 29.7 | 44 | 4.3 | 179 | 26 | 30 | 17 | 52.6215 | 0
2024-04-26 19:00 | 27.8 | 51 | 3.03 | 26 | 26 | 30 | 17 | 62.3151 | 0
2024-04-26 20:00 | 26.5 | 55 | 2.51 | 0 | 26 | 30 | 17 | 63.2869 | 0
2024-04-26 21:00 | 25.4 | 59 | 2.3 | 0 | 26 | 30 | 17 | 63.4191 | 0
2024-04-26 22:00 | 25 | 59 | 1.46 | 0 | 26 | 30 | 17 | 51.6134 | 0
2024-04-26 23:00 | 26 | 50 | 0.81 | 0 | 26 | 30 | 17 | 39.1887 | 0
2024-04-27 | 23.5 | 69 | 1.63 | 0 | 26 | 30 | 17 | 55.5121 | 0
2024-04-27 01:00 | 22.3 | 89 | 2.62 | 0 | 26 | 30 | 17 | 60.5885 | 0
2024-04-27 02:00 | 21.9 | 88 | 1.92 | 0 | 26 | 30 | 17 | 55.6237 | 0
2024-04-27 03:00 | 21.3 | 89 | 2.08 | 0 | 26 | 30 | 17 | 61.6061 | 0
2024-04-27 04:00 | 20.9 | 91 | 2.36 | 0 | 26 | 30 | 17 | 67.195 | 0
2024-04-27 05:00 | 21.9 | 92 | 2.13 | 0 | 26 | 30 | 17 | 55.0887 | 0
2024-04-27 06:00 | 21.7 | 93 | 2.62 | 1 | 26 | 30 | 17 | 61.8207 | 0
2024-04-27 07:00 | 22.8 | 88 | 1.9 | 81 | 26 | 30 | 17 | 37.7437 | 0
2024-04-27 08:00 | 25.7 | 70 | 1.8 | 275 | 26 | 30 | 17 | 5.5715 | 0
2024-04-27 09:00 | 29.1 | 49 | 2.2 | 499 | 26 | 30 | 17 | 0 | 0
2024-04-27 10:00 | 32.3 | 29 | 3.18 | 697 | 26 | 30 | 17 | 0 | 0
2024-04-27 11:00 | 34.5 | 19 | 3.72 | 859 | 26 | 30 | 17 | 0 | 0
2024-04-27 12:00 | 35.7 | 17 | 4.06 | 957 | 26 | 30 | 17 | 0 | 0
2024-04-27 13:00 | 35.7 | 22 | 5.66 | 976 | 26 | 30 | 17 | 0 | 0
2024-04-27 14:00 | 34 | 27 | 8.45 | 917 | 26 | 30 | 17 | 0 | 0
2024-04-27 15:00 | 33.3 | 33 | 7.52 | 792 | 26 | 30 | 17 | 0 | 0
2024-04-27 16:00 | 32.5 | 34 | 7.45 | 610 | 26 | 30 | 17 | 21.9309 | 0
2024-04-27 17:00 | 31.8 | 39 | 5.39 | 388 | 26 | 30 | 17 | 25.3216 | 0
2024-04-27 18:00 | 30.3 | 45 | 5.48 | 161 | 26 | 30 | 17 | 57.7043 | 0
2024-04-27 19:00 | 28.5 | 58 | 3.9 | 26 | 26 | 30 | 17 | 52.5472 | 0
2024-04-27 20:00 | 27.7 | 61 | 3.06 | 0 | 26 | 30 | 17 | 51.2412 | 0
2024-04-27 21:00 | 27 | 60 | 3.21 | 0 | 26 | 30 | 17 | 60.9573 | 0
2024-04-27 22:00 | 26.5 | 58 | 3.14 | 0 | 26 | 30 | 17 | 67.7678 | 0
2024-04-27 23:00 | 25.7 | 57 | 2.66 | 0 | 26 | 30 | 17 | 69.1332 | 0
2024-04-28 | 24.9 | 56 | 2.45 | 0 | 26 | 30 | 17 | 72.9296 | 0
2024-04-28 01:00 | 24.3 | 57 | 2.84 | 0 | 26 | 30 | 17 | 82.9662 | 0
2024-04-28 02:00 | 23.2 | 65 | 2.51 | 0 | 26 | 30 | 17 | 76.5625 | 0
2024-04-28 03:00 | 22.4 | 71 | 2.21 | 0 | 26 | 30 | 17 | 71.2785 | 0
2024-04-28 04:00 | 21.9 | 78 | 2 | 0 | 26 | 30 | 17 | 65.066 | 0
2024-04-28 05:00 | 22.9 | 70 | 2.12 | 0 | 26 | 30 | 17 | 67.093 | 0
2024-04-28 06:00 | 22.7 | 75 | 2.4 | 1 | 26 | 30 | 17 | 68.2243 | 0
2024-04-28 07:00 | 24.8 | 64 | 3.42 | 80 | 26 | 30 | 17 | 67.4302 | 0
2024-04-28 08:00 | 28.3 | 52 | 4.65 | 269 | 26 | 30 | 17 | 41.5549 | 0
2024-04-28 09:00 | 30.9 | 51 | 7.23 | 485 | 26 | 30 | 17 | 0 | 0
2024-04-28 10:00 | 33.2 | 43 | 6.04 | 680 | 26 | 30 | 17 | 0 | 0
2024-04-28 11:00 | 34.6 | 38 | 6.21 | 828 | 26 | 30 | 17 | 0 | 0
2024-04-28 12:00 | 34.8 | 33 | 6.38 | 731 | 26 | 30 | 17 | 0 | 0
2024-04-28 13:00 | 35.2 | 30 | 6.36 | 755 | 26 | 30 | 17 | 0 | 0
2024-04-28 14:00 | 36.4 | 25 | 5.31 | 836 | 26 | 30 | 17 | 0 | 0
2024-04-28 15:00 | 36 | 26 | 6.54 | 680 | 26 | 30 | 17 | 0 | 0
2024-04-28 16:00 | 36.2 | 23 | 6.4 | 525 | 26 | 30 | 17 | 22.1932 | 0
2024-04-28 17:00 | 35.6 | 24 | 7.73 | 354 | 26 | 30 | 17 | 60.1643 | 0
2024-04-28 18:00 | 34.5 | 25 | 6.04 | 148 | 26 | 30 | 17 | 80.2783 | 0
2024-04-28 19:00 | 32.7 | 27 | 7 | 24 | 26 | 30 | 17 | 120.678 | 0
2024-04-28 20:00 | 30.9 | 33 | 4.51 | 0 | 26 | 30 | 17 | 93.6929 | 0
2024-04-28 21:00 | 29.9 | 36 | 4.42 | 0 | 26 | 30 | 17 | 94.6425 | 0
2024-04-28 22:00 | 28.7 | 39 | 3.98 | 0 | 26 | 30 | 17 | 92.8363 | 0
2024-04-28 23:00 | 28 | 41 | 4.02 | 0 | 26 | 30 | 17 | 95.7312 | 0
2024-04-29 | 27.1 | 44 | 3.86 | 0 | 26 | 30 | 17 | 95.7057 | 0
2024-04-29 01:00 | 26.2 | 49 | 3.74 | 0 | 26 | 30 | 17 | 93.219 | 0
2024-04-29 02:00 | 25.4 | 54 | 3.54 | 0 | 26 | 30 | 17 | 89.3081 | 0
2024-04-29 03:00 | 24.7 | 57 | 3.67 | 0 | 26 | 30 | 17 | 93.0992 | 0
2024-04-29 04:00 | 24.4 | 56 | 4.11 | 0 | 26 | 30 | 17 | 104.3287 | 0
2024-04-29 05:00 | 25.7 | 50 | 1.8 | 0 | 26 | 30 | 17 | 62.1069 | 0
2024-04-29 06:00 | 25.5 | 49 | 2.33 | 1 | 26 | 30 | 17 | 74.5135 | 0
2024-04-29 07:00 | 28.2 | 46 | 3.18 | 81 | 26 | 30 | 17 | 61.7152 | 0
2024-04-29 08:00 | 30.8 | 42 | 2.24 | 270 | 26 | 30 | 17 | 9.888 | 0
2024-04-29 09:00 | 33.3 | 37 | 3.18 | 485 | 26 | 30 | 17 | 0 | 0
2024-04-29 10:00 | 35.2 | 36 | 6.32 | 681 | 26 | 30 | 17 | 0 | 0
2024-04-29 11:00 | 36.5 | 32 | 6.04 | 801 | 26 | 30 | 17 | 0 | 0
2024-04-29 12:00 | 38.1 | 25 | 5.22 | 897 | 26 | 30 | 17 | 0 | 0
2024-04-29 13:00 | 39.3 | 21 | 3.94 | 919 | 26 | 30 | 17 | 0 | 14.8814
2024-04-29 14:00 | 38.7 | 22 | 2.91 | 874 | 26 | 30 | 17 | 0 | 28.5085
2024-04-29 15:00 | 37.8 | 27 | 5.23 | 663 | 26 | 30 | 17 | 0 | 0
2024-04-29 16:00 | 37.4 | 28 | 4.56 | 573 | 26 | 30 | 17 | 0 | 0
2024-04-29 17:00 | 35.5 | 27 | 7.36 | 385 | 26 | 30 | 17 | 40.2574 | 0
2024-04-29 18:00 | 34.2 | 31 | 5.52 | 177 | 26 | 30 | 17 | 52.8972 | 0
2024-04-29 19:00 | 32.8 | 44 | 2.25 | 27 | 26 | 30 | 17 | 24.9802 | 0
2024-04-29 20:00 | 32.1 | 42 | 5.32 | 0 | 26 | 30 | 17 | 64.5307 | 0
2024-04-29 21:00 | 30.5 | 47 | 5.82 | 0 | 26 | 30 | 17 | 74.0655 | 0
2024-04-29 22:00 | 29.5 | 52 | 5.02 | 0 | 26 | 30 | 17 | 67.0384 | 0
2024-04-29 23:00 | 28.7 | 54 | 4.66 | 0 | 26 | 30 | 17 | 68.8898 | 0
2024-04-30 | 28.1 | 57 | 4.34 | 0 | 26 | 30 | 17 | 66.4468 | 0
2024-04-30 01:00 | 27.5 | 60 | 3.72 | 0 | 26 | 30 | 17 | 61.3283 | 0
2024-04-30 02:00 | 26.7 | 64 | 3.38 | 0 | 26 | 30 | 17 | 59.3273 | 0
2024-04-30 03:00 | 25.9 | 67 | 3.19 | 0 | 26 | 30 | 17 | 60.5711 | 0
2024-04-30 04:00 | 25.5 | 68 | 3.05 | 0 | 26 | 30 | 17 | 61.374 | 0
2024-04-30 05:00 | 26.3 | 63 | 2.69 | 0 | 26 | 30 | 17 | 56.8363 | 0
2024-04-30 06:00 | 26.3 | 59 | 4.31 | 2 | 26 | 30 | 17 | 82.0451 | 0
2024-04-30 07:00 | 28.9 | 51 | 3.58 | 83 | 26 | 30 | 17 | 51.1852 | 0
2024-04-30 08:00 | 31.1 | 53 | 3 | 270 | 26 | 30 | 17 | 0 | 0
2024-04-30 09:00 | 33.4 | 47 | 6.28 | 482 | 26 | 30 | 17 | 0 | 0
2024-04-30 10:00 | 35.2 | 41 | 7.3 | 677 | 26 | 30 | 17 | 0 | 0
2024-04-30 11:00 | 37.1 | 34 | 7.01 | 829 | 26 | 30 | 17 | 0 | 0
2024-04-30 12:00 | 38.9 | 27 | 5.8 | 917 | 26 | 30 | 17 | 0 | 4.76
2024-04-30 13:00 | 39.1 | 25 | 3.98 | 932 | 26 | 30 | 17 | 0 | 28.5835
2024-04-30 14:00 | 38.4 | 31 | 4.3 | 859 | 26 | 30 | 17 | 0 | 28.5522
2024-04-30 15:00 | 36.9 | 37 | 6.25 | 754 | 26 | 30 | 17 | 0 | 0
2024-04-30 16:00 | 36 | 37 | 6.02 | 579 | 26 | 30 | 17 | 0 | 0
2024-04-30 17:00 | 34.5 | 42 | 5.79 | 381 | 26 | 30 | 17 | 0 | 0
2024-04-30 18:00 | 33.3 | 45 | 4.47 | 173 | 26 | 30 | 17 | 12.5423 | 0
2024-04-30 19:00 | 32.4 | 47 | 3.59 | 27 | 26 | 30 | 17 | 32.2176 | 0
2024-04-30 20:00 | 31.4 | 50 | 3.3 | 0 | 26 | 30 | 17 | 37.4728 | 0
2024-04-30 21:00 | 30.6 | 53 | 2.91 | 0 | 26 | 30 | 17 | 36.4798 | 0
2024-04-30 22:00 | 30.2 | 54 | 2.84 | 0 | 26 | 30 | 17 | 37.822 | 0
2024-04-30 23:00 | 29.7 | 54 | 3.03 | 0 | 26 | 30 | 17 | 43.9803 | 0
2024-05-01 | 29.3 | 54 | 2.88 | 0 | 26 | 30 | 17 | 46.2441 | 0
2024-05-01 01:00 | 28.4 | 59 | 2.38 | 0 | 26 | 30 | 17 | 41.4281 | 0
2024-05-01 02:00 | 27.6 | 70 | 2.22 | 0 | 26 | 30 | 17 | 32.1572 | 0
2024-05-01 03:00 | 27.1 | 76 | 2.2 | 0 | 26 | 30 | 17 | 28.8811 | 0
2024-05-01 04:00 | 26.5 | 80 | 1.39 | 0 | 26 | 30 | 17 | 24.0779 | 0
2024-05-01 05:00 | 28.1 | 63 | 3.76 | 0 | 26 | 30 | 17 | 49.7293 | 0
2024-05-01 06:00 | 27.7 | 61 | 2.94 | 2 | 26 | 30 | 17 | 49.8027 | 0
2024-05-01 07:00 | 29.6 | 49 | 4.44 | 84 | 26 | 30 | 17 | 56.5905 | 0
2024-05-01 08:00 | 33 | 36 | 6.46 | 272 | 26 | 30 | 17 | 44.9688 | 0
2024-05-01 09:00 | 34.8 | 34 | 8.84 | 488 | 26 | 30 | 17 | 13.0152 | 0
2024-05-01 10:00 | 36.6 | 34 | 9.35 | 682 | 26 | 30 | 17 | 0 | 0
2024-05-01 11:00 | 36.9 | 34 | 8.56 | 830 | 26 | 30 | 17 | 0 | 0
2024-05-01 12:00 | 28.3 | 62 | 10.41 | 763 | 26 | 30 | 17 | 0 | 0
2024-05-01 13:00 | 30.7 | 54 | 6.26 | 517 | 26 | 30 | 17 | 0 | 0
2024-05-01 14:00 | 32 | 48 | 5.47 | 706 | 26 | 30 | 17 | 0 | 0
2024-05-01 15:00 | 32.2 | 47 | 5.91 | 637 | 26 | 30 | 17 | 0 | 0
2024-05-01 16:00 | 32.9 | 45 | 4.77 | 560 | 26 | 30 | 17 | 0 | 0
2024-05-01 17:00 | 34 | 40 | 5.5 | 371 | 26 | 30 | 17 | 0 | 0
2024-05-01 18:00 | 34.3 | 39 | 4.4 | 172 | 26 | 30 | 17 | 18.2309 | 0
2024-05-01 19:00 | 33.3 | 41 | 3.67 | 27 | 26 | 30 | 17 | 38.0235 | 0
2024-05-01 20:00 | 32.2 | 45 | 3.58 | 0 | 26 | 30 | 17 | 42.4283 | 0
2024-05-01 21:00 | 31.7 | 46 | 4.33 | 0 | 26 | 30 | 17 | 50.8268 | 0
2024-05-01 22:00 | 31.6 | 46 | 5.11 | 0 | 26 | 30 | 17 | 57.5321 | 0
2024-05-01 23:00 | 31.6 | 47 | 7.71 | 0 | 26 | 30 | 17 | 70.0349 | 0
2024-05-02 | 30.6 | 52 | 6.09 | 0 | 26 | 30 | 17 | 59.647 | 0
2024-05-02 01:00 | 31.6 | 42 | 5.94 | 0 | 26 | 30 | 17 | 75.6806 | 0
2024-05-02 02:00 | 31.4 | 41 | 5.38 | 0 | 26 | 30 | 17 | 76.4829 | 0
2024-05-02 03:00 | 31.1 | 42 | 7 | 0 | 26 | 30 | 17 | 91.0474 | 0
2024-05-02 04:00 | 25 | 84 | 8.12 | 0 | 26 | 30 | 17 | 76.7747 | 0
2024-05-02 05:00 | 24.9 | 81 | 6.23 | 0 | 26 | 30 | 17 | 73.9401 | 0
2024-05-02 06:00 | 24.8 | 83 | 5.32 | 0 | 26 | 30 | 17 | 64.9303 | 0
2024-05-02 07:00 | 24.9 | 82 | 2.84 | 37 | 26 | 30 | 17 | 41.4276 | 0
2024-05-02 08:00 | 24.5 | 80 | 2.97 | 46 | 26 | 30 | 17 | 47.8751 | 0
2024-05-02 09:00 | 24.2 | 81 | 1.88 | 106 | 26 | 30 | 17 | 29.8159 | 0
2024-05-02 10:00 | 24 | 81 | 1.22 | 86 | 26 | 30 | 17 | 25.7464 | 0
2024-05-02 11:00 | 24.2 | 80 | 4.38 | 198 | 26 | 30 | 17 | 44.1115 | 0
2024-05-02 12:00 | 24.8 | 73 | 5.46 | 200 | 26 | 30 | 17 | 58.9119 | 0
2024-05-02 13:00 | 24.7 | 73 | 4.88 | 147 | 26 | 30 | 17 | 61.7375 | 0
2024-05-02 14:00 | 24.7 | 79 | 4.05 | 101 | 26 | 30 | 17 | 49.7523 | 0
2024-05-02 15:00 | 25.4 | 77 | 3.79 | 177 | 26 | 30 | 17 | 32.2898 | 0
2024-05-02 16:00 | 25.5 | 74 | 3.2 | 154 | 26 | 30 | 17 | 33.6798 | 0
2024-05-02 17:00 | 26.5 | 70 | 2.59 | 219 | 26 | 30 | 17 | 15.2083 | 0
2024-05-02 18:00 | 26.2 | 74 | 2.19 | 148 | 26 | 30 | 17 | 18.7868 | 0
2024-05-02 19:00 | 24.9 | 82 | 2.42 | 29 | 26 | 30 | 17 | 38.8941 | 0
2024-05-02 20:00 | 24.2 | 85 | 2.69 | 0 | 26 | 30 | 17 | 48.1907 | 0
2024-05-02 21:00 | 23.8 | 88 | 2.98 | 0 | 26 | 30 | 17 | 51.1094 | 0
2024-05-02 22:00 | 23.3 | 88 | 3.42 | 0 | 26 | 30 | 17 | 60.4296 | 0
2024-05-02 23:00 | 22.9 | 89 | 3.22 | 0 | 26 | 30 | 17 | 61.4408 | 0
2024-05-03 | 22.7 | 89 | 3.32 | 0 | 26 | 30 | 17 | 64.5794 | 0
2024-05-03 01:00 | 22.5 | 90 | 3.32 | 0 | 26 | 30 | 17 | 65.4529 | 0
2024-05-03 02:00 | 22.3 | 92 | 3.26 | 0 | 26 | 30 | 17 | 64.4894 | 0
2024-05-03 03:00 | 22.2 | 92 | 3.32 | 0 | 26 | 30 | 17 | 66.1875 | 0
2024-05-03 04:00 | 22.2 | 90 | 3.55 | 0 | 26 | 30 | 17 | 71.1824 | 0
2024-05-03 05:00 | 22.7 | 91 | 3.4 | 0 | 26 | 30 | 17 | 62.8918 | 0
2024-05-03 06:00 | 22.5 | 90 | 3.61 | 2 | 26 | 30 | 17 | 68.2577 | 0
2024-05-03 07:00 | 23.3 | 88 | 3.11 | 85 | 26 | 30 | 17 | 45.958 | 0
2024-05-03 08:00 | 25 | 82 | 3.71 | 271 | 26 | 30 | 17 | 15.7235 | 0
2024-05-03 09:00 | 26.7 | 73 | 3.96 | 484 | 26 | 30 | 17 | 0 | 0
2024-05-03 10:00 | 28.1 | 66 | 3.94 | 688 | 26 | 30 | 17 | 0 | 0
2024-05-03 11:00 | 29.3 | 59 | 3.78 | 839 | 26 | 30 | 17 | 0 | 9.1805
2024-05-03 12:00 | 30.3 | 53 | 3.76 | 922 | 26 | 30 | 17 | 0 | 19.1909
2024-05-03 13:00 | 30.9 | 50 | 3.63 | 947 | 26 | 30 | 17 | 0 | 24.7762
2024-05-03 14:00 | 31 | 50 | 4.04 | 883 | 26 | 30 | 17 | 0 | 9.9287
2024-05-03 15:00 | 30.6 | 53 | 4.44 | 768 | 26 | 30 | 17 | 0 | 0
2024-05-03 16:00 | 29.6 | 59 | 4.61 | 602 | 26 | 30 | 17 | 0 | 0
2024-05-03 17:00 | 28.3 | 61 | 4.75 | 394 | 26 | 30 | 17 | 5.6412 | 0
2024-05-03 18:00 | 27.2 | 71 | 3.11 | 182 | 26 | 30 | 17 | 16.3191 | 0
2024-05-03 19:00 | 25.6 | 84 | 1.72 | 30 | 26 | 30 | 17 | 25.2651 | 0
2024-05-03 20:00 | 24.6 | 89 | 1.3 | 0 | 26 | 30 | 17 | 28.9503 | 0
2024-05-03 21:00 | 24.2 | 87 | 2.3 | 0 | 26 | 30 | 17 | 42.4557 | 0
2024-05-03 22:00 | 23.3 | 90 | 2.84 | 0 | 26 | 30 | 17 | 52.4477 | 0
2024-05-03 23:00 | 22.8 | 90 | 2.88 | 0 | 26 | 30 | 17 | 57.7473 | 0
2024-05-04 | 22.5 | 90 | 2.88 | 0 | 26 | 30 | 17 | 60.6594 | 0
2024-05-04 01:00 | 22 | 90 | 2.69 | 0 | 26 | 30 | 17 | 63.1246 | 0
2024-05-04 02:00 | 21.7 | 89 | 2.83 | 0 | 26 | 30 | 17 | 68.6862 | 0
2024-05-04 03:00 | 21.5 | 88 | 2.76 | 0 | 26 | 30 | 17 | 70.598 | 0
2024-05-04 04:00 | 21.3 | 88 | 2.83 | 0 | 26 | 30 | 17 | 73.3719 | 0
2024-05-04 05:00 | 23 | 83 | 3 | 0 | 26 | 30 | 17 | 65.2513 | 0
2024-05-04 06:00 | 23.1 | 82 | 3.4 | 3 | 26 | 30 | 17 | 69.777 | 0
2024-05-04 07:00 | 24.4 | 76 | 3.89 | 90 | 26 | 30 | 17 | 57.8967 | 0
2024-05-04 08:00 | 26.9 | 69 | 3.22 | 283 | 26 | 30 | 17 | 9.7152 | 0
2024-05-04 09:00 | 29.8 | 57 | 3.18 | 500 | 26 | 30 | 17 | 0 | 0
2024-05-04 10:00 | 32.1 | 44 | 2.82 | 698 | 26 | 30 | 17 | 0 | 5.6245
2024-05-04 11:00 | 33.7 | 37 | 2.56 | 850 | 26 | 30 | 17 | 0 | 30.8408
2024-05-04 12:00 | 34.8 | 32 | 1.55 | 937 | 26 | 30 | 17 | 0 | 65.3191
2024-05-04 13:00 | 35.4 | 30 | 0.28 | 954 | 26 | 30 | 17 | 0 | 96.3971
2024-05-04 14:00 | 31.3 | 52 | 9.01 | 898 | 26 | 30 | 17 | 0 | 0
2024-05-04 15:00 | 32.9 | 40 | 4.74 | 768 | 26 | 30 | 17 | 0 | 0
2024-05-04 16:00 | 33.2 | 40 | 3.96 | 601 | 26 | 30 | 17 | 0 | 0
2024-05-04 17:00 | 33 | 40 | 3.2 | 389 | 26 | 30 | 17 | 0 | 0
2024-05-04 18:00 | 31.9 | 48 | 2.55 | 181 | 26 | 30 | 17 | 6.843 | 0
2024-05-04 19:00 | 29.1 | 63 | 2.21 | 30 | 26 | 30 | 17 | 24.6955 | 0
2024-05-04 20:00 | 27.7 | 71 | 2.08 | 0 | 26 | 30 | 17 | 29.0922 | 0
2024-05-04 21:00 | 26.7 | 74 | 2.5 | 0 | 26 | 30 | 17 | 37.0016 | 0
2024-05-04 22:00 | 25.8 | 75 | 3.11 | 0 | 26 | 30 | 17 | 49.192 | 0
2024-05-04 23:00 | 24.9 | 79 | 3 | 0 | 26 | 30 | 17 | 51.7291 | 0
2024-05-05 | 24.3 | 81 | 2.98 | 0 | 26 | 30 | 17 | 54.8691 | 0
2024-05-05 01:00 | 24.1 | 79 | 3.42 | 0 | 26 | 30 | 17 | 64.0242 | 0
2024-05-05 02:00 | 23.7 | 77 | 3.18 | 0 | 26 | 30 | 17 | 68.0302 | 0
2024-05-05 03:00 | 23.1 | 79 | 2.86 | 0 | 26 | 30 | 17 | 67.2418 | 0
2024-05-05 04:00 | 22.6 | 80 | 3.13 | 0 | 26 | 30 | 17 | 74.254 | 0
2024-05-05 05:00 | 25 | 68 | 3.26 | 0 | 26 | 30 | 17 | 68.5715 | 0
2024-05-05 06:00 | 25 | 66 | 3.42 | 3 | 26 | 30 | 17 | 73.0135 | 0
2024-05-05 07:00 | 27 | 58 | 2.57 | 92 | 26 | 30 | 17 | 43.8424 | 0
2024-05-05 08:00 | 28.9 | 59 | 2.98 | 274 | 26 | 30 | 17 | 5.478 | 0
2024-05-05 09:00 | 30.8 | 55 | 1.98 | 491 | 26 | 30 | 17 | 0 | 2.0876
2024-05-05 10:00 | 33.2 | 47 | 3.02 | 697 | 26 | 30 | 17 | 0 | 17.8738
2024-05-05 11:00 | 34 | 41 | 3.54 | 846 | 26 | 30 | 17 | 0 | 23.1454
2024-05-05 12:00 | 35 | 35 | 2.62 | 934 | 26 | 30 | 17 | 0 | 46.8658
2024-05-05 13:00 | 35.8 | 33 | 3.61 | 954 | 26 | 30 | 17 | 0 | 32.5675
2024-05-05 14:00 | 36.1 | 31 | 4.75 | 900 | 26 | 30 | 17 | 0 | 2.1775
2024-05-05 15:00 | 35.8 | 29 | 4.74 | 782 | 26 | 30 | 17 | 0 | 0
2024-05-05 16:00 | 35.2 | 30 | 3.94 | 609 | 26 | 30 | 17 | 0 | 0
2024-05-05 17:00 | 34.8 | 27 | 3.3 | 398 | 26 | 30 | 17 | 5.8737 | 0
2024-05-05 18:00 | 33 | 32 | 3.3 | 186 | 26 | 30 | 17 | 36.8902 | 0
2024-05-05 19:00 | 30.4 | 46 | 3.19 | 31 | 26 | 30 | 17 | 49.6328 | 0
2024-05-05 20:00 | 29.2 | 53 | 2.2 | 0 | 26 | 30 | 17 | 41.5561 | 0
2024-05-05 21:00 | 28 | 62 | 1.51 | 0 | 26 | 30 | 17 | 31.7112 | 0
2024-05-05 22:00 | 27.6 | 66 | 0.85 | 0 | 26 | 30 | 17 | 23.0902 | 0
2024-05-05 23:00 | 26.8 | 68 | 1.12 | 0 | 26 | 30 | 17 | 29.2156 | 0
2024-05-06 | 25.3 | 70 | 1.8 | 0 | 26 | 30 | 17 | 45.485 | 0
2024-05-06 01:00 | 24.7 | 70 | 1.32 | 0 | 26 | 30 | 17 | 42.4448 | 0
2024-05-06 02:00 | 23.8 | 72 | 1.7 | 0 | 26 | 30 | 17 | 52.3388 | 0
2024-05-06 03:00 | 23.2 | 71 | 1.97 | 0 | 26 | 30 | 17 | 61.5731 | 0
2024-05-06 04:00 | 22.9 | 67 | 2.18 | 0 | 26 | 30 | 17 | 70.9327 | 0
2024-05-06 05:00 | 23.8 | 62 | 1.84 | 0 | 26 | 30 | 17 | 63.3119 | 0
2024-05-06 06:00 | 23.7 | 63 | 2 | 3 | 26 | 30 | 17 | 65.5931 | 0
2024-05-06 07:00 | 25.7 | 56 | 1.28 | 94 | 26 | 30 | 17 | 34.0661 | 0
2024-05-06 08:00 | 28.7 | 46 | 0.41 | 287 | 26 | 30 | 17 | 0 | 0
2024-05-06 09:00 | 31.3 | 37 | 0.2 | 505 | 26 | 30 | 17 | 0 | 26.0946
2024-05-06 10:00 | 34.4 | 25 | 1.3 | 704 | 26 | 30 | 17 | 0 | 29.7307
2024-05-06 11:00 | 37.3 | 16 | 2.8 | 856 | 26 | 30 | 17 | 0 | 3.3524
2024-05-06 12:00 | 38.6 | 16 | 2.05 | 945 | 26 | 30 | 17 | 0 | 44.2991
2024-05-06 13:00 | 38.2 | 21 | 3.89 | 963 | 26 | 30 | 17 | 0 | 12.5316
2024-05-06 14:00 | 37.7 | 21 | 5.24 | 906 | 26 | 30 | 17 | 0 | 0
2024-05-06 15:00 | 37 | 21 | 5.5 | 787 | 26 | 30 | 17 | 0 | 0
2024-05-06 16:00 | 35.8 | 25 | 5.71 | 613 | 26 | 30 | 17 | 0.0482 | 0
2024-05-06 17:00 | 33.7 | 30 | 5.05 | 403 | 26 | 30 | 17 | 26.5514 | 0
2024-05-06 18:00 | 31.6 | 45 | 4.65 | 189 | 26 | 30 | 17 | 31.4279 | 0
2024-05-06 19:00 | 29.5 | 63 | 3.14 | 32 | 26 | 30 | 17 | 26.3941 | 0
2024-05-06 20:00 | 28.5 | 68 | 2.69 | 0 | 26 | 30 | 17 | 29.9267 | 0
2024-05-06 21:00 | 28 | 68 | 2.77 | 0 | 26 | 30 | 17 | 35.2038 | 0
2024-05-06 22:00 | 27.4 | 69 | 2.55 | 0 | 26 | 30 | 17 | 37.7263 | 0
2024-05-06 23:00 | 26.5 | 72 | 2.06 | 0 | 26 | 30 | 17 | 37.4271 | 0
2024-05-07 | 25.9 | 70 | 2.28 | 0 | 26 | 30 | 17 | 46.7237 | 0
2024-05-07 01:00 | 25 | 69 | 1.97 | 0 | 26 | 30 | 17 | 50.8378 | 0
2024-05-07 02:00 | 24.7 | 64 | 2.43 | 0 | 26 | 30 | 17 | 64.9851 | 0
2024-05-07 03:00 | 24 | 61 | 2.2 | 0 | 26 | 30 | 17 | 69.5018 | 0
2024-05-07 04:00 | 23.7 | 57 | 2.3 | 0 | 26 | 30 | 17 | 77.468 | 0
2024-05-07 05:00 | 24.6 | 49 | 2.3 | 0 | 26 | 30 | 17 | 79.9374 | 0
2024-05-07 06:00 | 25.2 | 42 | 3.93 | 3 | 26 | 30 | 17 | 116.2346 | 0
2024-05-07 07:00 | 27.9 | 36 | 4.34 | 96 | 26 | 30 | 17 | 98.7084 | 0
2024-05-07 08:00 | 31.8 | 41 | 4.1 | 291 | 26 | 30 | 17 | 21.0611 | 0
2024-05-07 09:00 | 35.2 | 40 | 6.21 | 506 | 26 | 30 | 17 | 0 | 0
2024-05-07 10:00 | 38.2 | 30 | 6.77 | 699 | 26 | 30 | 17 | 0 | 0
2024-05-07 11:00 | 40.2 | 23 | 5.37 | 846 | 26 | 30 | 17 | 0 | 0
2024-05-07 12:00 | 41.3 | 19 | 3.95 | 903 | 26 | 30 | 17 | 0 | 22.1073
2024-05-07 13:00 | 39.2 | 29 | 6.97 | 874 | 26 | 30 | 17 | 0 | 0
2024-05-07 14:00 | 37.5 | 28 | 7.56 | 852 | 26 | 30 | 17 | 0 | 0
2024-05-07 15:00 | 37.2 | 25 | 7.49 | 774 | 26 | 30 | 17 | 0 | 0
2024-05-07 16:00 | 36.5 | 28 | 6.31 | 609 | 26 | 30 | 17 | 0 | 0
2024-05-07 17:00 | 33.4 | 45 | 5.48 | 398 | 26 | 30 | 17 | 0 | 0
2024-05-07 18:00 | 31.9 | 49 | 4.34 | 185 | 26 | 30 | 17 | 15.95 | 0
2024-05-07 19:00 | 30.4 | 57 | 3.92 | 32 | 26 | 30 | 17 | 32.6805 | 0
2024-05-07 20:00 | 29.9 | 57 | 3.26 | 0 | 26 | 30 | 17 | 38.36 | 0
2024-05-07 21:00 | 29.4 | 56 | 3.05 | 0 | 26 | 30 | 17 | 43.4471 | 0
2024-05-07 22:00 | 29 | 52 | 3.04 | 0 | 26 | 30 | 17 | 53.8975 | 0
2024-05-07 23:00 | 28.4 | 47 | 3 | 0 | 26 | 30 | 17 | 66.8416 | 0
2024-05-08 | 27.5 | 45 | 2.57 | 0 | 26 | 30 | 17 | 70.2067 | 0
2024-05-08 01:00 | 26.6 | 47 | 2.18 | 0 | 26 | 30 | 17 | 66.9679 | 0
2024-05-08 02:00 | 26.1 | 46 | 2.33 | 0 | 26 | 30 | 17 | 74.2008 | 0
2024-05-08 03:00 | 25.9 | 47 | 1.79 | 0 | 26 | 30 | 17 | 63.6713 | 0
2024-05-08 04:00 | 25.2 | 47 | 2.14 | 0 | 26 | 30 | 17 | 75.0247 | 0
2024-05-08 05:00 | 28.6 | 32 | 0.54 | 0 | 26 | 30 | 17 | 33.6232 | 0
2024-05-08 06:00 | 27.2 | 37 | 1.1 | 4 | 26 | 30 | 17 | 49.489 | 0
2024-05-08 07:00 | 28 | 34 | 1.02 | 96 | 26 | 30 | 17 | 33.8815 | 0
2024-05-08 08:00 | 30.5 | 30 | 1.14 | 289 | 26 | 30 | 17 | 3.8144 | 0
2024-05-08 09:00 | 32.9 | 31 | 0.28 | 504 | 26 | 30 | 17 | 0 | 27.6442
2024-05-08 10:00 | 36 | 25 | 0.86 | 699 | 26 | 30 | 17 | 0 | 51.3029
2024-05-08 11:00 | 38.4 | 21 | 0.45 | 847 | 26 | 30 | 17 | 0 | 85.5836
2024-05-08 12:00 | 39.8 | 20 | 3.32 | 935 | 26 | 30 | 17 | 0 | 30.09
2024-05-08 13:00 | 38 | 24 | 7.38 | 951 | 26 | 30 | 17 | 0 | 0
2024-05-08 14:00 | 37.1 | 29 | 6.73 | 899 | 26 | 30 | 17 | 0 | 0
2024-05-08 15:00 | 36.3 | 32 | 6.16 | 780 | 26 | 30 | 17 | 0 | 0
2024-05-08 16:00 | 35.4 | 36 | 6.19 | 606 | 26 | 30 | 17 | 0 | 0
2024-05-08 17:00 | 34.3 | 39 | 5.69 | 397 | 26 | 30 | 17 | 0 | 0
2024-05-08 18:00 | 33.3 | 43 | 3.19 | 186 | 26 | 30 | 17 | 8.4254 | 0
2024-05-08 19:00 | 32.1 | 48 | 2.76 | 32 | 26 | 30 | 17 | 26.7992 | 0
2024-05-08 20:00 | 31.2 | 54 | 1.22 | 0 | 26 | 30 | 17 | 17.2152 | 0
2024-05-08 21:00 | 30.5 | 57 | 2.14 | 0 | 26 | 30 | 17 | 25.3154 | 0
2024-05-08 22:00 | 29.2 | 65 | 1.56 | 0 | 26 | 30 | 17 | 21.0577 | 0
2024-05-08 23:00 | 28.2 | 73 | 1.8 | 0 | 26 | 30 | 17 | 21.0521 | 0
2024-05-09 | 27.1 | 81 | 1.6 | 0 | 26 | 30 | 17 | 20.1216 | 0
2024-05-09 01:00 | 26.5 | 85 | 1.77 | 0 | 26 | 30 | 17 | 21.6125 | 0
2024-05-09 02:00 | 26.2 | 86 | 2.1 | 0 | 26 | 30 | 17 | 24.5905 | 0
2024-05-09 03:00 | 26.2 | 85 | 2.33 | 0 | 26 | 30 | 17 | 26.8387 | 0
2024-05-09 04:00 | 25.8 | 86 | 2.33 | 0 | 26 | 30 | 17 | 29.3723 | 0
2024-05-09 05:00 | 26.4 | 78 | 2.52 | 0 | 26 | 30 | 17 | 34.7496 | 0
2024-05-09 06:00 | 26.1 | 79 | 2.42 | 4 | 26 | 30 | 17 | 35.0206 | 0
2024-05-09 07:00 | 27.8 | 70 | 1.92 | 98 | 26 | 30 | 17 | 15.1044 | 0
2024-05-09 08:00 | 30.6 | 58 | 1.43 | 293 | 26 | 30 | 17 | 0 | 0
2024-05-09 09:00 | 32.8 | 49 | 0.73 | 512 | 26 | 30 | 17 | 0 | 37.7011
2024-05-09 10:00 | 35.4 | 36 | 2.44 | 711 | 26 | 30 | 17 | 0 | 25.588
2024-05-09 11:00 | 37.1 | 26 | 4.4 | 862 | 26 | 30 | 17 | 0 | 0
2024-05-09 12:00 | 37.2 | 25 | 5.56 | 955 | 26 | 30 | 17 | 0 | 0
2024-05-09 13:00 | 36.9 | 27 | 6.66 | 973 | 26 | 30 | 17 | 0 | 0
2024-05-09 14:00 | 35.9 | 30 | 7.98 | 918 | 26 | 30 | 17 | 0 | 0
2024-05-09 15:00 | 36.2 | 28 | 7.44 | 801 | 26 | 30 | 17 | 0 | 0
2024-05-09 16:00 | 35.5 | 29 | 6.88 | 625 | 26 | 30 | 17 | 0 | 0
2024-05-09 17:00 | 33.7 | 36 | 6.48 | 409 | 26 | 30 | 17 | 17.2877 | 0
2024-05-09 18:00 | 31.5 | 46 | 6.48 | 193 | 26 | 30 | 17 | 41.8952 | 0
2024-05-09 19:00 | 29.9 | 53 | 5.54 | 34 | 26 | 30 | 17 | 58.5568 | 0
2024-05-09 20:00 | 29.6 | 49 | 5.32 | 0 | 26 | 30 | 17 | 75.976 | 0
2024-05-09 21:00 | 28.8 | 51 | 5.61 | 0 | 26 | 30 | 17 | 83.5767 | 0
2024-05-09 22:00 | 28 | 57 | 5.82 | 0 | 26 | 30 | 17 | 80.8089 | 0
2024-05-09 23:00 | 27.2 | 64 | 5.5 | 0 | 26 | 30 | 17 | 72.3262 | 0
2024-05-10 | 26.8 | 64 | 5.7 | 0 | 26 | 30 | 17 | 79.552 | 0
2024-05-10 01:00 | 26.3 | 66 | 5.6 | 0 | 26 | 30 | 17 | 81.1334 | 0
2024-05-10 02:00 | 25.6 | 71 | 5.2 | 0 | 26 | 30 | 17 | 76.6002 | 0
2024-05-10 03:00 | 25.1 | 75 | 4.62 | 0 | 26 | 30 | 17 | 70.3637 | 0
2024-05-10 04:00 | 24.5 | 79 | 4.39 | 0 | 26 | 30 | 17 | 68.8701 | 0
2024-05-10 05:00 | 24.7 | 78 | 4.24 | 0 | 26 | 30 | 17 | 66.7266 | 0
2024-05-10 06:00 | 24.5 | 76 | 4.2 | 4 | 26 | 30 | 17 | 71.5069 | 0
2024-05-10 07:00 | 25.9 | 67 | 3.77 | 105 | 26 | 30 | 17 | 52.5393 | 0
2024-05-10 08:00 | 27.6 | 57 | 4.78 | 307 | 26 | 30 | 17 | 35.0219 | 0
2024-05-10 09:00 | 29.1 | 50 | 4.69 | 529 | 26 | 30 | 17 | 2.2425 | 0
2024-05-10 10:00 | 30.3 | 46 | 4.9 | 728 | 26 | 30 | 17 | 0 | 0
2024-05-10 11:00 | 31.1 | 43 | 5.21 | 880 | 26 | 30 | 17 | 0 | 0
2024-05-10 12:00 | 31.8 | 39 | 5.23 | 971 | 26 | 30 | 17 | 0 | 0
2024-05-10 13:00 | 32.3 | 36 | 5.74 | 992 | 26 | 30 | 17 | 0 | 0
2024-05-10 14:00 | 32.4 | 36 | 6.3 | 943 | 26 | 30 | 17 | 0 | 0
2024-05-10 15:00 | 31.7 | 39 | 7.38 | 825 | 26 | 30 | 17 | 0 | 0
2024-05-10 16:00 | 30.9 | 44 | 7.2 | 643 | 26 | 30 | 17 | 1.8487 | 0
2024-05-10 17:00 | 30.2 | 46 | 6.89 | 424 | 26 | 30 | 17 | 32.6306 | 0
2024-05-10 18:00 | 29 | 52 | 5.85 | 202 | 26 | 30 | 17 | 53.1584 | 0
2024-05-10 19:00 | 28 | 57 | 4.7 | 37 | 26 | 30 | 17 | 65.9317 | 0
2024-05-10 20:00 | 27.4 | 60 | 3.21 | 0 | 26 | 30 | 17 | 57.1815 | 0
2024-05-10 21:00 | 26.6 | 66 | 2.38 | 0 | 26 | 30 | 17 | 46.9233 | 0
2024-05-10 22:00 | 25.7 | 73 | 2.1 | 0 | 26 | 30 | 17 | 43.0221 | 0
2024-05-10 23:00 | 25.1 | 77 | 2.3 | 0 | 26 | 30 | 17 | 45.57 | 0
2024-05-11 | 24.3 | 82 | 2.14 | 0 | 26 | 30 | 17 | 45.223 | 0
2024-05-11 01:00 | 23.4 | 87 | 1.92 | 0 | 26 | 30 | 17 | 45.225 | 0
2024-05-11 02:00 | 22.7 | 90 | 3.14 | 0 | 26 | 30 | 17 | 61.4668 | 0
2024-05-11 03:00 | 21.6 | 95 | 2.82 | 0 | 26 | 30 | 17 | 63.2457 | 0
2024-05-11 04:00 | 21.4 | 94 | 2.98 | 0 | 26 | 30 | 17 | 68.141 | 0
2024-05-11 05:00 | 21.7 | 93 | 2.62 | 0 | 26 | 30 | 17 | 61.9557 | 0
2024-05-11 06:00 | 21.3 | 94 | 2.8 | 5 | 26 | 30 | 17 | 66.1888 | 0
2024-05-11 07:00 | 22.8 | 85 | 3.01 | 105 | 26 | 30 | 17 | 50.7702 | 0
2024-05-11 08:00 | 25.9 | 70 | 2.8 | 305 | 26 | 30 | 17 | 11.0627 | 0
2024-05-11 09:00 | 28.6 | 56 | 2.56 | 527 | 26 | 30 | 17 | 0 | 0
2024-05-11 10:00 | 31 | 46 | 2.06 | 725 | 26 | 30 | 17 | 0 | 20.5749
2024-05-11 11:00 | 33 | 40 | 2.22 | 875 | 26 | 30 | 17 | 0 | 41.9816
2024-05-11 12:00 | 34.4 | 37 | 3.05 | 962 | 26 | 30 | 17 | 0 | 41.6818
2024-05-11 13:00 | 34.5 | 40 | 4.69 | 979 | 26 | 30 | 17 | 0 | 25.4009
2024-05-11 14:00 | 34.4 | 35 | 5.45 | 922 | 26 | 30 | 17 | 0 | 0
2024-05-11 15:00 | 33.9 | 39 | 5.16 | 802 | 26 | 30 | 17 | 0 | 0
2024-05-11 16:00 | 33.4 | 43 | 5.33 | 625 | 26 | 30 | 17 | 0 | 0
2024-05-11 17:00 | 31.9 | 49 | 5.05 | 412 | 26 | 30 | 17 | 0 | 0
2024-05-11 18:00 | 30.1 | 59 | 4.72 | 197 | 26 | 30 | 17 | 13.5087 | 0
2024-05-11 19:00 | 28.3 | 71 | 3.41 | 36 | 26 | 30 | 17 | 25.9291 | 0
2024-05-11 20:00 | 27.8 | 79 | 2.7 | 0 | 26 | 30 | 17 | 20.5603 | 0
2024-05-11 21:00 | 27.3 | 83 | 1.84 | 0 | 26 | 30 | 17 | 17.4387 | 0
2024-05-11 22:00 | 26.2 | 90 | 1.22 | 0 | 26 | 30 | 17 | 17.1325 | 0
2024-05-11 23:00 | 25.6 | 93 | 1.1 | 0 | 26 | 30 | 17 | 18.3976 | 0
2024-05-12 | 25.8 | 92 | 0.36 | 0 | 26 | 30 | 17 | 15.5112 | 0
2024-05-12 01:00 | 25.1 | 95 | 0.32 | 0 | 26 | 30 | 17 | 17.3745 | 0
2024-05-12 02:00 | 24 | 98 | 1 | 0 | 26 | 30 | 17 | 24.4697 | 0
2024-05-12 03:00 | 23 | 98 | 1.3 | 0 | 26 | 30 | 17 | 33.1996 | 0
2024-05-12 04:00 | 22.2 | 97 | 2.06 | 0 | 26 | 30 | 17 | 47.511 | 0
2024-05-12 05:00 | 22.1 | 100 | 2.06 | 0 | 26 | 30 | 17 | 45.7508 | 0
2024-05-12 06:00 | 21.3 | 99 | 1.36 | 4 | 26 | 30 | 17 | 43.6851 | 0
2024-05-12 07:00 | 21.2 | 99 | 0.92 | 79 | 26 | 30 | 17 | 27.9215 | 0
2024-05-12 08:00 | 24.6 | 82 | 1.17 | 256 | 26 | 30 | 17 | 0 | 0
2024-05-12 09:00 | 30.6 | 46 | 0 | 517 | 26 | 30 | 17 | 0 | 30.6379
2024-05-12 10:00 | 35.3 | 26 | 0.86 | 724 | 26 | 30 | 17 | 0 | 52.8592
2024-05-12 11:00 | 38 | 16 | 1.03 | 880 | 26 | 30 | 17 | 0 | 66.8388
2024-05-12 12:00 | 39.5 | 14 | 1.62 | 969 | 26 | 30 | 17 | 0 | 61.177
2024-05-12 13:00 | 40.3 | 15 | 2.09 | 982 | 26 | 30 | 17 | 0 | 54.9065
2024-05-12 14:00 | 40.6 | 15 | 3.42 | 926 | 26 | 30 | 17 | 0 | 15.5351
2024-05-12 15:00 | 38.1 | 26 | 6.77 | 804 | 26 | 30 | 17 | 0 | 0
2024-05-12 16:00 | 36.9 | 23 | 7.38 | 621 | 26 | 30 | 17 | 9.3504 | 0
2024-05-12 17:00 | 34.5 | 35 | 6.31 | 409 | 26 | 30 | 17 | 9.2494 | 0
2024-05-12 18:00 | 32.9 | 44 | 4.48 | 196 | 26 | 30 | 17 | 16.9973 | 0
2024-05-12 19:00 | 31.1 | 56 | 3.06 | 37 | 26 | 30 | 17 | 22.0393 | 0
2024-05-12 20:00 | 30.1 | 63 | 1.71 | 0 | 26 | 30 | 17 | 17.8 | 0
2024-05-12 21:00 | 29.6 | 62 | 1.99 | 0 | 26 | 30 | 17 | 24.5543 | 0
2024-05-12 22:00 | 30.1 | 53 | 0.67 | 0 | 26 | 30 | 17 | 17.4284 | 0
2024-05-12 23:00 | 28.7 | 54 | 1.41 | 0 | 26 | 30 | 17 | 34.0181 | 0
2024-05-13 | 27.6 | 51 | 1.79 | 0 | 26 | 30 | 17 | 49.4087 | 0
2024-05-13 01:00 | 26.8 | 46 | 2.27 | 0 | 26 | 30 | 17 | 68.4922 | 0
2024-05-13 02:00 | 26.6 | 48 | 1.2 | 0 | 26 | 30 | 17 | 46.7477 | 0
2024-05-13 03:00 | 25.8 | 53 | 1.25 | 0 | 26 | 30 | 17 | 47.9267 | 0
2024-05-13 04:00 | 24.7 | 56 | 2.79 | 0 | 26 | 30 | 17 | 80.2482 | 0
2024-05-13 05:00 | 25.4 | 53 | 3.16 | 0 | 26 | 30 | 17 | 84.7833 | 0
2024-05-13 06:00 | 26.4 | 45 | 4.34 | 5 | 26 | 30 | 17 | 107.1102 | 0
2024-05-13 07:00 | 29.4 | 36 | 5.2 | 104 | 26 | 30 | 17 | 96.2369 | 0
2024-05-13 08:00 | 32.1 | 40 | 5.85 | 301 | 26 | 30 | 17 | 34.2353 | 0
2024-05-13 09:00 | 34.6 | 39 | 7.62 | 518 | 26 | 30 | 17 | 0 | 0
2024-05-13 10:00 | 37.2 | 31 | 7.91 | 713 | 26 | 30 | 17 | 0 | 0
2024-05-13 11:00 | 39.4 | 23 | 7.28 | 862 | 26 | 30 | 17 | 0 | 0
2024-05-13 12:00 | 41 | 18 | 6.02 | 950 | 26 | 30 | 17 | 0 | 0
2024-05-13 13:00 | 42 | 15 | 4.25 | 967 | 26 | 30 | 17 | 0 | 14.1012
2024-05-13 14:00 | 42.5 | 13 | 3.22 | 913 | 26 | 30 | 17 | 0 | 24.1914
2024-05-13 15:00 | 41.2 | 20 | 4.21 | 794 | 26 | 30 | 17 | 0 | 6.0427
2024-05-13 16:00 | 39 | 28 | 5.62 | 615 | 26 | 30 | 17 | 0 | 0
2024-05-13 17:00 | 35.7 | 38 | 6.02 | 406 | 26 | 30 | 17 | 0 | 0
2024-05-13 18:00 | 34.3 | 43 | 4 | 195 | 26 | 30 | 17 | 1.5271 | 0
2024-05-13 19:00 | 32.6 | 54 | 4.74 | 37 | 26 | 30 | 17 | 15.1151 | 0
2024-05-13 20:00 | 32.3 | 48 | 2.72 | 0 | 26 | 30 | 17 | 29.0801 | 0
2024-05-13 21:00 | 31.7 | 47 | 2.62 | 0 | 26 | 30 | 17 | 35.2991 | 0
2024-05-13 22:00 | 31.1 | 46 | 2.4 | 0 | 26 | 30 | 17 | 39.7322 | 0
2024-05-13 23:00 | 30.2 | 45 | 2.32 | 0 | 26 | 30 | 17 | 47.1044 | 0
2024-05-14 | 29.6 | 43 | 2.91 | 0 | 26 | 30 | 17 | 62.6037 | 0
2024-05-14 01:00 | 29 | 39 | 2.79 | 0 | 26 | 30 | 17 | 71.9814 | 0
2024-05-14 02:00 | 28.5 | 37 | 2.91 | 0 | 26 | 30 | 17 | 80.8056 | 0
2024-05-14 03:00 | 28 | 37 | 3.16 | 0 | 26 | 30 | 17 | 88.8486 | 0
2024-05-14 04:00 | 27.9 | 41 | 3.8 | 0 | 26 | 30 | 17 | 93.2496 | 0
2024-05-14 05:00 | 28.3 | 43 | 3.28 | 0 | 26 | 30 | 17 | 78.369 | 0
2024-05-14 06:00 | 28.8 | 39 | 5.38 | 5 | 26 | 30 | 17 | 110.8146 | 0
2024-05-14 07:00 | 31.1 | 27 | 5.51 | 104 | 26 | 30 | 17 | 107.9281 | 0
2024-05-14 08:00 | 33.5 | 29 | 6 | 298 | 26 | 30 | 17 | 56.1533 | 0
2024-05-14 09:00 | 35.4 | 31 | 8.23 | 512 | 26 | 30 | 17 | 11.6017 | 0
2024-05-14 10:00 | 37.7 | 28 | 8.3 | 703 | 26 | 30 | 17 | 0 | 0
2024-05-14 11:00 | 39.6 | 21 | 7.92 | 851 | 26 | 30 | 17 | 0 | 0
2024-05-14 12:00 | 40.7 | 18 | 7.03 | 938 | 26 | 30 | 17 | 0 | 0
2024-05-14 13:00 | 41.5 | 16 | 6.63 | 956 | 26 | 30 | 17 | 0 | 0
2024-05-14 14:00 | 42.3 | 15 | 6.02 | 904 | 26 | 30 | 17 | 0 | 0
2024-05-14 15:00 | 42.5 | 14 | 4.27 | 785 | 26 | 30 | 17 | 0 | 0
2024-05-14 16:00 | 40.1 | 21 | 3.45 | 613 | 26 | 30 | 17 | 0 | 0
2024-05-14 17:00 | 39.9 | 17 | 2.91 | 406 | 26 | 30 | 17 | 0 | 0
2024-05-14 18:00 | 35.3 | 42 | 4.21 | 195 | 26 | 30 | 17 | 0 | 0
2024-05-14 19:00 | 32.6 | 47 | 6.35 | 37 | 26 | 30 | 17 | 42.5636 | 0
2024-05-14 20:00 | 34 | 37 | 3.61 | 0 | 26 | 30 | 17 | 44.4592 | 0
2024-05-14 21:00 | 33 | 37 | 4.07 | 0 | 26 | 30 | 17 | 58.1673 | 0
2024-05-14 22:00 | 32 | 40 | 3.77 | 0 | 26 | 30 | 17 | 57.6102 | 0
2024-05-14 23:00 | 31.4 | 41 | 3.18 | 0 | 26 | 30 | 17 | 54.743 | 0
2024-05-15 | 30.9 | 39 | 3.57 | 0 | 26 | 30 | 17 | 67.7696 | 0
2024-05-15 01:00 | 30.5 | 37 | 3.67 | 0 | 26 | 30 | 17 | 76.7856 | 0
2024-05-15 02:00 | 29.9 | 37 | 3.51 | 0 | 26 | 30 | 17 | 79.6273 | 0
2024-05-15 03:00 | 29.2 | 38 | 3.24 | 0 | 26 | 30 | 17 | 79.3242 | 0
2024-05-15 04:00 | 28.6 | 42 | 3.18 | 0 | 26 | 30 | 17 | 76.1522 | 0
2024-05-15 05:00 | 28.8 | 44 | 3.19 | 0 | 26 | 30 | 17 | 71.2139 | 0
2024-05-15 06:00 | 28.5 | 40 | 2.83 | 5 | 26 | 30 | 17 | 74.0114 | 0
2024-05-15 07:00 | 31.7 | 25 | 5.32 | 104 | 26 | 30 | 17 | 105.268 | 0
2024-05-15 08:00 | 34 | 25 | 7.16 | 297 | 26 | 30 | 17 | 77.8854 | 0
2024-05-15 09:00 | 35.8 | 25 | 8.3 | 510 | 26 | 30 | 17 | 36.2907 | 0
2024-05-15 10:00 | 37.7 | 23 | 7.99 | 702 | 26 | 30 | 17 | 0 | 0
2024-05-15 11:00 | 39.4 | 20 | 7.25 | 848 | 26 | 30 | 17 | 0 | 0
2024-05-15 12:00 | 40.6 | 18 | 6.04 | 934 | 26 | 30 | 17 | 0 | 0
2024-05-15 13:00 | 41.5 | 17 | 4.53 | 951 | 26 | 30 | 17 | 0 | 11.2527
2024-05-15 14:00 | 40.7 | 20 | 3.9 | 897 | 26 | 30 | 17 | 0 | 20.9873
2024-05-15 15:00 | 39.5 | 23 | 6.41 | 777 | 26 | 30 | 17 | 0 | 0
2024-05-15 16:00 | 38.2 | 25 | 7.12 | 606 | 26 | 30 | 17 | 0 | 0
2024-05-15 17:00 | 37.2 | 25 | 5.42 | 403 | 26 | 30 | 17 | 10.7015 | 0
2024-05-15 18:00 | 35.5 | 34 | 4.62 | 194 | 26 | 30 | 17 | 18.9718 | 0
2024-05-15 19:00 | 33.4 | 42 | 3.54 | 37 | 26 | 30 | 17 | 32.3102 | 0
2024-05-15 20:00 | 32.3 | 48 | 4.38 | 0 | 26 | 30 | 17 | 39.0465 | 0
2024-05-15 21:00 | 32.3 | 44 | 3.36 | 0 | 26 | 30 | 17 | 42.0023 | 0
2024-05-15 22:00 | 31.7 | 44 | 3.91 | 0 | 26 | 30 | 17 | 52.4385 | 0
2024-05-15 23:00 | 31 | 42 | 3.31 | 0 | 26 | 30 | 17 | 57.646 | 0
2024-05-16 | 30.3 | 42 | 3.24 | 0 | 26 | 30 | 17 | 62.8998 | 0
2024-05-16 01:00 | 29.8 | 40 | 3.13 | 0 | 26 | 30 | 17 | 69.3188 | 0
2024-05-16 02:00 | 29.3 | 40 | 3.07 | 0 | 26 | 30 | 17 | 72.4122 | 0
2024-05-16 03:00 | 28.6 | 39 | 2.71 | 0 | 26 | 30 | 17 | 73.5082 | 0
2024-05-16 04:00 | 28.3 | 37 | 3.3 | 0 | 26 | 30 | 17 | 89.0359 | 0
2024-05-16 05:00 | 28.5 | 38 | 2.77 | 0 | 26 | 30 | 17 | 76.7843 | 0
2024-05-16 06:00 | 28.6 | 35 | 3.22 | 6 | 26 | 30 | 17 | 88.0409 | 0
2024-05-16 07:00 | 30.8 | 30 | 2.62 | 105 | 26 | 30 | 17 | 57.3999 | 0
2024-05-16 08:00 | 34.3 | 26 | 2.94 | 299 | 26 | 30 | 17 | 20.4822 | 0
2024-05-16 09:00 | 37.7 | 22 | 4.22 | 512 | 26 | 30 | 17 | 0 | 0
2024-05-16 10:00 | 38.8 | 17 | 7.68 | 704 | 26 | 30 | 17 | 8.8415 | 0
2024-05-16 11:00 | 40.1 | 15 | 6.55 | 853 | 26 | 30 | 17 | 0 | 0
2024-05-16 12:00 | 41.2 | 14 | 4.84 | 941 | 26 | 30 | 17 | 0 | 0
2024-05-16 13:00 | 41.5 | 14 | 3.76 | 959 | 26 | 30 | 17 | 0 | 15.1081
2024-05-16 14:00 | 40.6 | 19 | 6.32 | 906 | 26 | 30 | 17 | 0 | 0
2024-05-16 15:00 | 39.4 | 19 | 8.59 | 786 | 26 | 30 | 17 | 0 | 0
2024-05-16 16:00 | 38.3 | 23 | 7.6 | 615 | 26 | 30 | 17 | 0 | 0
2024-05-16 17:00 | 36.7 | 24 | 7.28 | 409 | 26 | 30 | 17 | 34.8504 | 0
2024-05-16 18:00 | 34.1 | 35 | 6.3 | 198 | 26 | 30 | 17 | 42.9702 | 0
2024-05-16 19:00 | 32.4 | 44 | 3.94 | 39 | 26 | 30 | 17 | 40.1427 | 0
2024-05-16 20:00 | 31.6 | 50 | 3.21 | 0 | 26 | 30 | 17 | 34.9025 | 0
2024-05-16 21:00 | 31 | 52 | 3.54 | 0 | 26 | 30 | 17 | 38.9594 | 0
2024-05-16 22:00 | 30.7 | 47 | 2.85 | 0 | 26 | 30 | 17 | 45.8614 | 0
2024-05-16 23:00 | 30.2 | 44 | 3.01 | 0 | 26 | 30 | 17 | 57.2339 | 0
2024-05-17 | 29.6 | 42 | 2.6 | 0 | 26 | 30 | 17 | 59.9177 | 0
2024-05-17 01:00 | 29.4 | 39 | 3.13 | 0 | 26 | 30 | 17 | 74.2859 | 0
2024-05-17 02:00 | 28.2 | 42 | 2.06 | 0 | 26 | 30 | 17 | 60.6674 | 0
2024-05-17 03:00 | 27.7 | 43 | 2.15 | 0 | 26 | 30 | 17 | 64.1906 | 0
2024-05-17 04:00 | 27.2 | 45 | 2.26 | 0 | 26 | 30 | 17 | 66.9136 | 0
2024-05-17 05:00 | 27.3 | 48 | 2.22 | 0 | 26 | 30 | 17 | 61.8413 | 0
2024-05-17 06:00 | 27.5 | 47 | 2.86 | 6 | 26 | 30 | 17 | 71.1645 | 0
2024-05-17 07:00 | 29.6 | 40 | 1.8 | 105 | 26 | 30 | 17 | 35.9086 | 0
2024-05-17 08:00 | 33.5 | 30 | 1.8 | 298 | 26 | 30 | 17 | 0.9035 | 0
2024-05-17 09:00 | 37 | 20 | 2.14 | 510 | 26 | 30 | 17 | 0 | 0
2024-05-17 10:00 | 39.5 | 17 | 3.14 | 703 | 26 | 30 | 17 | 0 | 0
2024-05-17 11:00 | 40.8 | 16 | 3.38 | 849 | 26 | 30 | 17 | 0 | 10.9945
2024-05-17 12:00 | 41.6 | 15 | 3.5 | 935 | 26 | 30 | 17 | 0 | 22.1278
2024-05-17 13:00 | 41.3 | 17 | 5.64 | 952 | 26 | 30 | 17 | 0 | 0
2024-05-17 14:00 | 39.8 | 21 | 8.13 | 899 | 26 | 30 | 17 | 0 | 0
2024-05-17 15:00 | 38.4 | 25 | 8.02 | 781 | 26 | 30 | 17 | 0 | 0
2024-05-17 16:00 | 36.6 | 32 | 7.92 | 611 | 26 | 30 | 17 | 0 | 0
2024-05-17 17:00 | 35.8 | 33 | 6.37 | 407 | 26 | 30 | 17 | 0.4865 | 0
2024-05-17 18:00 | 34.3 | 40 | 5.5 | 198 | 26 | 30 | 17 | 17.4738 | 0
2024-05-17 19:00 | 32.2 | 52 | 3.77 | 39 | 26 | 30 | 17 | 21.9629 | 0
2024-05-17 20:00 | 31.8 | 56 | 2.2 | 0 | 26 | 30 | 17 | 16.523 | 0
2024-05-17 21:00 | 31.4 | 54 | 1.9 | 0 | 26 | 30 | 17 | 21.0217 | 0
2024-05-17 22:00 | 30.5 | 56 | 2.06 | 0 | 26 | 30 | 17 | 26.1772 | 0
2024-05-17 23:00 | 30 | 56 | 2.73 | 0 | 26 | 30 | 17 | 35.3693 | 0
2024-05-18 | 29.4 | 54 | 2.94 | 0 | 26 | 30 | 17 | 45.9155 | 0
2024-05-18 01:00 | 28.9 | 50 | 2.6 | 0 | 26 | 30 | 17 | 52.8947 | 0
2024-05-18 02:00 | 28.5 | 47 | 2.69 | 0 | 26 | 30 | 17 | 61.7463 | 0
2024-05-18 03:00 | 28 | 45 | 2.75 | 0 | 26 | 30 | 17 | 69.4465 | 0
2024-05-18 04:00 | 27.6 | 44 | 2.94 | 0 | 26 | 30 | 17 | 77.0015 | 0
2024-05-18 05:00 | 27.7 | 45 | 2.19 | 0 | 26 | 30 | 17 | 62.4082 | 0
2024-05-18 06:00 | 27.6 | 44 | 2.33 | 6 | 26 | 30 | 17 | 65.96 | 0
2024-05-18 07:00 | 29.4 | 38 | 1.49 | 107 | 26 | 30 | 17 | 33.2727 | 0
2024-05-18 08:00 | 33.2 | 29 | 1.26 | 301 | 26 | 30 | 17 | 0 | 0
2024-05-18 09:00 | 36.3 | 22 | 1.25 | 515 | 26 | 30 | 17 | 0 | 10.6237
2024-05-18 10:00 | 38.2 | 19 | 1.71 | 708 | 26 | 30 | 17 | 0 | 26.4711
2024-05-18 11:00 | 39.2 | 19 | 4.43 | 854 | 26 | 30 | 17 | 0 | 0
2024-05-18 12:00 | 39.2 | 19 | 5.46 | 940 | 26 | 30 | 17 | 0 | 0
2024-05-18 13:00 | 38.9 | 20 | 6.08 | 959 | 26 | 30 | 17 | 0 | 0
2024-05-18 14:00 | 38.4 | 22 | 6.41 | 908 | 26 | 30 | 17 | 0 | 0
2024-05-18 15:00 | 37.7 | 24 | 6.41 | 791 | 26 | 30 | 17 | 0 | 0
2024-05-18 16:00 | 37.2 | 25 | 6.26 | 620 | 26 | 30 | 17 | 0 | 0
2024-05-18 17:00 | 36.1 | 26 | 6.29 | 412 | 26 | 30 | 17 | 24.8739 | 0
2024-05-18 18:00 | 34.6 | 31 | 5.32 | 201 | 26 | 30 | 17 | 43.3997 | 0
2024-05-18 19:00 | 32.7 | 41 | 3.73 | 40 | 26 | 30 | 17 | 42.6681 | 0
2024-05-18 20:00 | 31.7 | 49 | 2.82 | 0 | 26 | 30 | 17 | 33.2128 | 0
2024-05-18 21:00 | 31.1 | 52 | 2.91 | 0 | 26 | 30 | 17 | 33.6987 | 0
2024-05-18 22:00 | 30.3 | 58 | 3 | 0 | 26 | 30 | 17 | 30.8802 | 0
2024-05-18 23:00 | 29.4 | 69 | 3.57 | 0 | 26 | 30 | 17 | 22.3825 | 0
2024-05-19 | 29 | 71 | 3.08 | 0 | 26 | 30 | 17 | 21.7437 | 0
2024-05-19 01:00 | 28.5 | 72 | 2.67 | 0 | 26 | 30 | 17 | 23.7819 | 0
2024-05-19 02:00 | 27.8 | 71 | 2.2 | 0 | 26 | 30 | 17 | 29.0661 | 0
2024-05-19 03:00 | 27.2 | 72 | 2 | 0 | 26 | 30 | 17 | 31.3685 | 0
2024-05-19 04:00 | 26.7 | 75 | 1.87 | 0 | 26 | 30 | 17 | 30.9726 | 0
2024-05-19 05:00 | 27.9 | 74 | 2.35 | 0 | 26 | 30 | 17 | 25.1605 | 0
2024-05-19 06:00 | 28.1 | 70 | 2.69 | 6 | 26 | 30 | 17 | 29.9491 | 0
2024-05-19 07:00 | 29.6 | 61 | 2.48 | 109 | 26 | 30 | 17 | 14.4723 | 0
2024-05-19 08:00 | 31.1 | 54 | 3.4 | 305 | 26 | 30 | 17 | 0 | 0
2024-05-19 09:00 | 32.2 | 51 | 3.96 | 521 | 26 | 30 | 17 | 0 | 0
2024-05-19 10:00 | 33.5 | 43 | 4.11 | 715 | 26 | 30 | 17 | 0 | 0
2024-05-19 11:00 | 34.6 | 36 | 4.9 | 866 | 26 | 30 | 17 | 0 | 0
2024-05-19 12:00 | 35 | 33 | 6.14 | 957 | 26 | 30 | 17 | 0 | 0
2024-05-19 13:00 | 35 | 31 | 7.05 | 980 | 26 | 30 | 17 | 0 | 0
2024-05-19 14:00 | 34.9 | 30 | 7.33 | 931 | 26 | 30 | 17 | 0 | 0
2024-05-19 15:00 | 34.4 | 32 | 7.22 | 817 | 26 | 30 | 17 | 0 | 0
2024-05-19 16:00 | 33.5 | 36 | 6.8 | 646 | 26 | 30 | 17 | 0 | 0
2024-05-19 17:00 | 32.1 | 48 | 6.7 | 433 | 26 | 30 | 17 | 0 | 0
2024-05-19 18:00 | 30.6 | 58 | 6.14 | 213 | 26 | 30 | 17 | 12.9001 | 0
2024-05-19 19:00 | 29.6 | 64 | 5.54 | 44 | 26 | 30 | 17 | 31.8062 | 0
2024-05-19 20:00 | 29 | 65 | 4.95 | 0 | 26 | 30 | 17 | 41.489 | 0
2024-05-19 21:00 | 28.5 | 67 | 3.67 | 0 | 26 | 30 | 17 | 37.1247 | 0
2024-05-19 22:00 | 27.7 | 72 | 3.26 | 0 | 26 | 30 | 17 | 34.9558 | 0
2024-05-19 23:00 | 27 | 75 | 3.26 | 0 | 26 | 30 | 17 | 37.6923 | 0
2024-05-20 | 26.3 | 75 | 3.62 | 0 | 26 | 30 | 17 | 47.8391 | 0
2024-05-20 01:00 | 25.7 | 76 | 3.92 | 0 | 26 | 30 | 17 | 55.3796 | 0
2024-05-20 02:00 | 25.3 | 76 | 4.18 | 0 | 26 | 30 | 17 | 62.2893 | 0
2024-05-20 03:00 | 24.8 | 79 | 4.15 | 0 | 26 | 30 | 17 | 63.0582 | 0
2024-05-20 04:00 | 24.3 | 82 | 4.22 | 0 | 26 | 30 | 17 | 64.8832 | 0
2024-05-20 05:00 | 24.8 | 81 | 4.37 | 0 | 26 | 30 | 17 | 61.5167 | 0
2024-05-20 06:00 | 24.8 | 81 | 4.44 | 7 | 26 | 30 | 17 | 61.1266 | 0
2024-05-20 07:00 | 26.1 | 75 | 3.71 | 112 | 26 | 30 | 17 | 35.6587 | 0
2024-05-20 08:00 | 28.8 | 62 | 4.74 | 310 | 26 | 30 | 17 | 8.2285 | 0
2024-05-20 09:00 | 31.4 | 48 | 4.98 | 526 | 26 | 30 | 17 | 0 | 0
2024-05-20 10:00 | 33.3 | 41 | 4.6 | 718 | 26 | 30 | 17 | 0 | 0
2024-05-20 11:00 | 35.2 | 35 | 4.4 | 865 | 26 | 30 | 17 | 0 | 6.8007
2024-05-20 12:00 | 36.7 | 29 | 4.7 | 951 | 26 | 30 | 17 | 0 | 9.2954
2024-05-20 13:00 | 36.9 | 30 | 5.8 | 971 | 26 | 30 | 17 | 0 | 0.5034
2024-05-20 14:00 | 35.5 | 40 | 7.72 | 920 | 26 | 30 | 17 | 0 | 0
2024-05-20 15:00 | 34.6 | 44 | 7.72 | 803 | 26 | 30 | 17 | 0 | 0
2024-05-20 16:00 | 33.7 | 49 | 7.62 | 630 | 26 | 30 | 17 | 0 | 0
2024-05-20 17:00 | 32.6 | 52 | 7.3 | 422 | 26 | 30 | 17 | 0 | 0
2024-05-20 18:00 | 30.8 | 66 | 6.6 | 208 | 26 | 30 | 17 | 0 | 0
2024-05-20 19:00 | 29.5 | 74 | 5.61 | 43 | 26 | 30 | 17 | 6.8634 | 0
2024-05-20 20:00 | 29 | 75 | 4.84 | 0 | 26 | 30 | 17 | 17.4487 | 0
2024-05-20 21:00 | 28.5 | 79 | 3.45 | 0 | 26 | 30 | 17 | 14.2623 | 0
2024-05-20 22:00 | 27.8 | 83 | 2.28 | 0 | 26 | 30 | 17 | 14.0391 | 0
2024-05-20 23:00 | 27.1 | 86 | 2.2 | 0 | 26 | 30 | 17 | 16.751 | 0
2024-05-21 | 26.3 | 89 | 2.38 | 0 | 26 | 30 | 17 | 21.2438 | 0
2024-05-21 01:00 | 25.6 | 88 | 3.2 | 0 | 26 | 30 | 17 | 33.2509 | 0
2024-05-21 02:00 | 25 | 88 | 3.41 | 0 | 26 | 30 | 17 | 41.2599 | 0
2024-05-21 03:00 | 24.5 | 89 | 3.31 | 0 | 26 | 30 | 17 | 44.8963 | 0
2024-05-21 04:00 | 24 | 90 | 3.41 | 0 | 26 | 30 | 17 | 49.8768 | 0
2024-05-21 05:00 | 24.3 | 91 | 3.31 | 0 | 26 | 30 | 17 | 44.3989 | 0
2024-05-21 06:00 | 24.1 | 89 | 3.5 | 7 | 26 | 30 | 17 | 49.8619 | 0
2024-05-21 07:00 | 25.5 | 80 | 2.7 | 112 | 26 | 30 | 17 | 26.8925 | 0
2024-05-21 08:00 | 28 | 68 | 3.37 | 308 | 26 | 30 | 17 | 0 | 0
2024-05-21 09:00 | 30.3 | 59 | 3.11 | 523 | 26 | 30 | 17 | 0 | 0
2024-05-21 10:00 | 32.7 | 47 | 2.95 | 716 | 26 | 30 | 17 | 0 | 16.9233
2024-05-21 11:00 | 34.3 | 43 | 3.91 | 862 | 26 | 30 | 17 | 0 | 27.8193
2024-05-21 12:00 | 34.3 | 47 | 5.31 | 946 | 26 | 30 | 17 | 0 | 33.0806
2024-05-21 13:00 | 34.4 | 41 | 5.82 | 961 | 26 | 30 | 17 | 0 | 8.9375
2024-05-21 14:00 | 34.8 | 38 | 5.55 | 914 | 26 | 30 | 17 | 0 | 0.8782
2024-05-21 15:00 | 34.6 | 36 | 5.46 | 798 | 26 | 30 | 17 | 0 | 0
2024-05-21 16:00 | 33.7 | 41 | 5.15 | 627 | 26 | 30 | 17 | 0 | 0
2024-05-21 17:00 | 32.7 | 48 | 4.63 | 420 | 26 | 30 | 17 | 0 | 0
2024-05-21 18:00 | 31.5 | 56 | 3.76 | 207 | 26 | 30 | 17 | 0 | 0
2024-05-21 19:00 | 30.1 | 65 | 3.08 | 43 | 26 | 30 | 17 | 14.7404 | 0
2024-05-21 20:00 | 29.3 | 71 | 2.41 | 0 | 26 | 30 | 17 | 16.6232 | 0
2024-05-21 21:00 | 28.5 | 76 | 1.25 | 0 | 26 | 30 | 17 | 13.4064 | 0
2024-05-21 22:00 | 27.5 | 82 | 1.17 | 0 | 26 | 30 | 17 | 14.6174 | 0
2024-05-21 23:00 | 26.8 | 86 | 1.12 | 0 | 26 | 30 | 17 | 15.8421 | 0
2024-05-22 | 26.3 | 85 | 2.47 | 0 | 26 | 30 | 17 | 26.545 | 0
2024-05-22 01:00 | 25.4 | 88 | 2.28 | 0 | 26 | 30 | 17 | 30.4803 | 0
2024-05-22 02:00 | 25 | 89 | 2.52 | 0 | 26 | 30 | 17 | 34.5223 | 0
2024-05-22 03:00 | 24.5 | 89 | 2.6 | 0 | 26 | 30 | 17 | 39.8907 | 0
2024-05-22 04:00 | 24.1 | 89 | 2.9 | 0 | 26 | 30 | 17 | 46.1496 | 0
2024-05-22 05:00 | 24.3 | 86 | 2.41 | 0 | 26 | 30 | 17 | 43.6178 | 0
2024-05-22 06:00 | 24.2 | 83 | 2.53 | 7 | 26 | 30 | 17 | 48.0282 | 0
2024-05-22 07:00 | 26.1 | 70 | 2.3 | 112 | 26 | 30 | 17 | 30.1932 | 0
2024-05-22 08:00 | 29.4 | 54 | 2.01 | 309 | 26 | 30 | 17 | 0 | 0
2024-05-22 09:00 | 32.8 | 37 | 1.99 | 525 | 26 | 30 | 17 | 0 | 0
2024-05-22 10:00 | 35.5 | 27 | 2.19 | 718 | 26 | 30 | 17 | 0 | 14.6442
2024-05-22 11:00 | 37.3 | 22 | 2.94 | 866 | 26 | 30 | 17 | 0 | 16.7186
2024-05-22 12:00 | 38.2 | 21 | 4.43 | 952 | 26 | 30 | 17 | 0 | 0.0021
2024-05-22 13:00 | 38.2 | 21 | 5.64 | 970 | 26 | 30 | 17 | 0 | 0
2024-05-22 14:00 | 37.4 | 23 | 6.1 | 918 | 26 | 30 | 17 | 0 | 0
2024-05-22 15:00 | 36.4 | 28 | 5.6 | 800 | 26 | 30 | 17 | 0 | 0
2024-05-22 16:00 | 35.9 | 29 | 5.22 | 627 | 26 | 30 | 17 | 0 | 0
2024-05-22 17:00 | 34.9 | 32 | 4.74 | 420 | 26 | 30 | 17 | 2.3536 | 0
2024-05-22 18:00 | 33.6 | 37 | 3.58 | 208 | 26 | 30 | 17 | 19.8771 | 0
2024-05-22 19:00 | 32.4 | 39 | 1.73 | 44 | 26 | 30 | 17 | 27.5832 | 0
2024-05-22 20:00 | 31.2 | 46 | 0.61 | 0 | 26 | 30 | 17 | 16.2931 | 0
2024-05-22 21:00 | 30.9 | 45 | 0.8 | 0 | 26 | 30 | 17 | 21.4528 | 0
2024-05-22 22:00 | 29.3 | 48 | 2.01 | 0 | 26 | 30 | 17 | 45.1591 | 0
2024-05-22 23:00 | 28.7 | 49 | 1.73 | 0 | 26 | 30 | 17 | 43.8453 | 0
2024-05-23 | 28 | 48 | 1.75 | 0 | 26 | 30 | 17 | 49.5547 | 0
2024-05-23 01:00 | 27.3 | 46 | 1.87 | 0 | 26 | 30 | 17 | 58.0622 | 0
2024-05-23 02:00 | 27 | 42 | 1.82 | 0 | 26 | 30 | 17 | 63.135 | 0
2024-05-23 03:00 | 26.3 | 40 | 2.81 | 0 | 26 | 30 | 17 | 89.8615 | 0
2024-05-23 04:00 | 26.3 | 36 | 3.34 | 0 | 26 | 30 | 17 | 106.2528 | 0
2024-05-23 05:00 | 25.9 | 38 | 3.14 | 0 | 26 | 30 | 17 | 102.071 | 0
2024-05-23 06:00 | 26 | 38 | 3.13 | 7 | 26 | 30 | 17 | 100.2189 | 0
2024-05-23 07:00 | 28.4 | 31 | 2.25 | 115 | 26 | 30 | 17 | 61.8245 | 0
2024-05-23 08:00 | 32.7 | 23 | 2.48 | 315 | 26 | 30 | 17 | 27.0327 | 0
2024-05-23 09:00 | 35.9 | 17 | 2.13 | 531 | 26 | 30 | 17 | 0 | 0
2024-05-23 10:00 | 38.4 | 14 | 1.86 | 726 | 26 | 30 | 17 | 0 | 15.3644
2024-05-23 11:00 | 40.5 | 13 | 3.2 | 875 | 26 | 30 | 17 | 0 | 6.4254
2024-05-23 12:00 | 40.7 | 14 | 5.19 | 963 | 26 | 30 | 17 | 0 | 0
2024-05-23 13:00 | 40.1 | 17 | 6.86 | 982 | 26 | 30 | 17 | 0 | 0
2024-05-23 14:00 | 38.2 | 25 | 8.1 | 927 | 26 | 30 | 17 | 0 | 0
2024-05-23 15:00 | 37.3 | 27 | 8.05 | 807 | 26 | 30 | 17 | 0 | 0
2024-05-23 16:00 | 36.5 | 32 | 6.8 | 633 | 26 | 30 | 17 | 0 | 0
2024-05-23 17:00 | 35.4 | 34 | 6.14 | 427 | 26 | 30 | 17 | 0 | 0
2024-05-23 18:00 | 33.5 | 43 | 5.57 | 212 | 26 | 30 | 17 | 16.2805 | 0
2024-05-23 19:00 | 31.8 | 53 | 4.04 | 46 | 26 | 30 | 17 | 24.3667 | 0
2024-05-23 20:00 | 31.5 | 51 | 4.75 | 0 | 26 | 30 | 17 | 42.7907 | 0
2024-05-23 21:00 | 30.9 | 56 | 4.23 | 0 | 26 | 30 | 17 | 34.9499 | 0
2024-05-23 22:00 | 30.6 | 59 | 3.71 | 0 | 26 | 30 | 17 | 29.3356 | 0
2024-05-23 23:00 | 30.2 | 58 | 3.59 | 0 | 26 | 30 | 17 | 35.3007 | 0
2024-05-24 | 29.6 | 62 | 3.73 | 0 | 26 | 30 | 17 | 34.6134 | 0
2024-05-24 01:00 | 29.1 | 65 | 3.61 | 0 | 26 | 30 | 17 | 33.7702 | 0
2024-05-24 02:00 | 28.3 | 68 | 3.04 | 0 | 26 | 30 | 17 | 33.949 | 0
2024-05-24 03:00 | 27.8 | 69 | 3 | 0 | 26 | 30 | 17 | 37.1667 | 0
2024-05-24 04:00 | 27.7 | 69 | 3.2 | 0 | 26 | 30 | 17 | 39.5203 | 0
2024-05-24 05:00 | 28.6 | 63 | 3.49 | 0 | 26 | 30 | 17 | 42.3307 | 0
2024-05-24 06:00 | 27.8 | 65 | 2.71 | 8 | 26 | 30 | 17 | 39.9832 | 0
2024-05-24 07:00 | 30.7 | 53 | 2.86 | 115 | 26 | 30 | 17 | 19.6654 | 0
2024-05-24 08:00 | 33.1 | 45 | 3.19 | 314 | 26 | 30 | 17 | 0 | 0
2024-05-24 09:00 | 35.2 | 35 | 5.98 | 534 | 26 | 30 | 17 | 0 | 0
2024-05-24 10:00 | 36.1 | 34 | 7.62 | 731 | 26 | 30 | 17 | 0 | 0
2024-05-24 11:00 | 36.8 | 32 | 8.89 | 881 | 26 | 30 | 17 | 0 | 0
2024-05-24 12:00 | 37.2 | 31 | 9.15 | 971 | 26 | 30 | 17 | 0 | 0
2024-05-24 13:00 | 37 | 33 | 8.97 | 991 | 26 | 30 | 17 | 0 | 0
2024-05-24 14:00 | 36.5 | 35 | 8.56 | 937 | 26 | 30 | 17 | 0 | 0
2024-05-24 15:00 | 36 | 38 | 7.83 | 816 | 26 | 30 | 17 | 0 | 0
2024-05-24 16:00 | 35.2 | 40 | 7.08 | 641 | 26 | 30 | 17 | 0 | 0
2024-05-24 17:00 | 34.2 | 44 | 6.42 | 431 | 26 | 30 | 17 | 0 | 0
2024-05-24 18:00 | 32.9 | 50 | 5.92 | 214 | 26 | 30 | 17 | 2.2981 | 0
2024-05-24 19:00 | 31.6 | 58 | 4 | 47 | 26 | 30 | 17 | 14.4321 | 0
2024-05-24 20:00 | 31.1 | 58 | 2.9 | 0 | 26 | 30 | 17 | 22.5015 | 0
2024-05-24 21:00 | 30.3 | 62 | 2.51 | 0 | 26 | 30 | 17 | 21.4917 | 0
2024-05-24 22:00 | 29.7 | 64 | 2.68 | 0 | 26 | 30 | 17 | 24.6839 | 0
2024-05-24 23:00 | 29.4 | 66 | 3.4 | 0 | 26 | 30 | 17 | 27.5171 | 0
2024-05-25 | 29 | 68 | 3.81 | 0 | 26 | 30 | 17 | 29.9732 | 0
2024-05-25 01:00 | 28.5 | 68 | 3.16 | 0 | 26 | 30 | 17 | 32.5542 | 0
2024-05-25 02:00 | 28 | 68 | 3.4 | 0 | 26 | 30 | 17 | 39.3074 | 0
2024-05-25 03:00 | 27.5 | 69 | 4.05 | 0 | 26 | 30 | 17 | 47.3733 | 0
2024-05-25 04:00 | 27.1 | 69 | 3.96 | 0 | 26 | 30 | 17 | 51.4947 | 0
2024-05-25 05:00 | 27 | 72 | 3.57 | 0 | 26 | 30 | 17 | 44.596 | 0
2024-05-25 06:00 | 26.7 | 71 | 3.59 | 8 | 26 | 30 | 17 | 48.6793 | 0
2024-05-25 07:00 | 28.5 | 63 | 3.21 | 116 | 26 | 30 | 17 | 25.7385 | 0
2024-05-25 08:00 | 31.8 | 50 | 3.4 | 314 | 26 | 30 | 17 | 0 | 0
2024-05-25 09:00 | 34.4 | 42 | 3.42 | 529 | 26 | 30 | 17 | 0 | 0
2024-05-25 10:00 | 36.2 | 34 | 3.67 | 723 | 26 | 30 | 17 | 0 | 7.0286
2024-05-25 11:00 | 37.3 | 31 | 4.1 | 873 | 26 | 30 | 17 | 0 | 21.8508
2024-05-25 12:00 | 38.1 | 27 | 4.67 | 963 | 26 | 30 | 17 | 0 | 18.7822
2024-05-25 13:00 | 38.4 | 26 | 5.32 | 984 | 26 | 30 | 17 | 0 | 10.496
2024-05-25 14:00 | 37.9 | 30 | 5.95 | 935 | 26 | 30 | 17 | 0 | 6.1838
2024-05-25 15:00 | 37 | 35 | 5.96 | 818 | 26 | 30 | 17 | 0 | 0.1058
2024-05-25 16:00 | 35.9 | 42 | 5.41 | 644 | 26 | 30 | 17 | 0 | 0
2024-05-25 17:00 | 34.6 | 47 | 4.77 | 433 | 26 | 30 | 17 | 0 | 0
2024-05-25 18:00 | 32.9 | 59 | 4.17 | 217 | 26 | 30 | 17 | 0 | 0
2024-05-25 19:00 | 31.1 | 73 | 3.36 | 48 | 26 | 30 | 17 | 0 | 0
2024-05-25 20:00 | 30.3 | 78 | 2.89 | 0 | 26 | 30 | 17 | 0 | 0
2024-05-25 21:00 | 29.9 | 75 | 2.46 | 0 | 26 | 30 | 17 | 4.8068 | 0
2024-05-25 22:00 | 28.9 | 78 | 1.21 | 0 | 26 | 30 | 17 | 8.8637 | 0
2024-05-25 23:00 | 29.4 | 75 | 0.58 | 0 | 26 | 30 | 17 | 6.9955 | 0
2024-05-26 | 27.8 | 82 | 1.2 | 0 | 26 | 30 | 17 | 12.7485 | 0
2024-05-26 01:00 | 26.7 | 85 | 2.02 | 0 | 26 | 30 | 17 | 20.9791 | 0
2024-05-26 02:00 | 26.3 | 86 | 2.42 | 0 | 26 | 30 | 17 | 25.0806 | 0
2024-05-26 03:00 | 25.7 | 89 | 2.71 | 0 | 26 | 30 | 17 | 28.5353 | 0
2024-05-26 04:00 | 24.7 | 93 | 2.85 | 0 | 26 | 30 | 17 | 34.5919 | 0
2024-05-26 05:00 | 24.6 | 94 | 2.87 | 0 | 26 | 30 | 17 | 34.5029 | 0
2024-05-26 06:00 | 24.4 | 90 | 2.73 | 8 | 26 | 30 | 17 | 39.5434 | 0
2024-05-26 07:00 | 26.7 | 73 | 1.8 | 116 | 26 | 30 | 17 | 16.8168 | 0
2024-05-26 08:00 | 30.5 | 55 | 2.15 | 315 | 26 | 30 | 17 | 0 | 0
2024-05-26 09:00 | 34.5 | 38 | 2.98 | 530 | 26 | 30 | 17 | 0 | 0
2024-05-26 10:00 | 37.5 | 29 | 3.08 | 723 | 26 | 30 | 17 | 0 | 14.9484
2024-05-26 11:00 | 39.7 | 25 | 2.91 | 869 | 26 | 30 | 17 | 0 | 44.1733
2024-05-26 12:00 | 40.8 | 26 | 3.49 | 955 | 26 | 30 | 17 | 0 | 58.9551
2024-05-26 13:00 | 40.4 | 31 | 4.44 | 971 | 26 | 30 | 17 | 0 | 64.5282
2024-05-26 14:00 | 41 | 23 | 4.46 | 918 | 26 | 30 | 17 | 0 | 29.65
2024-05-26 15:00 | 41 | 21 | 5.11 | 805 | 26 | 30 | 17 | 0 | 0
2024-05-26 16:00 | 38.4 | 34 | 6.01 | 635 | 26 | 30 | 17 | 0 | 0
2024-05-26 17:00 | 37 | 36 | 4.89 | 423 | 26 | 30 | 17 | 0 | 0
2024-05-26 18:00 | 34.9 | 48 | 3.62 | 211 | 26 | 30 | 17 | 0 | 0
2024-05-26 19:00 | 32.9 | 61 | 2.72 | 47 | 26 | 30 | 17 | 0 | 0
2024-05-26 20:00 | 31.5 | 71 | 2.28 | 0 | 26 | 30 | 17 | 0 | 0
2024-05-26 21:00 | 30.7 | 78 | 3.2 | 0 | 26 | 30 | 17 | 0 | 0
2024-05-26 22:00 | 30.2 | 79 | 2.18 | 0 | 26 | 30 | 17 | 0 | 0
2024-05-26 23:00 | 29.2 | 81 | 1.39 | 0 | 26 | 30 | 17 | 3.976 | 0
2024-05-27 | 28.7 | 79 | 1.6 | 0 | 26 | 30 | 17 | 9.9079 | 0
2024-05-27 01:00 | 29.8 | 71 | 0.86 | 0 | 26 | 30 | 17 | 8.2538 | 0
2024-05-27 02:00 | 27.7 | 77 | 1.79 | 0 | 26 | 30 | 17 | 20.5095 | 0
2024-05-27 03:00 | 27.3 | 75 | 1.9 | 0 | 26 | 30 | 17 | 26.4906 | 0
2024-05-27 04:00 | 26.8 | 73 | 2.24 | 0 | 26 | 30 | 17 | 35.3608 | 0
2024-05-27 05:00 | 28.2 | 62 | 1.68 | 0 | 26 | 30 | 17 | 32.2 | 0
2024-05-27 06:00 | 28 | 51 | 5.18 | 8 | 26 | 30 | 17 | 88.1405 | 0
2024-05-27 07:00 | 29.7 | 42 | 3.41 | 114 | 26 | 30 | 17 | 54.8134 | 0
2024-05-27 08:00 | 33.3 | 32 | 2.82 | 310 | 26 | 30 | 17 | 11.7199 | 0
2024-05-27 09:00 | 37.7 | 21 | 2.9 | 524 | 26 | 30 | 17 | 0 | 0
2024-05-27 10:00 | 40.2 | 18 | 3.44 | 718 | 26 | 30 | 17 | 0 | 0
2024-05-27 11:00 | 41.5 | 19 | 4.04 | 864 | 26 | 30 | 17 | 0 | 16.9692
2024-05-27 12:00 | 41.6 | 23 | 5.08 | 949 | 26 | 30 | 17 | 0 | 31.4973
2024-05-27 13:00 | 41.9 | 23 | 5.22 | 968 | 26 | 30 | 17 | 0 | 35.6423
2024-05-27 14:00 | 41.6 | 23 | 5.19 | 919 | 26 | 30 | 17 | 0 | 25.9952
2024-05-27 15:00 | 41.2 | 25 | 4.52 | 804 | 26 | 30 | 17 | 0 | 24.2487
2024-05-27 16:00 | 39.6 | 30 | 4.99 | 637 | 26 | 30 | 17 | 0 | 0
2024-05-27 17:00 | 37 | 38 | 4.7 | 428 | 26 | 30 | 17 | 0 | 0
2024-05-27 18:00 | 35.9 | 41 | 3.28 | 215 | 26 | 30 | 17 | 0 | 0
2024-05-27 19:00 | 34.5 | 48 | 2.42 | 49 | 26 | 30 | 17 | 1.6781 | 0
2024-05-27 20:00 | 33.2 | 54 | 1.32 | 0 | 26 | 30 | 17 | 5.4653 | 0
2024-05-27 21:00 | 32.6 | 56 | 0.98 | 0 | 26 | 30 | 17 | 5.6227 | 0
2024-05-27 22:00 | 32 | 56 | 1.2 | 0 | 26 | 30 | 17 | 10.2222 | 0
2024-05-27 23:00 | 31.2 | 54 | 1.53 | 0 | 26 | 30 | 17 | 19.7502 | 0
2024-05-28 | 30.3 | 54 | 2.47 | 0 | 26 | 30 | 17 | 33.977 | 0
2024-05-28 01:00 | 29.8 | 54 | 3.27 | 0 | 26 | 30 | 17 | 45.0547 | 0
2024-05-28 02:00 | 28.7 | 56 | 3.23 | 0 | 26 | 30 | 17 | 51.6965 | 0
2024-05-28 03:00 | 28 | 56 | 3.61 | 0 | 26 | 30 | 17 | 62.3135 | 0
2024-05-28 04:00 | 27.5 | 58 | 3.83 | 0 | 26 | 30 | 17 | 66.0583 | 0
2024-05-28 05:00 | 28 | 59 | 3.8 | 0 | 26 | 30 | 17 | 58.642 | 0
2024-05-28 06:00 | 27.6 | 59 | 3.83 | 8 | 26 | 30 | 17 | 62.0922 | 0
2024-05-28 07:00 | 29.2 | 55 | 4.18 | 118 | 26 | 30 | 17 | 40.8656 | 0
2024-05-28 08:00 | 32.3 | 45 | 5.26 | 316 | 26 | 30 | 17 | 9.93 | 0
2024-05-28 09:00 | 34.8 | 36 | 6.22 | 532 | 26 | 30 | 17 | 0 | 0
2024-05-28 10:00 | 36.8 | 32 | 6.37 | 727 | 26 | 30 | 17 | 0 | 0
2024-05-28 11:00 | 38.7 | 29 | 6.64 | 876 | 26 | 30 | 17 | 0 | 0
2024-05-28 12:00 | 40.1 | 27 | 6.46 | 964 | 26 | 30 | 17 | 0 | 18.3834
2024-05-28 13:00 | 40.8 | 26 | 5.9 | 981 | 26 | 30 | 17 | 0 | 31.1915
2024-05-28 14:00 | 40.6 | 28 | 5.65 | 930 | 26 | 30 | 17 | 0 | 34.7426
2024-05-28 15:00 | 39.3 | 35 | 5.8 | 812 | 26 | 30 | 17 | 0 | 33.5773
2024-05-28 16:00 | 38.4 | 36 | 5.6 | 640 | 26 | 30 | 17 | 0 | 3.9154
2024-05-28 17:00 | 36.2 | 39 | 5.02 | 434 | 26 | 30 | 17 | 0 | 0
2024-05-28 18:00 | 34.3 | 48 | 4.12 | 222 | 26 | 30 | 17 | 0 | 0
2024-05-28 19:00 | 32 | 62 | 3.16 | 51 | 26 | 30 | 17 | 0 | 0
2024-05-28 20:00 | 30.8 | 70 | 1.5 | 0 | 26 | 30 | 17 | 3.722 | 0
2024-05-28 21:00 | 30 | 75 | 0.6 | 0 | 26 | 30 | 17 | 4.091 | 0
2024-05-28 22:00 | 28.6 | 82 | 1.35 | 0 | 26 | 30 | 17 | 7.4328 | 0
2024-05-28 23:00 | 27.9 | 89 | 2.56 | 0 | 26 | 30 | 17 | 4.9932 | 0
2024-05-29 | 27.1 | 86 | 2.82 | 0 | 26 | 30 | 17 | 18.1268 | 0
2024-05-29 01:00 | 26.4 | 81 | 2.88 | 0 | 26 | 30 | 17 | 32.9143 | 0
2024-05-29 02:00 | 25.6 | 87 | 3.26 | 0 | 26 | 30 | 17 | 34.9992 | 0
2024-05-29 03:00 | 24.9 | 93 | 3.55 | 0 | 26 | 30 | 17 | 35.8369 | 0
2024-05-29 04:00 | 24.3 | 95 | 3.52 | 0 | 26 | 30 | 17 | 40.0813 | 0
2024-05-29 05:00 | 24.3 | 100 | 3.26 | 0 | 26 | 30 | 17 | 31.886 | 0
2024-05-29 06:00 | 24.2 | 100 | 3.67 | 8 | 26 | 30 | 17 | 33.7493 | 0
2024-05-29 07:00 | 24.9 | 98 | 3.62 | 98 | 26 | 30 | 17 | 15.3881 | 0
2024-05-29 08:00 | 27.2 | 86 | 3.61 | 264 | 26 | 30 | 17 | 0 | 0
2024-05-29 09:00 | 30.9 | 66 | 3.51 | 533 | 26 | 30 | 17 | 0 | 4.7031
2024-05-29 10:00 | 34.3 | 49 | 3.47 | 729 | 26 | 30 | 17 | 0 | 31.6938
2024-05-29 11:00 | 37.3 | 37 | 3.58 | 878 | 26 | 30 | 17 | 0 | 49.3056
2024-05-29 12:00 | 39.6 | 31 | 3.35 | 964 | 26 | 30 | 17 | 0 | 68.0171
2024-05-29 13:00 | 40.6 | 30 | 3.72 | 976 | 26 | 30 | 17 | 0 | 71.4705
2024-05-29 14:00 | 40.4 | 33 | 4.61 | 918 | 26 | 30 | 17 | 0 | 64.1829
2024-05-29 15:00 | 40.3 | 30 | 4.72 | 799 | 26 | 30 | 17 | 0 | 32.846
2024-05-29 16:00 | 39.7 | 28 | 4.3 | 631 | 26 | 30 | 17 | 0 | 0.3346
2024-05-29 17:00 | 37.6 | 34 | 4.48 | 427 | 26 | 30 | 17 | 0 | 0
2024-05-29 18:00 | 35.4 | 48 | 3.81 | 216 | 26 | 30 | 17 | 0 | 0
2024-05-29 19:00 | 33.1 | 63 | 2.69 | 50 | 26 | 30 | 17 | 0 | 0
2024-05-29 20:00 | 31.8 | 74 | 2.16 | 0 | 26 | 30 | 17 | 0 | 0
2024-05-29 21:00 | 30.7 | 83 | 2.02 | 0 | 26 | 30 | 17 | 0 | 0
2024-05-29 22:00 | 29.9 | 88 | 2.16 | 0 | 26 | 30 | 17 | 0 | 0
2024-05-29 23:00 | 29.2 | 90 | 2.19 | 0 | 26 | 30 | 17 | 0.5314 | 0
2024-05-30 | 28.5 | 88 | 2.72 | 0 | 26 | 30 | 17 | 2.0422 | 0
2024-05-30 01:00 | 27.8 | 86 | 3.08 | 0 | 26 | 30 | 17 | 10.5048 | 0
2024-05-30 02:00 | 27.1 | 89 | 3.16 | 0 | 26 | 30 | 17 | 14.1417 | 0
2024-05-30 03:00 | 26.5 | 93 | 2.79 | 0 | 26 | 30 | 17 | 14.8095 | 0
2024-05-30 04:00 | 25.9 | 94 | 3.14 | 0 | 26 | 30 | 17 | 20.8816 | 0
2024-05-30 05:00 | 25.8 | 95 | 2.67 | 0 | 26 | 30 | 17 | 19.6104 | 0
2024-05-30 06:00 | 25.5 | 96 | 2.92 | 9 | 26 | 30 | 17 | 20.9841 | 0
2024-05-30 07:00 | 27.3 | 85 | 2.82 | 117 | 26 | 30 | 17 | 1.6047 | 0
2024-05-30 08:00 | 30 | 70 | 3.45 | 315 | 26 | 30 | 17 | 0 | 0
2024-05-30 09:00 | 33 | 55 | 3.44 | 533 | 26 | 30 | 17 | 0 | 5.6569
2024-05-30 10:00 | 36 | 43 | 2.14 | 727 | 26 | 30 | 17 | 0 | 51.9287
2024-05-30 11:00 | 38.7 | 31 | 1.62 | 872 | 26 | 30 | 17 | 0 | 76.4448
2024-05-30 12:00 | 40.3 | 29 | 2.86 | 958 | 26 | 30 | 17 | 0 | 74.0785
2024-05-30 13:00 | 39.7 | 39 | 3.98 | 973 | 26 | 30 | 17 | 0 | 92.0196
2024-05-30 14:00 | 39.6 | 34 | 5.02 | 914 | 26 | 30 | 17 | 0 | 53.9668
2024-05-30 15:00 | 39.7 | 29 | 4.32 | 801 | 26 | 30 | 17 | 0 | 26.9599
2024-05-30 16:00 | 39.5 | 30 | 3.61 | 633 | 26 | 30 | 17 | 0 | 15.4513
2024-05-30 17:00 | 38.6 | 31 | 3.89 | 427 | 26 | 30 | 17 | 0 | 0
2024-05-30 18:00 | 36.8 | 35 | 3.68 | 215 | 26 | 30 | 17 | 0 | 0
2024-05-30 19:00 | 33.5 | 60 | 3.2 | 51 | 26 | 30 | 17 | 0 | 0
2024-05-30 20:00 | 32 | 73 | 2.6 | 0 | 26 | 30 | 17 | 0 | 0
2024-05-30 21:00 | 31 | 83 | 0.51 | 0 | 26 | 30 | 17 | 0 | 0
2024-05-30 22:00 | 31.2 | 75 | 2.48 | 0 | 26 | 30 | 17 | 0 | 0
2024-05-30 23:00 | 31.1 | 65 | 2.38 | 0 | 26 | 30 | 17 | 8.8391 | 0
2024-05-31 | 30 | 66 | 1.84 | 0 | 26 | 30 | 17 | 15.4573 | 0
2024-05-31 01:00 | 29.4 | 69 | 2.43 | 0 | 26 | 30 | 17 | 18.7053 | 0
2024-05-31 02:00 | 28.5 | 79 | 2.41 | 0 | 26 | 30 | 17 | 12.8456 | 0
2024-05-31 03:00 | 27.3 | 87 | 1.84 | 0 | 26 | 30 | 17 | 13.1067 | 0
2024-05-31 04:00 | 26.6 | 84 | 1.8 | 0 | 26 | 30 | 17 | 21.9597 | 0
2024-05-31 05:00 | 28.6 | 83 | 0.14 | 0 | 26 | 30 | 17 | 7.1734 | 0
2024-05-31 06:00 | 28.5 | 85 | 0.61 | 8 | 26 | 30 | 17 | 4.8164 | 0
2024-05-31 07:00 | 28.9 | 81 | 1.33 | 114 | 26 | 30 | 17 | 0 | 0
2024-05-31 08:00 | 31 | 75 | 1.08 | 306 | 26 | 30 | 17 | 0 | 15.9379
2024-05-31 09:00 | 33.3 | 65 | 0.67 | 518 | 26 | 30 | 17 | 0 | 54.3966
2024-05-31 10:00 | 36 | 52 | 0.6 | 709 | 26 | 30 | 17 | 0 | 84.4504
2024-05-31 11:00 | 38.5 | 42 | 1.3 | 856 | 26 | 30 | 17 | 0 | 97.3418
2024-05-31 12:00 | 40.3 | 38 | 2.39 | 942 | 26 | 30 | 17 | 0 | 103.2755
2024-05-31 13:00 | 41.5 | 34 | 3.36 | 959 | 26 | 30 | 17 | 0 | 96.9808
2024-05-31 14:00 | 42.6 | 23 | 4.97 | 910 | 26 | 30 | 17 | 0 | 38.8668
2024-05-31 15:00 | 41.2 | 20 | 5.94 | 801 | 26 | 30 | 17 | 0 | 0
2024-05-31 16:00 | 39.6 | 27 | 4.89 | 636 | 26 | 30 | 17 | 0 | 0
2024-05-31 17:00 | 39 | 22 | 4.42 | 432 | 26 | 30 | 17 | 0 | 0
2024-05-31 18:00 | 37 | 32 | 3.88 | 219 | 26 | 30 | 17 | 1.8367 | 0
2024-05-31 19:00 | 34.4 | 51 | 3.23 | 52 | 26 | 30 | 17 | 0 | 0
2024-05-31 20:00 | 32.9 | 64 | 2.31 | 0 | 26 | 30 | 17 | 0 | 0
2024-05-31 21:00 | 32.4 | 63 | 2.31 | 0 | 26 | 30 | 17 | 0 | 0
2024-05-31 22:00 | 31.2 | 65 | 1.5 | 0 | 26 | 30 | 17 | 6.5823 | 0
2024-05-31 23:00 | 30.5 | 63 | 1.99 | 0 | 26 | 30 | 17 | 16.0181 | 0
2024-06-01 | 29.7 | 64 | 2 | 0 | 26 | 30 | 22 | 21.0087 | 0
2024-06-01 01:00 | 28.9 | 66 | 1.93 | 0 | 26 | 30 | 22 | 24.3798 | 0
2024-06-01 02:00 | 28.6 | 64 | 2.51 | 0 | 26 | 30 | 22 | 33.4973 | 0
2024-06-01 03:00 | 28.2 | 56 | 2.55 | 0 | 26 | 30 | 22 | 48.6964 | 0
2024-06-01 04:00 | 27.9 | 51 | 2.62 | 0 | 26 | 30 | 22 | 59.0559 | 0
2024-06-01 05:00 | 29.8 | 52 | 1.17 | 0 | 26 | 30 | 22 | 26.282 | 0
2024-06-01 06:00 | 30.4 | 49 | 1 | 8 | 26 | 30 | 22 | 22.419 | 0
2024-06-01 07:00 | 31 | 46 | 1.22 | 115 | 26 | 30 | 22 | 10.6634 | 0
2024-06-01 08:00 | 34.1 | 38 | 1.02 | 309 | 26 | 30 | 22 | 0 | 0
2024-06-01 09:00 | 37 | 30 | 1.22 | 522 | 26 | 30 | 22 | 0 | 27.4637
2024-06-01 10:00 | 40 | 21 | 0.99 | 714 | 26 | 30 | 22 | 0 | 61.4466
2024-06-01 11:00 | 42.9 | 14 | 1.91 | 862 | 26 | 30 | 22 | 0 | 55.8319
2024-06-01 12:00 | 45.1 | 9 | 3.2 | 952 | 26 | 30 | 22 | 0 | 32.0178
2024-06-01 13:00 | 45.8 | 7 | 3.98 | 973 | 26 | 30 | 22 | 0 | 12.1754
2024-06-01 14:00 | 45.8 | 6 | 4.2 | 924 | 26 | 30 | 22 | 0 | 0
2024-06-01 15:00 | 45 | 6 | 4.21 | 810 | 26 | 30 | 22 | 0 | 0
2024-06-01 16:00 | 42.8 | 12 | 4.72 | 640 | 26 | 30 | 22 | 0 | 0
2024-06-01 17:00 | 40.6 | 16 | 3.61 | 435 | 26 | 30 | 22 | 0 | 0
2024-06-01 18:00 | 37.8 | 30 | 3.4 | 221 | 26 | 30 | 22 | 0 | 0
2024-06-01 19:00 | 35.5 | 43 | 2.92 | 53 | 26 | 30 | 22 | 3.993 | 0
2024-06-01 20:00 | 33.9 | 54 | 2.83 | 0 | 26 | 30 | 22 | 2.0658 | 0
2024-06-01 21:00 | 32.9 | 60 | 2.1 | 0 | 26 | 30 | 22 | 0.2877 | 0
2024-06-01 22:00 | 31.7 | 65 | 1.36 | 0 | 26 | 30 | 22 | 2.7758 | 0
2024-06-01 23:00 | 31.2 | 69 | 0.85 | 0 | 26 | 30 | 22 | 1.9305 | 0
2024-06-02 | 29.9 | 73 | 1.53 | 0 | 26 | 30 | 22 | 7.065 | 0
2024-06-02 01:00 | 29.4 | 72 | 2.33 | 0 | 26 | 30 | 22 | 13.8941 | 0
2024-06-02 02:00 | 28.7 | 73 | 2.62 | 0 | 26 | 30 | 22 | 19.9539 | 0
2024-06-02 03:00 | 28 | 74 | 2.89 | 0 | 26 | 30 | 22 | 26.5286 | 0
2024-06-02 04:00 | 27.6 | 70 | 3.3 | 0 | 26 | 30 | 22 | 39.2921 | 0
2024-06-02 05:00 | 28.7 | 57 | 3.22 | 0 | 26 | 30 | 22 | 49.4461 | 0
2024-06-02 06:00 | 28.8 | 52 | 3.47 | 9 | 26 | 30 | 22 | 58.5913 | 0
2024-06-02 07:00 | 31.2 | 42 | 3.45 | 116 | 26 | 30 | 22 | 41.142 | 0
2024-06-02 08:00 | 34.5 | 35 | 3.09 | 311 | 26 | 30 | 22 | 0 | 0
2024-06-02 09:00 | 36.9 | 33 | 3.24 | 524 | 26 | 30 | 22 | 0 | 0
2024-06-02 10:00 | 38.8 | 30 | 3.76 | 715 | 26 | 30 | 22 | 0 | 18.3592
2024-06-02 11:00 | 40.3 | 28 | 4.4 | 862 | 26 | 30 | 22 | 0 | 37.6707
2024-06-02 12:00 | 40.9 | 28 | 4.94 | 949 | 26 | 30 | 22 | 0 | 49.923
2024-06-02 13:00 | 40.5 | 29 | 5.63 | 970 | 26 | 30 | 22 | 0 | 45.1575
2024-06-02 14:00 | 39.7 | 33 | 5.88 | 920 | 26 | 30 | 22 | 0 | 44.6139
2024-06-02 15:00 | 38.6 | 39 | 5.59 | 805 | 26 | 30 | 22 | 0 | 43.3511
2024-06-02 16:00 | 37.9 | 41 | 5.02 | 637 | 26 | 30 | 22 | 0 | 23.5183
2024-06-02 17:00 | 36.7 | 45 | 4.11 | 432 | 26 | 30 | 22 | 0 | 2.1394
2024-06-02 18:00 | 35.3 | 51 | 3.57 | 221 | 26 | 30 | 22 | 0 | 0
2024-06-02 19:00 | 33.5 | 62 | 3.4 | 53 | 26 | 30 | 22 | 0 | 0
2024-06-02 20:00 | 32.6 | 67 | 2.91 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-02 21:00 | 32 | 70 | 2.51 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-02 22:00 | 31.3 | 72 | 2.82 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-02 23:00 | 30.7 | 74 | 2.98 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-03 | 30.1 | 75 | 3.16 | 0 | 26 | 30 | 22 | 2.1473 | 0
2024-06-03 01:00 | 29.6 | 74 | 3.31 | 0 | 26 | 30 | 22 | 9.8894 | 0
2024-06-03 02:00 | 29.2 | 72 | 3.49 | 0 | 26 | 30 | 22 | 18.6173 | 0
2024-06-03 03:00 | 28.8 | 72 | 3.19 | 0 | 26 | 30 | 22 | 22.3824 | 0
2024-06-03 04:00 | 28.2 | 74 | 2.87 | 0 | 26 | 30 | 22 | 24.3847 | 0
2024-06-03 05:00 | 28.3 | 82 | 2.16 | 0 | 26 | 30 | 22 | 10.3757 | 0
2024-06-03 06:00 | 28.3 | 79 | 2.86 | 9 | 26 | 30 | 22 | 14.3483 | 0
2024-06-03 07:00 | 29.8 | 70 | 2.84 | 116 | 26 | 30 | 22 | 0 | 0
2024-06-03 08:00 | 32.7 | 52 | 3.67 | 312 | 26 | 30 | 22 | 0 | 0
2024-06-03 09:00 | 34.9 | 41 | 3.61 | 527 | 26 | 30 | 22 | 0 | 0
2024-06-03 10:00 | 37 | 33 | 3.54 | 719 | 26 | 30 | 22 | 0 | 14.2735
2024-06-03 11:00 | 39 | 27 | 3.41 | 866 | 26 | 30 | 22 | 0 | 36.2118
2024-06-03 12:00 | 40.7 | 23 | 3.36 | 952 | 26 | 30 | 22 | 0 | 50.0413
2024-06-03 13:00 | 41.6 | 23 | 3.54 | 971 | 26 | 30 | 22 | 0 | 57.4872
2024-06-03 14:00 | 40.6 | 32 | 4.98 | 917 | 26 | 30 | 22 | 0 | 59.7347
2024-06-03 15:00 | 39.1 | 40 | 6.43 | 796 | 26 | 30 | 22 | 0 | 49.1222
2024-06-03 16:00 | 38 | 40 | 6.57 | 624 | 26 | 30 | 22 | 0 | 6.7303
2024-06-03 17:00 | 36.2 | 42 | 5.22 | 428 | 26 | 30 | 22 | 0 | 0
2024-06-03 18:00 | 34.7 | 49 | 3.86 | 219 | 26 | 30 | 22 | 0 | 0
2024-06-03 19:00 | 33.2 | 57 | 2.66 | 54 | 26 | 30 | 22 | 0 | 0
2024-06-03 20:00 | 32.3 | 62 | 1.92 | 0 | 26 | 30 | 22 | 2.3161 | 0
2024-06-03 21:00 | 31.6 | 67 | 1.49 | 0 | 26 | 30 | 22 | 1.2034 | 0
2024-06-03 22:00 | 31 | 72 | 1.61 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-03 23:00 | 30.4 | 75 | 2.2 | 0 | 26 | 30 | 22 | 0.0683 | 0
2024-06-04 | 29.6 | 77 | 1.98 | 0 | 26 | 30 | 22 | 4.8989 | 0
2024-06-04 01:00 | 28.7 | 83 | 1.49 | 0 | 26 | 30 | 22 | 5.6776 | 0
2024-06-04 02:00 | 28.1 | 85 | 2.1 | 0 | 26 | 30 | 22 | 8.4473 | 0
2024-06-04 03:00 | 27.6 | 87 | 2.5 | 0 | 26 | 30 | 22 | 10.9155 | 0
2024-06-04 04:00 | 27.3 | 87 | 2.38 | 0 | 26 | 30 | 22 | 13.8343 | 0
2024-06-04 05:00 | 28 | 80 | 3.21 | 0 | 26 | 30 | 22 | 17.9877 | 0
2024-06-04 06:00 | 27.9 | 79 | 4.01 | 9 | 26 | 30 | 22 | 21.5603 | 0
2024-06-04 07:00 | 29.1 | 73 | 2.92 | 114 | 26 | 30 | 22 | 1.3055 | 0
2024-06-04 08:00 | 31.2 | 63 | 3.41 | 306 | 26 | 30 | 22 | 0 | 0
2024-06-04 09:00 | 34.1 | 50 | 3.23 | 514 | 26 | 30 | 22 | 0 | 6.5559
2024-06-04 10:00 | 36.5 | 41 | 3.24 | 700 | 26 | 30 | 22 | 0 | 33.6595
2024-06-04 11:00 | 38.4 | 35 | 3.08 | 841 | 26 | 30 | 22 | 0 | 56.5939
2024-06-04 12:00 | 39.4 | 33 | 3.4 | 925 | 26 | 30 | 22 | 0 | 67.4527
2024-06-04 13:00 | 38.2 | 46 | 4.7 | 945 | 26 | 30 | 22 | 0 | 90.9468
2024-06-04 14:00 | 37 | 49 | 5.88 | 892 | 26 | 30 | 22 | 0 | 71.068
2024-06-04 15:00 | 37.2 | 47 | 5.38 | 782 | 26 | 30 | 22 | 0 | 54.0648
2024-06-04 16:00 | 37.3 | 48 | 5.1 | 618 | 26 | 30 | 22 | 0 | 39.0143
2024-06-04 17:00 | 36.1 | 49 | 4.47 | 419 | 26 | 30 | 22 | 0 | 2.5725
2024-06-04 18:00 | 35 | 52 | 4.03 | 216 | 26 | 30 | 22 | 0 | 0
2024-06-04 19:00 | 33.9 | 54 | 1.89 | 53 | 26 | 30 | 22 | 0 | 0
2024-06-04 20:00 | 33.4 | 55 | 0.32 | 0 | 26 | 30 | 22 | 1.8933 | 0
2024-06-04 21:00 | 33.1 | 54 | 1.92 | 0 | 26 | 30 | 22 | 7.8953 | 0
2024-06-04 22:00 | 32.5 | 55 | 2.24 | 0 | 26 | 30 | 22 | 12.1837 | 0
2024-06-04 23:00 | 31.4 | 64 | 1.9 | 0 | 26 | 30 | 22 | 6.8824 | 0
2024-06-05 | 30.3 | 72 | 1.62 | 0 | 26 | 30 | 22 | 5.2045 | 0
2024-06-05 01:00 | 29.6 | 78 | 2 | 0 | 26 | 30 | 22 | 3.5923 | 0
2024-06-05 02:00 | 28.8 | 84 | 2.21 | 0 | 26 | 30 | 22 | 2.9884 | 0
2024-06-05 03:00 | 28 | 91 | 2.02 | 0 | 26 | 30 | 22 | 4.6591 | 0
2024-06-05 04:00 | 27.3 | 93 | 1.92 | 0 | 26 | 30 | 22 | 6.9439 | 0
2024-06-05 05:00 | 27.7 | 93 | 2.05 | 0 | 26 | 30 | 22 | 5.5764 | 0
2024-06-05 06:00 | 27.4 | 93 | 1.98 | 9 | 26 | 30 | 22 | 5.3703 | 0
2024-06-05 07:00 | 28.8 | 84 | 1.8 | 115 | 26 | 30 | 22 | 0 | 0
2024-06-05 08:00 | 31.3 | 62 | 3.31 | 308 | 26 | 30 | 22 | 0 | 0
2024-06-05 09:00 | 34.1 | 47 | 3.3 | 519 | 26 | 30 | 22 | 0 | 0
2024-06-05 10:00 | 36.4 | 38 | 4.02 | 708 | 26 | 30 | 22 | 0 | 14.7322
2024-06-05 11:00 | 38 | 33 | 4.43 | 854 | 26 | 30 | 22 | 0 | 29.9716
2024-06-05 12:00 | 38.7 | 34 | 4.61 | 944 | 26 | 30 | 22 | 0 | 51.8465
2024-06-05 13:00 | 38.7 | 38 | 5.51 | 966 | 26 | 30 | 22 | 0 | 62.7636
2024-06-05 14:00 | 38.5 | 30 | 6.66 | 915 | 26 | 30 | 22 | 0 | 3.9603
2024-06-05 15:00 | 37.6 | 32 | 6.48 | 810 | 26 | 30 | 22 | 0 | 0
2024-06-05 16:00 | 36.5 | 37 | 6.11 | 646 | 26 | 30 | 22 | 0 | 0
2024-06-05 17:00 | 35.3 | 37 | 5.02 | 445 | 26 | 30 | 22 | 0 | 0
2024-06-05 18:00 | 33.7 | 47 | 3.89 | 233 | 26 | 30 | 22 | 0 | 0
2024-06-05 19:00 | 31.8 | 60 | 2.75 | 58 | 26 | 30 | 22 | 3.3537 | 0
2024-06-05 20:00 | 30.6 | 71 | 2.44 | 0 | 26 | 30 | 22 | 4.0014 | 0
2024-06-05 21:00 | 29.8 | 77 | 2.4 | 0 | 26 | 30 | 22 | 2.7596 | 0
2024-06-05 22:00 | 29.5 | 75 | 2.33 | 0 | 26 | 30 | 22 | 8.6427 | 0
2024-06-05 23:00 | 29 | 75 | 1 | 0 | 26 | 30 | 22 | 10.1889 | 0
2024-06-06 | 27.8 | 78 | 2.31 | 0 | 26 | 30 | 22 | 20.4961 | 0
2024-06-06 01:00 | 26.7 | 80 | 2.83 | 0 | 26 | 30 | 22 | 30.7745 | 0
2024-06-06 02:00 | 26.3 | 76 | 2.77 | 0 | 26 | 30 | 22 | 39.8627 | 0
2024-06-06 03:00 | 25.9 | 72 | 2.52 | 0 | 26 | 30 | 22 | 46.5246 | 0
2024-06-06 04:00 | 25.3 | 70 | 2.47 | 0 | 26 | 30 | 22 | 53.466 | 0
2024-06-06 05:00 | 25.6 | 66 | 2.69 | 0 | 26 | 30 | 22 | 58.4776 | 0
2024-06-06 06:00 | 25.4 | 63 | 2.79 | 9 | 26 | 30 | 22 | 64.0613 | 0
2024-06-06 07:00 | 27.5 | 52 | 2.45 | 120 | 26 | 30 | 22 | 42.1712 | 0
2024-06-06 08:00 | 31 | 39 | 2.14 | 318 | 26 | 30 | 22 | 4.7338 | 0
2024-06-06 09:00 | 34.4 | 28 | 2.33 | 534 | 26 | 30 | 22 | 0 | 0
2024-06-06 10:00 | 37 | 21 | 1.92 | 728 | 26 | 30 | 22 | 0 | 21.2617
2024-06-06 11:00 | 38.3 | 21 | 2.75 | 875 | 26 | 30 | 22 | 0 | 27.6647
2024-06-06 12:00 | 37.8 | 33 | 4.2 | 959 | 26 | 30 | 22 | 0 | 45.0208
2024-06-06 13:00 | 37.8 | 32 | 4.83 | 973 | 26 | 30 | 22 | 0 | 34.6829
2024-06-06 14:00 | 38.1 | 30 | 5 | 928 | 26 | 30 | 22 | 0 | 21.9479
2024-06-06 15:00 | 38 | 31 | 5.66 | 817 | 26 | 30 | 22 | 0 | 1.0264
2024-06-06 16:00 | 37.5 | 29 | 5.69 | 648 | 26 | 30 | 22 | 0 | 0
2024-06-06 17:00 | 36.1 | 32 | 5.02 | 444 | 26 | 30 | 22 | 0 | 0
2024-06-06 18:00 | 34.8 | 41 | 3.62 | 230 | 26 | 30 | 22 | 0 | 0
2024-06-06 19:00 | 32.8 | 54 | 3.26 | 58 | 26 | 30 | 22 | 6.2593 | 0
2024-06-06 20:00 | 31.2 | 68 | 2.83 | 0 | 26 | 30 | 22 | 2.7967 | 0
2024-06-06 21:00 | 30.3 | 77 | 1.65 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-06 22:00 | 29.6 | 79 | 2.15 | 0 | 26 | 30 | 22 | 2.1107 | 0
2024-06-06 23:00 | 28.6 | 81 | 1.9 | 0 | 26 | 30 | 22 | 8.718 | 0
2024-06-07 | 27.6 | 82 | 1.82 | 0 | 26 | 30 | 22 | 15.8958 | 0
2024-06-07 01:00 | 27 | 79 | 2.5 | 0 | 26 | 30 | 22 | 27.5048 | 0
2024-06-07 02:00 | 26.3 | 75 | 2.5 | 0 | 26 | 30 | 22 | 39.0879 | 0
2024-06-07 03:00 | 25.5 | 67 | 2.98 | 0 | 26 | 30 | 22 | 61.52 | 0
2024-06-07 04:00 | 24.7 | 61 | 2.7 | 0 | 26 | 30 | 22 | 72.1562 | 0
2024-06-07 05:00 | 25.4 | 56 | 2.58 | 0 | 26 | 30 | 22 | 70.9339 | 0
2024-06-07 06:00 | 25.7 | 53 | 2.7 | 9 | 26 | 30 | 22 | 73.1502 | 0
2024-06-07 07:00 | 28.4 | 46 | 2.47 | 120 | 26 | 30 | 22 | 44.0734 | 0
2024-06-07 08:00 | 32.9 | 42 | 2.62 | 319 | 26 | 30 | 22 | 0 | 0
2024-06-07 09:00 | 37.2 | 37 | 2.55 | 529 | 26 | 30 | 22 | 0 | 16.4855
2024-06-07 10:00 | 40.6 | 24 | 3.01 | 719 | 26 | 30 | 22 | 0 | 27.0963
2024-06-07 11:00 | 41.1 | 21 | 3.24 | 865 | 26 | 30 | 22 | 0 | 36.78
2024-06-07 12:00 | 38.2 | 35 | 7.46 | 947 | 26 | 30 | 22 | 0 | 20.9334
2024-06-07 13:00 | 38 | 40 | 6.26 | 958 | 26 | 30 | 22 | 0 | 54.1878
2024-06-07 14:00 | 37.5 | 37 | 7.68 | 911 | 26 | 30 | 22 | 0 | 12.7345
2024-06-07 15:00 | 36.6 | 41 | 7.28 | 798 | 26 | 30 | 22 | 0 | 5.6315
2024-06-07 16:00 | 35.5 | 44 | 6.95 | 634 | 26 | 30 | 22 | 0 | 0
2024-06-07 17:00 | 35 | 46 | 4.43 | 433 | 26 | 30 | 22 | 0 | 0
2024-06-07 18:00 | 34.1 | 40 | 3.51 | 225 | 26 | 30 | 22 | 4.3152 | 0
2024-06-07 19:00 | 33 | 43 | 2.01 | 58 | 26 | 30 | 22 | 18.543 | 0
2024-06-07 20:00 | 31.6 | 49 | 0.8 | 0 | 26 | 30 | 22 | 15.0911 | 0
2024-06-07 21:00 | 31.1 | 48 | 0.9 | 0 | 26 | 30 | 22 | 19.5345 | 0
2024-06-07 22:00 | 31.2 | 45 | 0.85 | 0 | 26 | 30 | 22 | 20.7301 | 0
2024-06-07 23:00 | 30.8 | 46 | 0.85 | 0 | 26 | 30 | 22 | 21.7689 | 0
2024-06-08 | 30.3 | 51 | 0.61 | 0 | 26 | 30 | 22 | 16.7673 | 0
2024-06-08 01:00 | 28.8 | 55 | 1.25 | 0 | 26 | 30 | 22 | 30.1165 | 0
2024-06-08 02:00 | 26.6 | 57 | 2.24 | 0 | 26 | 30 | 22 | 55.732 | 0
2024-06-08 03:00 | 25.6 | 57 | 1.82 | 0 | 26 | 30 | 22 | 55.9111 | 0
2024-06-08 04:00 | 26 | 55 | 1.3 | 0 | 26 | 30 | 22 | 46.0447 | 0
2024-06-08 05:00 | 25.5 | 55 | 1.84 | 0 | 26 | 30 | 22 | 58.812 | 0
2024-06-08 06:00 | 27.3 | 48 | 0.71 | 9 | 26 | 30 | 22 | 31.269 | 0
2024-06-08 07:00 | 28.1 | 48 | 2.48 | 115 | 26 | 30 | 22 | 44.2775 | 0
2024-06-08 08:00 | 31.6 | 45 | 2.04 | 305 | 26 | 30 | 22 | 0 | 0
2024-06-08 09:00 | 35.1 | 39 | 2.34 | 506 | 26 | 30 | 22 | 0 | 4.2487
2024-06-08 10:00 | 38.4 | 34 | 3.75 | 695 | 26 | 30 | 22 | 0 | 25.1207
2024-06-08 11:00 | 41 | 25 | 4.24 | 838 | 26 | 30 | 22 | 0 | 31.5655
2024-06-08 12:00 | 42.3 | 18 | 3.38 | 926 | 26 | 30 | 22 | 0 | 41.0876
2024-06-08 13:00 | 41.7 | 23 | 4.07 | 949 | 26 | 30 | 22 | 0 | 47.5844
2024-06-08 14:00 | 40.1 | 29 | 6.82 | 899 | 26 | 30 | 22 | 0 | 17.938
2024-06-08 15:00 | 39.6 | 26 | 7.12 | 788 | 26 | 30 | 22 | 0 | 0
2024-06-08 16:00 | 39 | 27 | 6.04 | 624 | 26 | 30 | 22 | 0 | 0
2024-06-08 17:00 | 38.6 | 38 | 6.45 | 423 | 26 | 30 | 22 | 0 | 0
2024-06-08 18:00 | 38.3 | 41 | 6.1 | 217 | 26 | 30 | 22 | 0 | 0
2024-06-08 19:00 | 37 | 47 | 5.02 | 55 | 26 | 30 | 22 | 0 | 0
2024-06-08 20:00 | 36.6 | 45 | 4.62 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-08 21:00 | 34.9 | 57 | 7.96 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-08 22:00 | 34.1 | 61 | 7.43 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-08 23:00 | 33.6 | 61 | 6.14 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-09 | 33.3 | 57 | 5.1 | 0 | 26 | 30 | 22 | 1.2286 | 0
2024-06-09 01:00 | 33 | 53 | 4.53 | 0 | 26 | 30 | 22 | 16.866 | 0
2024-06-09 02:00 | 31.4 | 56 | 1.52 | 0 | 26 | 30 | 22 | 15.7798 | 0
2024-06-09 03:00 | 32.1 | 52 | 0.45 | 0 | 26 | 30 | 22 | 8.9559 | 0
2024-06-09 04:00 | 31.7 | 53 | 0.63 | 0 | 26 | 30 | 22 | 9.8625 | 0
2024-06-09 05:00 | 30.8 | 63 | 2.63 | 0 | 26 | 30 | 22 | 15.3872 | 0
2024-06-09 06:00 | 30.4 | 65 | 2.6 | 8 | 26 | 30 | 22 | 14.7526 | 0
2024-06-09 07:00 | 32.2 | 60 | 2.62 | 110 | 26 | 30 | 22 | 0 | 0
2024-06-09 08:00 | 34.6 | 52 | 3.36 | 293 | 26 | 30 | 22 | 0 | 0
2024-06-09 09:00 | 36.8 | 41 | 4.77 | 497 | 26 | 30 | 22 | 0 | 0
2024-06-09 10:00 | 39.3 | 31 | 5.89 | 685 | 26 | 30 | 22 | 0 | 0
2024-06-09 11:00 | 41.4 | 23 | 5.43 | 830 | 26 | 30 | 22 | 0 | 9.8317
2024-06-09 12:00 | 42.7 | 20 | 4.34 | 917 | 26 | 30 | 22 | 0 | 35.8722
2024-06-09 13:00 | 44 | 18 | 3.01 | 939 | 26 | 30 | 22 | 0 | 62.5852
2024-06-09 14:00 | 43.3 | 19 | 2.72 | 885 | 26 | 30 | 22 | 0 | 58.7817
2024-06-09 15:00 | 41 | 35 | 7.27 | 757 | 26 | 30 | 22 | 0 | 44.6474
2024-06-09 16:00 | 40 | 37 | 8.01 | 603 | 26 | 30 | 22 | 0 | 13.9824
2024-06-09 17:00 | 39.3 | 34 | 7.82 | 418 | 26 | 30 | 22 | 0 | 0
2024-06-09 18:00 | 37.9 | 36 | 7.61 | 217 | 26 | 30 | 22 | 0 | 0
2024-06-09 19:00 | 36.4 | 42 | 6.09 | 56 | 26 | 30 | 22 | 0.2589 | 0
2024-06-09 20:00 | 36 | 45 | 4.49 | 0 | 26 | 30 | 22 | 2.1264 | 0
2024-06-09 21:00 | 35.7 | 41 | 3.92 | 0 | 26 | 30 | 22 | 17.3317 | 0
2024-06-09 22:00 | 35.5 | 36 | 3.97 | 0 | 26 | 30 | 22 | 34.3559 | 0
2024-06-09 23:00 | 34.7 | 37 | 2.75 | 0 | 26 | 30 | 22 | 30.8434 | 0
2024-06-10 | 34.1 | 42 | 3.2 | 0 | 26 | 30 | 22 | 27.9494 | 0
2024-06-10 01:00 | 33.3 | 49 | 3.04 | 0 | 26 | 30 | 22 | 19.1659 | 0
2024-06-10 02:00 | 32.4 | 51 | 3.05 | 0 | 26 | 30 | 22 | 23.7921 | 0
2024-06-10 03:00 | 31.8 | 52 | 2.98 | 0 | 26 | 30 | 22 | 27.2216 | 0
2024-06-10 04:00 | 31.3 | 50 | 3.62 | 0 | 26 | 30 | 22 | 40.2532 | 0
2024-06-10 05:00 | 31.7 | 52 | 3.74 | 0 | 26 | 30 | 22 | 32.2623 | 0
2024-06-10 06:00 | 31.5 | 47 | 3.55 | 8 | 26 | 30 | 22 | 43.1501 | 0
2024-06-10 07:00 | 33.1 | 40 | 3.34 | 111 | 26 | 30 | 22 | 27.8522 | 0
2024-06-10 08:00 | 35.3 | 34 | 4.4 | 296 | 26 | 30 | 22 | 5.2419 | 0
2024-06-10 09:00 | 37.4 | 31 | 5.33 | 502 | 26 | 30 | 22 | 0 | 0
2024-06-10 10:00 | 39.5 | 27 | 4.59 | 689 | 26 | 30 | 22 | 0 | 0
2024-06-10 11:00 | 41.3 | 23 | 3.56 | 835 | 26 | 30 | 22 | 0 | 36.1504
2024-06-10 12:00 | 42.5 | 20 | 2.82 | 924 | 26 | 30 | 22 | 0 | 59.7491
2024-06-10 13:00 | 42.7 | 22 | 4.96 | 946 | 26 | 30 | 22 | 0 | 41.0757
2024-06-10 14:00 | 42.1 | 23 | 5.97 | 896 | 26 | 30 | 22 | 0 | 20.57
2024-06-10 15:00 | 41.3 | 24 | 6.52 | 778 | 26 | 30 | 22 | 0 | 0
2024-06-10 16:00 | 39.9 | 28 | 6.36 | 623 | 26 | 30 | 22 | 0 | 0
2024-06-10 17:00 | 38.8 | 31 | 6.14 | 425 | 26 | 30 | 22 | 0 | 0
2024-06-10 18:00 | 36.8 | 40 | 6.13 | 222 | 26 | 30 | 22 | 0 | 0
2024-06-10 19:00 | 35 | 47 | 5.1 | 58 | 26 | 30 | 22 | 1.2246 | 0
2024-06-10 20:00 | 33.9 | 57 | 2.91 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-10 21:00 | 33.4 | 56 | 0.64 | 0 | 26 | 30 | 22 | 0.1321 | 0
2024-06-10 22:00 | 33 | 52 | 2.25 | 0 | 26 | 30 | 22 | 13.0514 | 0
2024-06-10 23:00 | 32 | 50 | 2.16 | 0 | 26 | 30 | 22 | 23.9321 | 0
2024-06-11 | 30.9 | 50 | 1.71 | 0 | 26 | 30 | 22 | 28.01 | 0
2024-06-11 01:00 | 30.6 | 48 | 2.26 | 0 | 26 | 30 | 22 | 38.5545 | 0
2024-06-11 02:00 | 30 | 47 | 2.06 | 0 | 26 | 30 | 22 | 41.9848 | 0
2024-06-11 03:00 | 29.8 | 46 | 2.9 | 0 | 26 | 30 | 22 | 55.2182 | 0
2024-06-11 04:00 | 28.9 | 47 | 2.56 | 0 | 26 | 30 | 22 | 56.4215 | 0
2024-06-11 05:00 | 29.9 | 41 | 2.38 | 0 | 26 | 30 | 22 | 55.601 | 0
2024-06-11 06:00 | 30 | 40 | 2.75 | 8 | 26 | 30 | 22 | 60.7321 | 0
2024-06-11 07:00 | 32 | 34 | 3.21 | 111 | 26 | 30 | 22 | 48.8748 | 0
2024-06-11 08:00 | 35.1 | 25 | 4.3 | 299 | 26 | 30 | 22 | 33.5167 | 0
2024-06-11 09:00 | 38.2 | 21 | 5.69 | 507 | 26 | 30 | 22 | 3.9865 | 0
2024-06-11 10:00 | 40.9 | 20 | 6.95 | 697 | 26 | 30 | 22 | 0 | 0
2024-06-11 11:00 | 42.8 | 17 | 6.79 | 842 | 26 | 30 | 22 | 0 | 0
2024-06-11 12:00 | 44 | 15 | 6.84 | 928 | 26 | 30 | 22 | 0 | 0
2024-06-11 13:00 | 43.4 | 18 | 7.91 | 950 | 26 | 30 | 22 | 0 | 0
2024-06-11 14:00 | 42.6 | 19 | 8.3 | 903 | 26 | 30 | 22 | 0 | 0
2024-06-11 15:00 | 41.4 | 21 | 7.67 | 795 | 26 | 30 | 22 | 0 | 0
2024-06-11 16:00 | 39.1 | 31 | 6.86 | 631 | 26 | 30 | 22 | 0 | 0
2024-06-11 17:00 | 39.3 | 24 | 6.04 | 432 | 26 | 30 | 22 | 0 | 0
2024-06-11 18:00 | 36.7 | 37 | 5.25 | 225 | 26 | 30 | 22 | 0 | 0
2024-06-11 19:00 | 34.9 | 48 | 4.05 | 58 | 26 | 30 | 22 | 0 | 0
2024-06-11 20:00 | 33.8 | 56 | 2.25 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-11 21:00 | 32.9 | 60 | 1.82 | 0 | 26 | 30 | 22 | 0.3172 | 0
2024-06-11 22:00 | 31.8 | 67 | 1.49 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-11 23:00 | 31.3 | 70 | 0.92 | 0 | 26 | 30 | 22 | 0.5212 | 0
2024-06-12 | 30.1 | 72 | 1.65 | 0 | 26 | 30 | 22 | 6.7848 | 0
2024-06-12 01:00 | 29.3 | 74 | 1.61 | 0 | 26 | 30 | 22 | 10.6352 | 0
2024-06-12 02:00 | 29.1 | 70 | 2.51 | 0 | 26 | 30 | 22 | 20.1667 | 0
2024-06-12 03:00 | 28.4 | 68 | 2.5 | 0 | 26 | 30 | 22 | 29.4997 | 0
2024-06-12 04:00 | 27.8 | 63 | 3.42 | 0 | 26 | 30 | 22 | 49.8158 | 0
2024-06-12 05:00 | 29.3 | 51 | 3.93 | 0 | 26 | 30 | 22 | 61.373 | 0
2024-06-12 06:00 | 29.6 | 47 | 4.39 | 8 | 26 | 30 | 22 | 70.2721 | 0
2024-06-12 07:00 | 31.7 | 38 | 4.78 | 112 | 26 | 30 | 22 | 59.9042 | 0
2024-06-12 08:00 | 34.4 | 31 | 4.78 | 301 | 26 | 30 | 22 | 26.3984 | 0
2024-06-12 09:00 | 38.1 | 24 | 5.32 | 508 | 26 | 30 | 22 | 0 | 0
2024-06-12 10:00 | 41.3 | 17 | 6.31 | 697 | 26 | 30 | 22 | 0 | 0
2024-06-12 11:00 | 42.8 | 13 | 6.87 | 844 | 26 | 30 | 22 | 0 | 0
2024-06-12 12:00 | 42.4 | 17 | 8 | 932 | 26 | 30 | 22 | 0 | 0
2024-06-12 13:00 | 42 | 17 | 8.55 | 952 | 26 | 30 | 22 | 0 | 0
2024-06-12 14:00 | 41 | 21 | 8.4 | 906 | 26 | 30 | 22 | 0 | 0
2024-06-12 15:00 | 39.8 | 27 | 7.54 | 793 | 26 | 30 | 22 | 0 | 0
2024-06-12 16:00 | 38.7 | 32 | 6.04 | 629 | 26 | 30 | 22 | 0 | 0
2024-06-12 17:00 | 38.2 | 28 | 4.05 | 430 | 26 | 30 | 22 | 0 | 0
2024-06-12 18:00 | 37.2 | 30 | 3.54 | 225 | 26 | 30 | 22 | 2.5272 | 0
2024-06-12 19:00 | 35.7 | 34 | 2.7 | 59 | 26 | 30 | 22 | 21.0656 | 0
2024-06-12 20:00 | 34.2 | 42 | 1.58 | 0 | 26 | 30 | 22 | 16.134 | 0
2024-06-12 21:00 | 32.9 | 46 | 1.56 | 0 | 26 | 30 | 22 | 18.7644 | 0
2024-06-12 22:00 | 32.3 | 47 | 2.31 | 0 | 26 | 30 | 22 | 27.5693 | 0
2024-06-12 23:00 | 31.4 | 50 | 2.44 | 0 | 26 | 30 | 22 | 30.7934 | 0
2024-06-13 | 30.7 | 52 | 2.84 | 0 | 26 | 30 | 22 | 36.4654 | 0
2024-06-13 01:00 | 30.4 | 50 | 3.45 | 0 | 26 | 30 | 22 | 48.0005 | 0
2024-06-13 02:00 | 30 | 47 | 3.64 | 0 | 26 | 30 | 22 | 59.6829 | 0
2024-06-13 03:00 | 29.8 | 44 | 4.2 | 0 | 26 | 30 | 22 | 73.9651 | 0
2024-06-13 04:00 | 29.5 | 42 | 3.86 | 0 | 26 | 30 | 22 | 77.0963 | 0
2024-06-13 05:00 | 29.9 | 35 | 3.71 | 0 | 26 | 30 | 22 | 85.8446 | 0
2024-06-13 06:00 | 29.8 | 34 | 3.49 | 8 | 26 | 30 | 22 | 84.1966 | 0
2024-06-13 07:00 | 31.6 | 30 | 2.89 | 113 | 26 | 30 | 22 | 54.856 | 0
2024-06-13 08:00 | 34.7 | 26 | 2.47 | 303 | 26 | 30 | 22 | 9.7753 | 0
2024-06-13 09:00 | 37.7 | 24 | 3.61 | 512 | 26 | 30 | 22 | 0 | 0
2024-06-13 10:00 | 39.4 | 26 | 4.71 | 699 | 26 | 30 | 22 | 0 | 0
2024-06-13 11:00 | 40.4 | 30 | 5.33 | 843 | 26 | 30 | 22 | 0 | 34.5929
2024-06-13 12:00 | 40.6 | 32 | 6.6 | 928 | 26 | 30 | 22 | 0 | 47.9179
2024-06-13 13:00 | 40.1 | 34 | 6.64 | 947 | 26 | 30 | 22 | 0 | 53.2596
2024-06-13 14:00 | 40.7 | 31 | 5.28 | 901 | 26 | 30 | 22 | 0 | 51.5412
2024-06-13 15:00 | 40.2 | 34 | 5.19 | 793 | 26 | 30 | 22 | 0 | 45.0433
2024-06-13 16:00 | 40.1 | 34 | 5.24 | 630 | 26 | 30 | 22 | 0 | 21.2718
2024-06-13 17:00 | 38.6 | 34 | 5.72 | 433 | 26 | 30 | 22 | 0 | 0
2024-06-13 18:00 | 37.9 | 35 | 5.09 | 228 | 26 | 30 | 22 | 0 | 0
2024-06-13 19:00 | 37.4 | 32 | 4.34 | 60 | 26 | 30 | 22 | 20.9718 | 0
2024-06-13 20:00 | 36.3 | 33 | 4.55 | 0 | 26 | 30 | 22 | 38.6435 | 0
2024-06-13 21:00 | 34.6 | 44 | 4.02 | 0 | 26 | 30 | 22 | 21.3368 | 0
2024-06-13 22:00 | 33.7 | 50 | 3.89 | 0 | 26 | 30 | 22 | 15.068 | 0
2024-06-13 23:00 | 33.3 | 50 | 3.91 | 0 | 26 | 30 | 22 | 19.7669 | 0
2024-06-14 | 32 | 54 | 2.9 | 0 | 26 | 30 | 22 | 21.025 | 0
2024-06-14 01:00 | 31.2 | 57 | 3.18 | 0 | 26 | 30 | 22 | 24.3415 | 0
2024-06-14 02:00 | 30.6 | 57 | 3.33 | 0 | 26 | 30 | 22 | 31.2764 | 0
2024-06-14 03:00 | 29.8 | 54 | 3.73 | 0 | 26 | 30 | 22 | 48.2899 | 0
2024-06-14 04:00 | 29 | 52 | 4.18 | 0 | 26 | 30 | 22 | 64.8428 | 0
2024-06-14 05:00 | 29.9 | 56 | 4.02 | 0 | 26 | 30 | 22 | 45.0796 | 0
2024-06-14 06:00 | 30 | 59 | 4.44 | 9 | 26 | 30 | 22 | 38.3867 | 0
2024-06-14 07:00 | 32.3 | 54 | 4.26 | 116 | 26 | 30 | 22 | 6.8073 | 0
2024-06-14 08:00 | 35.1 | 46 | 4.18 | 307 | 26 | 30 | 22 | 0 | 0
2024-06-14 09:00 | 37.1 | 32 | 6.48 | 516 | 26 | 30 | 22 | 0 | 0
2024-06-14 10:00 | 37.9 | 30 | 7.18 | 708 | 26 | 30 | 22 | 0 | 0
2024-06-14 11:00 | 38.1 | 31 | 7.93 | 856 | 26 | 30 | 22 | 0 | 0
2024-06-14 12:00 | 38.4 | 31 | 8.21 | 944 | 26 | 30 | 22 | 0 | 0
2024-06-14 13:00 | 38.6 | 32 | 8.39 | 965 | 26 | 30 | 22 | 0 | 4.6124
2024-06-14 14:00 | 38.7 | 31 | 8.42 | 918 | 26 | 30 | 22 | 0 | 0
2024-06-14 15:00 | 38.2 | 33 | 8.3 | 809 | 26 | 30 | 22 | 0 | 0
2024-06-14 16:00 | 37.6 | 34 | 7.92 | 643 | 26 | 30 | 22 | 0 | 0
2024-06-14 17:00 | 36.3 | 40 | 6.28 | 439 | 26 | 30 | 22 | 0 | 0
2024-06-14 18:00 | 35.4 | 43 | 4.88 | 231 | 26 | 30 | 22 | 0 | 0
2024-06-14 19:00 | 33.8 | 50 | 3.83 | 62 | 26 | 30 | 22 | 5.4099 | 0
2024-06-14 20:00 | 32.8 | 56 | 2.75 | 0 | 26 | 30 | 22 | 8.8918 | 0
2024-06-14 21:00 | 32 | 61 | 2.58 | 0 | 26 | 30 | 22 | 7.1412 | 0
2024-06-14 22:00 | 30.8 | 64 | 2.79 | 0 | 26 | 30 | 22 | 14.0764 | 0
2024-06-14 23:00 | 29.8 | 61 | 3.01 | 0 | 26 | 30 | 22 | 30.2269 | 0
2024-06-15 | 29.1 | 59 | 2.92 | 0 | 26 | 30 | 22 | 39.7604 | 0
2024-06-15 01:00 | 28.1 | 58 | 2.91 | 0 | 26 | 30 | 22 | 50.3953 | 0
2024-06-15 02:00 | 26.7 | 55 | 2.86 | 0 | 26 | 30 | 22 | 66.2197 | 0
2024-06-15 03:00 | 26.3 | 47 | 2.86 | 0 | 26 | 30 | 22 | 80.5106 | 0
2024-06-15 04:00 | 26.1 | 42 | 3.24 | 0 | 26 | 30 | 22 | 95.9254 | 0
2024-06-15 05:00 | 26.7 | 39 | 2.78 | 0 | 26 | 30 | 22 | 87.2587 | 0
2024-06-15 06:00 | 26.7 | 36 | 2.86 | 9 | 26 | 30 | 22 | 91.8266 | 0
2024-06-15 07:00 | 29.1 | 29 | 2.31 | 116 | 26 | 30 | 22 | 61.0778 | 0
2024-06-15 08:00 | 33.3 | 21 | 2.3 | 310 | 26 | 30 | 22 | 23.7022 | 0
2024-06-15 09:00 | 37.7 | 15 | 2.06 | 525 | 26 | 30 | 22 | 0 | 0
2024-06-15 10:00 | 40 | 11 | 1.58 | 719 | 26 | 30 | 22 | 0 | 25.8626
2024-06-15 11:00 | 41.3 | 10 | 2.73 | 870 | 26 | 30 | 22 | 0 | 14.4992
2024-06-15 12:00 | 41.7 | 12 | 4.06 | 962 | 26 | 30 | 22 | 0 | 3.6063
2024-06-15 13:00 | 41.8 | 11 | 4.4 | 985 | 26 | 30 | 22 | 0 | 0
2024-06-15 14:00 | 41.4 | 12 | 4.53 | 939 | 26 | 30 | 22 | 0 | 0
2024-06-15 15:00 | 40.8 | 16 | 4.46 | 824 | 26 | 30 | 22 | 0 | 0
2024-06-15 16:00 | 39.7 | 21 | 4.69 | 654 | 26 | 30 | 22 | 0 | 0
2024-06-15 17:00 | 39.3 | 19 | 3.58 | 450 | 26 | 30 | 22 | 0 | 0
2024-06-15 18:00 | 38.1 | 23 | 2.56 | 237 | 26 | 30 | 22 | 4.0895 | 0
2024-06-15 19:00 | 36.1 | 34 | 2.5 | 64 | 26 | 30 | 22 | 15.6893 | 0
2024-06-15 20:00 | 34.4 | 42 | 2.5 | 0 | 26 | 30 | 22 | 21.136 | 0
2024-06-15 21:00 | 33.1 | 46 | 2.79 | 0 | 26 | 30 | 22 | 26.0115 | 0
2024-06-15 22:00 | 32 | 43 | 2.98 | 0 | 26 | 30 | 22 | 43.0587 | 0
2024-06-15 23:00 | 31 | 35 | 2.96 | 0 | 26 | 30 | 22 | 66.1516 | 0
2024-06-16 | 30.1 | 32 | 3.01 | 0 | 26 | 30 | 22 | 78.9305 | 0
2024-06-16 01:00 | 29.5 | 30 | 3.22 | 0 | 26 | 30 | 22 | 90.4311 | 0
2024-06-16 02:00 | 28.6 | 26 | 3.22 | 0 | 26 | 30 | 22 | 103.5329 | 0
2024-06-16 03:00 | 28.5 | 22 | 3.35 | 0 | 26 | 30 | 22 | 113.8841 | 0
2024-06-16 04:00 | 28 | 20 | 3.3 | 0 | 26 | 30 | 22 | 119.1986 | 0
2024-06-16 05:00 | 28.8 | 19 | 3.91 | 0 | 26 | 30 | 22 | 129.8622 | 0
2024-06-16 06:00 | 29.2 | 17 | 4.11 | 8 | 26 | 30 | 22 | 134.6315 | 0
2024-06-16 07:00 | 30.7 | 18 | 2.5 | 115 | 26 | 30 | 22 | 73.3211 | 0
2024-06-16 08:00 | 33.1 | 24 | 0.86 | 306 | 26 | 30 | 22 | 0 | 0
2024-06-16 09:00 | 36.9 | 28 | 1.22 | 516 | 26 | 30 | 22 | 0 | 23.3597
2024-06-16 10:00 | 41.5 | 18 | 2.33 | 708 | 26 | 30 | 22 | 0 | 27.5376
2024-06-16 11:00 | 43.9 | 9 | 3.05 | 854 | 26 | 30 | 22 | 0 | 15.1935
2024-06-16 12:00 | 44.8 | 8 | 2.12 | 948 | 26 | 30 | 22 | 0 | 54.1887
2024-06-16 13:00 | 44.9 | 10 | 3.39 | 971 | 26 | 30 | 22 | 0 | 33.2696
2024-06-16 14:00 | 44 | 15 | 6.11 | 917 | 26 | 30 | 22 | 0 | 0
2024-06-16 15:00 | 42.1 | 22 | 7.6 | 764 | 26 | 30 | 22 | 0 | 0
2024-06-16 16:00 | 41.3 | 22 | 7.16 | 638 | 26 | 30 | 22 | 0 | 0
2024-06-16 17:00 | 39.7 | 28 | 6.53 | 431 | 26 | 30 | 22 | 0 | 0
2024-06-16 18:00 | 37.9 | 35 | 6.65 | 231 | 26 | 30 | 22 | 0 | 0
2024-06-16 19:00 | 35.8 | 46 | 5.3 | 62 | 26 | 30 | 22 | 0 | 0
2024-06-16 20:00 | 34.1 | 60 | 3.63 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-16 21:00 | 34.1 | 48 | 2.66 | 0 | 26 | 30 | 22 | 12.3431 | 0
2024-06-16 22:00 | 33 | 48 | 2.36 | 0 | 26 | 30 | 22 | 20.5482 | 0
2024-06-16 23:00 | 32.2 | 42 | 2.56 | 0 | 26 | 30 | 22 | 39.2555 | 0
2024-06-17 | 32.1 | 40 | 1.22 | 0 | 26 | 30 | 22 | 26.5728 | 0
2024-06-17 01:00 | 30.2 | 46 | 1.9 | 0 | 26 | 30 | 22 | 39.931 | 0
2024-06-17 02:00 | 29.4 | 56 | 2.32 | 0 | 26 | 30 | 22 | 36.7028 | 0
2024-06-17 03:00 | 28.8 | 58 | 1.6 | 0 | 26 | 30 | 22 | 31.3891 | 0
2024-06-17 04:00 | 28.2 | 62 | 2.77 | 0 | 26 | 30 | 22 | 42.0731 | 0
2024-06-17 05:00 | 28.3 | 73 | 1.98 | 0 | 26 | 30 | 22 | 21.0004 | 0
2024-06-17 06:00 | 28.4 | 68 | 2.11 | 8 | 26 | 30 | 22 | 25.9742 | 0
2024-06-17 07:00 | 30.1 | 54 | 2.01 | 110 | 26 | 30 | 22 | 16.4201 | 0
2024-06-17 08:00 | 33.8 | 42 | 2.19 | 296 | 26 | 30 | 22 | 0 | 0
2024-06-17 09:00 | 37.9 | 29 | 3.04 | 504 | 26 | 30 | 22 | 0 | 0
2024-06-17 10:00 | 40.8 | 22 | 4.16 | 693 | 26 | 30 | 22 | 0 | 0
2024-06-17 11:00 | 42.8 | 19 | 3.91 | 839 | 26 | 30 | 22 | 0 | 28.4065
2024-06-17 12:00 | 44.7 | 14 | 3.24 | 929 | 26 | 30 | 22 | 0 | 46.3272
2024-06-17 13:00 | 45.4 | 13 | 3.23 | 954 | 26 | 30 | 22 | 0 | 50.6786
2024-06-17 14:00 | 45.1 | 15 | 5.02 | 894 | 26 | 30 | 22 | 0 | 20.3787
2024-06-17 15:00 | 44.2 | 15 | 6.94 | 783 | 26 | 30 | 22 | 0 | 0
2024-06-17 16:00 | 42 | 21 | 7.26 | 605 | 26 | 30 | 22 | 0 | 0
2024-06-17 17:00 | 38.3 | 40 | 7.07 | 431 | 26 | 30 | 22 | 0 | 0
2024-06-17 18:00 | 36.3 | 51 | 6.38 | 224 | 26 | 30 | 22 | 0 | 0
2024-06-17 19:00 | 34.3 | 65 | 5.02 | 60 | 26 | 30 | 22 | 0 | 0
2024-06-17 20:00 | 33.7 | 70 | 3.35 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-17 21:00 | 33.7 | 64 | 2.34 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-17 22:00 | 33 | 64 | 1.75 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-17 23:00 | 32.2 | 67 | 1.12 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-18 | 31.3 | 67 | 1.71 | 0 | 26 | 30 | 22 | 3.5038 | 0
2024-06-18 01:00 | 30.9 | 66 | 1.4 | 0 | 26 | 30 | 22 | 7.2947 | 0
2024-06-18 02:00 | 30.4 | 66 | 2.64 | 0 | 26 | 30 | 22 | 14.2925 | 0
2024-06-18 03:00 | 29.4 | 70 | 2.15 | 0 | 26 | 30 | 22 | 16.179 | 0
2024-06-18 04:00 | 28.8 | 70 | 1.82 | 0 | 26 | 30 | 22 | 19.7656 | 0
2024-06-18 05:00 | 29.9 | 54 | 2.56 | 0 | 26 | 30 | 22 | 37.7588 | 0
2024-06-18 06:00 | 29.8 | 47 | 2.2 | 8 | 26 | 30 | 22 | 44.0604 | 0
2024-06-18 07:00 | 32.3 | 37 | 1.75 | 108 | 26 | 30 | 22 | 22.2267 | 0
2024-06-18 08:00 | 36 | 26 | 1.04 | 285 | 26 | 30 | 22 | 0 | 0
2024-06-18 09:00 | 39.3 | 18 | 1.14 | 493 | 26 | 30 | 22 | 0 | 19.373
2024-06-18 10:00 | 41.6 | 14 | 1.36 | 608 | 26 | 30 | 22 | 0 | 31.0601
2024-06-18 11:00 | 43.2 | 14 | 2.91 | 802 | 26 | 30 | 22 | 0 | 25.5849
2024-06-18 12:00 | 43.6 | 17 | 3.28 | 869 | 26 | 30 | 22 | 0 | 41.4501
2024-06-18 13:00 | 43.9 | 17 | 4.82 | 943 | 26 | 30 | 22 | 0 | 29.2213
2024-06-18 14:00 | 42.8 | 19 | 6.13 | 901 | 26 | 30 | 22 | 0 | 4.841
2024-06-18 15:00 | 40.3 | 30 | 6.44 | 792 | 26 | 30 | 22 | 0 | 15.5323
2024-06-18 16:00 | 39.5 | 33 | 6.55 | 627 | 26 | 30 | 22 | 0 | 0
2024-06-18 17:00 | 38.7 | 33 | 5.24 | 431 | 26 | 30 | 22 | 0 | 0
2024-06-18 18:00 | 36.8 | 43 | 5.23 | 226 | 26 | 30 | 22 | 0 | 0
2024-06-18 19:00 | 35.1 | 53 | 4.02 | 61 | 26 | 30 | 22 | 0 | 0
2024-06-18 20:00 | 34.1 | 60 | 0.73 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-18 21:00 | 33.4 | 62 | 0.95 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-18 22:00 | 32.8 | 63 | 1.97 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-18 23:00 | 32.1 | 66 | 2.48 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-19 | 31.3 | 71 | 2.34 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-19 01:00 | 30.2 | 77 | 1.63 | 0 | 26 | 30 | 22 | 0.1535 | 0
2024-06-19 02:00 | 29.7 | 80 | 1.8 | 0 | 26 | 30 | 22 | 0.4542 | 0
2024-06-19 03:00 | 29.2 | 81 | 1.68 | 0 | 26 | 30 | 22 | 3.6829 | 0
2024-06-19 04:00 | 29.3 | 79 | 2.6 | 0 | 26 | 30 | 22 | 4.7292 | 0
2024-06-19 05:00 | 30 | 71 | 2.45 | 0 | 26 | 30 | 22 | 9.8828 | 0
2024-06-19 06:00 | 31.1 | 63 | 2.33 | 6 | 26 | 30 | 22 | 10.9855 | 0
2024-06-19 07:00 | 33 | 50 | 3.14 | 82 | 26 | 30 | 22 | 9.2985 | 0
2024-06-19 08:00 | 36.1 | 34 | 3.01 | 222 | 26 | 30 | 22 | 0 | 0
2024-06-19 09:00 | 39.6 | 24 | 3.33 | 491 | 26 | 30 | 22 | 0 | 0
2024-06-19 10:00 | 41.9 | 21 | 3.83 | 667 | 26 | 30 | 22 | 0 | 6.7822
2024-06-19 11:00 | 43.1 | 20 | 4.21 | 813 | 26 | 30 | 22 | 0 | 27.5604
2024-06-19 12:00 | 42.1 | 28 | 5.19 | 921 | 26 | 30 | 22 | 0 | 58.4816
2024-06-19 13:00 | 41.8 | 29 | 6.4 | 943 | 26 | 30 | 22 | 0 | 52.7437
2024-06-19 14:00 | 41.4 | 30 | 7.62 | 900 | 26 | 30 | 22 | 0 | 37.7495
2024-06-19 15:00 | 39.9 | 36 | 8.1 | 790 | 26 | 30 | 22 | 0 | 30.7078
2024-06-19 16:00 | 39.1 | 40 | 7.52 | 625 | 26 | 30 | 22 | 0 | 20.0871
2024-06-19 17:00 | 37.7 | 44 | 7.18 | 427 | 26 | 30 | 22 | 0 | 0
2024-06-19 18:00 | 36.7 | 48 | 5.25 | 224 | 26 | 30 | 22 | 0 | 0
2024-06-19 19:00 | 35.7 | 49 | 4.13 | 61 | 26 | 30 | 22 | 0 | 0
2024-06-19 20:00 | 35.2 | 49 | 3.64 | 0 | 26 | 30 | 22 | 0.0212 | 0
2024-06-19 21:00 | 34.6 | 53 | 2.6 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-19 22:00 | 33.8 | 56 | 2.62 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-19 23:00 | 33.1 | 56 | 2.8 | 0 | 26 | 30 | 22 | 5.9831 | 0
2024-06-20 | 32.5 | 57 | 2.9 | 0 | 26 | 30 | 22 | 10.1814 | 0
2024-06-20 01:00 | 32.4 | 59 | 3 | 0 | 26 | 30 | 22 | 7.3387 | 0
2024-06-20 02:00 | 31.7 | 64 | 2.56 | 0 | 26 | 30 | 22 | 4.7751 | 0
2024-06-20 03:00 | 31 | 66 | 2.83 | 0 | 26 | 30 | 22 | 8.5306 | 0
2024-06-20 04:00 | 30.4 | 64 | 3.41 | 0 | 26 | 30 | 22 | 19.9536 | 0
2024-06-20 05:00 | 30.9 | 54 | 3.2 | 0 | 26 | 30 | 22 | 33.358 | 0
2024-06-20 06:00 | 31.3 | 50 | 3.13 | 6 | 26 | 30 | 22 | 36.0279 | 0
2024-06-20 07:00 | 32.9 | 42 | 3.14 | 92 | 26 | 30 | 22 | 26.1655 | 0
2024-06-20 08:00 | 35.6 | 33 | 3.31 | 196 | 26 | 30 | 22 | 10.7122 | 0
2024-06-20 09:00 | 38.8 | 25 | 3.83 | 492 | 26 | 30 | 22 | 0 | 0
2024-06-20 10:00 | 40.8 | 19 | 4.24 | 679 | 26 | 30 | 22 | 0 | 0
2024-06-20 11:00 | 41.9 | 18 | 4.22 | 834 | 26 | 30 | 22 | 0 | 10.2677
2024-06-20 12:00 | 41.6 | 23 | 4.68 | 920 | 26 | 30 | 22 | 0 | 34.1487
2024-06-20 13:00 | 41.5 | 26 | 5.12 | 937 | 26 | 30 | 22 | 0 | 44.0309
2024-06-20 14:00 | 41.6 | 26 | 5.02 | 892 | 26 | 30 | 22 | 0 | 40.2599
2024-06-20 15:00 | 41.4 | 27 | 4.8 | 784 | 26 | 30 | 22 | 0 | 30.4882
2024-06-20 16:00 | 41.1 | 27 | 4.7 | 625 | 26 | 30 | 22 | 0 | 6.6969
2024-06-20 17:00 | 39.5 | 27 | 5.3 | 429 | 26 | 30 | 22 | 0 | 0
2024-06-20 18:00 | 37.5 | 38 | 5.18 | 226 | 26 | 30 | 22 | 0 | 0
2024-06-20 19:00 | 35.7 | 49 | 3.51 | 61 | 26 | 30 | 22 | 0 | 0
2024-06-20 20:00 | 35.2 | 46 | 1.93 | 0 | 26 | 30 | 22 | 4.7052 | 0
2024-06-20 21:00 | 34.5 | 43 | 2.02 | 0 | 26 | 30 | 22 | 15.5872 | 0
2024-06-20 22:00 | 34.2 | 39 | 3.03 | 0 | 26 | 30 | 22 | 32.8011 | 0
2024-06-20 23:00 | 33.8 | 40 | 3.53 | 0 | 26 | 30 | 22 | 37.7281 | 0
2024-06-21 | 33.3 | 35 | 3.61 | 0 | 26 | 30 | 22 | 55.2773 | 0
2024-06-21 01:00 | 32.5 | 31 | 2.1 | 0 | 26 | 30 | 22 | 49.8276 | 0
2024-06-21 02:00 | 33 | 45 | 0.2 | 0 | 26 | 30 | 22 | 10.8989 | 0
2024-06-21 03:00 | 32 | 44 | 2.01 | 0 | 26 | 30 | 22 | 31.8474 | 0
2024-06-21 04:00 | 31.8 | 41 | 2.38 | 0 | 26 | 30 | 22 | 42.0734 | 0
2024-06-21 05:00 | 29.9 | 62 | 1.8 | 0 | 26 | 30 | 22 | 20.8496 | 0
2024-06-21 06:00 | 30.6 | 44 | 2.41 | 6 | 26 | 30 | 22 | 45.5873 | 0
2024-06-21 07:00 | 31.9 | 35 | 1.7 | 94 | 26 | 30 | 22 | 28.3885 | 0
2024-06-21 08:00 | 35.4 | 26 | 1.53 | 288 | 26 | 30 | 22 | 0 | 0
2024-06-21 09:00 | 38.5 | 18 | 1.6 | 493 | 26 | 30 | 22 | 0 | 1.096
2024-06-21 10:00 | 40.3 | 16 | 0.42 | 682 | 26 | 30 | 22 | 0 | 65.1114
2024-06-21 11:00 | 42.1 | 14 | 0.85 | 828 | 26 | 30 | 22 | 0 | 80.163
2024-06-21 12:00 | 43.1 | 15 | 2.67 | 918 | 26 | 30 | 22 | 0 | 49.3156
2024-06-21 13:00 | 42 | 25 | 5.08 | 940 | 26 | 30 | 22 | 0 | 45.9
2024-06-21 14:00 | 41.2 | 29 | 5.52 | 891 | 26 | 30 | 22 | 0 | 44.7924
2024-06-21 15:00 | 40 | 37 | 5.33 | 775 | 26 | 30 | 22 | 0 | 52.5692
2024-06-21 16:00 | 38.7 | 43 | 5.1 | 623 | 26 | 30 | 22 | 0 | 40.6891
2024-06-21 17:00 | 37.8 | 47 | 5.3 | 427 | 26 | 30 | 22 | 0 | 15.9465
2024-06-21 18:00 | 37.4 | 43 | 4.11 | 226 | 26 | 30 | 22 | 0 | 0
2024-06-21 19:00 | 37 | 40 | 2.5 | 62 | 26 | 30 | 22 | 0 | 0
2024-06-21 20:00 | 35.9 | 46 | 1.44 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-21 21:00 | 34.8 | 51 | 1.91 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-21 22:00 | 33.7 | 56 | 2.28 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-21 23:00 | 32.7 | 67 | 2.28 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-22 | 31.7 | 76 | 2.27 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-22 01:00 | 30.7 | 80 | 2.16 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-22 02:00 | 29.8 | 84 | 1.56 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-22 03:00 | 29.1 | 88 | 1.52 | 0 | 26 | 30 | 22 | 2.0872 | 0
2024-06-22 04:00 | 29.8 | 86 | 0.22 | 0 | 26 | 30 | 22 | 2.9821 | 0
2024-06-22 05:00 | 29.5 | 95 | 2.79 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-22 06:00 | 29.5 | 87 | 2.28 | 7 | 26 | 30 | 22 | 0 | 0
2024-06-22 07:00 | 31.1 | 72 | 1.3 | 99 | 26 | 30 | 22 | 0 | 0
2024-06-22 08:00 | 33.9 | 57 | 1.02 | 288 | 26 | 30 | 22 | 0 | 15.0694
2024-06-22 09:00 | 37.6 | 41 | 2.71 | 494 | 26 | 30 | 22 | 0 | 22.9706
2024-06-22 10:00 | 41.2 | 27 | 2.21 | 683 | 26 | 30 | 22 | 0 | 48.9741
2024-06-22 11:00 | 44 | 18 | 0.95 | 829 | 26 | 30 | 22 | 0 | 91.1307
2024-06-22 12:00 | 45.9 | 14 | 1.39 | 919 | 26 | 30 | 22 | 0 | 92.3369
2024-06-22 13:00 | 45.9 | 19 | 4.1 | 942 | 26 | 30 | 22 | 0 | 68.6384
2024-06-22 14:00 | 43.7 | 28 | 6.91 | 893 | 26 | 30 | 22 | 0 | 65.9183
2024-06-22 15:00 | 41 | 37 | 6.88 | 662 | 26 | 30 | 22 | 0 | 45.3849
2024-06-22 16:00 | 40 | 38 | 6.89 | 559 | 26 | 30 | 22 | 0 | 19.5289
2024-06-22 17:00 | 38 | 47 | 4.87 | 435 | 26 | 30 | 22 | 0 | 22.181
2024-06-22 18:00 | 36.8 | 51 | 4.3 | 228 | 26 | 30 | 22 | 0 | 0
2024-06-22 19:00 | 35.4 | 58 | 2.62 | 63 | 26 | 30 | 22 | 0 | 0
2024-06-22 20:00 | 34.5 | 64 | 1.25 | 1 | 26 | 30 | 22 | 0 | 0
2024-06-22 21:00 | 33.6 | 68 | 0.92 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-22 22:00 | 32.9 | 71 | 0.67 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-22 23:00 | 33 | 67 | 0.3 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-23 | 32.5 | 68 | 0.58 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-23 01:00 | 30.5 | 75 | 1.53 | 0 | 26 | 30 | 22 | 0.2435 | 0
2024-06-23 02:00 | 30 | 76 | 2.1 | 0 | 26 | 30 | 22 | 2.5336 | 0
2024-06-23 03:00 | 29.2 | 78 | 1.68 | 0 | 26 | 30 | 22 | 7.0589 | 0
2024-06-23 04:00 | 28.9 | 75 | 1.43 | 0 | 26 | 30 | 22 | 12.1 | 0
2024-06-23 05:00 | 28.9 | 79 | 1.9 | 0 | 26 | 30 | 22 | 8.5154 | 0
2024-06-23 06:00 | 29.4 | 70 | 2.44 | 7 | 26 | 30 | 22 | 16.1539 | 0
2024-06-23 07:00 | 31.2 | 55 | 1.94 | 104 | 26 | 30 | 22 | 7.1193 | 0
2024-06-23 08:00 | 34.9 | 37 | 2.46 | 287 | 26 | 30 | 22 | 0 | 0
2024-06-23 09:00 | 38.1 | 30 | 2.3 | 493 | 26 | 30 | 22 | 0 | 6.5442
2024-06-23 10:00 | 41.4 | 22 | 1.71 | 682 | 26 | 30 | 22 | 0 | 47.368
2024-06-23 11:00 | 43.7 | 18 | 0.45 | 829 | 26 | 30 | 22 | 0 | 99.3011
2024-06-23 12:00 | 45.4 | 15 | 0.81 | 920 | 26 | 30 | 22 | 0 | 108.447
2024-06-23 13:00 | 46.6 | 14 | 2.58 | 945 | 26 | 30 | 22 | 0 | 74.1568
2024-06-23 14:00 | 47 | 15 | 4 | 902 | 26 | 30 | 22 | 0 | 53.4738
2024-06-23 15:00 | 46.6 | 16 | 4.96 | 757 | 26 | 30 | 22 | 0 | 23.6867
2024-06-23 16:00 | 45.7 | 16 | 5.78 | 592 | 26 | 30 | 22 | 0 | 0
2024-06-23 17:00 | 42.8 | 24 | 5 | 432 | 26 | 30 | 22 | 0 | 0
2024-06-23 18:00 | 40.3 | 33 | 4.23 | 226 | 26 | 30 | 22 | 0 | 0
2024-06-23 19:00 | 38 | 44 | 3.76 | 63 | 26 | 30 | 22 | 0 | 0
2024-06-23 20:00 | 36.1 | 55 | 2.33 | 1 | 26 | 30 | 22 | 0 | 0
2024-06-23 21:00 | 34.7 | 67 | 1.53 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-23 22:00 | 33.7 | 73 | 0.71 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-23 23:00 | 32.8 | 73 | 1.42 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-24 | 31.8 | 82 | 1.57 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-24 01:00 | 31.1 | 91 | 1.92 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-24 02:00 | 31.2 | 87 | 2.83 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-24 03:00 | 30.5 | 81 | 2.48 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-24 04:00 | 29.6 | 82 | 1.7 | 0 | 26 | 30 | 22 | 0.259 | 0
2024-06-24 05:00 | 29.9 | 65 | 1.52 | 0 | 26 | 30 | 22 | 15.7933 | 0
2024-06-24 06:00 | 30.5 | 56 | 1.58 | 5 | 26 | 30 | 22 | 21.5574 | 0
2024-06-24 07:00 | 32.6 | 44 | 1.58 | 96 | 26 | 30 | 22 | 10.5118 | 0
2024-06-24 08:00 | 35.9 | 30 | 1.63 | 232 | 26 | 30 | 22 | 0 | 0
2024-06-24 09:00 | 39.3 | 20 | 1.92 | 362 | 26 | 30 | 22 | 0 | 0
2024-06-24 10:00 | 42.7 | 13 | 1.84 | 606 | 26 | 30 | 22 | 0 | 19.559
2024-06-24 11:00 | 45.3 | 9 | 0.95 | 831 | 26 | 30 | 22 | 0 | 80.8839
2024-06-24 12:00 | 47.1 | 7 | 1.32 | 927 | 26 | 30 | 22 | 0 | 83.4871
2024-06-24 13:00 | 47.9 | 8 | 3.78 | 952 | 26 | 30 | 22 | 0 | 32.848
2024-06-24 14:00 | 45.9 | 14 | 6.29 | 906 | 26 | 30 | 22 | 0 | 6.6945
2024-06-24 15:00 | 43.2 | 20 | 6.58 | 793 | 26 | 30 | 22 | 0 | 0
2024-06-24 16:00 | 41.9 | 22 | 6.8 | 627 | 26 | 30 | 22 | 0 | 0
2024-06-24 17:00 | 40.7 | 26 | 5.64 | 431 | 26 | 30 | 22 | 0 | 0
2024-06-24 18:00 | 38.5 | 37 | 4.96 | 229 | 26 | 30 | 22 | 0 | 0
2024-06-24 19:00 | 36.2 | 53 | 4.16 | 64 | 26 | 30 | 22 | 0 | 0
2024-06-24 20:00 | 35 | 63 | 3.54 | 1 | 26 | 30 | 22 | 0 | 0
2024-06-24 21:00 | 34.3 | 67 | 2.7 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-24 22:00 | 33.7 | 69 | 2.83 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-24 23:00 | 32.8 | 72 | 1.93 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-25 | 31.8 | 76 | 1.39 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-25 01:00 | 32.6 | 72 | 0.6 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-25 02:00 | 32.2 | 72 | 0.45 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-25 03:00 | 30.7 | 75 | 1.35 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-25 04:00 | 29.7 | 75 | 2.06 | 0 | 26 | 30 | 22 | 6.636 | 0
2024-06-25 05:00 | 29.9 | 69 | 2.69 | 0 | 26 | 30 | 22 | 14.4503 | 0
2024-06-25 06:00 | 29.4 | 67 | 2.78 | 7 | 26 | 30 | 22 | 22.0245 | 0
2024-06-25 07:00 | 31.3 | 56 | 1.86 | 102 | 26 | 30 | 22 | 4.7658 | 0
2024-06-25 08:00 | 35.6 | 41 | 1.39 | 285 | 26 | 30 | 22 | 0 | 0
2024-06-25 09:00 | 38.6 | 28 | 0.8 | 491 | 26 | 30 | 22 | 0 | 39.7516
2024-06-25 10:00 | 41.1 | 20 | 0.73 | 681 | 26 | 30 | 22 | 0 | 68.5554
2024-06-25 11:00 | 43.2 | 15 | 2.24 | 829 | 26 | 30 | 22 | 0 | 47.6636
2024-06-25 12:00 | 43.6 | 15 | 5.05 | 921 | 26 | 30 | 22 | 0 | 9.1707
2024-06-25 13:00 | 42.7 | 17 | 6.17 | 945 | 26 | 30 | 22 | 0 | 0
2024-06-25 14:00 | 42.5 | 18 | 5.95 | 902 | 26 | 30 | 22 | 0 | 0
2024-06-25 15:00 | 41.8 | 21 | 6.3 | 795 | 26 | 30 | 22 | 0 | 0
2024-06-25 16:00 | 40.7 | 28 | 5.99 | 633 | 26 | 30 | 22 | 0 | 0
2024-06-25 17:00 | 39.7 | 27 | 5.16 | 435 | 26 | 30 | 22 | 0 | 0
2024-06-25 18:00 | 38.4 | 33 | 4.51 | 229 | 26 | 30 | 22 | 0 | 0
2024-06-25 19:00 | 36.6 | 44 | 3.5 | 64 | 26 | 30 | 22 | 0 | 0
2024-06-25 20:00 | 35.3 | 54 | 2.6 | 1 | 26 | 30 | 22 | 0 | 0
2024-06-25 21:00 | 34.5 | 59 | 1.94 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-25 22:00 | 33.6 | 64 | 2.52 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-25 23:00 | 32.7 | 69 | 2.83 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-26 | 32.3 | 67 | 3.45 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-26 01:00 | 31.7 | 68 | 3.74 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-26 02:00 | 31.1 | 75 | 3.64 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-26 03:00 | 30.6 | 80 | 3.4 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-26 04:00 | 30.3 | 81 | 3.67 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-26 05:00 | 29.6 | 86 | 2.93 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-26 06:00 | 29.4 | 84 | 3.21 | 7 | 26 | 30 | 22 | 0 | 0
2024-06-26 07:00 | 31.1 | 74 | 3.13 | 101 | 26 | 30 | 22 | 0 | 0
2024-06-26 08:00 | 33.8 | 61 | 3.4 | 281 | 26 | 30 | 22 | 0 | 0
2024-06-26 09:00 | 36.4 | 48 | 3.4 | 484 | 26 | 30 | 22 | 0 | 20.843
2024-06-26 10:00 | 38.6 | 40 | 2.95 | 672 | 26 | 30 | 22 | 0 | 51.4873
2024-06-26 11:00 | 41.1 | 32 | 2.77 | 819 | 26 | 30 | 22 | 0 | 73.4158
2024-06-26 12:00 | 42.9 | 26 | 4.69 | 913 | 26 | 30 | 22 | 0 | 61.7941
2024-06-26 13:00 | 42.5 | 26 | 5.82 | 943 | 26 | 30 | 22 | 0 | 50.386
2024-06-26 14:00 | 42.7 | 23 | 5.46 | 905 | 26 | 30 | 22 | 0 | 34.9017
2024-06-26 15:00 | 42.3 | 24 | 5.46 | 801 | 26 | 30 | 22 | 0 | 21.384
2024-06-26 16:00 | 41.9 | 24 | 4.47 | 641 | 26 | 30 | 22 | 0 | 6.9671
2024-06-26 17:00 | 40.1 | 32 | 5.24 | 442 | 26 | 30 | 22 | 0 | 0
2024-06-26 18:00 | 37 | 51 | 6.18 | 233 | 26 | 30 | 22 | 0 | 0
2024-06-26 19:00 | 35.6 | 56 | 4.35 | 65 | 26 | 30 | 22 | 0 | 0
2024-06-26 20:00 | 34.8 | 60 | 2.6 | 1 | 26 | 30 | 22 | 0 | 0
2024-06-26 21:00 | 34.1 | 62 | 1.64 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-26 22:00 | 33.2 | 62 | 2.06 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-26 23:00 | 32.3 | 61 | 2.6 | 0 | 26 | 30 | 22 | 4.2202 | 0
2024-06-27 | 31.4 | 61 | 2.77 | 0 | 26 | 30 | 22 | 13.374 | 0
2024-06-27 01:00 | 30.8 | 60 | 3.35 | 0 | 26 | 30 | 22 | 23.2906 | 0
2024-06-27 02:00 | 30.5 | 57 | 3.72 | 0 | 26 | 30 | 22 | 34.4289 | 0
2024-06-27 03:00 | 30.1 | 54 | 3.76 | 0 | 26 | 30 | 22 | 45.333 | 0
2024-06-27 04:00 | 29.5 | 53 | 3.91 | 0 | 26 | 30 | 22 | 54.9753 | 0
2024-06-27 05:00 | 29.5 | 53 | 3.6 | 0 | 26 | 30 | 22 | 52.3025 | 0
2024-06-27 06:00 | 29.6 | 48 | 4.12 | 7 | 26 | 30 | 22 | 65.4853 | 0
2024-06-27 07:00 | 31.9 | 36 | 3.83 | 104 | 26 | 30 | 22 | 53.8552 | 0
2024-06-27 08:00 | 34.8 | 29 | 2.12 | 288 | 26 | 30 | 22 | 0.4559 | 0
2024-06-27 09:00 | 36.9 | 25 | 2.8 | 496 | 26 | 30 | 22 | 0 | 0
2024-06-27 10:00 | 39 | 22 | 3.16 | 685 | 26 | 30 | 22 | 0 | 0.8778
2024-06-27 11:00 | 40.1 | 23 | 4.01 | 831 | 26 | 30 | 22 | 0 | 17.4342
2024-06-27 12:00 | 40.4 | 25 | 4.95 | 918 | 26 | 30 | 22 | 0 | 26.2689
2024-06-27 13:00 | 40.7 | 24 | 5 | 941 | 26 | 30 | 22 | 0 | 27.4768
2024-06-27 14:00 | 40.9 | 22 | 4.62 | 899 | 26 | 30 | 22 | 0 | 20.4871
2024-06-27 15:00 | 40.6 | 24 | 4.68 | 792 | 26 | 30 | 22 | 0 | 10.788
2024-06-27 16:00 | 39.7 | 27 | 5.02 | 632 | 26 | 30 | 22 | 0 | 0
2024-06-27 17:00 | 38.3 | 34 | 4.49 | 434 | 26 | 30 | 22 | 0 | 0
2024-06-27 18:00 | 37.1 | 41 | 3.74 | 229 | 26 | 30 | 22 | 0 | 0
2024-06-27 19:00 | 35.7 | 50 | 3.01 | 64 | 26 | 30 | 22 | 0 | 0
2024-06-27 20:00 | 34.5 | 61 | 2.37 | 1 | 26 | 30 | 22 | 0 | 0
2024-06-27 21:00 | 33.7 | 66 | 1.49 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-27 22:00 | 33 | 70 | 0.85 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-27 23:00 | 32.1 | 72 | 1.12 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-28 | 31.5 | 71 | 1.9 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-28 01:00 | 30.9 | 71 | 0.73 | 0 | 26 | 30 | 22 | 2.0819 | 0
2024-06-28 02:00 | 30.2 | 73 | 0.85 | 0 | 26 | 30 | 22 | 4.4908 | 0
2024-06-28 03:00 | 29.2 | 75 | 1.6 | 0 | 26 | 30 | 22 | 10.2861 | 0
2024-06-28 04:00 | 28.7 | 74 | 1.82 | 0 | 26 | 30 | 22 | 15.9165 | 0
2024-06-28 05:00 | 28.8 | 76 | 1.99 | 0 | 26 | 30 | 22 | 13.173 | 0
2024-06-28 06:00 | 28.5 | 73 | 2.25 | 6 | 26 | 30 | 22 | 19.6581 | 0
2024-06-28 07:00 | 30.4 | 59 | 2.16 | 101 | 26 | 30 | 22 | 9.494 | 0
2024-06-28 08:00 | 33.4 | 47 | 1.61 | 282 | 26 | 30 | 22 | 0 | 0
2024-06-28 09:00 | 35.9 | 40 | 0.95 | 489 | 26 | 30 | 22 | 0 | 36.3585
2024-06-28 10:00 | 36.9 | 41 | 4.12 | 675 | 26 | 30 | 22 | 0 | 24.3288
2024-06-28 11:00 | 38.2 | 37 | 3.8 | 818 | 26 | 30 | 22 | 0 | 48.899
2024-06-28 12:00 | 39.3 | 33 | 4.26 | 910 | 26 | 30 | 22 | 0 | 54.3543
2024-06-28 13:00 | 38.7 | 37 | 5.53 | 934 | 26 | 30 | 22 | 0 | 53.8686
2024-06-28 14:00 | 38.5 | 40 | 5.02 | 889 | 26 | 30 | 22 | 0 | 61.8747
2024-06-28 15:00 | 38.6 | 39 | 5.45 | 781 | 26 | 30 | 22 | 0 | 41.1891
2024-06-28 16:00 | 37.9 | 42 | 5.06 | 622 | 26 | 30 | 22 | 0 | 25.1376
2024-06-28 17:00 | 37.7 | 37 | 4.03 | 423 | 26 | 30 | 22 | 0 | 0
2024-06-28 18:00 | 36.8 | 42 | 3.86 | 211 | 26 | 30 | 22 | 0 | 0
2024-06-28 19:00 | 34.8 | 54 | 3.48 | 62 | 26 | 30 | 22 | 0 | 0
2024-06-28 20:00 | 33.6 | 65 | 2.83 | 1 | 26 | 30 | 22 | 0 | 0
2024-06-28 21:00 | 33.2 | 69 | 2.42 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-28 22:00 | 32.8 | 72 | 2.75 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-28 23:00 | 32.3 | 76 | 1.94 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-29 | 31.7 | 80 | 2.2 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-29 01:00 | 31.3 | 84 | 2.15 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-29 02:00 | 31 | 88 | 1.75 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-29 03:00 | 30.5 | 90 | 1.04 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-29 04:00 | 30.2 | 91 | 0.81 | 0 | 26 | 30 | 22 | 0.6639 | 0
2024-06-29 05:00 | 30.5 | 88 | 2.06 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-29 06:00 | 30.6 | 87 | 2.13 | 5 | 26 | 30 | 22 | 0 | 0
2024-06-29 07:00 | 31.6 | 80 | 1.84 | 94 | 26 | 30 | 22 | 0 | 0
2024-06-29 08:00 | 33.5 | 65 | 1.5 | 264 | 26 | 30 | 22 | 0 | 13.2137
2024-06-29 09:00 | 35.8 | 47 | 0.7 | 453 | 26 | 30 | 22 | 0 | 43.1461
2024-06-29 10:00 | 38.4 | 36 | 0.2 | 642 | 26 | 30 | 22 | 0 | 70.7411
2024-06-29 11:00 | 40.7 | 28 | 0.71 | 800 | 26 | 30 | 22 | 0 | 93.0702
2024-06-29 12:00 | 41.2 | 32 | 3.72 | 883 | 26 | 30 | 22 | 0 | 73.6062
2024-06-29 13:00 | 39.4 | 39 | 7.04 | 910 | 26 | 30 | 22 | 0 | 61.0564
2024-06-29 14:00 | 38.9 | 45 | 7.03 | 867 | 26 | 30 | 22 | 0 | 78.2019
2024-06-29 15:00 | 38.2 | 45 | 7.27 | 746 | 26 | 30 | 22 | 0 | 47.5918
2024-06-29 16:00 | 37.6 | 53 | 6.01 | 605 | 26 | 30 | 22 | 0 | 59.6423
2024-06-29 17:00 | 36 | 52 | 5.17 | 417 | 26 | 30 | 22 | 0 | 6.4425
2024-06-29 18:00 | 35 | 56 | 4.11 | 217 | 26 | 30 | 22 | 0 | 0
2024-06-29 19:00 | 33.9 | 61 | 3.02 | 62 | 26 | 30 | 22 | 0 | 0
2024-06-29 20:00 | 32.9 | 72 | 2.26 | 1 | 26 | 30 | 22 | 0 | 0
2024-06-29 21:00 | 32.5 | 75 | 1.75 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-29 22:00 | 32.2 | 76 | 1.56 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-29 23:00 | 31.5 | 77 | 1.7 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-30 | 30.7 | 79 | 2.08 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-30 01:00 | 30 | 82 | 1.89 | 0 | 26 | 30 | 22 | 0 | 0
2024-06-30 02:00 | 29.2 | 86 | 1.66 | 0 | 26 | 30 | 22 | 1.5338 | 0
2024-06-30 03:00 | 28.6 | 89 | 1.33 | 0 | 26 | 30 | 22 | 3.8197 | 0
2024-06-30 04:00 | 28.3 | 89 | 1.9 | 0 | 26 | 30 | 22 | 3.8732 | 0
2024-06-30 05:00 | 28.8 | 83 | 1.8 | 0 | 26 | 30 | 22 | 4.6632 | 0
2024-06-30 06:00 | 28.6 | 81 | 1.88 | 6 | 26 | 30 | 22 | 7.8962 | 0
2024-06-30 07:00 | 30.1 | 70 | 1.73 | 95 | 26 | 30 | 22 | 0 | 0
2024-06-30 08:00 | 32.5 | 57 | 1.4 | 270 | 26 | 30 | 22 | 0 | 0
2024-06-30 09:00 | 35 | 44 | 2 | 473 | 26 | 30 | 22 | 0 | 14.3559
2024-06-30 10:00 | 37.2 | 35 | 2.34 | 660 | 26 | 30 | 22 | 0 | 32.9477
2024-06-30 11:00 | 39.2 | 27 | 3.21 | 807 | 26 | 30 | 22 | 0 | 33.3531
2024-06-30 12:00 | 40.3 | 24 | 4.63 | 899 | 26 | 30 | 22 | 0 | 22.8284
2024-06-30 13:00 | 40.7 | 23 | 5.63 | 925 | 26 | 30 | 22 | 0 | 11.8763
2024-06-30 14:00 | 40 | 26 | 7.06 | 884 | 26 | 30 | 22 | 0 | 0
2024-06-30 15:00 | 39 | 30 | 7.12 | 779 | 26 | 30 | 22 | 0 | 0
2024-06-30 16:00 | 38.1 | 35 | 6.45 | 619 | 26 | 30 | 22 | 0 | 0
2024-06-30 17:00 | 37 | 36 | 4.96 | 423 | 26 | 30 | 22 | 0 | 0
2024-06-30 18:00 | 35.7 | 42 | 4.1 | 224 | 26 | 30 | 22 | 0 | 0
2024-06-30 19:00 | 34.7 | 48 | 3.42 | 63 | 26 | 30 | 22 | 0 | 0
2024-06-30 20:00 | 33.8 | 53 | 3.04 | 1 | 26 | 30 | 22 | 5.2555 | 0
2024-06-30 21:00 | 33 | 57 | 2.1 | 0 | 26 | 30 | 22 | 4.3087 | 0
2024-06-30 22:00 | 32.2 | 62 | 1.77 | 0 | 26 | 30 | 22 | 3.0584 | 0
2024-06-30 23:00 | 31.5 | 65 | 1.93 | 0 | 26 | 30 | 22 | 4.6822 | 0
2024-07-01 | 30.8 | 65 | 1.96 | 0 | 26 | 30 | 22 | 10.562 | 0
2024-07-01 01:00 | 30.4 | 64 | 2.57 | 0 | 26 | 30 | 22 | 17.3698 | 0
2024-07-01 02:00 | 29.9 | 63 | 3.01 | 0 | 26 | 30 | 22 | 25.7085 | 0
2024-07-01 03:00 | 29.5 | 66 | 2.86 | 0 | 26 | 30 | 22 | 23.9492 | 0
2024-07-01 04:00 | 29.1 | 68 | 2.83 | 0 | 26 | 30 | 22 | 24.5471 | 0
2024-07-01 05:00 | 29 | 65 | 2.8 | 0 | 26 | 30 | 22 | 30.1802 | 0
2024-07-01 06:00 | 29 | 61 | 2.91 | 6 | 26 | 30 | 22 | 36.5336 | 0
2024-07-01 07:00 | 30.6 | 50 | 2.8 | 94 | 26 | 30 | 22 | 27.839 | 0
2024-07-01 08:00 | 33.1 | 42 | 3.57 | 269 | 26 | 30 | 22 | 3.6616 | 0
2024-07-01 09:00 | 35.3 | 41 | 4.74 | 471 | 26 | 30 | 22 | 0 | 0
2024-07-01 10:00 | 37.6 | 31 | 4.92 | 658 | 26 | 30 | 22 | 0 | 0
2024-07-01 11:00 | 39.2 | 27 | 4.98 | 806 | 26 | 30 | 22 | 0 | 6.0211
2024-07-01 12:00 | 39.9 | 28 | 5.1 | 895 | 26 | 30 | 22 | 0 | 28.8585
2024-07-01 13:00 | 40 | 29 | 5.85 | 917 | 26 | 30 | 22 | 0 | 29.0705
2024-07-01 14:00 | 39.5 | 31 | 6.75 | 874 | 26 | 30 | 22 | 0 | 17.1409
2024-07-01 15:00 | 38.6 | 38 | 7.13 | 763 | 26 | 30 | 22 | 0 | 21.3806
2024-07-01 16:00 | 38.2 | 38 | 6.9 | 607 | 26 | 30 | 22 | 0 | 0
2024-07-01 17:00 | 37.3 | 36 | 6.41 | 421 | 26 | 30 | 22 | 0 | 0
2024-07-01 18:00 | 36.5 | 39 | 5.42 | 224 | 26 | 30 | 22 | 0 | 0
2024-07-01 19:00 | 35.1 | 50 | 4.66 | 63 | 26 | 30 | 22 | 0 | 0
2024-07-01 20:00 | 34.4 | 51 | 3.16 | 1 | 26 | 30 | 22 | 3.6014 | 0
2024-07-01 21:00 | 33.7 | 53 | 2.41 | 0 | 26 | 30 | 22 | 5.5861 | 0
2024-07-01 22:00 | 33 | 55 | 2.39 | 0 | 26 | 30 | 22 | 8.2035 | 0
2024-07-01 23:00 | 32.4 | 53 | 2.95 | 0 | 26 | 30 | 22 | 19.3077 | 0
2024-07-02 | 32 | 47 | 3.29 | 0 | 26 | 30 | 22 | 37.4201 | 0
2024-07-02 01:00 | 31.4 | 44 | 3.35 | 0 | 26 | 30 | 22 | 49.8263 | 0
2024-07-02 02:00 | 30.9 | 42 | 3.42 | 0 | 26 | 30 | 22 | 59.1778 | 0
2024-07-02 03:00 | 30.3 | 40 | 3.26 | 0 | 26 | 30 | 22 | 66.3762 | 0
2024-07-02 04:00 | 30 | 36 | 2.8 | 0 | 26 | 30 | 22 | 69.2615 | 0
2024-07-02 05:00 | 29.2 | 42 | 2.63 | 0 | 26 | 30 | 22 | 62.7539 | 0
2024-07-02 06:00 | 29 | 37 | 3.2 | 5 | 26 | 30 | 22 | 80.6425 | 0
2024-07-02 07:00 | 31.5 | 28 | 3.32 | 79 | 26 | 30 | 22 | 71.0515 | 0
2024-07-02 08:00 | 34.2 | 21 | 2.93 | 216 | 26 | 30 | 22 | 42.5882 | 0
2024-07-02 09:00 | 37.4 | 16 | 4.4 | 481 | 26 | 30 | 22 | 20.3359 | 0
2024-07-02 10:00 | 39.5 | 15 | 4.94 | 673 | 26 | 30 | 22 | 0 | 0
2024-07-02 11:00 | 41.3 | 14 | 4.68 | 824 | 26 | 30 | 22 | 0 | 0
2024-07-02 12:00 | 42.7 | 15 | 4.75 | 915 | 26 | 30 | 22 | 0 | 5.1781
2024-07-02 13:00 | 43.1 | 19 | 4.88 | 936 | 26 | 30 | 22 | 0 | 29.789
2024-07-02 14:00 | 42.3 | 27 | 5 | 885 | 26 | 30 | 22 | 0 | 52.8391
2024-07-02 15:00 | 41.4 | 33 | 5.35 | 772 | 26 | 30 | 22 | 0 | 52.8409
2024-07-02 16:00 | 41 | 28 | 5.83 | 613 | 26 | 30 | 22 | 0 | 0
2024-07-02 17:00 | 39.6 | 32 | 5.1 | 424 | 26 | 30 | 22 | 0 | 0
2024-07-02 18:00 | 38.4 | 39 | 3.47 | 224 | 26 | 30 | 22 | 0 | 0
2024-07-02 19:00 | 36.6 | 47 | 3.92 | 63 | 26 | 30 | 22 | 0 | 0
2024-07-02 20:00 | 34.6 | 59 | 2.56 | 1 | 26 | 30 | 22 | 0 | 0
2024-07-02 21:00 | 33.6 | 73 | 2.22 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-02 22:00 | 33.1 | 74 | 2.56 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-02 23:00 | 32.2 | 76 | 2.28 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-03 | 31.3 | 76 | 1.75 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-03 01:00 | 30.5 | 76 | 1.63 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-03 02:00 | 29.8 | 78 | 1.75 | 0 | 26 | 30 | 22 | 2.0937 | 0
2024-07-03 03:00 | 29.4 | 83 | 2.56 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-03 04:00 | 28.8 | 90 | 2.42 | 0 | 26 | 30 | 22 | 1.4627 | 0
2024-07-03 05:00 | 28.7 | 92 | 2.55 | 0 | 26 | 30 | 22 | 1.5964 | 0
2024-07-03 06:00 | 28.7 | 92 | 3.04 | 5 | 26 | 30 | 22 | 0.1395 | 0
2024-07-03 07:00 | 29.8 | 86 | 2.8 | 94 | 26 | 30 | 22 | 0 | 0
2024-07-03 08:00 | 31.9 | 75 | 3.75 | 270 | 26 | 30 | 22 | 0 | 0.4383
2024-07-03 09:00 | 35.1 | 53 | 3.92 | 472 | 26 | 30 | 22 | 0 | 13.1913
2024-07-03 10:00 | 38.5 | 34 | 3.83 | 661 | 26 | 30 | 22 | 0 | 20.5771
2024-07-03 11:00 | 40.8 | 27 | 3.67 | 809 | 26 | 30 | 22 | 0 | 41.2524
2024-07-03 12:00 | 42.5 | 23 | 3.14 | 900 | 26 | 30 | 22 | 0 | 61.7691
2024-07-03 13:00 | 43.8 | 20 | 2.42 | 926 | 26 | 30 | 22 | 0 | 76.5299
2024-07-03 14:00 | 43.2 | 28 | 3.45 | 883 | 26 | 30 | 22 | 0 | 81.451
2024-07-03 15:00 | 41.6 | 40 | 5.55 | 770 | 26 | 30 | 22 | 0 | 90.312
2024-07-03 16:00 | 40.2 | 40 | 6.93 | 607 | 26 | 30 | 22 | 0 | 40.5264
2024-07-03 17:00 | 38.7 | 47 | 6.75 | 420 | 26 | 30 | 22 | 0 | 25.1973
2024-07-03 18:00 | 36.6 | 55 | 7.82 | 222 | 26 | 30 | 22 | 0 | 0
2024-07-03 19:00 | 35.8 | 55 | 7.81 | 62 | 26 | 30 | 22 | 0 | 0
2024-07-03 20:00 | 35.1 | 60 | 6.41 | 1 | 26 | 30 | 22 | 0 | 0
2024-07-03 21:00 | 34.9 | 59 | 5.32 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-03 22:00 | 34.6 | 59 | 4.61 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-03 23:00 | 34.1 | 60 | 3.9 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-04 | 33.7 | 60 | 3.81 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-04 01:00 | 33.2 | 61 | 3.92 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-04 02:00 | 32.7 | 63 | 3.91 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-04 03:00 | 32.2 | 63 | 3.97 | 0 | 26 | 30 | 22 | 0.864 | 0
2024-07-04 04:00 | 32.1 | 62 | 3.94 | 0 | 26 | 30 | 22 | 4.5949 | 0
2024-07-04 05:00 | 31.7 | 60 | 3.68 | 0 | 26 | 30 | 22 | 13.9727 | 0
2024-07-04 06:00 | 31.3 | 61 | 4.79 | 5 | 26 | 30 | 22 | 17.919 | 0
2024-07-04 07:00 | 32.5 | 59 | 4.61 | 91 | 26 | 30 | 22 | 0 | 0
2024-07-04 08:00 | 35.2 | 50 | 5.69 | 263 | 26 | 30 | 22 | 0 | 0
2024-07-04 09:00 | 37.7 | 43 | 7.41 | 463 | 26 | 30 | 22 | 0 | 0
2024-07-04 10:00 | 38.6 | 40 | 8.37 | 646 | 26 | 30 | 22 | 0 | 8.6778
2024-07-04 11:00 | 38.9 | 41 | 8.41 | 794 | 26 | 30 | 22 | 0 | 40.3893
2024-07-04 12:00 | 39.4 | 38 | 8.32 | 886 | 26 | 30 | 22 | 0 | 45.1076
2024-07-04 13:00 | 39.5 | 39 | 8.37 | 916 | 26 | 30 | 22 | 0 | 57.0083
2024-07-04 14:00 | 39.5 | 38 | 8.55 | 876 | 26 | 30 | 22 | 0 | 44.5147
2024-07-04 15:00 | 38.9 | 40 | 8.63 | 772 | 26 | 30 | 22 | 0 | 30.3023
2024-07-04 16:00 | 38.2 | 43 | 8.44 | 614 | 26 | 30 | 22 | 0 | 13.3826
2024-07-04 17:00 | 37.2 | 44 | 8.96 | 419 | 26 | 30 | 22 | 0 | 0
2024-07-04 18:00 | 36.3 | 47 | 8.96 | 220 | 26 | 30 | 22 | 0 | 0
2024-07-04 19:00 | 35.4 | 49 | 8.02 | 62 | 26 | 30 | 22 | 0 | 0
2024-07-04 20:00 | 34.9 | 52 | 6.52 | 1 | 26 | 30 | 22 | 0 | 0
2024-07-04 21:00 | 34.4 | 54 | 5.4 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-04 22:00 | 34 | 55 | 4.83 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-04 23:00 | 33.4 | 56 | 4.03 | 0 | 26 | 30 | 22 | 3.113 | 0
2024-07-05 | 32.6 | 58 | 3.4 | 0 | 26 | 30 | 22 | 7.6468 | 0
2024-07-05 01:00 | 31.8 | 58 | 3.4 | 0 | 26 | 30 | 22 | 16.6234 | 0
2024-07-05 02:00 | 31.2 | 57 | 4.03 | 0 | 26 | 30 | 22 | 27.7637 | 0
2024-07-05 03:00 | 30.7 | 56 | 4.4 | 0 | 26 | 30 | 22 | 37.8138 | 0
2024-07-05 04:00 | 30.3 | 58 | 4.52 | 0 | 26 | 30 | 22 | 38.586 | 0
2024-07-05 05:00 | 30.2 | 53 | 4.65 | 0 | 26 | 30 | 22 | 52.65 | 0
2024-07-05 06:00 | 30.1 | 52 | 4.6 | 5 | 26 | 30 | 22 | 55.2376 | 0
2024-07-05 07:00 | 31.2 | 45 | 4.1 | 88 | 26 | 30 | 22 | 44.427 | 0
2024-07-05 08:00 | 33.6 | 38 | 5.12 | 246 | 26 | 30 | 22 | 23.3761 | 0
2024-07-05 09:00 | 35.9 | 38 | 5.63 | 447 | 26 | 30 | 22 | 0 | 0
2024-07-05 10:00 | 37.7 | 36 | 5.45 | 638 | 26 | 30 | 22 | 0 | 0
2024-07-05 11:00 | 39.4 | 31 | 5.16 | 792 | 26 | 30 | 22 | 0 | 21.3755
2024-07-05 12:00 | 40.2 | 30 | 5.39 | 888 | 26 | 30 | 22 | 0 | 37.4749
2024-07-05 13:00 | 40.1 | 34 | 5.72 | 914 | 26 | 30 | 22 | 0 | 55.7509
2024-07-05 14:00 | 39.7 | 37 | 5.8 | 873 | 26 | 30 | 22 | 0 | 58.2485
2024-07-05 15:00 | 39.1 | 42 | 5.81 | 767 | 26 | 30 | 22 | 0 | 58.1947
2024-07-05 16:00 | 38.3 | 47 | 5.82 | 607 | 26 | 30 | 22 | 0 | 46.1604
2024-07-05 17:00 | 37.4 | 47 | 5.5 | 413 | 26 | 30 | 22 | 0 | 6.6894
2024-07-05 18:00 | 36.2 | 51 | 5.57 | 214 | 26 | 30 | 22 | 0 | 0
2024-07-05 19:00 | 34.7 | 59 | 5.68 | 61 | 26 | 30 | 22 | 0 | 0
2024-07-05 20:00 | 33.9 | 66 | 5.69 | 1 | 26 | 30 | 22 | 0 | 0
2024-07-05 21:00 | 33.5 | 67 | 5.22 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-05 22:00 | 33 | 70 | 4.47 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-05 23:00 | 32.6 | 71 | 3.89 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-06 | 32.1 | 72 | 3.62 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-06 01:00 | 31.5 | 74 | 3.32 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-06 02:00 | 31 | 73 | 3.4 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-06 03:00 | 30.7 | 73 | 3.73 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-06 04:00 | 30.3 | 72 | 3.92 | 0 | 26 | 30 | 22 | 5.223 | 0
2024-07-06 05:00 | 30.2 | 73 | 3.31 | 0 | 26 | 30 | 22 | 4.6269 | 0
2024-07-06 06:00 | 30 | 73 | 3.7 | 5 | 26 | 30 | 22 | 6.3716 | 0
2024-07-06 07:00 | 30.9 | 68 | 3.8 | 89 | 26 | 30 | 22 | 0 | 0
2024-07-06 08:00 | 32.7 | 60 | 4.71 | 260 | 26 | 30 | 22 | 0 | 0
2024-07-06 09:00 | 34.3 | 54 | 4.52 | 458 | 26 | 30 | 22 | 0 | 0
2024-07-06 10:00 | 36.1 | 47 | 3.92 | 643 | 26 | 30 | 22 | 0 | 31.1887
2024-07-06 11:00 | 37.9 | 40 | 3.62 | 793 | 26 | 30 | 22 | 0 | 53.7914
2024-07-06 12:00 | 39.5 | 35 | 3.8 | 883 | 26 | 30 | 22 | 0 | 65.1945
2024-07-06 13:00 | 40.5 | 32 | 4.43 | 909 | 26 | 30 | 22 | 0 | 62.4806
2024-07-06 14:00 | 40.3 | 32 | 5.24 | 865 | 26 | 30 | 22 | 0 | 46.4658
2024-07-06 15:00 | 39.5 | 32 | 5.79 | 759 | 26 | 30 | 22 | 0 | 16.1213
2024-07-06 16:00 | 38.9 | 34 | 5.1 | 606 | 26 | 30 | 22 | 0 | 3.4344
2024-07-06 17:00 | 38.7 | 33 | 4.08 | 422 | 26 | 30 | 22 | 0 | 0
2024-07-06 18:00 | 37.7 | 36 | 3.81 | 222 | 26 | 30 | 22 | 0 | 0
2024-07-06 19:00 | 36.7 | 37 | 3.11 | 62 | 26 | 30 | 22 | 7.174 | 0
2024-07-06 20:00 | 35.7 | 41 | 1.32 | 1 | 26 | 30 | 22 | 6.2562 | 0
2024-07-06 21:00 | 34.6 | 47 | 0.81 | 0 | 26 | 30 | 22 | 2.4615 | 0
2024-07-06 22:00 | 33.7 | 47 | 2.16 | 0 | 26 | 30 | 22 | 15.5666 | 0
2024-07-06 23:00 | 32.4 | 56 | 1.3 | 0 | 26 | 30 | 22 | 8.0822 | 0
2024-07-07 | 32.2 | 61 | 0.81 | 0 | 26 | 30 | 22 | 2.7737 | 0
2024-07-07 01:00 | 30.5 | 66 | 1.5 | 0 | 26 | 30 | 22 | 10.3736 | 0
2024-07-07 02:00 | 30.1 | 64 | 1.94 | 0 | 26 | 30 | 22 | 17.517 | 0
2024-07-07 03:00 | 29.4 | 64 | 2.18 | 0 | 26 | 30 | 22 | 24.4737 | 0
2024-07-07 04:00 | 29 | 64 | 2.38 | 0 | 26 | 30 | 22 | 29.1105 | 0
2024-07-07 05:00 | 29.7 | 59 | 2.02 | 0 | 26 | 30 | 22 | 27.7053 | 0
2024-07-07 06:00 | 29.8 | 56 | 2.41 | 4 | 26 | 30 | 22 | 33.7032 | 0
2024-07-07 07:00 | 31.2 | 47 | 1.84 | 89 | 26 | 30 | 22 | 19.249 | 0
2024-07-07 08:00 | 34.7 | 35 | 1.52 | 262 | 26 | 30 | 22 | 0 | 0
2024-07-07 09:00 | 37.9 | 26 | 1.71 | 465 | 26 | 30 | 22 | 0 | 5.8581
2024-07-07 10:00 | 40.7 | 17 | 1.84 | 654 | 26 | 30 | 22 | 0 | 25.1854
2024-07-07 11:00 | 43.1 | 10 | 3 | 805 | 26 | 30 | 22 | 0 | 8.8325
2024-07-07 12:00 | 44.3 | 9 | 4.24 | 900 | 26 | 30 | 22 | 0 | 0
2024-07-07 13:00 | 44.1 | 12 | 5.07 | 928 | 26 | 30 | 22 | 0 | 0
2024-07-07 14:00 | 43 | 14 | 6.07 | 885 | 26 | 30 | 22 | 0 | 0
2024-07-07 15:00 | 40.7 | 26 | 6.08 | 779 | 26 | 30 | 22 | 0 | 1.8432
2024-07-07 16:00 | 40 | 30 | 6.03 | 617 | 26 | 30 | 22 | 0 | 0
2024-07-07 17:00 | 39.7 | 23 | 5.31 | 423 | 26 | 30 | 22 | 0 | 0
2024-07-07 18:00 | 38 | 32 | 4.17 | 223 | 26 | 30 | 22 | 0 | 0
2024-07-07 19:00 | 36.2 | 45 | 2.78 | 62 | 26 | 30 | 22 | 0 | 0
2024-07-07 20:00 | 34.8 | 57 | 2.02 | 1 | 26 | 30 | 22 | 0 | 0
2024-07-07 21:00 | 34.1 | 60 | 0.22 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-07 22:00 | 33.2 | 57 | 1.5 | 0 | 26 | 30 | 22 | 2.009 | 0
2024-07-07 23:00 | 32.8 | 53 | 2.16 | 0 | 26 | 30 | 22 | 12.6965 | 0
2024-07-08 | 31.8 | 51 | 1.84 | 0 | 26 | 30 | 22 | 21.6357 | 0
2024-07-08 01:00 | 32.4 | 44 | 1.08 | 0 | 26 | 30 | 22 | 19.0112 | 0
2024-07-08 02:00 | 32.8 | 40 | 0.32 | 0 | 26 | 30 | 22 | 14.5363 | 0
2024-07-08 03:00 | 32.2 | 40 | 0.58 | 0 | 26 | 30 | 22 | 15.8179 | 0
2024-07-08 04:00 | 29.8 | 40 | 2.33 | 0 | 26 | 30 | 22 | 57.0119 | 0
2024-07-08 05:00 | 30.3 | 46 | 2.22 | 0 | 26 | 30 | 22 | 43.2534 | 0
2024-07-08 06:00 | 30.4 | 56 | 2.56 | 4 | 26 | 30 | 22 | 29.7497 | 0
2024-07-08 07:00 | 31.7 | 56 | 2.21 | 88 | 26 | 30 | 22 | 5.3132 | 0
2024-07-08 08:00 | 34.2 | 42 | 1.9 | 260 | 26 | 30 | 22 | 0 | 0
2024-07-08 09:00 | 37.7 | 28 | 1.61 | 463 | 26 | 30 | 22 | 0 | 10.4713
2024-07-08 10:00 | 41 | 18 | 1.21 | 654 | 26 | 30 | 22 | 0 | 46.4696
2024-07-08 11:00 | 43.4 | 14 | 1.4 | 804 | 26 | 30 | 22 | 0 | 64.5444
2024-07-08 12:00 | 44 | 19 | 3.74 | 897 | 26 | 30 | 22 | 0 | 49.4833
2024-07-08 13:00 | 43 | 23 | 5.8 | 904 | 26 | 30 | 22 | 0 | 34.8004
2024-07-08 14:00 | 42.7 | 20 | 6.36 | 876 | 26 | 30 | 22 | 0 | 3.3086
2024-07-08 15:00 | 41.8 | 24 | 6.49 | 773 | 26 | 30 | 22 | 0 | 0
2024-07-08 16:00 | 40.2 | 31 | 6.17 | 612 | 26 | 30 | 22 | 0 | 0
2024-07-08 17:00 | 39.4 | 34 | 5.04 | 423 | 26 | 30 | 22 | 0 | 0
2024-07-08 18:00 | 38.4 | 35 | 4.71 | 221 | 26 | 30 | 22 | 0 | 0
2024-07-08 19:00 | 36.2 | 49 | 3.35 | 61 | 26 | 30 | 22 | 0 | 0
2024-07-08 20:00 | 35.1 | 62 | 2.82 | 1 | 26 | 30 | 22 | 0 | 0
2024-07-08 21:00 | 34.7 | 64 | 2.53 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-08 22:00 | 34.2 | 66 | 1.14 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-08 23:00 | 33.3 | 73 | 1.27 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-09 | 32.7 | 80 | 1.9 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-09 01:00 | 32.4 | 81 | 2.97 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-09 02:00 | 32.1 | 76 | 3.55 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-09 03:00 | 31.9 | 69 | 4.38 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-09 04:00 | 31.9 | 67 | 4.7 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-09 05:00 | 32.2 | 65 | 4.11 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-09 06:00 | 32.2 | 62 | 4.5 | 4 | 26 | 30 | 22 | 2.5833 | 0
2024-07-09 07:00 | 33.3 | 55 | 5.4 | 86 | 26 | 30 | 22 | 0 | 0
2024-07-09 08:00 | 35.7 | 50 | 7.82 | 257 | 26 | 30 | 22 | 0 | 0
2024-07-09 09:00 | 38 | 47 | 7.52 | 457 | 26 | 30 | 22 | 0 | 14.1427
2024-07-09 10:00 | 41.3 | 33 | 7.59 | 644 | 26 | 30 | 22 | 0 | 20.7044
2024-07-09 11:00 | 44 | 23 | 6.36 | 792 | 26 | 30 | 22 | 0 | 27.562
2024-07-09 12:00 | 45.8 | 19 | 4.59 | 883 | 26 | 30 | 22 | 0 | 54.2349
2024-07-09 13:00 | 47 | 16 | 4.3 | 909 | 26 | 30 | 22 | 0 | 56.1058
2024-07-09 14:00 | 47.6 | 16 | 5.2 | 866 | 26 | 30 | 22 | 0 | 46.3577
2024-07-09 15:00 | 47.8 | 17 | 5.82 | 759 | 26 | 30 | 22 | 0 | 35.4951
2024-07-09 16:00 | 47.1 | 19 | 6.41 | 601 | 26 | 30 | 22 | 0 | 15.6017
2024-07-09 17:00 | 44.6 | 27 | 6.48 | 337 | 26 | 30 | 22 | 0 | 0.4507
2024-07-09 18:00 | 43.2 | 30 | 5.87 | 178 | 26 | 30 | 22 | 0 | 0
2024-07-09 19:00 | 41.6 | 32 | 5.2 | 58 | 26 | 30 | 22 | 0 | 0
2024-07-09 20:00 | 40.3 | 33 | 4.21 | 1 | 26 | 30 | 22 | 0 | 0
2024-07-09 21:00 | 38.7 | 37 | 4.4 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-09 22:00 | 36.7 | 45 | 4.01 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-09 23:00 | 35.7 | 50 | 4.02 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-10 | 34.9 | 54 | 3.61 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-10 01:00 | 34.4 | 56 | 2.45 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-10 02:00 | 33.9 | 54 | 3.89 | 0 | 26 | 30 | 22 | 2.1472 | 0
2024-07-10 03:00 | 33.5 | 52 | 3.77 | 0 | 26 | 30 | 22 | 12.0282 | 0
2024-07-10 04:00 | 32.5 | 60 | 4.9 | 0 | 26 | 30 | 22 | 4.2216 | 0
2024-07-10 05:00 | 32.9 | 53 | 2.81 | 0 | 26 | 30 | 22 | 13.9714 | 0
2024-07-10 06:00 | 33.6 | 40 | 3.26 | 4 | 26 | 30 | 22 | 37.0865 | 0
2024-07-10 07:00 | 35 | 35 | 3.05 | 84 | 26 | 30 | 22 | 23.9615 | 0
2024-07-10 08:00 | 36.6 | 35 | 3.64 | 250 | 26 | 30 | 22 | 0 | 0
2024-07-10 09:00 | 38.4 | 32 | 3.4 | 446 | 26 | 30 | 22 | 0 | 0
2024-07-10 10:00 | 40.5 | 28 | 2.66 | 632 | 26 | 30 | 22 | 0 | 32.4392
2024-07-10 11:00 | 42.8 | 23 | 2.82 | 782 | 26 | 30 | 22 | 0 | 53.095
2024-07-10 12:00 | 44.5 | 18 | 1.93 | 874 | 26 | 30 | 22 | 0 | 77.0846
2024-07-10 13:00 | 44.9 | 19 | 2.83 | 902 | 26 | 30 | 22 | 0 | 71.2458
2024-07-10 14:00 | 44.5 | 22 | 5.16 | 858 | 26 | 30 | 22 | 0 | 47.5584
2024-07-10 15:00 | 43.6 | 24 | 6.44 | 753 | 26 | 30 | 22 | 0 | 22.4782
2024-07-10 16:00 | 42.7 | 27 | 6.45 | 596 | 26 | 30 | 22 | 0 | 6.9483
2024-07-10 17:00 | 39.6 | 37 | 7.14 | 406 | 26 | 30 | 22 | 0 | 0
2024-07-10 18:00 | 39.2 | 34 | 5.3 | 211 | 26 | 30 | 22 | 0 | 0
2024-07-10 19:00 | 38.6 | 35 | 3.86 | 59 | 26 | 30 | 22 | 0 | 0
2024-07-10 20:00 | 38.7 | 34 | 3.12 | 1 | 26 | 30 | 22 | 5.0799 | 0
2024-07-10 21:00 | 38.6 | 35 | 3.14 | 0 | 26 | 30 | 22 | 3.2599 | 0
2024-07-10 22:00 | 38.2 | 42 | 3.24 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-10 23:00 | 37.1 | 51 | 2.81 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-11 | 36.4 | 53 | 2.28 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-11 01:00 | 35.7 | 55 | 1.84 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-11 02:00 | 35 | 58 | 1.64 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-11 03:00 | 34.4 | 61 | 2.06 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-11 04:00 | 33.8 | 64 | 3.04 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-11 05:00 | 34 | 61 | 2.41 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-11 06:00 | 34.3 | 59 | 2.19 | 4 | 26 | 30 | 22 | 0 | 0
2024-07-11 07:00 | 36.8 | 37 | 5 | 80 | 26 | 30 | 22 | 9.6755 | 0
2024-07-11 08:00 | 37.3 | 43 | 6.11 | 243 | 26 | 30 | 22 | 0 | 0
2024-07-11 09:00 | 38.9 | 38 | 6.84 | 430 | 26 | 30 | 22 | 0 | 0
2024-07-11 10:00 | 40.6 | 33 | 6.77 | 599 | 26 | 30 | 22 | 0 | 7.8422
2024-07-11 11:00 | 42.2 | 29 | 5.77 | 765 | 26 | 30 | 22 | 0 | 39.2795
2024-07-11 12:00 | 43.6 | 26 | 5.06 | 861 | 26 | 30 | 22 | 0 | 60.022
2024-07-11 13:00 | 44.6 | 24 | 4.53 | 890 | 26 | 30 | 22 | 0 | 69.6917
2024-07-11 14:00 | 43.6 | 30 | 6.08 | 851 | 26 | 30 | 22 | 0 | 75.4033
2024-07-11 15:00 | 42.2 | 32 | 7.82 | 745 | 26 | 30 | 22 | 0 | 42.8639
2024-07-11 16:00 | 41.1 | 36 | 6.8 | 591 | 26 | 30 | 22 | 0 | 32.0706
2024-07-11 17:00 | 39.6 | 40 | 5.69 | 404 | 26 | 30 | 22 | 0 | 8.3591
2024-07-11 18:00 | 37.8 | 45 | 5.3 | 211 | 26 | 30 | 22 | 0 | 0
2024-07-11 19:00 | 36.4 | 55 | 4.08 | 59 | 26 | 30 | 22 | 0 | 0
2024-07-11 20:00 | 35.7 | 63 | 2.8 | 1 | 26 | 30 | 22 | 0 | 0
2024-07-11 21:00 | 35 | 66 | 2.24 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-11 22:00 | 34.5 | 71 | 0.54 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-11 23:00 | 34.2 | 73 | 0.36 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-12 | 33.8 | 73 | 0.2 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-12 01:00 | 32.9 | 78 | 0.9 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-12 02:00 | 32.5 | 80 | 1.49 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-12 03:00 | 32.1 | 79 | 1.49 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-12 04:00 | 31.7 | 77 | 1.33 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-12 05:00 | 33 | 64 | 2.35 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-12 06:00 | 33.2 | 57 | 2.69 | 3 | 26 | 30 | 22 | 2.5149 | 0
2024-07-12 07:00 | 34.8 | 47 | 3.81 | 81 | 26 | 30 | 22 | 0 | 0
2024-07-12 08:00 | 36.1 | 43 | 7.76 | 245 | 26 | 30 | 22 | 0 | 0
2024-07-12 09:00 | 37.8 | 39 | 8.45 | 441 | 26 | 30 | 22 | 0 | 0
2024-07-12 10:00 | 39.7 | 35 | 7.91 | 631 | 26 | 30 | 22 | 0 | 0.6713
2024-07-12 11:00 | 41.4 | 31 | 7.32 | 775 | 26 | 30 | 22 | 0 | 29.1923
2024-07-12 12:00 | 43 | 28 | 6.79 | 869 | 26 | 30 | 22 | 0 | 52.2367
2024-07-12 13:00 | 44 | 25 | 6.23 | 897 | 26 | 30 | 22 | 0 | 55.5362
2024-07-12 14:00 | 42.2 | 37 | 6.89 | 856 | 26 | 30 | 22 | 0 | 93.172
2024-07-12 15:00 | 41 | 34 | 8.03 | 750 | 26 | 30 | 22 | 0 | 33.6556
2024-07-12 16:00 | 39.9 | 39 | 7.5 | 600 | 26 | 30 | 22 | 0 | 26.0589
2024-07-12 17:00 | 39.1 | 38 | 5.54 | 409 | 26 | 30 | 22 | 0 | 0
2024-07-12 18:00 | 37.2 | 48 | 5 | 214 | 26 | 30 | 22 | 0 | 0
2024-07-12 19:00 | 35.7 | 61 | 4.01 | 60 | 26 | 30 | 22 | 0 | 0
2024-07-12 20:00 | 34.8 | 66 | 3 | 1 | 26 | 30 | 22 | 0 | 0
2024-07-12 21:00 | 34.2 | 69 | 2.21 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-12 22:00 | 33.7 | 72 | 1.75 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-12 23:00 | 33 | 74 | 1.92 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-13 | 32.2 | 76 | 2.33 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-13 01:00 | 31.6 | 76 | 2.6 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-13 02:00 | 30.9 | 75 | 3.1 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-13 03:00 | 30.3 | 77 | 3.21 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-13 04:00 | 30 | 73 | 3.51 | 0 | 26 | 30 | 22 | 7.0351 | 0
2024-07-13 05:00 | 30 | 73 | 3.07 | 0 | 26 | 30 | 22 | 6.9783 | 0
2024-07-13 06:00 | 29.7 | 70 | 2.73 | 3 | 26 | 30 | 22 | 14.5274 | 0
2024-07-13 07:00 | 31 | 63 | 2.66 | 84 | 26 | 30 | 22 | 2.1845 | 0
2024-07-13 08:00 | 33.8 | 51 | 3.22 | 253 | 26 | 30 | 22 | 0 | 0
2024-07-13 09:00 | 37.3 | 36 | 3.98 | 455 | 26 | 30 | 22 | 0 | 0
2024-07-13 10:00 | 40.2 | 26 | 3.54 | 646 | 26 | 30 | 22 | 0 | 11.8685
2024-07-13 11:00 | 42.2 | 21 | 4.05 | 797 | 26 | 30 | 22 | 0 | 23.6747
2024-07-13 12:00 | 43.7 | 17 | 4.79 | 891 | 26 | 30 | 22 | 0 | 20.6955
2024-07-13 13:00 | 44.5 | 16 | 5.62 | 922 | 26 | 30 | 22 | 0 | 15.5491
2024-07-13 14:00 | 43.7 | 18 | 6.91 | 884 | 26 | 30 | 22 | 0 | 0
2024-07-13 15:00 | 43.1 | 17 | 6.21 | 780 | 26 | 30 | 22 | 0 | 0
2024-07-13 16:00 | 41.9 | 22 | 5.47 | 618 | 26 | 30 | 22 | 0 | 0
2024-07-13 17:00 | 41.6 | 20 | 3.92 | 423 | 26 | 30 | 22 | 0 | 0
2024-07-13 18:00 | 40.2 | 26 | 3.45 | 221 | 26 | 30 | 22 | 0 | 0
2024-07-13 19:00 | 38.1 | 35 | 2.64 | 61 | 26 | 30 | 22 | 0 | 0
2024-07-13 20:00 | 36.3 | 47 | 2.06 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-13 21:00 | 35.1 | 54 | 1.4 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-13 22:00 | 34 | 56 | 1.52 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-13 23:00 | 33.1 | 57 | 1.44 | 0 | 26 | 30 | 22 | 2.6269 | 0
2024-07-14 | 32.4 | 57 | 1.3 | 0 | 26 | 30 | 22 | 6.9534 | 0
2024-07-14 01:00 | 31.7 | 58 | 2.12 | 0 | 26 | 30 | 22 | 13.7235 | 0
2024-07-14 02:00 | 31.2 | 59 | 2.7 | 0 | 26 | 30 | 22 | 18.6774 | 0
2024-07-14 03:00 | 30.3 | 57 | 2.62 | 0 | 26 | 30 | 22 | 29.9463 | 0
2024-07-14 04:00 | 29.8 | 52 | 2.73 | 0 | 26 | 30 | 22 | 43.3695 | 0
2024-07-14 05:00 | 29.9 | 49 | 2.01 | 0 | 26 | 30 | 22 | 39.3784 | 0
2024-07-14 06:00 | 29.7 | 45 | 2.5 | 3 | 26 | 30 | 22 | 52.2463 | 0
2024-07-14 07:00 | 31.1 | 35 | 1.91 | 83 | 26 | 30 | 22 | 37.961 | 0
2024-07-14 08:00 | 33.9 | 32 | 1.49 | 254 | 26 | 30 | 22 | 0 | 0
2024-07-14 09:00 | 35.4 | 41 | 0.7 | 456 | 26 | 30 | 22 | 0 | 36.4256
2024-07-14 10:00 | 37.5 | 37 | 1.06 | 645 | 26 | 30 | 22 | 0 | 59.8766
2024-07-14 11:00 | 40.4 | 25 | 2.5 | 793 | 26 | 30 | 22 | 0 | 47.5439
2024-07-14 12:00 | 42.8 | 20 | 3.11 | 890 | 26 | 30 | 22 | 0 | 52.4094
2024-07-14 13:00 | 43.8 | 19 | 3.08 | 920 | 26 | 30 | 22 | 0 | 61.1229
2024-07-14 14:00 | 41.5 | 39 | 4.72 | 879 | 26 | 30 | 22 | 0 | 100.3824
2024-07-14 15:00 | 40.1 | 43 | 5.73 | 764 | 26 | 30 | 22 | 0 | 79.313
2024-07-14 16:00 | 39.6 | 45 | 4.6 | 606 | 26 | 30 | 22 | 0 | 62.0576
2024-07-14 17:00 | 39.4 | 40 | 4.56 | 418 | 26 | 30 | 22 | 0 | 13.8567
2024-07-14 18:00 | 38 | 42 | 4.38 | 218 | 26 | 30 | 22 | 0 | 0
2024-07-14 19:00 | 36.6 | 48 | 3 | 60 | 26 | 30 | 22 | 0 | 0
2024-07-14 20:00 | 35.3 | 57 | 2.84 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-14 21:00 | 34.6 | 63 | 2.12 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-14 22:00 | 34 | 68 | 2 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-14 23:00 | 33.2 | 74 | 2.28 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-15 | 32.5 | 79 | 1.75 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-15 01:00 | 32 | 82 | 1.6 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-15 02:00 | 31.5 | 85 | 1.9 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-15 03:00 | 30.9 | 89 | 1.98 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-15 04:00 | 30.4 | 92 | 2.44 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-15 05:00 | 30.5 | 94 | 1.96 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-15 06:00 | 30.1 | 96 | 1.75 | 3 | 26 | 30 | 22 | 0 | 0
2024-07-15 07:00 | 30.9 | 89 | 2.38 | 79 | 26 | 30 | 22 | 0 | 0
2024-07-15 08:00 | 32.6 | 76 | 2.4 | 244 | 26 | 30 | 22 | 0 | 13.8432
2024-07-15 09:00 | 34.8 | 61 | 2.06 | 445 | 26 | 30 | 22 | 0 | 38.4278
2024-07-15 10:00 | 37 | 48 | 0.94 | 633 | 26 | 30 | 22 | 0 | 71.0143
2024-07-15 11:00 | 39.2 | 39 | 0.89 | 781 | 26 | 30 | 22 | 0 | 93.0025
2024-07-15 12:00 | 40.9 | 34 | 1.2 | 874 | 26 | 30 | 22 | 0 | 103.2663
2024-07-15 13:00 | 41.7 | 34 | 2.44 | 901 | 26 | 30 | 22 | 0 | 99.1262
2024-07-15 14:00 | 41.3 | 42 | 4.07 | 860 | 26 | 30 | 22 | 0 | 109.426
2024-07-15 15:00 | 40.3 | 44 | 5.79 | 755 | 26 | 30 | 22 | 0 | 86.3021
2024-07-15 16:00 | 38.9 | 48 | 6 | 597 | 26 | 30 | 22 | 0 | 59.3664
2024-07-15 17:00 | 37.4 | 51 | 5.63 | 400 | 26 | 30 | 22 | 0 | 20.8719
2024-07-15 18:00 | 36.8 | 56 | 4.19 | 205 | 26 | 30 | 22 | 0 | 8.104
2024-07-15 19:00 | 35.5 | 66 | 3.31 | 56 | 26 | 30 | 22 | 0 | 0.4779
2024-07-15 20:00 | 35.1 | 67 | 2.91 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-15 21:00 | 34.7 | 68 | 2.24 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-15 22:00 | 34.2 | 72 | 1.84 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-15 23:00 | 33.8 | 76 | 1.97 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-16 | 33.5 | 78 | 2.02 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-16 01:00 | 33.2 | 79 | 1.98 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-16 02:00 | 32.8 | 81 | 1.58 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-16 03:00 | 32.4 | 84 | 0.72 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-16 04:00 | 32.2 | 85 | 2.18 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-16 05:00 | 32.5 | 82 | 2.62 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-16 06:00 | 32.6 | 76 | 3.3 | 3 | 26 | 30 | 22 | 0 | 0
2024-07-16 07:00 | 34.1 | 64 | 5.61 | 77 | 26 | 30 | 22 | 0 | 0
2024-07-16 08:00 | 36 | 54 | 7.1 | 238 | 26 | 30 | 22 | 0 | 0
2024-07-16 09:00 | 38.4 | 46 | 7.16 | 434 | 26 | 30 | 22 | 0 | 14.95
2024-07-16 10:00 | 41.6 | 34 | 5.54 | 618 | 26 | 30 | 22 | 0 | 38.865
2024-07-16 11:00 | 43.9 | 27 | 3.71 | 767 | 26 | 30 | 22 | 0 | 66.6317
2024-07-16 12:00 | 45.5 | 22 | 2.19 | 859 | 26 | 30 | 22 | 0 | 89.7971
2024-07-16 13:00 | 46.8 | 19 | 2.14 | 889 | 26 | 30 | 22 | 0 | 93.6924
2024-07-16 14:00 | 46.9 | 20 | 5.63 | 850 | 26 | 30 | 22 | 0 | 59.4075
2024-07-16 15:00 | 45 | 31 | 8.35 | 746 | 26 | 30 | 22 | 0 | 88.2665
2024-07-16 16:00 | 43.8 | 35 | 6.82 | 584 | 26 | 30 | 22 | 0 | 73.1061
2024-07-16 17:00 | 43.1 | 34 | 7.28 | 399 | 26 | 30 | 22 | 0 | 27.971
2024-07-16 18:00 | 42.3 | 33 | 6.04 | 207 | 26 | 30 | 22 | 0 | 0
2024-07-16 19:00 | 40.7 | 36 | 4.67 | 57 | 26 | 30 | 22 | 0 | 0
2024-07-16 20:00 | 39.1 | 42 | 3.7 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-16 21:00 | 38.7 | 40 | 3.55 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-16 22:00 | 38 | 41 | 2.75 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-16 23:00 | 37 | 43 | 2.31 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-17 | 35.7 | 47 | 1.94 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-17 01:00 | 34.3 | 70 | 3.67 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-17 02:00 | 33.5 | 84 | 3.81 | 0 | 26 | 30 | 22 | 0 | 4.9999
2024-07-17 03:00 | 33.3 | 83 | 3.54 | 0 | 26 | 30 | 22 | 0 | 3.6089
2024-07-17 04:00 | 32.9 | 81 | 2.84 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-17 05:00 | 33 | 84 | 2.24 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-17 06:00 | 32.9 | 81 | 2.47 | 3 | 26 | 30 | 22 | 0 | 0
2024-07-17 07:00 | 34 | 67 | 1.7 | 75 | 26 | 30 | 22 | 0 | 0
2024-07-17 08:00 | 36.7 | 45 | 3 | 235 | 26 | 30 | 22 | 0 | 0
2024-07-17 09:00 | 39.1 | 31 | 5.94 | 432 | 26 | 30 | 22 | 0 | 0
2024-07-17 10:00 | 40.9 | 28 | 5.46 | 614 | 26 | 30 | 22 | 0 | 0
2024-07-17 11:00 | 42.8 | 24 | 4.9 | 770 | 26 | 30 | 22 | 0 | 29.2351
2024-07-17 12:00 | 44.4 | 21 | 4.44 | 865 | 26 | 30 | 22 | 0 | 49.494
2024-07-17 13:00 | 44.8 | 22 | 5.24 | 894 | 26 | 30 | 22 | 0 | 55.2576
2024-07-17 14:00 | 42.5 | 31 | 7.57 | 854 | 26 | 30 | 22 | 0 | 57.3515
2024-07-17 15:00 | 40.7 | 39 | 7.57 | 753 | 26 | 30 | 22 | 0 | 61.701
2024-07-17 16:00 | 39.4 | 46 | 6.59 | 596 | 26 | 30 | 22 | 0 | 57.4304
2024-07-17 17:00 | 38.1 | 52 | 5.33 | 403 | 26 | 30 | 22 | 0 | 38.1245
2024-07-17 18:00 | 36.9 | 58 | 4.62 | 204 | 26 | 30 | 22 | 0 | 15.4545
2024-07-17 19:00 | 35.9 | 62 | 3.68 | 55 | 26 | 30 | 22 | 0 | 0
2024-07-17 20:00 | 35.3 | 66 | 2.94 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-17 21:00 | 34.7 | 69 | 1.93 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-17 22:00 | 34.2 | 71 | 1.75 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-17 23:00 | 33.9 | 74 | 1.96 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-18 | 33.7 | 78 | 2.25 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-18 01:00 | 33.4 | 80 | 2.88 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-18 02:00 | 33.4 | 80 | 3.28 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-18 03:00 | 33.2 | 78 | 3.61 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-18 04:00 | 33 | 75 | 3.82 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-18 05:00 | 33 | 66 | 3.67 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-18 06:00 | 33.1 | 59 | 3.86 | 2 | 26 | 30 | 22 | 0 | 0
2024-07-18 07:00 | 34.4 | 43 | 5.22 | 70 | 26 | 30 | 22 | 21.459 | 0
2024-07-18 08:00 | 36 | 35 | 5.73 | 186 | 26 | 30 | 22 | 15.7077 | 0
2024-07-18 09:00 | 37.8 | 33 | 6.2 | 362 | 26 | 30 | 22 | 0 | 0
2024-07-18 10:00 | 39.9 | 28 | 6.28 | 539 | 26 | 30 | 22 | 0 | 0
2024-07-18 11:00 | 41.4 | 24 | 6.57 | 694 | 26 | 30 | 22 | 0 | 0
2024-07-18 12:00 | 41.7 | 24 | 5.35 | 526 | 26 | 30 | 22 | 0 | 0
2024-07-18 13:00 | 42.2 | 26 | 5.2 | 806 | 26 | 30 | 22 | 0 | 33.9643
2024-07-18 14:00 | 41.5 | 33 | 5.48 | 825 | 26 | 30 | 22 | 0 | 60.5824
2024-07-18 15:00 | 40.6 | 36 | 5.42 | 733 | 26 | 30 | 22 | 0 | 50.3485
2024-07-18 16:00 | 39.6 | 40 | 4.92 | 559 | 26 | 30 | 22 | 0 | 33.49
2024-07-18 17:00 | 38 | 50 | 5.29 | 398 | 26 | 30 | 22 | 0 | 27.5835
2024-07-18 18:00 | 36.3 | 62 | 5.02 | 203 | 26 | 30 | 22 | 0 | 19.2637
2024-07-18 19:00 | 35.6 | 63 | 3.92 | 56 | 26 | 30 | 22 | 0 | 0
2024-07-18 20:00 | 34.9 | 64 | 3.4 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-18 21:00 | 34.5 | 67 | 2.63 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-18 22:00 | 34.1 | 72 | 2.2 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-18 23:00 | 33.6 | 76 | 1.48 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-19 | 33.1 | 79 | 1.08 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-19 01:00 | 32.8 | 79 | 1.81 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-19 02:00 | 32.4 | 77 | 2.31 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-19 03:00 | 32 | 77 | 2.4 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-19 04:00 | 31.7 | 79 | 2.18 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-19 05:00 | 32.5 | 76 | 2.32 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-19 06:00 | 32.2 | 77 | 2.73 | 2 | 26 | 30 | 22 | 0 | 0
2024-07-19 07:00 | 32.8 | 76 | 2.9 | 67 | 26 | 30 | 22 | 0 | 0
2024-07-19 08:00 | 34 | 71 | 2.8 | 227 | 26 | 30 | 22 | 0 | 16.8682
2024-07-19 09:00 | 35.8 | 62 | 2.53 | 420 | 26 | 30 | 22 | 0 | 45.0838
2024-07-19 10:00 | 37.7 | 52 | 2.18 | 587 | 26 | 30 | 22 | 0 | 66.6607
2024-07-19 11:00 | 39.2 | 47 | 1.99 | 753 | 26 | 30 | 22 | 0 | 92.8668
2024-07-19 12:00 | 39.8 | 49 | 3.45 | 840 | 26 | 30 | 22 | 0 | 113.2519
2024-07-19 13:00 | 39.1 | 58 | 5.19 | 870 | 26 | 30 | 22 | 0 | 144.2839
2024-07-19 14:00 | 39.1 | 53 | 5.85 | 832 | 26 | 30 | 22 | 0 | 118.3668
2024-07-19 15:00 | 39.1 | 52 | 5.68 | 741 | 26 | 30 | 22 | 0 | 101.277
2024-07-19 16:00 | 38.6 | 53 | 5.41 | 589 | 26 | 30 | 22 | 0 | 76.0985
2024-07-19 17:00 | 38.1 | 53 | 5.17 | 400 | 26 | 30 | 22 | 0 | 42.057
2024-07-19 18:00 | 36.5 | 60 | 4.34 | 208 | 26 | 30 | 22 | 0 | 16.8561
2024-07-19 19:00 | 34.9 | 71 | 3.54 | 56 | 26 | 30 | 22 | 0 | 5.0724
2024-07-19 20:00 | 34.1 | 76 | 2.94 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-19 21:00 | 33.7 | 76 | 2.83 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-19 22:00 | 33.3 | 79 | 0.92 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-19 23:00 | 33 | 81 | 0.81 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-20 | 32.6 | 85 | 1.34 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-20 01:00 | 32.1 | 89 | 1.51 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-20 02:00 | 31.5 | 93 | 1.62 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-20 03:00 | 30.9 | 96 | 1.12 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-20 04:00 | 30.5 | 98 | 0.2 | 0 | 26 | 30 | 22 | 1.5392 | 0
2024-07-20 05:00 | 30.3 | 94 | 1.33 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-20 06:00 | 29.9 | 96 | 1.42 | 2 | 26 | 30 | 22 | 0 | 0
2024-07-20 07:00 | 30.8 | 91 | 1.82 | 75 | 26 | 30 | 22 | 0 | 0
2024-07-20 08:00 | 32.5 | 75 | 0.36 | 240 | 26 | 30 | 22 | 0 | 20.2094
2024-07-20 09:00 | 35.1 | 60 | 1.61 | 434 | 26 | 30 | 22 | 0 | 40.9179
2024-07-20 10:00 | 37.4 | 56 | 2.63 | 621 | 26 | 30 | 22 | 0 | 75.8771
2024-07-20 11:00 | 39.3 | 51 | 3.34 | 769 | 26 | 30 | 22 | 0 | 103.7841
2024-07-20 12:00 | 39.4 | 52 | 5.05 | 860 | 26 | 30 | 22 | 0 | 122.1035
2024-07-20 13:00 | 39.7 | 51 | 4.95 | 888 | 26 | 30 | 22 | 0 | 126.5643
2024-07-20 14:00 | 39.2 | 56 | 5.58 | 852 | 26 | 30 | 22 | 0 | 136.2648
2024-07-20 15:00 | 38.8 | 59 | 6.22 | 748 | 26 | 30 | 22 | 0 | 130.5051
2024-07-20 16:00 | 38.3 | 58 | 6.78 | 590 | 26 | 30 | 22 | 0 | 95.2912
2024-07-20 17:00 | 37.2 | 59 | 5.44 | 404 | 26 | 30 | 22 | 0 | 50.9453
2024-07-20 18:00 | 36.4 | 64 | 4.78 | 208 | 26 | 30 | 22 | 0 | 28.7725
2024-07-20 19:00 | 35.3 | 69 | 3.77 | 55 | 26 | 30 | 22 | 0 | 5.5051
2024-07-20 20:00 | 34.8 | 72 | 3.18 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-20 21:00 | 34.5 | 74 | 2.55 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-20 22:00 | 34.3 | 75 | 2.26 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-20 23:00 | 34.1 | 77 | 2.28 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-21 | 33.8 | 77 | 2.59 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-21 01:00 | 33.4 | 79 | 2.66 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-21 02:00 | 33 | 81 | 2.12 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-21 03:00 | 32.8 | 81 | 1.8 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-21 04:00 | 32.6 | 81 | 1.43 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-21 05:00 | 32.6 | 83 | 0.54 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-21 06:00 | 32.6 | 83 | 0.67 | 2 | 26 | 30 | 22 | 0 | 0
2024-07-21 07:00 | 33.4 | 78 | 1.02 | 73 | 26 | 30 | 22 | 0 | 4.2954
2024-07-21 08:00 | 34.7 | 71 | 2.57 | 233 | 26 | 30 | 22 | 0 | 26.3604
2024-07-21 09:00 | 36.3 | 65 | 3.5 | 428 | 26 | 30 | 22 | 0 | 59.0736
2024-07-21 10:00 | 38.8 | 53 | 3.51 | 616 | 26 | 30 | 22 | 0 | 82.9242
2024-07-21 11:00 | 41.2 | 43 | 1.51 | 768 | 26 | 30 | 22 | 0 | 105.0818
2024-07-21 12:00 | 42.4 | 38 | 3.06 | 861 | 26 | 30 | 22 | 0 | 110.1063
2024-07-21 13:00 | 40.4 | 54 | 6.41 | 890 | 26 | 30 | 22 | 0 | 159.1346
2024-07-21 14:00 | 40.1 | 52 | 6.07 | 849 | 26 | 30 | 22 | 0 | 135.6631
2024-07-21 15:00 | 40 | 54 | 5.66 | 749 | 26 | 30 | 22 | 0 | 128.7051
2024-07-21 16:00 | 38.8 | 56 | 6.93 | 590 | 26 | 30 | 22 | 0 | 96.3968
2024-07-21 17:00 | 37.9 | 59 | 5.52 | 403 | 26 | 30 | 22 | 0 | 63.9032
2024-07-21 18:00 | 36.6 | 65 | 5.28 | 207 | 26 | 30 | 22 | 0 | 36.5612
2024-07-21 19:00 | 35.5 | 69 | 4.05 | 55 | 26 | 30 | 22 | 0 | 8.7877
2024-07-21 20:00 | 34.9 | 74 | 3.26 | 0 | 26 | 30 | 22 | 0 | 4.8508
2024-07-21 21:00 | 34.4 | 76 | 2.58 | 0 | 26 | 30 | 22 | 0 | 1.6067
2024-07-21 22:00 | 34 | 80 | 2.91 | 0 | 26 | 30 | 22 | 0 | 5.0369
2024-07-21 23:00 | 33.7 | 81 | 2.72 | 0 | 26 | 30 | 22 | 0 | 3.2729
2024-07-22 | 33.4 | 82 | 1.61 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-22 01:00 | 32.9 | 86 | 1.1 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-22 02:00 | 32.4 | 88 | 1.42 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-22 03:00 | 32 | 90 | 1.87 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-22 04:00 | 31.3 | 92 | 2.02 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-22 05:00 | 31.8 | 88 | 1.34 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-22 06:00 | 31.4 | 90 | 1.06 | 2 | 26 | 30 | 22 | 0 | 0
2024-07-22 07:00 | 32 | 86 | 0.85 | 74 | 26 | 30 | 22 | 0 | 2.3706
2024-07-22 08:00 | 33.4 | 78 | 0.89 | 236 | 26 | 30 | 22 | 0 | 26.4507
2024-07-22 09:00 | 35.3 | 69 | 0.92 | 432 | 26 | 30 | 22 | 0 | 56.64
2024-07-22 10:00 | 37.5 | 60 | 0.41 | 620 | 26 | 30 | 22 | 0 | 86.0326
2024-07-22 11:00 | 39.2 | 53 | 1.92 | 770 | 26 | 30 | 22 | 0 | 108.4674
2024-07-22 12:00 | 40.6 | 47 | 2.22 | 865 | 26 | 30 | 22 | 0 | 120.5879
2024-07-22 13:00 | 41.6 | 44 | 3.23 | 895 | 26 | 30 | 22 | 0 | 126.3229
2024-07-22 14:00 | 41.5 | 47 | 4.74 | 853 | 26 | 30 | 22 | 0 | 133.6112
2024-07-22 15:00 | 40.3 | 47 | 6.65 | 746 | 26 | 30 | 22 | 0 | 100.3659
2024-07-22 16:00 | 39.1 | 52 | 5.86 | 590 | 26 | 30 | 22 | 0 | 81.0133
2024-07-22 17:00 | 37.9 | 53 | 5.64 | 403 | 26 | 30 | 22 | 0 | 38.4059
2024-07-22 18:00 | 36.8 | 54 | 4.43 | 207 | 26 | 30 | 22 | 0 | 0.9112
2024-07-22 19:00 | 35.8 | 62 | 3.28 | 54 | 26 | 30 | 22 | 0 | 0
2024-07-22 20:00 | 34.6 | 73 | 2.97 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-22 21:00 | 34 | 79 | 2.91 | 0 | 26 | 30 | 22 | 0 | 3.3902
2024-07-22 22:00 | 33.5 | 81 | 2.59 | 0 | 26 | 30 | 22 | 0 | 0.4986
2024-07-22 23:00 | 33.1 | 83 | 2.7 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-23 | 32.8 | 85 | 1.98 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-23 01:00 | 32.5 | 87 | 1.26 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-23 02:00 | 32.1 | 88 | 1.14 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-23 03:00 | 31.8 | 89 | 1.63 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-23 04:00 | 31.4 | 91 | 1.82 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-23 05:00 | 31.7 | 86 | 1.84 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-23 06:00 | 31.3 | 87 | 2.19 | 2 | 26 | 30 | 22 | 0 | 0
2024-07-23 07:00 | 32.2 | 82 | 2.12 | 69 | 26 | 30 | 22 | 0 | 0
2024-07-23 08:00 | 33.9 | 71 | 1.8 | 236 | 26 | 30 | 22 | 0 | 19.7268
2024-07-23 09:00 | 35.5 | 62 | 3.32 | 438 | 26 | 30 | 22 | 0 | 41.6637
2024-07-23 10:00 | 37.5 | 48 | 4.28 | 625 | 26 | 30 | 22 | 0 | 47.4145
2024-07-23 11:00 | 38.9 | 44 | 4.3 | 776 | 26 | 30 | 22 | 0 | 72.397
2024-07-23 12:00 | 39.8 | 41 | 4.95 | 869 | 26 | 30 | 22 | 0 | 82.3682
2024-07-23 13:00 | 40 | 41 | 5.68 | 899 | 26 | 30 | 22 | 0 | 86.3566
2024-07-23 14:00 | 39.8 | 42 | 5.88 | 862 | 26 | 30 | 22 | 0 | 82.1932
2024-07-23 15:00 | 39.7 | 41 | 5.57 | 760 | 26 | 30 | 22 | 0 | 63.2777
2024-07-23 16:00 | 38.9 | 45 | 5.38 | 604 | 26 | 30 | 22 | 0 | 48.4351
2024-07-23 17:00 | 37 | 52 | 5.76 | 407 | 26 | 30 | 22 | 0 | 18.6418
2024-07-23 18:00 | 35.5 | 62 | 5.66 | 209 | 26 | 30 | 22 | 0 | 4.9723
2024-07-23 19:00 | 34.5 | 66 | 5.2 | 54 | 26 | 30 | 22 | 0 | 0
2024-07-23 20:00 | 34.1 | 69 | 4.44 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-23 21:00 | 33.9 | 71 | 3.41 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-23 22:00 | 33.7 | 73 | 3.04 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-23 23:00 | 33.5 | 76 | 2.82 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-24 | 33 | 80 | 2.75 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-24 01:00 | 32.3 | 83 | 2.34 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-24 02:00 | 31.7 | 84 | 2.88 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-24 03:00 | 31 | 85 | 3.04 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-24 04:00 | 30.5 | 87 | 3.28 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-24 05:00 | 30.7 | 85 | 2.98 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-24 06:00 | 30.4 | 83 | 3.16 | 2 | 26 | 30 | 22 | 0 | 0
2024-07-24 07:00 | 31.3 | 77 | 3.22 | 73 | 26 | 30 | 22 | 0 | 0
2024-07-24 08:00 | 33.5 | 65 | 4.03 | 241 | 26 | 30 | 22 | 0 | 0
2024-07-24 09:00 | 36 | 53 | 4.69 | 444 | 26 | 30 | 22 | 0 | 16.4327
2024-07-24 10:00 | 38.5 | 40 | 4.88 | 636 | 26 | 30 | 22 | 0 | 28.8022
2024-07-24 11:00 | 40.6 | 26 | 6.01 | 788 | 26 | 30 | 22 | 0 | 2.5679
2024-07-24 12:00 | 41.1 | 24 | 6.81 | 890 | 26 | 30 | 22 | 0 | 2.7521
2024-07-24 13:00 | 41.1 | 26 | 6.99 | 924 | 26 | 30 | 22 | 0 | 17.1085
2024-07-24 14:00 | 40.9 | 26 | 7.16 | 883 | 26 | 30 | 22 | 0 | 6.919
2024-07-24 15:00 | 40.7 | 27 | 7.18 | 778 | 26 | 30 | 22 | 0 | 0
2024-07-24 16:00 | 40 | 29 | 7.35 | 618 | 26 | 30 | 22 | 0 | 0
2024-07-24 17:00 | 38.7 | 30 | 6.13 | 418 | 26 | 30 | 22 | 0 | 0
2024-07-24 18:00 | 37.6 | 35 | 5.1 | 215 | 26 | 30 | 22 | 0 | 0
2024-07-24 19:00 | 36.3 | 43 | 3.91 | 55 | 26 | 30 | 22 | 0 | 0
2024-07-24 20:00 | 35.2 | 51 | 2.72 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-24 21:00 | 34.3 | 53 | 2.76 | 0 | 26 | 30 | 22 | 0.1535 | 0
2024-07-24 22:00 | 33.6 | 53 | 2.83 | 0 | 26 | 30 | 22 | 7.1701 | 0
2024-07-24 23:00 | 32.7 | 53 | 2.78 | 0 | 26 | 30 | 22 | 15.7937 | 0
2024-07-25 | 31.8 | 56 | 2.69 | 0 | 26 | 30 | 22 | 18.3262 | 0
2024-07-25 01:00 | 31.1 | 58 | 3.2 | 0 | 26 | 30 | 22 | 23.4897 | 0
2024-07-25 02:00 | 30.7 | 60 | 3.28 | 0 | 26 | 30 | 22 | 24.098 | 0
2024-07-25 03:00 | 30.1 | 62 | 3.54 | 0 | 26 | 30 | 22 | 27.7597 | 0
2024-07-25 04:00 | 29.8 | 57 | 3.54 | 0 | 26 | 30 | 22 | 40.9167 | 0
2024-07-25 05:00 | 30 | 59 | 3.42 | 0 | 26 | 30 | 22 | 34.1608 | 0
2024-07-25 06:00 | 29.9 | 52 | 3.37 | 2 | 26 | 30 | 22 | 48.0056 | 0
2024-07-25 07:00 | 31.4 | 43 | 2.95 | 74 | 26 | 30 | 22 | 37.8734 | 0
2024-07-25 08:00 | 34.3 | 33 | 2.28 | 244 | 26 | 30 | 22 | 4.3455 | 0
2024-07-25 09:00 | 37 | 32 | 3.08 | 448 | 26 | 30 | 22 | 0 | 0
2024-07-25 10:00 | 39.2 | 33 | 3.99 | 640 | 26 | 30 | 22 | 0 | 19.8678
2024-07-25 11:00 | 41.1 | 25 | 5.81 | 793 | 26 | 30 | 22 | 0 | 6.7582
2024-07-25 12:00 | 41.3 | 25 | 6.48 | 891 | 26 | 30 | 22 | 0 | 15.0276
2024-07-25 13:00 | 41.3 | 27 | 6.43 | 922 | 26 | 30 | 22 | 0 | 31.025
2024-07-25 14:00 | 41.2 | 27 | 6.64 | 881 | 26 | 30 | 22 | 0 | 22.0373
2024-07-25 15:00 | 41.3 | 25 | 6.45 | 777 | 26 | 30 | 22 | 0 | 0
2024-07-25 16:00 | 40.8 | 26 | 5.87 | 619 | 26 | 30 | 22 | 0 | 0
2024-07-25 17:00 | 40.1 | 26 | 4.64 | 420 | 26 | 30 | 22 | 0 | 0
2024-07-25 18:00 | 38.9 | 33 | 3.9 | 214 | 26 | 30 | 22 | 0 | 0
2024-07-25 19:00 | 37.3 | 42 | 3.52 | 54 | 26 | 30 | 22 | 0 | 0
2024-07-25 20:00 | 35.7 | 53 | 3.06 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-25 21:00 | 34.6 | 60 | 3.13 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-25 22:00 | 33.9 | 65 | 2.52 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-25 23:00 | 33.2 | 68 | 2.97 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-26 | 32.7 | 68 | 3.55 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-26 01:00 | 32.2 | 70 | 3.42 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-26 02:00 | 31.7 | 72 | 3.05 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-26 03:00 | 31.5 | 74 | 3.05 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-26 04:00 | 30.9 | 72 | 3.05 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-26 05:00 | 30.6 | 78 | 2.15 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-26 06:00 | 30.7 | 73 | 3.1 | 2 | 26 | 30 | 22 | 0 | 0
2024-07-26 07:00 | 31.7 | 62 | 3.2 | 72 | 26 | 30 | 22 | 0 | 0
2024-07-26 08:00 | 34.5 | 51 | 2.75 | 240 | 26 | 30 | 22 | 0 | 0
2024-07-26 09:00 | 37.3 | 45 | 3 | 444 | 26 | 30 | 22 | 0 | 20.6664
2024-07-26 10:00 | 39.8 | 34 | 3.62 | 634 | 26 | 30 | 22 | 0 | 33.1761
2024-07-26 11:00 | 41.5 | 25 | 4.68 | 786 | 26 | 30 | 22 | 0 | 24.1208
2024-07-26 12:00 | 42 | 23 | 5.06 | 884 | 26 | 30 | 22 | 0 | 28.6776
2024-07-26 13:00 | 42.2 | 23 | 5.68 | 915 | 26 | 30 | 22 | 0 | 27.714
2024-07-26 14:00 | 42 | 24 | 6.31 | 875 | 26 | 30 | 22 | 0 | 18.3609
2024-07-26 15:00 | 41.8 | 24 | 6.04 | 769 | 26 | 30 | 22 | 0 | 4.3911
2024-07-26 16:00 | 41.3 | 24 | 5.59 | 609 | 26 | 30 | 22 | 0 | 0
2024-07-26 17:00 | 39.7 | 31 | 5.35 | 412 | 26 | 30 | 22 | 0 | 0
2024-07-26 18:00 | 38.4 | 37 | 4.62 | 210 | 26 | 30 | 22 | 0 | 0
2024-07-26 19:00 | 37.1 | 44 | 3.67 | 53 | 26 | 30 | 22 | 0 | 0
2024-07-26 20:00 | 36.2 | 47 | 2.28 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-26 21:00 | 35.4 | 47 | 2.72 | 0 | 26 | 30 | 22 | 2.492 | 0
2024-07-26 22:00 | 34.6 | 49 | 2.8 | 0 | 26 | 30 | 22 | 5.8544 | 0
2024-07-26 23:00 | 33.8 | 50 | 3.09 | 0 | 26 | 30 | 22 | 12.1517 | 0
2024-07-27 | 33.2 | 48 | 3.62 | 0 | 26 | 30 | 22 | 24.839 | 0
2024-07-27 01:00 | 32.8 | 47 | 3.64 | 0 | 26 | 30 | 22 | 31.5685 | 0
2024-07-27 02:00 | 32.1 | 51 | 3.39 | 0 | 26 | 30 | 22 | 28.4623 | 0
2024-07-27 03:00 | 31.7 | 52 | 3.48 | 0 | 26 | 30 | 22 | 30.9139 | 0
2024-07-27 04:00 | 31.1 | 51 | 2.86 | 0 | 26 | 30 | 22 | 34.8214 | 0
2024-07-27 05:00 | 30.5 | 53 | 2.75 | 0 | 26 | 30 | 22 | 35.8033 | 0
2024-07-27 06:00 | 30.1 | 53 | 2.93 | 1 | 26 | 30 | 22 | 40.6972 | 0
2024-07-27 07:00 | 31.7 | 46 | 3.01 | 72 | 26 | 30 | 22 | 30.3418 | 0
2024-07-27 08:00 | 34.8 | 36 | 2.88 | 241 | 26 | 30 | 22 | 0.7458 | 0
2024-07-27 09:00 | 37.5 | 33 | 3.89 | 445 | 26 | 30 | 22 | 0 | 0
2024-07-27 10:00 | 39.5 | 35 | 5.03 | 637 | 26 | 30 | 22 | 0 | 20.3974
2024-07-27 11:00 | 41 | 31 | 6.71 | 788 | 26 | 30 | 22 | 0 | 28.7802
2024-07-27 12:00 | 40.8 | 33 | 7.57 | 888 | 26 | 30 | 22 | 0 | 44.9585
2024-07-27 13:00 | 40.9 | 31 | 7.41 | 917 | 26 | 30 | 22 | 0 | 39.4106
2024-07-27 14:00 | 41.2 | 28 | 7.26 | 878 | 26 | 30 | 22 | 0 | 21.873
2024-07-27 15:00 | 41.1 | 28 | 7.27 | 772 | 26 | 30 | 22 | 0 | 5.9218
2024-07-27 16:00 | 40.6 | 31 | 6.86 | 611 | 26 | 30 | 22 | 0 | 0
2024-07-27 17:00 | 39.4 | 31 | 5.67 | 412 | 26 | 30 | 22 | 0 | 0
2024-07-27 18:00 | 38 | 37 | 4.9 | 210 | 26 | 30 | 22 | 0 | 0
2024-07-27 19:00 | 36.6 | 47 | 4.55 | 52 | 26 | 30 | 22 | 0 | 0
2024-07-27 20:00 | 35.5 | 57 | 5 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-27 21:00 | 34.9 | 59 | 5.5 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-27 22:00 | 34.6 | 61 | 5.77 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-27 23:00 | 34.2 | 63 | 5.08 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-28 | 34 | 63 | 4.92 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-28 01:00 | 33.8 | 63 | 4.74 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-28 02:00 | 33.4 | 64 | 4.55 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-28 03:00 | 32.9 | 64 | 4.27 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-28 04:00 | 32.5 | 64 | 4.21 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-28 05:00 | 32.2 | 64 | 4.13 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-28 06:00 | 32.2 | 67 | 4.33 | 1 | 26 | 30 | 22 | 0 | 0
2024-07-28 07:00 | 33.5 | 65 | 4.33 | 69 | 26 | 30 | 22 | 0 | 0
2024-07-28 08:00 | 35.8 | 58 | 4.38 | 234 | 26 | 30 | 22 | 0 | 3.0968
2024-07-28 09:00 | 38.2 | 42 | 6.13 | 435 | 26 | 30 | 22 | 0 | 0
2024-07-28 10:00 | 38.9 | 41 | 7.01 | 628 | 26 | 30 | 22 | 0 | 24.9332
2024-07-28 11:00 | 39.5 | 40 | 7.3 | 779 | 26 | 30 | 22 | 0 | 49.3835
2024-07-28 12:00 | 39.8 | 41 | 7.52 | 871 | 26 | 30 | 22 | 0 | 72.2905
2024-07-28 13:00 | 39.8 | 43 | 7.72 | 903 | 26 | 30 | 22 | 0 | 87.751
2024-07-28 14:00 | 39.7 | 43 | 8.41 | 863 | 26 | 30 | 22 | 0 | 78.668
2024-07-28 15:00 | 39.3 | 43 | 8.76 | 758 | 26 | 30 | 22 | 0 | 54.9075
2024-07-28 16:00 | 38.9 | 43 | 8.6 | 600 | 26 | 30 | 22 | 0 | 25.4668
2024-07-28 17:00 | 37.7 | 44 | 8.52 | 407 | 26 | 30 | 22 | 0 | 0
2024-07-28 18:00 | 36.8 | 50 | 8.1 | 206 | 26 | 30 | 22 | 0 | 0
2024-07-28 19:00 | 35.7 | 56 | 7.61 | 51 | 26 | 30 | 22 | 0 | 0
2024-07-28 20:00 | 35.2 | 58 | 5.94 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-28 21:00 | 34.8 | 61 | 4.81 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-28 22:00 | 34.4 | 62 | 4.43 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-28 23:00 | 33.7 | 63 | 3.44 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-29 | 33.1 | 64 | 3.74 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-29 01:00 | 32.6 | 65 | 3.31 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-29 02:00 | 32 | 66 | 3.67 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-29 03:00 | 31.6 | 64 | 4.28 | 0 | 26 | 30 | 22 | 6.2987 | 0
2024-07-29 04:00 | 31.2 | 64 | 4.52 | 0 | 26 | 30 | 22 | 11.8988 | 0
2024-07-29 05:00 | 31.2 | 63 | 4.59 | 0 | 26 | 30 | 22 | 14.506 | 0
2024-07-29 06:00 | 30.9 | 63 | 4.36 | 1 | 26 | 30 | 22 | 18.0956 | 0
2024-07-29 07:00 | 31.8 | 59 | 3.96 | 69 | 26 | 30 | 22 | 6.2576 | 0
2024-07-29 08:00 | 34 | 51 | 4.4 | 233 | 26 | 30 | 22 | 0 | 0
2024-07-29 09:00 | 36.2 | 47 | 4.65 | 435 | 26 | 30 | 22 | 0 | 0
2024-07-29 10:00 | 38.1 | 41 | 4.21 | 625 | 26 | 30 | 22 | 0 | 31.3072
2024-07-29 11:00 | 39.7 | 38 | 3.75 | 778 | 26 | 30 | 22 | 0 | 64.3734
2024-07-29 12:00 | 40.8 | 37 | 3.65 | 871 | 26 | 30 | 22 | 0 | 86.8057
2024-07-29 13:00 | 40.6 | 41 | 5.04 | 896 | 26 | 30 | 22 | 0 | 97.5713
2024-07-29 14:00 | 40.1 | 44 | 5.84 | 852 | 26 | 30 | 22 | 0 | 95.8635
2024-07-29 15:00 | 39.9 | 45 | 5.8 | 746 | 26 | 30 | 22 | 0 | 83.0718
2024-07-29 16:00 | 39.4 | 46 | 5.6 | 589 | 26 | 30 | 22 | 0 | 58.4535
2024-07-29 17:00 | 38.2 | 49 | 5.41 | 400 | 26 | 30 | 22 | 0 | 26.6229
2024-07-29 18:00 | 36.6 | 59 | 5.52 | 202 | 26 | 30 | 22 | 0 | 12.729
2024-07-29 19:00 | 35.3 | 67 | 5.26 | 49 | 26 | 30 | 22 | 0 | 0
2024-07-29 20:00 | 34.6 | 72 | 4.65 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-29 21:00 | 34.3 | 73 | 4.02 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-29 22:00 | 34 | 73 | 3.24 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-29 23:00 | 33.6 | 74 | 3.04 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-30 | 33.1 | 75 | 2.92 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-30 01:00 | 32.6 | 76 | 2.18 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-30 02:00 | 32.1 | 78 | 2.02 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-30 03:00 | 31.7 | 79 | 2.14 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-30 04:00 | 31.3 | 81 | 2.28 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-30 05:00 | 31.3 | 77 | 1.75 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-30 06:00 | 31 | 77 | 2.64 | 1 | 26 | 30 | 22 | 0 | 0
2024-07-30 07:00 | 32.8 | 71 | 3.01 | 66 | 26 | 30 | 22 | 0 | 0
2024-07-30 08:00 | 35.1 | 61 | 5.72 | 230 | 26 | 30 | 22 | 0 | 0
2024-07-30 09:00 | 37.6 | 51 | 7.3 | 431 | 26 | 30 | 22 | 0 | 23.852
2024-07-30 10:00 | 40.1 | 41 | 7.14 | 619 | 26 | 30 | 22 | 0 | 45.2439
2024-07-30 11:00 | 42.4 | 32 | 5.9 | 770 | 26 | 30 | 22 | 0 | 58.6933
2024-07-30 12:00 | 44.3 | 26 | 5.12 | 863 | 26 | 30 | 22 | 0 | 68.7415
2024-07-30 13:00 | 45.2 | 25 | 4.85 | 884 | 26 | 30 | 22 | 0 | 79.1238
2024-07-30 14:00 | 45.9 | 26 | 6.38 | 832 | 26 | 30 | 22 | 0 | 80.9493
2024-07-30 15:00 | 46.2 | 27 | 6.77 | 732 | 26 | 30 | 22 | 0 | 78.6165
2024-07-30 16:00 | 45.1 | 29 | 7.45 | 572 | 26 | 30 | 22 | 0 | 51.8028
2024-07-30 17:00 | 43.9 | 30 | 7.61 | 384 | 26 | 30 | 22 | 0 | 11.7746
2024-07-30 18:00 | 42.1 | 33 | 7.8 | 194 | 26 | 30 | 22 | 0 | 0
2024-07-30 19:00 | 39.3 | 43 | 7.62 | 47 | 26 | 30 | 22 | 0 | 0
2024-07-30 20:00 | 36.4 | 56 | 6.49 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-30 21:00 | 35.9 | 57 | 4.53 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-30 22:00 | 35.7 | 58 | 4.66 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-30 23:00 | 35.5 | 58 | 3.14 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-31 | 35.4 | 59 | 1.7 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-31 01:00 | 34.9 | 60 | 2.12 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-31 02:00 | 34.5 | 65 | 2.26 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-31 03:00 | 34.4 | 71 | 1.87 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-31 04:00 | 33.9 | 75 | 1.32 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-31 05:00 | 33.7 | 61 | 5.32 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-31 06:00 | 34.9 | 52 | 5.06 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-31 07:00 | 36.9 | 32 | 5.29 | 29 | 26 | 30 | 22 | 35.3028 | 0
2024-07-31 08:00 | 38.4 | 32 | 6.2 | 226 | 26 | 30 | 22 | 0 | 0
2024-07-31 09:00 | 40.2 | 29 | 7.32 | 427 | 26 | 30 | 22 | 0 | 0
2024-07-31 10:00 | 42 | 25 | 7.3 | 617 | 26 | 30 | 22 | 0 | 0
2024-07-31 11:00 | 43.7 | 21 | 6.04 | 766 | 26 | 30 | 22 | 0 | 10.6066
2024-07-31 12:00 | 45 | 18 | 4.13 | 865 | 26 | 30 | 22 | 0 | 44.1028
2024-07-31 13:00 | 44.6 | 20 | 3.79 | 891 | 26 | 30 | 22 | 0 | 57.9728
2024-07-31 14:00 | 43.3 | 28 | 6.79 | 850 | 26 | 30 | 22 | 0 | 54.382
2024-07-31 15:00 | 42.7 | 29 | 6.44 | 700 | 26 | 30 | 22 | 0 | 33.2054
2024-07-31 16:00 | 42 | 31 | 5.58 | 562 | 26 | 30 | 22 | 0 | 21.1756
2024-07-31 17:00 | 40.9 | 33 | 4.4 | 376 | 26 | 30 | 22 | 0 | 0
2024-07-31 18:00 | 40 | 36 | 4.43 | 194 | 26 | 30 | 22 | 0 | 0
2024-07-31 19:00 | 38.4 | 43 | 4.1 | 44 | 26 | 30 | 22 | 0 | 0
2024-07-31 20:00 | 38.2 | 41 | 3.68 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-31 21:00 | 37.8 | 40 | 2.73 | 0 | 26 | 30 | 22 | 0 | 0
2024-07-31 22:00 | 37.5 | 38 | 2.51 | 0 | 26 | 30 | 22 | 3.9113 | 0
2024-07-31 23:00 | 37.3 | 41 | 2.75 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-01 | 36.6 | 51 | 2.82 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-01 01:00 | 35.8 | 58 | 2.96 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-01 02:00 | 35.5 | 60 | 2.53 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-01 03:00 | 34.5 | 64 | 1.43 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-01 04:00 | 34.7 | 63 | 1.44 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-01 05:00 | 34.9 | 62 | 1.77 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-01 06:00 | 35.1 | 50 | 2.12 | 1 | 26 | 30 | 22 | 0 | 0
2024-08-01 07:00 | 37.3 | 28 | 3.35 | 64 | 26 | 30 | 22 | 27.8005 | 0
2024-08-01 08:00 | 38.9 | 26 | 4.26 | 214 | 26 | 30 | 22 | 5.779 | 0
2024-08-01 09:00 | 40.8 | 24 | 4.2 | 404 | 26 | 30 | 22 | 0 | 0
2024-08-01 10:00 | 42.7 | 21 | 4.97 | 598 | 26 | 30 | 22 | 0 | 0
2024-08-01 11:00 | 43.9 | 19 | 5.15 | 749 | 26 | 30 | 22 | 0 | 9.3224
2024-08-01 12:00 | 44.7 | 18 | 4.7 | 861 | 26 | 30 | 22 | 0 | 33.1071
2024-08-01 13:00 | 44.8 | 20 | 4.81 | 888 | 26 | 30 | 22 | 0 | 47.3943
2024-08-01 14:00 | 44 | 24 | 6.52 | 850 | 26 | 30 | 22 | 0 | 40.6009
2024-08-01 15:00 | 42.9 | 25 | 7.87 | 748 | 26 | 30 | 22 | 0 | 6.6022
2024-08-01 16:00 | 41.4 | 31 | 7.68 | 590 | 26 | 30 | 22 | 0 | 1.896
2024-08-01 17:00 | 39.5 | 38 | 6.86 | 395 | 26 | 30 | 22 | 0 | 0
2024-08-01 18:00 | 37.3 | 54 | 5.9 | 197 | 26 | 30 | 22 | 0 | 3.634
2024-08-01 19:00 | 36.2 | 59 | 4.98 | 46 | 26 | 30 | 22 | 0 | 0
2024-08-01 20:00 | 35.4 | 67 | 3.97 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-01 21:00 | 34.9 | 69 | 3.18 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-01 22:00 | 34.5 | 74 | 2.2 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-01 23:00 | 34.3 | 74 | 1.68 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-02 | 34 | 75 | 1.39 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-02 01:00 | 33.6 | 76 | 2.05 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-02 02:00 | 33.2 | 77 | 2.77 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-02 03:00 | 32.7 | 77 | 2.84 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-02 04:00 | 32.3 | 79 | 2.47 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-02 05:00 | 32.6 | 79 | 2.43 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-02 06:00 | 32.3 | 78 | 2.73 | 1 | 26 | 30 | 22 | 0 | 0
2024-08-02 07:00 | 33 | 73 | 2.85 | 64 | 26 | 30 | 22 | 0 | 0
2024-08-02 08:00 | 34.7 | 62 | 3.67 | 226 | 26 | 30 | 22 | 0 | 1.1531
2024-08-02 09:00 | 36.6 | 52 | 3.54 | 423 | 26 | 30 | 22 | 0 | 25.2805
2024-08-02 10:00 | 38.5 | 46 | 4.2 | 616 | 26 | 30 | 22 | 0 | 53.1993
2024-08-02 11:00 | 40.4 | 40 | 4.8 | 768 | 26 | 30 | 22 | 0 | 73.7424
2024-08-02 12:00 | 41.7 | 38 | 5.07 | 862 | 26 | 30 | 22 | 0 | 95.3108
2024-08-02 13:00 | 41.6 | 39 | 5.51 | 889 | 26 | 30 | 22 | 0 | 101.3
2024-08-02 14:00 | 40.9 | 41 | 6.14 | 846 | 26 | 30 | 22 | 0 | 92.9482
2024-08-02 15:00 | 40.7 | 41 | 5.94 | 745 | 26 | 30 | 22 | 0 | 76.3134
2024-08-02 16:00 | 39.8 | 45 | 5.49 | 587 | 26 | 30 | 22 | 0 | 60.4793
2024-08-02 17:00 | 38.5 | 47 | 4.59 | 393 | 26 | 30 | 22 | 0 | 25.1152
2024-08-02 18:00 | 37 | 56 | 4.49 | 196 | 26 | 30 | 22 | 0 | 9.1596
2024-08-02 19:00 | 35.9 | 63 | 4.1 | 43 | 26 | 30 | 22 | 0 | 0
2024-08-02 20:00 | 35.1 | 68 | 3.4 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-02 21:00 | 34.5 | 74 | 3.49 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-02 22:00 | 34.1 | 76 | 3.38 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-02 23:00 | 33.8 | 79 | 3.54 | 0 | 26 | 30 | 22 | 0 | 1.6156
2024-08-03 | 33.5 | 81 | 3.74 | 0 | 26 | 30 | 22 | 0 | 2.2972
2024-08-03 01:00 | 33.2 | 81 | 2.92 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-03 02:00 | 32.8 | 80 | 1.98 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-03 03:00 | 32.5 | 80 | 2.06 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-03 04:00 | 32.3 | 79 | 2.52 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-03 05:00 | 33 | 73 | 3.1 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-03 06:00 | 32.6 | 78 | 2.16 | 1 | 26 | 30 | 22 | 0 | 0
2024-08-03 07:00 | 33 | 76 | 1.71 | 62 | 26 | 30 | 22 | 0 | 0
2024-08-03 08:00 | 34.2 | 69 | 1.43 | 218 | 26 | 30 | 22 | 0 | 18.3373
2024-08-03 09:00 | 36 | 59 | 1.63 | 414 | 26 | 30 | 22 | 0 | 43.9299
2024-08-03 10:00 | 38.1 | 49 | 2.3 | 583 | 26 | 30 | 22 | 0 | 62.6251
2024-08-03 11:00 | 40.2 | 41 | 3.23 | 723 | 26 | 30 | 22 | 0 | 76.3489
2024-08-03 12:00 | 41.8 | 36 | 3.4 | 833 | 26 | 30 | 22 | 0 | 90.9109
2024-08-03 13:00 | 42.1 | 38 | 4.62 | 870 | 26 | 30 | 22 | 0 | 103.4263
2024-08-03 14:00 | 41 | 42 | 5.85 | 827 | 26 | 30 | 22 | 0 | 97.8563
2024-08-03 15:00 | 40.7 | 37 | 5.89 | 709 | 26 | 30 | 22 | 0 | 51.0449
2024-08-03 16:00 | 39.4 | 43 | 5.95 | 467 | 26 | 30 | 22 | 0 | 26.7757
2024-08-03 17:00 | 37.3 | 55 | 5.02 | 219 | 26 | 30 | 22 | 0 | 12.3564
2024-08-03 18:00 | 36.5 | 59 | 4.34 | 120 | 26 | 30 | 22 | 0 | 1.6703
2024-08-03 19:00 | 35.1 | 70 | 3.72 | 36 | 26 | 30 | 22 | 0 | 2.7006
2024-08-03 20:00 | 34.5 | 74 | 2.4 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-03 21:00 | 34.2 | 75 | 3.44 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-03 22:00 | 33.9 | 74 | 3.88 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-03 23:00 | 33.5 | 75 | 3.06 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-04 | 33.1 | 77 | 3.04 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-04 01:00 | 32.7 | 78 | 3.62 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-04 02:00 | 32.5 | 78 | 3.48 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-04 03:00 | 32.1 | 81 | 2.69 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-04 04:00 | 31.9 | 83 | 2.28 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-04 05:00 | 32.4 | 75 | 2.47 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-04 06:00 | 31.8 | 77 | 3.04 | 1 | 26 | 30 | 22 | 0 | 0
2024-08-04 07:00 | 32.5 | 74 | 3.59 | 61 | 26 | 30 | 22 | 0 | 0
2024-08-04 08:00 | 33.6 | 76 | 3.7 | 221 | 26 | 30 | 22 | 0 | 21.0395
2024-08-04 09:00 | 34.8 | 71 | 2.6 | 407 | 26 | 30 | 22 | 0 | 51.0254
2024-08-04 10:00 | 36.3 | 64 | 2.59 | 574 | 26 | 30 | 22 | 0 | 75.9182
2024-08-04 11:00 | 37.3 | 57 | 3.5 | 560 | 26 | 30 | 22 | 0 | 67.5932
2024-08-04 12:00 | 38.8 | 45 | 4.63 | 800 | 26 | 30 | 22 | 0 | 76.4919
2024-08-04 13:00 | 39 | 40 | 5.3 | 682 | 26 | 30 | 22 | 0 | 39.0875
2024-08-04 14:00 | 39.1 | 41 | 5.32 | 732 | 26 | 30 | 22 | 0 | 51.5681
2024-08-04 15:00 | 38.8 | 45 | 5.35 | 682 | 26 | 30 | 22 | 0 | 57.4946
2024-08-04 16:00 | 37.9 | 50 | 5.35 | 592 | 26 | 30 | 22 | 0 | 51.9458
2024-08-04 17:00 | 35.9 | 61 | 5.81 | 398 | 26 | 30 | 22 | 0 | 33.773
2024-08-04 18:00 | 34.9 | 66 | 5.38 | 197 | 26 | 30 | 22 | 0 | 7.4936
2024-08-04 19:00 | 33.9 | 72 | 4.75 | 44 | 26 | 30 | 22 | 0 | 0
2024-08-04 20:00 | 33.6 | 72 | 3.63 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-04 21:00 | 33.5 | 72 | 3.83 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-04 22:00 | 33.4 | 72 | 2.45 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-04 23:00 | 33 | 74 | 1.39 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-05 | 32.8 | 74 | 1.8 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-05 01:00 | 32.6 | 73 | 1.63 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-05 02:00 | 32.6 | 70 | 1.24 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-05 03:00 | 31.8 | 72 | 1.3 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-05 04:00 | 31.4 | 72 | 2.75 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-05 05:00 | 31.1 | 77 | 2.91 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-05 06:00 | 31.5 | 75 | 3.69 | 1 | 26 | 30 | 22 | 0 | 0
2024-08-05 07:00 | 32.7 | 73 | 5.66 | 57 | 26 | 30 | 22 | 0 | 0
2024-08-05 08:00 | 34.1 | 66 | 5.63 | 220 | 26 | 30 | 22 | 0 | 0
2024-08-05 09:00 | 36.4 | 56 | 4.63 | 412 | 26 | 30 | 22 | 0 | 28.6801
2024-08-05 10:00 | 38.3 | 49 | 3.38 | 604 | 26 | 30 | 22 | 0 | 62.5726
2024-08-05 11:00 | 39.7 | 44 | 2.09 | 755 | 26 | 30 | 22 | 0 | 90.2434
2024-08-05 12:00 | 41.4 | 38 | 1.36 | 841 | 26 | 30 | 22 | 0 | 107.4422
2024-08-05 13:00 | 42.1 | 35 | 1.7 | 691 | 26 | 30 | 22 | 0 | 83.0262
2024-08-05 14:00 | 39.5 | 53 | 6.95 | 471 | 26 | 30 | 22 | 0 | 79.7269
2024-08-05 15:00 | 40.1 | 43 | 6.89 | 352 | 26 | 30 | 22 | 0 | 21.0751
2024-08-05 16:00 | 37.5 | 51 | 9.05 | 185 | 26 | 30 | 22 | 0 | 0
2024-08-05 17:00 | 37.9 | 49 | 7.61 | 240 | 26 | 30 | 22 | 0 | 0
2024-08-05 18:00 | 37.4 | 51 | 6.4 | 81 | 26 | 30 | 22 | 0 | 0
2024-08-05 19:00 | 36.6 | 54 | 6.22 | 30 | 26 | 30 | 22 | 0 | 0
2024-08-05 20:00 | 35.9 | 57 | 5.68 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-05 21:00 | 34.9 | 61 | 6.17 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-05 22:00 | 34.7 | 62 | 6.03 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-05 23:00 | 35 | 61 | 5.63 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-06 | 34.7 | 61 | 6.01 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-06 01:00 | 33.5 | 64 | 5.28 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-06 02:00 | 33.7 | 63 | 2.92 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-06 03:00 | 34.1 | 61 | 0.91 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-06 04:00 | 34.1 | 62 | 2.88 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-06 05:00 | 31.1 | 61 | 6.28 | 0 | 26 | 30 | 22 | 24.1977 | 0
2024-08-06 06:00 | 31.3 | 59 | 5.81 | 0 | 26 | 30 | 22 | 26.2448 | 0
2024-08-06 07:00 | 32 | 52 | 6.18 | 36 | 26 | 30 | 22 | 33.648 | 0
2024-08-06 08:00 | 33.5 | 40 | 3.88 | 184 | 26 | 30 | 22 | 18.3448 | 0
2024-08-06 09:00 | 34.4 | 39 | 5.3 | 349 | 26 | 30 | 22 | 0 | 0
2024-08-06 10:00 | 34.8 | 41 | 6.49 | 501 | 26 | 30 | 22 | 0 | 0
2024-08-06 11:00 | 35.6 | 40 | 5.77 | 656 | 26 | 30 | 22 | 0 | 0
2024-08-06 12:00 | 36.2 | 40 | 5.59 | 721 | 26 | 30 | 22 | 0 | 1.7094
2024-08-06 13:00 | 37 | 38 | 4.42 | 801 | 26 | 30 | 22 | 0 | 29.0501
2024-08-06 14:00 | 37.7 | 35 | 3.14 | 754 | 26 | 30 | 22 | 0 | 37.4482
2024-08-06 15:00 | 37.8 | 37 | 4.3 | 558 | 26 | 30 | 22 | 0 | 3.6204
2024-08-06 16:00 | 36.5 | 43 | 5.63 | 385 | 26 | 30 | 22 | 0 | 0
2024-08-06 17:00 | 36.5 | 51 | 6.35 | 340 | 26 | 30 | 22 | 0 | 0
2024-08-06 18:00 | 35.9 | 54 | 6.48 | 171 | 26 | 30 | 22 | 0 | 0
2024-08-06 19:00 | 35.3 | 54 | 5.66 | 39 | 26 | 30 | 22 | 0 | 0
2024-08-06 20:00 | 35.4 | 49 | 4.74 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-06 21:00 | 35.1 | 50 | 4.11 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-06 22:00 | 34.6 | 55 | 2.9 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-06 23:00 | 34.3 | 58 | 1.94 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-07 | 34.2 | 60 | 0.95 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-07 01:00 | 33.9 | 61 | 0.61 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-07 02:00 | 33.6 | 60 | 1.35 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-07 03:00 | 33.4 | 58 | 1.84 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-07 04:00 | 33.1 | 57 | 2.06 | 0 | 26 | 30 | 22 | 3.415 | 0
2024-08-07 05:00 | 33.2 | 59 | 3.28 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-07 06:00 | 32.8 | 64 | 4.03 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-07 07:00 | 33.1 | 65 | 4.66 | 58 | 26 | 30 | 22 | 0 | 0
2024-08-07 08:00 | 34.7 | 58 | 5.69 | 216 | 26 | 30 | 22 | 0 | 0
2024-08-07 09:00 | 36.8 | 48 | 5.61 | 411 | 26 | 30 | 22 | 0 | 0.272
2024-08-07 10:00 | 38.5 | 41 | 3.81 | 588 | 26 | 30 | 22 | 0 | 34.5182
2024-08-07 11:00 | 39.6 | 38 | 1.71 | 674 | 26 | 30 | 22 | 0 | 68.5672
2024-08-07 12:00 | 40.1 | 36 | 0.5 | 586 | 26 | 30 | 22 | 0 | 72.0465
2024-08-07 13:00 | 41 | 34 | 1.25 | 689 | 26 | 30 | 22 | 0 | 78.1982
2024-08-07 14:00 | 42 | 32 | 2.86 | 816 | 26 | 30 | 22 | 0 | 80.4991
2024-08-07 15:00 | 41.5 | 36 | 6 | 726 | 26 | 30 | 22 | 0 | 60.3165
2024-08-07 16:00 | 40 | 39 | 7.5 | 564 | 26 | 30 | 22 | 0 | 23.0778
2024-08-07 17:00 | 37.4 | 46 | 6.13 | 370 | 26 | 30 | 22 | 0 | 0
2024-08-07 18:00 | 36.4 | 49 | 5.19 | 181 | 26 | 30 | 22 | 0 | 0
2024-08-07 19:00 | 35.5 | 54 | 4.27 | 39 | 26 | 30 | 22 | 0 | 0
2024-08-07 20:00 | 35 | 58 | 2.82 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-07 21:00 | 34.7 | 60 | 2.04 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-07 22:00 | 34.4 | 63 | 1.48 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-07 23:00 | 34.2 | 66 | 2.91 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-08 | 34.1 | 65 | 2.62 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-08 01:00 | 33.9 | 66 | 2.44 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-08 02:00 | 33.5 | 65 | 2.69 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-08 03:00 | 32.9 | 65 | 4 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-08 04:00 | 32.8 | 65 | 4.79 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-08 05:00 | 32.4 | 66 | 5.66 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-08 06:00 | 32.2 | 65 | 6.48 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-08 07:00 | 33 | 62 | 7.13 | 56 | 26 | 30 | 22 | 0 | 0
2024-08-08 08:00 | 34.5 | 58 | 6.5 | 216 | 26 | 30 | 22 | 0 | 0
2024-08-08 09:00 | 36.9 | 49 | 6.11 | 419 | 26 | 30 | 22 | 0 | 4.3112
2024-08-08 10:00 | 39.1 | 40 | 4.27 | 611 | 26 | 30 | 22 | 0 | 37.9349
2024-08-08 11:00 | 40.6 | 34 | 2.19 | 763 | 26 | 30 | 22 | 0 | 73.6362
2024-08-08 12:00 | 41.7 | 31 | 0.61 | 858 | 26 | 30 | 22 | 0 | 111.0018
2024-08-08 13:00 | 42.7 | 29 | 2.12 | 888 | 26 | 30 | 22 | 0 | 94.648
2024-08-08 14:00 | 42.2 | 34 | 5.99 | 847 | 26 | 30 | 22 | 0 | 76.8173
2024-08-08 15:00 | 40.3 | 45 | 7.5 | 737 | 26 | 30 | 22 | 0 | 87.8103
2024-08-08 16:00 | 39 | 50 | 8.53 | 528 | 26 | 30 | 22 | 0 | 60.6484
2024-08-08 17:00 | 39.2 | 51 | 5.92 | 380 | 26 | 30 | 22 | 0 | 49.8422
2024-08-08 18:00 | 39.3 | 42 | 4.39 | 183 | 26 | 30 | 22 | 0 | 0
2024-08-08 19:00 | 37.8 | 45 | 7.34 | 39 | 26 | 30 | 22 | 0 | 0
2024-08-08 20:00 | 35.5 | 54 | 7.6 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-08 21:00 | 34.2 | 59 | 7.22 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-08 22:00 | 33.6 | 61 | 6.5 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-08 23:00 | 33.5 | 61 | 6.2 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-09 | 32.8 | 64 | 5.26 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-09 01:00 | 32.4 | 64 | 6.15 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-09 02:00 | 32.4 | 63 | 7.5 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-09 03:00 | 32.1 | 65 | 7.22 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-09 04:00 | 31.6 | 68 | 7.72 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-09 05:00 | 31.4 | 69 | 7.75 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-09 06:00 | 31.5 | 67 | 7.81 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-09 07:00 | 32.5 | 62 | 8.2 | 58 | 26 | 30 | 22 | 0 | 0
2024-08-09 08:00 | 33.9 | 58 | 7.65 | 218 | 26 | 30 | 22 | 0 | 0
2024-08-09 09:00 | 36.4 | 48 | 7.91 | 418 | 26 | 30 | 22 | 0 | 0
2024-08-09 10:00 | 38.6 | 41 | 7.5 | 609 | 26 | 30 | 22 | 0 | 14.2356
2024-08-09 11:00 | 40.4 | 36 | 6.33 | 761 | 26 | 30 | 22 | 0 | 45.702
2024-08-09 12:00 | 42 | 33 | 5.12 | 855 | 26 | 30 | 22 | 0 | 73.8506
2024-08-09 13:00 | 42.9 | 30 | 4.53 | 881 | 26 | 30 | 22 | 0 | 78.19
2024-08-09 14:00 | 43.6 | 29 | 4.94 | 840 | 26 | 30 | 22 | 0 | 74.0082
2024-08-09 15:00 | 43.7 | 28 | 5.36 | 732 | 26 | 30 | 22 | 0 | 52.7973
2024-08-09 16:00 | 43.6 | 29 | 5.76 | 568 | 26 | 30 | 22 | 0 | 32.7332
2024-08-09 17:00 | 40.5 | 36 | 7.92 | 373 | 26 | 30 | 22 | 0 | 0
2024-08-09 18:00 | 38.5 | 40 | 7.93 | 180 | 26 | 30 | 22 | 0 | 0
2024-08-09 19:00 | 36.3 | 47 | 7.92 | 38 | 26 | 30 | 22 | 0 | 0
2024-08-09 20:00 | 34.7 | 52 | 7.41 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-09 21:00 | 33.5 | 57 | 6.4 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-09 22:00 | 32.8 | 60 | 6.1 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-09 23:00 | 32.5 | 59 | 5.81 | 0 | 26 | 30 | 22 | 7.1346 | 0
2024-08-10 | 32.3 | 59 | 5.93 | 0 | 26 | 30 | 22 | 10.4106 | 0
2024-08-10 01:00 | 31.4 | 64 | 6.62 | 0 | 26 | 30 | 22 | 9.5406 | 0
2024-08-10 02:00 | 31 | 66 | 6.12 | 0 | 26 | 30 | 22 | 10.1414 | 0
2024-08-10 03:00 | 30.9 | 67 | 6.62 | 0 | 26 | 30 | 22 | 8.7747 | 0
2024-08-10 04:00 | 30.4 | 69 | 7.07 | 0 | 26 | 30 | 22 | 11.6317 | 0
2024-08-10 05:00 | 30.3 | 69 | 6.85 | 0 | 26 | 30 | 22 | 13.4726 | 0
2024-08-10 06:00 | 30.1 | 71 | 6.61 | 0 | 26 | 30 | 22 | 10.8409 | 0
2024-08-10 07:00 | 31.2 | 65 | 7.35 | 58 | 26 | 30 | 22 | 2.0149 | 0
2024-08-10 08:00 | 33.1 | 56 | 6.53 | 218 | 26 | 30 | 22 | 0 | 0
2024-08-10 09:00 | 35.3 | 50 | 6.69 | 420 | 26 | 30 | 22 | 0 | 0
2024-08-10 10:00 | 37.7 | 41 | 5.5 | 605 | 26 | 30 | 22 | 0 | 12.4007
2024-08-10 11:00 | 39.3 | 36 | 3.81 | 761 | 26 | 30 | 22 | 0 | 49.9227
2024-08-10 12:00 | 40.6 | 33 | 2.61 | 855 | 26 | 30 | 22 | 0 | 78.5547
2024-08-10 13:00 | 41.7 | 30 | 1.91 | 879 | 26 | 30 | 22 | 0 | 91.1876
2024-08-10 14:00 | 42.6 | 27 | 2.19 | 834 | 26 | 30 | 22 | 0 | 80.0804
2024-08-10 15:00 | 43.1 | 26 | 2.91 | 725 | 26 | 30 | 22 | 0 | 57.1874
2024-08-10 16:00 | 42.7 | 28 | 3.4 | 570 | 26 | 30 | 22 | 0 | 34.6338
2024-08-10 17:00 | 42 | 29 | 5.1 | 299 | 26 | 30 | 22 | 0 | 0
2024-08-10 18:00 | 40.7 | 32 | 6.2 | 181 | 26 | 30 | 22 | 0 | 0
2024-08-10 19:00 | 38.8 | 37 | 6.6 | 37 | 26 | 30 | 22 | 0 | 0
2024-08-10 20:00 | 36.4 | 46 | 6.52 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-10 21:00 | 34.8 | 53 | 5.21 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-10 22:00 | 33.8 | 58 | 4.96 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-10 23:00 | 33.1 | 58 | 4.55 | 0 | 26 | 30 | 22 | 1.4804 | 0
2024-08-11 | 32.3 | 61 | 5.32 | 0 | 26 | 30 | 22 | 4.1689 | 0
2024-08-11 01:00 | 31.8 | 62 | 5.55 | 0 | 26 | 30 | 22 | 8.9993 | 0
2024-08-11 02:00 | 31.5 | 62 | 5.31 | 0 | 26 | 30 | 22 | 13.5585 | 0
2024-08-11 03:00 | 31.1 | 64 | 4.96 | 0 | 26 | 30 | 22 | 13.7089 | 0
2024-08-11 04:00 | 30.8 | 66 | 4.84 | 0 | 26 | 30 | 22 | 12.7437 | 0
2024-08-11 05:00 | 30.9 | 67 | 4.95 | 0 | 26 | 30 | 22 | 8.6981 | 0
2024-08-11 06:00 | 30.4 | 70 | 4.83 | 0 | 26 | 30 | 22 | 8.4364 | 0
2024-08-11 07:00 | 31.2 | 67 | 4.46 | 57 | 26 | 30 | 22 | 0 | 0
2024-08-11 08:00 | 34.9 | 49 | 3.05 | 219 | 26 | 30 | 22 | 0 | 0
2024-08-11 09:00 | 37.7 | 37 | 4.37 | 420 | 26 | 30 | 22 | 0 | 0
2024-08-11 10:00 | 39.5 | 33 | 4.6 | 610 | 26 | 30 | 22 | 0 | 12.5303
2024-08-11 11:00 | 41 | 30 | 3.79 | 750 | 26 | 30 | 22 | 0 | 45.1542
2024-08-11 12:00 | 42.2 | 28 | 2.73 | 855 | 26 | 30 | 22 | 0 | 75.8236
2024-08-11 13:00 | 42.7 | 27 | 1.65 | 862 | 26 | 30 | 22 | 0 | 92.2964
2024-08-11 14:00 | 42.3 | 29 | 3.69 | 668 | 26 | 30 | 22 | 0 | 44.8969
2024-08-11 15:00 | 42.1 | 31 | 4.96 | 626 | 26 | 30 | 22 | 0 | 35.4184
2024-08-11 16:00 | 41.5 | 34 | 5.78 | 541 | 26 | 30 | 22 | 0 | 25.6733
2024-08-11 17:00 | 39.6 | 39 | 5.6 | 375 | 26 | 30 | 22 | 0 | 0.2443
2024-08-11 18:00 | 38.3 | 44 | 4.7 | 178 | 26 | 30 | 22 | 0 | 0
2024-08-11 19:00 | 36.8 | 52 | 4.24 | 36 | 26 | 30 | 22 | 0 | 0
2024-08-11 20:00 | 36.1 | 57 | 3.51 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-11 21:00 | 35.6 | 60 | 2.86 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-11 22:00 | 35.4 | 58 | 2.92 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-11 23:00 | 35.2 | 55 | 2.42 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-12 | 34.4 | 58 | 2.11 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-12 01:00 | 33.7 | 61 | 2.2 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-12 02:00 | 33.2 | 64 | 2.16 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-12 03:00 | 32.7 | 66 | 2.86 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-12 04:00 | 32.2 | 70 | 2.76 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-12 05:00 | 32.6 | 67 | 2.59 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-12 06:00 | 32.4 | 63 | 2.21 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-12 07:00 | 33.5 | 55 | 1.61 | 58 | 26 | 30 | 22 | 0 | 0
2024-08-12 08:00 | 35.9 | 45 | 2.04 | 221 | 26 | 30 | 22 | 0 | 0
2024-08-12 09:00 | 39.1 | 35 | 2.69 | 426 | 26 | 30 | 22 | 0 | 12.0054
2024-08-12 10:00 | 41.5 | 29 | 4.3 | 621 | 26 | 30 | 22 | 0 | 23.8237
2024-08-12 11:00 | 43.2 | 25 | 3.58 | 775 | 26 | 30 | 22 | 0 | 53.3182
2024-08-12 12:00 | 44.1 | 23 | 2.53 | 871 | 26 | 30 | 22 | 0 | 79.5967
2024-08-12 13:00 | 43.3 | 30 | 4.7 | 899 | 26 | 30 | 22 | 0 | 84.624
2024-08-12 14:00 | 42.1 | 34 | 6.89 | 853 | 26 | 30 | 22 | 0 | 72.4305
2024-08-12 15:00 | 41.4 | 36 | 6.72 | 744 | 26 | 30 | 22 | 0 | 58.2423
2024-08-12 16:00 | 40.7 | 38 | 6.54 | 582 | 26 | 30 | 22 | 0 | 36.3495
2024-08-12 17:00 | 38.9 | 42 | 5.5 | 383 | 26 | 30 | 22 | 0 | 4.8094
2024-08-12 18:00 | 38 | 47 | 4.48 | 182 | 26 | 30 | 22 | 0 | 0
2024-08-12 19:00 | 36.3 | 55 | 3.77 | 35 | 26 | 30 | 22 | 0 | 0
2024-08-12 20:00 | 35.6 | 62 | 3.55 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-12 21:00 | 35.6 | 57 | 2.38 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-12 22:00 | 35.4 | 57 | 2.3 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-12 23:00 | 34.7 | 59 | 1.63 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-13 | 34 | 61 | 1.73 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-13 01:00 | 33.1 | 66 | 1.3 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-13 02:00 | 32.7 | 64 | 1.92 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-13 03:00 | 32.4 | 65 | 2.78 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-13 04:00 | 32 | 71 | 3.11 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-13 05:00 | 33 | 59 | 3.04 | 0 | 26 | 30 | 22 | 0.9228 | 0
2024-08-13 06:00 | 32.5 | 67 | 3.77 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-13 07:00 | 33.5 | 64 | 4.63 | 57 | 26 | 30 | 22 | 0 | 0
2024-08-13 08:00 | 37.4 | 39 | 4.44 | 219 | 26 | 30 | 22 | 0 | 0
2024-08-13 09:00 | 39 | 33 | 5.4 | 423 | 26 | 30 | 22 | 0 | 0
2024-08-13 10:00 | 40.8 | 30 | 5.1 | 616 | 26 | 30 | 22 | 0 | 11.3351
2024-08-13 11:00 | 42.5 | 27 | 4.79 | 768 | 26 | 30 | 22 | 0 | 41.4354
2024-08-13 12:00 | 43.9 | 24 | 4.11 | 864 | 26 | 30 | 22 | 0 | 62.3775
2024-08-13 13:00 | 44.9 | 23 | 3.26 | 893 | 26 | 30 | 22 | 0 | 80.5643
2024-08-13 14:00 | 44.6 | 26 | 4.49 | 852 | 26 | 30 | 22 | 0 | 75.3137
2024-08-13 15:00 | 43.2 | 30 | 7 | 741 | 26 | 30 | 22 | 0 | 50.0735
2024-08-13 16:00 | 41.7 | 34 | 7.16 | 576 | 26 | 30 | 22 | 0 | 26.9528
2024-08-13 17:00 | 40.2 | 36 | 6 | 381 | 26 | 30 | 22 | 0 | 0
2024-08-13 18:00 | 38.2 | 48 | 5.07 | 178 | 26 | 30 | 22 | 0 | 0
2024-08-13 19:00 | 36.9 | 54 | 3.81 | 34 | 26 | 30 | 22 | 0 | 0
2024-08-13 20:00 | 36.6 | 54 | 3.52 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-13 21:00 | 37.3 | 44 | 2.44 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-13 22:00 | 37 | 45 | 1.93 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-13 23:00 | 36.1 | 50 | 2.2 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-14 | 35 | 57 | 3.1 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-14 01:00 | 34.3 | 60 | 3.74 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-14 02:00 | 33.6 | 64 | 3.51 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-14 03:00 | 33.2 | 67 | 3.7 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-14 04:00 | 32.3 | 71 | 4.2 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-14 05:00 | 31.8 | 73 | 5.24 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-14 06:00 | 31.9 | 73 | 4.75 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-14 07:00 | 34.6 | 56 | 4.05 | 55 | 26 | 30 | 22 | 0 | 0
2024-08-14 08:00 | 37 | 39 | 5.02 | 217 | 26 | 30 | 22 | 0 | 0
2024-08-14 09:00 | 38.5 | 36 | 5.91 | 419 | 26 | 30 | 22 | 0 | 0
2024-08-14 10:00 | 40.2 | 32 | 6.08 | 611 | 26 | 30 | 22 | 0 | 3.3434
2024-08-14 11:00 | 41.9 | 29 | 5.5 | 765 | 26 | 30 | 22 | 0 | 37.2902
2024-08-14 12:00 | 43.3 | 26 | 4.23 | 861 | 26 | 30 | 22 | 0 | 63.68
2024-08-14 13:00 | 44.4 | 23 | 3.04 | 889 | 26 | 30 | 22 | 0 | 78.0123
2024-08-14 14:00 | 43.9 | 26 | 3.97 | 847 | 26 | 30 | 22 | 0 | 70.7282
2024-08-14 15:00 | 42.5 | 31 | 7.08 | 737 | 26 | 30 | 22 | 0 | 43.9074
2024-08-14 16:00 | 41.4 | 35 | 6.84 | 572 | 26 | 30 | 22 | 0 | 28.6499
2024-08-14 17:00 | 40.4 | 39 | 5.24 | 376 | 26 | 30 | 22 | 0 | 14.3546
2024-08-14 18:00 | 39.1 | 43 | 4.9 | 177 | 26 | 30 | 22 | 0 | 0
2024-08-14 19:00 | 38.2 | 46 | 3.26 | 33 | 26 | 30 | 22 | 0 | 0
2024-08-14 20:00 | 37.9 | 49 | 3.1 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-14 21:00 | 37.5 | 53 | 1.68 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-14 22:00 | 36.9 | 53 | 1.61 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-14 23:00 | 36.3 | 52 | 3.52 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-15 | 35.6 | 55 | 3.85 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-15 01:00 | 35 | 58 | 3.48 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-15 02:00 | 34.2 | 61 | 3.54 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-15 03:00 | 33.6 | 63 | 3.26 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-15 04:00 | 33.4 | 64 | 2.21 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-15 05:00 | 33.6 | 62 | 2.67 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-15 06:00 | 33.2 | 63 | 2.43 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-15 07:00 | 34.4 | 57 | 2.02 | 55 | 26 | 30 | 22 | 0 | 0
2024-08-15 08:00 | 37.4 | 38 | 2.5 | 217 | 26 | 30 | 22 | 0 | 0
2024-08-15 09:00 | 39.2 | 32 | 3.59 | 422 | 26 | 30 | 22 | 0 | 0
2024-08-15 10:00 | 40.9 | 29 | 4.38 | 615 | 26 | 30 | 22 | 0 | 15.3793
2024-08-15 11:00 | 42.6 | 26 | 4.34 | 770 | 26 | 30 | 22 | 0 | 42.5514
2024-08-15 12:00 | 44.1 | 23 | 3.97 | 867 | 26 | 30 | 22 | 0 | 61.6426
2024-08-15 13:00 | 44.5 | 24 | 4.79 | 895 | 26 | 30 | 22 | 0 | 67.0031
2024-08-15 14:00 | 42.6 | 33 | 7.22 | 851 | 26 | 30 | 22 | 0 | 73.4096
2024-08-15 15:00 | 41.2 | 37 | 7.07 | 742 | 26 | 30 | 22 | 0 | 59.0711
2024-08-15 16:00 | 40.6 | 38 | 6.79 | 580 | 26 | 30 | 22 | 0 | 33.3383
2024-08-15 17:00 | 39.5 | 39 | 5.39 | 378 | 26 | 30 | 22 | 0 | 0.4095
2024-08-15 18:00 | 38.6 | 42 | 4.7 | 177 | 26 | 30 | 22 | 0 | 0
2024-08-15 19:00 | 37.4 | 44 | 3.41 | 32 | 26 | 30 | 22 | 0 | 0
2024-08-15 20:00 | 35.4 | 62 | 3.83 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-15 21:00 | 34.5 | 71 | 2.75 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-15 22:00 | 34.1 | 75 | 2.1 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-15 23:00 | 33.6 | 77 | 1.4 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-16 | 33.1 | 80 | 0.89 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-16 01:00 | 32.5 | 82 | 1.28 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-16 02:00 | 31.9 | 84 | 1.17 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-16 03:00 | 31.4 | 86 | 1.13 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-16 04:00 | 30.9 | 87 | 1.75 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-16 05:00 | 31.1 | 85 | 0.85 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-16 06:00 | 30.7 | 85 | 1.36 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-16 07:00 | 31.4 | 77 | 0.89 | 56 | 26 | 30 | 22 | 0 | 0
2024-08-16 08:00 | 33.3 | 61 | 1.25 | 223 | 26 | 30 | 22 | 0 | 3.8312
2024-08-16 09:00 | 35.8 | 47 | 1 | 430 | 26 | 30 | 22 | 0 | 34.7317
2024-08-16 10:00 | 38.2 | 38 | 1 | 628 | 26 | 30 | 22 | 0 | 63.8237
2024-08-16 11:00 | 40 | 32 | 2.61 | 784 | 26 | 30 | 22 | 0 | 60.9243
2024-08-16 12:00 | 40.4 | 35 | 3.92 | 881 | 26 | 30 | 22 | 0 | 74.0246
2024-08-16 13:00 | 40.5 | 36 | 4.82 | 908 | 26 | 30 | 22 | 0 | 76.3451
2024-08-16 14:00 | 40.1 | 36 | 5.3 | 865 | 26 | 30 | 22 | 0 | 61.7395
2024-08-16 15:00 | 39.7 | 37 | 4.81 | 756 | 26 | 30 | 22 | 0 | 49.4525
2024-08-16 16:00 | 38.8 | 40 | 4.83 | 589 | 26 | 30 | 22 | 0 | 26.9443
2024-08-16 17:00 | 37.9 | 40 | 4.43 | 385 | 26 | 30 | 22 | 0 | 0
2024-08-16 18:00 | 36.8 | 45 | 3.9 | 180 | 26 | 30 | 22 | 0 | 0
2024-08-16 19:00 | 35.2 | 54 | 3.64 | 32 | 26 | 30 | 22 | 0 | 0
2024-08-16 20:00 | 34.2 | 63 | 2.94 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-16 21:00 | 33.5 | 70 | 2.43 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-16 22:00 | 33 | 74 | 2.52 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-16 23:00 | 32.8 | 75 | 2.28 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-17 | 32.6 | 76 | 1.99 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-17 01:00 | 32.3 | 78 | 1.68 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-17 02:00 | 31.9 | 80 | 1.7 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-17 03:00 | 31.7 | 77 | 2.28 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-17 04:00 | 31.3 | 74 | 3.69 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-17 05:00 | 30.6 | 77 | 6.61 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-17 06:00 | 30.3 | 76 | 6.94 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-17 07:00 | 31.2 | 72 | 7.71 | 52 | 26 | 30 | 22 | 0 | 0
2024-08-17 08:00 | 33.4 | 63 | 6.71 | 212 | 26 | 30 | 22 | 0 | 0
2024-08-17 09:00 | 36.3 | 53 | 7.02 | 404 | 26 | 30 | 22 | 0 | 4.7476
2024-08-17 10:00 | 39.3 | 41 | 6.51 | 618 | 26 | 30 | 22 | 0 | 33.1332
2024-08-17 11:00 | 41 | 37 | 5.41 | 766 | 26 | 30 | 22 | 0 | 65.6573
2024-08-17 12:00 | 42.3 | 35 | 5.38 | 854 | 26 | 30 | 22 | 0 | 87.0815
2024-08-17 13:00 | 43.1 | 33 | 5.91 | 875 | 26 | 30 | 22 | 0 | 89.3971
2024-08-17 14:00 | 43.5 | 32 | 5.4 | 843 | 26 | 30 | 22 | 0 | 87.1872
2024-08-17 15:00 | 44.4 | 29 | 4.41 | 734 | 26 | 30 | 22 | 0 | 72.849
2024-08-17 16:00 | 43.9 | 31 | 6.5 | 570 | 26 | 30 | 22 | 0 | 47.0577
2024-08-17 17:00 | 39.8 | 41 | 8.42 | 341 | 26 | 30 | 22 | 0 | 0
2024-08-17 18:00 | 38.2 | 43 | 8.52 | 169 | 26 | 30 | 22 | 0 | 0
2024-08-17 19:00 | 36.3 | 48 | 7.6 | 30 | 26 | 30 | 22 | 0 | 0
2024-08-17 20:00 | 35 | 55 | 6.93 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-17 21:00 | 33.8 | 59 | 7.53 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-17 22:00 | 32.8 | 64 | 7.92 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-17 23:00 | 32.2 | 66 | 7.3 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-18 | 31.9 | 66 | 6.33 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-18 01:00 | 31.7 | 66 | 5.7 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-18 02:00 | 31.2 | 68 | 6.28 | 0 | 26 | 30 | 22 | 0.2908 | 0
2024-08-18 03:00 | 31.1 | 66 | 6.84 | 0 | 26 | 30 | 22 | 8.35 | 0
2024-08-18 04:00 | 30.8 | 70 | 7.02 | 0 | 26 | 30 | 22 | 0.5687 | 0
2024-08-18 05:00 | 31.1 | 69 | 6.99 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-18 06:00 | 30.7 | 70 | 7.48 | 0 | 26 | 30 | 22 | 2.1696 | 0
2024-08-18 07:00 | 31.4 | 67 | 9.92 | 52 | 26 | 30 | 22 | 0 | 0
2024-08-18 08:00 | 32.9 | 62 | 7.62 | 201 | 26 | 30 | 22 | 0 | 0
2024-08-18 09:00 | 35.3 | 53 | 7.93 | 404 | 26 | 30 | 22 | 0 | 0
2024-08-18 10:00 | 37.3 | 46 | 7.52 | 582 | 26 | 30 | 22 | 0 | 12.0954
2024-08-18 11:00 | 38.8 | 42 | 7.18 | 756 | 26 | 30 | 22 | 0 | 44.8329
2024-08-18 12:00 | 40.2 | 38 | 6.11 | 840 | 26 | 30 | 22 | 0 | 64.7691
2024-08-18 13:00 | 41.3 | 36 | 5.17 | 880 | 26 | 30 | 22 | 0 | 81.747
2024-08-18 14:00 | 42 | 34 | 4.64 | 837 | 26 | 30 | 22 | 0 | 78.8855
2024-08-18 15:00 | 42.5 | 32 | 3.91 | 727 | 26 | 30 | 22 | 0 | 65.7138
2024-08-18 16:00 | 42.8 | 32 | 3.85 | 555 | 26 | 30 | 22 | 0 | 46.3726
2024-08-18 17:00 | 40.2 | 39 | 7.88 | 360 | 26 | 30 | 22 | 0 | 0
2024-08-18 18:00 | 38.3 | 43 | 8.2 | 166 | 26 | 30 | 22 | 0 | 0
2024-08-18 19:00 | 36.6 | 47 | 8 | 28 | 26 | 30 | 22 | 0 | 0
2024-08-18 20:00 | 34.3 | 58 | 7.78 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-18 21:00 | 32.9 | 63 | 7.42 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-18 22:00 | 33.2 | 60 | 6.93 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-18 23:00 | 32.4 | 62 | 6.6 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-19 | 32.4 | 62 | 6.01 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-19 01:00 | 32 | 65 | 5.5 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-19 02:00 | 32 | 65 | 6.22 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-19 03:00 | 31.8 | 67 | 6.81 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-19 04:00 | 31.7 | 67 | 6.48 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-19 05:00 | 31.8 | 63 | 5.35 | 0 | 26 | 30 | 22 | 6.0223 | 0
2024-08-19 06:00 | 31.4 | 64 | 4.74 | 0 | 26 | 30 | 22 | 9.1981 | 0
2024-08-19 07:00 | 32 | 61 | 4.55 | 49 | 26 | 30 | 22 | 1.9564 | 0
2024-08-19 08:00 | 33.5 | 55 | 4.06 | 115 | 26 | 30 | 22 | 0 | 0
2024-08-19 09:00 | 35.7 | 48 | 3.83 | 337 | 26 | 30 | 22 | 0 | 0
2024-08-19 10:00 | 37.3 | 43 | 3.73 | 506 | 26 | 30 | 22 | 0 | 16.5281
2024-08-19 11:00 | 38.7 | 40 | 3.2 | 693 | 26 | 30 | 22 | 0 | 53.0029
2024-08-19 12:00 | 39.8 | 37 | 2.65 | 782 | 26 | 30 | 22 | 0 | 72.3989
2024-08-19 13:00 | 40.8 | 35 | 2.21 | 848 | 26 | 30 | 22 | 0 | 89.1185
2024-08-19 14:00 | 41.6 | 33 | 1.75 | 836 | 26 | 30 | 22 | 0 | 93.7855
2024-08-19 15:00 | 41.8 | 34 | 2.24 | 724 | 26 | 30 | 22 | 0 | 77.8476
2024-08-19 16:00 | 41.7 | 35 | 4.03 | 559 | 26 | 30 | 22 | 0 | 45.2964
2024-08-19 17:00 | 40.2 | 40 | 3.9 | 360 | 26 | 30 | 22 | 0 | 20.2761
2024-08-19 18:00 | 39.1 | 43 | 3.91 | 164 | 26 | 30 | 22 | 0 | 0
2024-08-19 19:00 | 38.3 | 44 | 3.89 | 26 | 26 | 30 | 22 | 0 | 0
2024-08-19 20:00 | 37.1 | 46 | 5.17 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-19 21:00 | 35.9 | 49 | 4.87 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-19 22:00 | 35.2 | 51 | 3.61 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-19 23:00 | 34.8 | 53 | 2.6 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-20 | 34.3 | 54 | 2.6 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-20 01:00 | 32.9 | 59 | 4.7 | 0 | 26 | 30 | 22 | 1.3801 | 0
2024-08-20 02:00 | 31.5 | 67 | 5.82 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-20 03:00 | 31.7 | 65 | 5.62 | 0 | 26 | 30 | 22 | 1.5421 | 0
2024-08-20 04:00 | 31.2 | 68 | 5.7 | 0 | 26 | 30 | 22 | 0.8315 | 0
2024-08-20 05:00 | 32 | 66 | 3.1 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-20 06:00 | 32.3 | 65 | 1.55 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-20 07:00 | 33.5 | 60 | 0.78 | 50 | 26 | 30 | 22 | 0 | 0
2024-08-20 08:00 | 36 | 45 | 2.82 | 204 | 26 | 30 | 22 | 0 | 0
2024-08-20 09:00 | 37.4 | 38 | 4.52 | 411 | 26 | 30 | 22 | 0 | 0
2024-08-20 10:00 | 38.4 | 37 | 4.16 | 606 | 26 | 30 | 22 | 0 | 18.6705
2024-08-20 11:00 | 39.5 | 35 | 3.18 | 756 | 26 | 30 | 22 | 0 | 54.5639
2024-08-20 12:00 | 40.5 | 33 | 2.12 | 849 | 26 | 30 | 22 | 0 | 82.7735
2024-08-20 13:00 | 41.1 | 32 | 1.32 | 857 | 26 | 30 | 22 | 0 | 96.8772
2024-08-20 14:00 | 40.8 | 35 | 3.83 | 827 | 26 | 30 | 22 | 0 | 72.0873
2024-08-20 15:00 | 40.2 | 37 | 5.17 | 723 | 26 | 30 | 22 | 0 | 49.4422
2024-08-20 16:00 | 39.1 | 41 | 6.16 | 558 | 26 | 30 | 22 | 0 | 23.4194
2024-08-20 17:00 | 38.1 | 44 | 5.82 | 354 | 26 | 30 | 22 | 0 | 0
2024-08-20 18:00 | 37.2 | 48 | 5.6 | 160 | 26 | 30 | 22 | 0 | 0
2024-08-20 19:00 | 36 | 55 | 5.12 | 26 | 26 | 30 | 22 | 0 | 0
2024-08-20 20:00 | 35.8 | 50 | 4.82 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-20 21:00 | 34 | 56 | 5.92 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-20 22:00 | 32.7 | 62 | 6.5 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-20 23:00 | 32.2 | 61 | 7.09 | 0 | 26 | 30 | 22 | 5.1581 | 0
2024-08-21 | 32.3 | 59 | 6.59 | 0 | 26 | 30 | 22 | 10.5657 | 0
2024-08-21 01:00 | 31.9 | 60 | 5.53 | 0 | 26 | 30 | 22 | 13.4536 | 0
2024-08-21 02:00 | 31.7 | 60 | 4.75 | 0 | 26 | 30 | 22 | 15.5968 | 0
2024-08-21 03:00 | 31.4 | 62 | 4.9 | 0 | 26 | 30 | 22 | 14.6542 | 0
2024-08-21 04:00 | 31.4 | 62 | 4.11 | 0 | 26 | 30 | 22 | 13.6967 | 0
2024-08-21 05:00 | 32.2 | 53 | 4.19 | 0 | 26 | 30 | 22 | 26.0263 | 0
2024-08-21 06:00 | 31.4 | 57 | 4.28 | 0 | 26 | 30 | 22 | 26.2003 | 0
2024-08-21 07:00 | 31.2 | 60 | 5.22 | 51 | 26 | 30 | 22 | 16.6906 | 0
2024-08-21 08:00 | 32.1 | 57 | 5.16 | 214 | 26 | 30 | 22 | 0 | 0
2024-08-21 09:00 | 33.5 | 53 | 4.66 | 418 | 26 | 30 | 22 | 0 | 0
2024-08-21 10:00 | 35.2 | 48 | 4.27 | 611 | 26 | 30 | 22 | 0 | 15.2732
2024-08-21 11:00 | 37 | 44 | 3.93 | 764 | 26 | 30 | 22 | 0 | 49.0866
2024-08-21 12:00 | 38.6 | 39 | 4.1 | 861 | 26 | 30 | 22 | 0 | 63.174
2024-08-21 13:00 | 39.9 | 36 | 4.6 | 886 | 26 | 30 | 22 | 0 | 67.0572
2024-08-21 14:00 | 40.5 | 34 | 3.8 | 840 | 26 | 30 | 22 | 0 | 66.8965
2024-08-21 15:00 | 40.1 | 33 | 2.8 | 729 | 26 | 30 | 22 | 0 | 54.8671
2024-08-21 16:00 | 39.8 | 34 | 3.41 | 563 | 26 | 30 | 22 | 0 | 25.8147
2024-08-21 17:00 | 39 | 36 | 3.48 | 364 | 26 | 30 | 22 | 0 | 0
2024-08-21 18:00 | 37.9 | 37 | 4.56 | 164 | 26 | 30 | 22 | 0 | 0
2024-08-21 19:00 | 36.7 | 41 | 4.87 | 25 | 26 | 30 | 22 | 3.5571 | 0
2024-08-21 20:00 | 35.7 | 44 | 5.15 | 0 | 26 | 30 | 22 | 9.8159 | 0
2024-08-21 21:00 | 34.6 | 46 | 5.48 | 0 | 26 | 30 | 22 | 18.5803 | 0
2024-08-21 22:00 | 33.6 | 50 | 5.03 | 0 | 26 | 30 | 22 | 18.5977 | 0
2024-08-21 23:00 | 32.7 | 52 | 5.09 | 0 | 26 | 30 | 22 | 25.0273 | 0
2024-08-22 | 31.9 | 56 | 4.85 | 0 | 26 | 30 | 22 | 23.917 | 0
2024-08-22 01:00 | 31.2 | 60 | 4.71 | 0 | 26 | 30 | 22 | 22.4375 | 0
2024-08-22 02:00 | 30.6 | 62 | 4.9 | 0 | 26 | 30 | 22 | 26.0486 | 0
2024-08-22 03:00 | 31.3 | 59 | 3.47 | 0 | 26 | 30 | 22 | 20.2508 | 0
2024-08-22 04:00 | 32.8 | 49 | 5.01 | 0 | 26 | 30 | 22 | 32.3571 | 0
2024-08-22 05:00 | 32.2 | 53 | 4.43 | 0 | 26 | 30 | 22 | 26.847 | 0
2024-08-22 06:00 | 32.3 | 52 | 4.93 | 0 | 26 | 30 | 22 | 29.9771 | 0
2024-08-22 07:00 | 32.5 | 53 | 4.65 | 51 | 26 | 30 | 22 | 16.7875 | 0
2024-08-22 08:00 | 33.3 | 52 | 5.4 | 214 | 26 | 30 | 22 | 0 | 0
2024-08-22 09:00 | 34.7 | 48 | 4.95 | 418 | 26 | 30 | 22 | 0 | 0
2024-08-22 10:00 | 36.1 | 44 | 3.64 | 612 | 26 | 30 | 22 | 0 | 21.0721
2024-08-22 11:00 | 37.5 | 40 | 2.61 | 765 | 26 | 30 | 22 | 0 | 57.3478
2024-08-22 12:00 | 38.8 | 36 | 2.48 | 858 | 26 | 30 | 22 | 0 | 73.0099
2024-08-22 13:00 | 39.8 | 34 | 2.41 | 885 | 26 | 30 | 22 | 0 | 80.8612
2024-08-22 14:00 | 39 | 40 | 5.24 | 838 | 26 | 30 | 22 | 0 | 60.5428
2024-08-22 15:00 | 37.8 | 44 | 6.19 | 707 | 26 | 30 | 22 | 0 | 35.8971
2024-08-22 16:00 | 37.6 | 45 | 5.35 | 558 | 26 | 30 | 22 | 0 | 22.1118
2024-08-22 17:00 | 36.6 | 46 | 4.72 | 211 | 26 | 30 | 22 | 0 | 0
2024-08-22 18:00 | 35.9 | 50 | 4.61 | 125 | 26 | 30 | 22 | 0 | 0
2024-08-22 19:00 | 34.7 | 56 | 3.38 | 22 | 26 | 30 | 22 | 0 | 0
2024-08-22 20:00 | 34.4 | 58 | 2.6 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-22 21:00 | 34.1 | 59 | 2.3 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-22 22:00 | 33.9 | 59 | 1.96 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-22 23:00 | 33.5 | 61 | 2.06 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-23 | 32.9 | 66 | 2.31 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-23 01:00 | 32.3 | 74 | 2.95 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-23 02:00 | 31.9 | 75 | 3.4 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-23 03:00 | 31.6 | 72 | 2.84 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-23 04:00 | 31.3 | 71 | 2.51 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-23 05:00 | 31.1 | 72 | 2.06 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-23 06:00 | 31 | 68 | 2.2 | 0 | 26 | 30 | 22 | 4.8199 | 0
2024-08-23 07:00 | 31.8 | 61 | 2.09 | 50 | 26 | 30 | 22 | 1.474 | 0
2024-08-23 08:00 | 33.9 | 52 | 2.26 | 213 | 26 | 30 | 22 | 0 | 0
2024-08-23 09:00 | 36.6 | 41 | 2.1 | 409 | 26 | 30 | 22 | 0 | 10.8637
2024-08-23 10:00 | 38.2 | 36 | 1.8 | 571 | 26 | 30 | 22 | 0 | 39.35
2024-08-23 11:00 | 39.6 | 33 | 1.44 | 749 | 26 | 30 | 22 | 0 | 72.9215
2024-08-23 12:00 | 40.8 | 30 | 2.28 | 851 | 26 | 30 | 22 | 0 | 75.54
2024-08-23 13:00 | 41.2 | 31 | 4.26 | 888 | 26 | 30 | 22 | 0 | 65.3031
2024-08-23 14:00 | 40.9 | 32 | 5.73 | 841 | 26 | 30 | 22 | 0 | 47.3226
2024-08-23 15:00 | 40.2 | 32 | 6.03 | 730 | 26 | 30 | 22 | 0 | 19.8404
2024-08-23 16:00 | 39.3 | 36 | 5.64 | 564 | 26 | 30 | 22 | 0 | 7.0855
2024-08-23 17:00 | 37.4 | 45 | 6.31 | 362 | 26 | 30 | 22 | 0 | 0
2024-08-23 18:00 | 35.8 | 52 | 5.5 | 162 | 26 | 30 | 22 | 0 | 0
2024-08-23 19:00 | 34.4 | 63 | 5.06 | 23 | 26 | 30 | 22 | 0 | 0
2024-08-23 20:00 | 33.7 | 71 | 4.95 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-23 21:00 | 33.6 | 69 | 2.18 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-23 22:00 | 33.2 | 69 | 1.02 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-23 23:00 | 32.8 | 71 | 0.92 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-24 | 32.4 | 73 | 0.82 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-24 01:00 | 31.8 | 78 | 1.96 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-24 02:00 | 31.4 | 83 | 2.42 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-24 03:00 | 31 | 86 | 2.51 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-24 04:00 | 30.7 | 87 | 2.28 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-24 05:00 | 30.9 | 80 | 1.78 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-24 06:00 | 30.7 | 79 | 1.94 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-24 07:00 | 31.4 | 74 | 1.9 | 50 | 26 | 30 | 22 | 0 | 0
2024-08-24 08:00 | 34.1 | 57 | 1.64 | 214 | 26 | 30 | 22 | 0 | 0
2024-08-24 09:00 | 37.6 | 34 | 5.3 | 423 | 26 | 30 | 22 | 0 | 0
2024-08-24 10:00 | 39.6 | 30 | 5.67 | 620 | 26 | 30 | 22 | 0 | 0
2024-08-24 11:00 | 41.2 | 27 | 4.88 | 773 | 26 | 30 | 22 | 0 | 25.7757
2024-08-24 12:00 | 42.2 | 25 | 3.19 | 866 | 26 | 30 | 22 | 0 | 61.1131
2024-08-24 13:00 | 42 | 29 | 3.4 | 886 | 26 | 30 | 22 | 0 | 74.1322
2024-08-24 14:00 | 41.4 | 32 | 5.73 | 842 | 26 | 30 | 22 | 0 | 54.6291
2024-08-24 15:00 | 40.7 | 34 | 6.14 | 714 | 26 | 30 | 22 | 0 | 34.6579
2024-08-24 16:00 | 39.9 | 36 | 5.32 | 520 | 26 | 30 | 22 | 0 | 12.1873
2024-08-24 17:00 | 39 | 38 | 4.49 | 339 | 26 | 30 | 22 | 0 | 0
2024-08-24 18:00 | 37.8 | 41 | 3.28 | 144 | 26 | 30 | 22 | 0 | 0
2024-08-24 19:00 | 37 | 42 | 3.09 | 21 | 26 | 30 | 22 | 0 | 0
2024-08-24 20:00 | 35.7 | 51 | 3.31 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-24 21:00 | 35.2 | 53 | 2.14 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-24 22:00 | 35.2 | 52 | 0.1 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-24 23:00 | 34.7 | 53 | 0.7 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-25 | 34.1 | 52 | 2.04 | 0 | 26 | 30 | 22 | 3.3525 | 0
2024-08-25 01:00 | 33.6 | 53 | 1.75 | 0 | 26 | 30 | 22 | 5.1222 | 0
2024-08-25 02:00 | 33 | 55 | 1.7 | 0 | 26 | 30 | 22 | 6.5782 | 0
2024-08-25 03:00 | 32.1 | 79 | 4.1 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-25 04:00 | 31.7 | 84 | 3 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-25 05:00 | 31.9 | 82 | 2.06 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-25 06:00 | 31.5 | 84 | 2.05 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-25 07:00 | 31.9 | 81 | 2.28 | 50 | 26 | 30 | 22 | 0 | 0
2024-08-25 08:00 | 33.8 | 68 | 2.3 | 215 | 26 | 30 | 22 | 0 | 8.8339
2024-08-25 09:00 | 36.8 | 44 | 3.44 | 425 | 26 | 30 | 22 | 0 | 5.7397
2024-08-25 10:00 | 39.8 | 26 | 4.9 | 624 | 26 | 30 | 22 | 0 | 0
2024-08-25 11:00 | 41.7 | 23 | 4.63 | 784 | 26 | 30 | 22 | 0 | 17.5206
2024-08-25 12:00 | 43.3 | 20 | 4.36 | 880 | 26 | 30 | 22 | 0 | 36.4323
2024-08-25 13:00 | 44 | 19 | 4.42 | 906 | 26 | 30 | 22 | 0 | 41.118
2024-08-25 14:00 | 42.3 | 25 | 7.08 | 858 | 26 | 30 | 22 | 0 | 18.764
2024-08-25 15:00 | 40.9 | 29 | 7.38 | 734 | 26 | 30 | 22 | 0 | 2.7747
2024-08-25 16:00 | 39.3 | 35 | 7.18 | 546 | 26 | 30 | 22 | 0 | 0
2024-08-25 17:00 | 37.3 | 45 | 5.14 | 366 | 26 | 30 | 22 | 0 | 0
2024-08-25 18:00 | 35.2 | 58 | 5.28 | 160 | 26 | 30 | 22 | 0 | 0
2024-08-25 19:00 | 34.2 | 66 | 3.67 | 22 | 26 | 30 | 22 | 0 | 0
2024-08-25 20:00 | 33.7 | 70 | 2.44 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-25 21:00 | 33.3 | 73 | 1.52 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-25 22:00 | 32.6 | 76 | 1.65 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-25 23:00 | 31.8 | 78 | 1.4 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-26 | 31.2 | 81 | 0.64 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-26 01:00 | 30.5 | 85 | 1.12 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-26 02:00 | 30.5 | 84 | 1.8 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-26 03:00 | 30 | 85 | 2.15 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-26 04:00 | 29.5 | 87 | 2.42 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-26 05:00 | 30.7 | 71 | 3.62 | 0 | 26 | 30 | 22 | 2.3165 | 0
2024-08-26 06:00 | 30.5 | 68 | 3.61 | 0 | 26 | 30 | 22 | 11.0578 | 0
2024-08-26 07:00 | 31.6 | 59 | 3.7 | 50 | 26 | 30 | 22 | 10.6881 | 0
2024-08-26 08:00 | 33.7 | 50 | 2.06 | 219 | 26 | 30 | 22 | 0 | 0
2024-08-26 09:00 | 35.5 | 44 | 2.16 | 428 | 26 | 30 | 22 | 0 | 9.6649
2024-08-26 10:00 | 38.1 | 35 | 3.29 | 626 | 26 | 30 | 22 | 0 | 21.9107
2024-08-26 11:00 | 39 | 37 | 4.65 | 781 | 26 | 30 | 22 | 0 | 44.9537
2024-08-26 12:00 | 39.3 | 37 | 5.35 | 873 | 26 | 30 | 22 | 0 | 55.6337
2024-08-26 13:00 | 38.9 | 42 | 5.67 | 898 | 26 | 30 | 22 | 0 | 73.4101
2024-08-26 14:00 | 38.6 | 44 | 5.59 | 850 | 26 | 30 | 22 | 0 | 71.5409
2024-08-26 15:00 | 38 | 49 | 5.46 | 736 | 26 | 30 | 22 | 0 | 68.5109
2024-08-26 16:00 | 37.2 | 54 | 4.89 | 564 | 26 | 30 | 22 | 0 | 53.8139
2024-08-26 17:00 | 36.4 | 55 | 4.34 | 364 | 26 | 30 | 22 | 0 | 19.9257
2024-08-26 18:00 | 35.2 | 61 | 3.26 | 159 | 26 | 30 | 22 | 0 | 0
2024-08-26 19:00 | 34.2 | 67 | 2.59 | 21 | 26 | 30 | 22 | 0 | 0
2024-08-26 20:00 | 33.7 | 70 | 2.56 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-26 21:00 | 33.2 | 73 | 2.55 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-26 22:00 | 32.8 | 76 | 1.71 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-26 23:00 | 32.2 | 79 | 1.7 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-27 | 31.4 | 82 | 2.06 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-27 01:00 | 30.8 | 85 | 1.5 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-27 02:00 | 30.8 | 85 | 1.7 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-27 03:00 | 30.7 | 87 | 2.2 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-27 04:00 | 30.2 | 89 | 2.33 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-27 05:00 | 30 | 85 | 2.5 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-27 06:00 | 29.7 | 84 | 2.5 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-27 07:00 | 30.6 | 78 | 2.26 | 50 | 26 | 30 | 22 | 0 | 0
2024-08-27 08:00 | 33.2 | 64 | 2.08 | 222 | 26 | 30 | 22 | 0 | 0
2024-08-27 09:00 | 36.5 | 48 | 1.94 | 438 | 26 | 30 | 22 | 0 | 29.6054
2024-08-27 10:00 | 39.7 | 33 | 2.62 | 641 | 26 | 30 | 22 | 0 | 41.6959
2024-08-27 11:00 | 42.2 | 25 | 1.94 | 798 | 26 | 30 | 22 | 0 | 70.7702
2024-08-27 12:00 | 42 | 31 | 4.75 | 893 | 26 | 30 | 22 | 0 | 71.6744
2024-08-27 13:00 | 38.9 | 45 | 6.97 | 912 | 26 | 30 | 22 | 0 | 84.4664
2024-08-27 14:00 | 38.5 | 53 | 6 | 860 | 26 | 30 | 22 | 0 | 110.8656
2024-08-27 15:00 | 38.2 | 51 | 6.02 | 740 | 26 | 30 | 22 | 0 | 79.8852
2024-08-27 16:00 | 37.6 | 56 | 5.28 | 573 | 26 | 30 | 22 | 0 | 68.8721
2024-08-27 17:00 | 37.1 | 52 | 5.16 | 366 | 26 | 30 | 22 | 0 | 17.0229
2024-08-27 18:00 | 35.1 | 66 | 4.34 | 159 | 26 | 30 | 22 | 0 | 7.3549
2024-08-27 19:00 | 33.8 | 77 | 3.68 | 20 | 26 | 30 | 22 | 0 | 0
2024-08-27 20:00 | 33 | 84 | 1.75 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-27 21:00 | 32.5 | 88 | 0.45 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-27 22:00 | 32.1 | 88 | 1.49 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-27 23:00 | 31.3 | 92 | 0.5 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-28 | 30.5 | 94 | 1.32 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-28 01:00 | 29.9 | 97 | 2.14 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-28 02:00 | 29.3 | 99 | 1.64 | 0 | 26 | 30 | 22 | 1.2756 | 0
2024-08-28 03:00 | 29.2 | 100 | 2.62 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-28 04:00 | 29.4 | 99 | 2.33 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-28 05:00 | 30.1 | 99 | 2.72 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-28 06:00 | 29.9 | 99 | 2.75 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-28 07:00 | 29.5 | 98 | 3.31 | 37 | 26 | 30 | 22 | 0 | 0
2024-08-28 08:00 | 30.7 | 87 | 3.32 | 176 | 26 | 30 | 22 | 0 | 0
2024-08-28 09:00 | 35.1 | 57 | 3.32 | 437 | 26 | 30 | 22 | 0 | 23.7023
2024-08-28 10:00 | 40 | 28 | 2.92 | 642 | 26 | 30 | 22 | 0 | 25.6495
2024-08-28 11:00 | 42.8 | 17 | 1.3 | 803 | 26 | 30 | 22 | 0 | 70.6057
2024-08-28 12:00 | 44.6 | 13 | 0.92 | 904 | 26 | 30 | 22 | 0 | 96.1598
2024-08-28 13:00 | 46 | 11 | 2.47 | 930 | 26 | 30 | 22 | 0 | 59.273
2024-08-28 14:00 | 45 | 16 | 5.94 | 879 | 26 | 30 | 22 | 0 | 10.9824
2024-08-28 15:00 | 41.4 | 29 | 6.96 | 755 | 26 | 30 | 22 | 0 | 16.9108
2024-08-28 16:00 | 40.2 | 34 | 6.36 | 574 | 26 | 30 | 22 | 0 | 6.51
2024-08-28 17:00 | 39.1 | 37 | 5.39 | 361 | 26 | 30 | 22 | 0 | 0
2024-08-28 18:00 | 36.3 | 56 | 5.52 | 157 | 26 | 30 | 22 | 0 | 0
2024-08-28 19:00 | 34.4 | 73 | 4.12 | 19 | 26 | 30 | 22 | 0 | 0
2024-08-28 20:00 | 33.5 | 80 | 1.98 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-28 21:00 | 32.8 | 84 | 0.54 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-28 22:00 | 32.2 | 86 | 0.36 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-28 23:00 | 31.2 | 90 | 1.28 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-29 | 31.7 | 85 | 0.86 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-29 01:00 | 30.7 | 89 | 1.3 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-29 02:00 | 29.8 | 94 | 3.21 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-29 03:00 | 29.1 | 94 | 2.51 | 0 | 26 | 30 | 22 | 0.2734 | 0
2024-08-29 04:00 | 28.6 | 91 | 2.43 | 0 | 26 | 30 | 22 | 2.1294 | 0
2024-08-29 05:00 | 28.9 | 94 | 2.5 | 0 | 26 | 30 | 22 | 0.9843 | 0
2024-08-29 06:00 | 28.6 | 87 | 2.61 | 0 | 26 | 30 | 22 | 1.8528 | 0
2024-08-29 07:00 | 29.6 | 71 | 2.62 | 50 | 26 | 30 | 22 | 7.3519 | 0
2024-08-29 08:00 | 33.4 | 48 | 2.14 | 224 | 26 | 30 | 22 | 0 | 0
2024-08-29 09:00 | 37.4 | 32 | 1.77 | 443 | 26 | 30 | 22 | 0 | 9.6179
2024-08-29 10:00 | 40.3 | 23 | 0.94 | 648 | 26 | 30 | 22 | 0 | 58.1613
2024-08-29 11:00 | 42.5 | 18 | 0.5 | 807 | 26 | 30 | 22 | 0 | 92.3259
2024-08-29 12:00 | 43.9 | 17 | 3.11 | 904 | 26 | 30 | 22 | 0 | 51.504
2024-08-29 13:00 | 42.6 | 24 | 5.59 | 924 | 26 | 30 | 22 | 0 | 40.2817
2024-08-29 14:00 | 41.8 | 26 | 5.45 | 875 | 26 | 30 | 22 | 0 | 35.7611
2024-08-29 15:00 | 40.5 | 35 | 5.03 | 756 | 26 | 30 | 22 | 0 | 49.9059
2024-08-29 16:00 | 39.6 | 41 | 3.96 | 565 | 26 | 30 | 22 | 0 | 43.801
2024-08-29 17:00 | 38.1 | 46 | 4.03 | 365 | 26 | 30 | 22 | 0 | 14.8776
2024-08-29 18:00 | 36.4 | 57 | 4.1 | 156 | 26 | 30 | 22 | 0 | 0
2024-08-29 19:00 | 34.8 | 68 | 2.95 | 18 | 26 | 30 | 22 | 0 | 0
2024-08-29 20:00 | 34.2 | 70 | 2.12 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-29 21:00 | 33.5 | 75 | 3.07 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-29 22:00 | 32.7 | 80 | 3.5 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-29 23:00 | 32.1 | 82 | 3.28 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-30 | 31.5 | 83 | 2.55 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-30 01:00 | 30.6 | 88 | 1.08 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-30 02:00 | 30.2 | 89 | 1.43 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-30 03:00 | 30.1 | 88 | 2.48 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-30 04:00 | 29.2 | 91 | 2.73 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-30 05:00 | 29.8 | 93 | 2.44 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-30 06:00 | 30.2 | 93 | 2.5 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-30 07:00 | 30.3 | 95 | 2.26 | 48 | 26 | 30 | 22 | 0 | 0
2024-08-30 08:00 | 32 | 88 | 2.2 | 214 | 26 | 30 | 22 | 0 | 23.553
2024-08-30 09:00 | 33.6 | 81 | 0.8 | 423 | 26 | 30 | 22 | 0 | 55.6536
2024-08-30 10:00 | 35.4 | 71 | 0.61 | 619 | 26 | 30 | 22 | 0 | 84.3968
2024-08-30 11:00 | 37.2 | 62 | 0.32 | 768 | 26 | 30 | 22 | 0 | 105.7822
2024-08-30 12:00 | 39.1 | 52 | 0.54 | 873 | 26 | 30 | 22 | 0 | 121.8591
2024-08-30 13:00 | 40.7 | 43 | 1.65 | 897 | 26 | 30 | 22 | 0 | 117.9654
2024-08-30 14:00 | 41.1 | 43 | 3.89 | 850 | 26 | 30 | 22 | 0 | 109.6273
2024-08-30 15:00 | 41 | 39 | 4.56 | 735 | 26 | 30 | 22 | 0 | 74.3823
2024-08-30 16:00 | 40.7 | 34 | 4.49 | 567 | 26 | 30 | 22 | 0 | 26.6368
2024-08-30 17:00 | 36.8 | 52 | 4.61 | 361 | 26 | 30 | 22 | 0 | 14.0313
2024-08-30 18:00 | 35 | 65 | 4.98 | 152 | 26 | 30 | 22 | 0 | 0.4614
2024-08-30 19:00 | 34 | 74 | 3.08 | 17 | 26 | 30 | 22 | 0 | 0
2024-08-30 20:00 | 33.5 | 79 | 1.33 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-30 21:00 | 33.4 | 79 | 2.14 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-30 22:00 | 32.7 | 79 | 3.98 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-30 23:00 | 32.1 | 85 | 2.33 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-31 | 32.3 | 88 | 1.27 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-31 01:00 | 32 | 90 | 1.1 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-31 02:00 | 31.7 | 90 | 2.02 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-31 03:00 | 31.3 | 92 | 1.62 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-31 04:00 | 30.6 | 94 | 2.69 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-31 05:00 | 30.7 | 97 | 2.53 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-31 06:00 | 30.4 | 99 | 2.69 | 0 | 26 | 30 | 22 | 0 | 0
2024-08-31 07:00 | 30.9 | 91 | 2.82 | 46 | 26 | 30 | 22 | 0 | 0
2024-08-31 08:00 | 34.7 | 51 | 5.48 | 218 | 26 | 30 | 22 | 0 | 0
2024-08-31 09:00 | 38.5 | 28 | 6.62 | 436 | 26 | 30 | 22 | 0 | 0
2024-08-31 10:00 | 40.5 | 23 | 7.72 | 641 | 26 | 30 | 22 | 0 | 0
2024-08-31 11:00 | 42.5 | 15 | 9.59 | 796 | 26 | 30 | 22 | 0 | 0
2024-08-31 12:00 | 43.4 | 13 | 9.22 | 894 | 26 | 30 | 22 | 0 | 0
2024-08-31 13:00 | 43.9 | 14 | 8.43 | 916 | 26 | 30 | 22 | 0 | 0
2024-08-31 14:00 | 44.1 | 15 | 7.68 | 863 | 26 | 30 | 22 | 0 | 0
2024-08-31 15:00 | 44.1 | 14 | 6.82 | 741 | 26 | 30 | 22 | 0 | 0
2024-08-31 16:00 | 43.6 | 15 | 6.81 | 565 | 26 | 30 | 22 | 0 | 0
2024-08-31 17:00 | 43.4 | 14 | 7.2 | 346 | 26 | 30 | 22 | 17.1407 | 0
2024-08-31 18:00 | 40.1 | 21 | 9.14 | 145 | 26 | 30 | 22 | 49.9922 | 0
2024-08-31 19:00 | 38.9 | 23 | 6.94 | 14 | 26 | 30 | 22 | 61.6649 | 0
2024-08-31 20:00 | 37.1 | 26 | 5.71 | 0 | 26 | 30 | 22 | 63.3801 | 0
2024-08-31 21:00 | 35.4 | 30 | 4.1 | 0 | 26 | 30 | 22 | 54.0425 | 0
2024-08-31 22:00 | 34 | 37 | 4.26 | 0 | 26 | 30 | 22 | 48.9404 | 0
2024-08-31 23:00 | 33.1 | 42 | 3.82 | 0 | 26 | 30 | 22 | 41.7508 | 0
2024-09-01 | 32.1 | 49 | 4.51 | 0 | 26 | 30 | 17 | 39.4665 | 0
2024-09-01 01:00 | 31.5 | 53 | 4.84 | 0 | 26 | 30 | 17 | 37.837 | 0
2024-09-01 02:00 | 31.4 | 51 | 5.64 | 0 | 26 | 30 | 17 | 48.7394 | 0
2024-09-01 03:00 | 30.6 | 55 | 5.19 | 0 | 26 | 30 | 17 | 46.0951 | 0
2024-09-01 04:00 | 30.4 | 46 | 3.92 | 0 | 26 | 30 | 17 | 61.2051 | 0
2024-09-01 05:00 | 30.2 | 61 | 4.51 | 0 | 26 | 30 | 17 | 33.0106 | 0
2024-09-01 06:00 | 29.6 | 67 | 4.61 | 0 | 26 | 30 | 17 | 27.151 | 0
2024-09-01 07:00 | 29.7 | 72 | 5.15 | 47 | 26 | 30 | 17 | 8.0428 | 0
2024-09-01 08:00 | 32.1 | 61 | 5.46 | 217 | 26 | 30 | 17 | 0 | 0
2024-09-01 09:00 | 35 | 47 | 4.74 | 429 | 26 | 30 | 17 | 0 | 0
2024-09-01 10:00 | 37.9 | 31 | 3.5 | 630 | 26 | 30 | 17 | 0 | 4.5239
2024-09-01 11:00 | 39.7 | 23 | 2.33 | 788 | 26 | 30 | 17 | 0 | 39.2211
2024-09-01 12:00 | 41.2 | 21 | 2.26 | 885 | 26 | 30 | 17 | 0 | 58.5176
2024-09-01 13:00 | 42.5 | 20 | 2.28 | 906 | 26 | 30 | 17 | 0 | 66.7415
2024-09-01 14:00 | 43.1 | 18 | 2.11 | 854 | 26 | 30 | 17 | 0 | 61.317
2024-09-01 15:00 | 40.7 | 30 | 7.02 | 734 | 26 | 30 | 17 | 0 | 7.3348
2024-09-01 16:00 | 38.7 | 43 | 7.96 | 555 | 26 | 30 | 17 | 0 | 16.8605
2024-09-01 17:00 | 37 | 46 | 7.17 | 347 | 26 | 30 | 17 | 0 | 0
2024-09-01 18:00 | 35.7 | 50 | 6.2 | 143 | 26 | 30 | 17 | 0 | 0
2024-09-01 19:00 | 34.7 | 56 | 4.79 | 15 | 26 | 30 | 17 | 0 | 0
2024-09-01 20:00 | 34.3 | 58 | 3.71 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-01 21:00 | 33.9 | 59 | 3.47 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-01 22:00 | 33.3 | 58 | 2.77 | 0 | 26 | 30 | 17 | 0.0519 | 0
2024-09-01 23:00 | 32.2 | 56 | 2.89 | 0 | 26 | 30 | 17 | 15.3733 | 0
2024-09-02 | 31 | 58 | 2.82 | 0 | 26 | 30 | 17 | 23.1215 | 0
2024-09-02 01:00 | 30.1 | 61 | 3.48 | 0 | 26 | 30 | 17 | 29.7787 | 0
2024-09-02 02:00 | 29.4 | 60 | 3.27 | 0 | 26 | 30 | 17 | 37.9485 | 0
2024-09-02 03:00 | 29.2 | 59 | 4.68 | 0 | 26 | 30 | 17 | 51.4905 | 0
2024-09-02 04:00 | 29.2 | 58 | 4.67 | 0 | 26 | 30 | 17 | 53.7476 | 0
2024-09-02 05:00 | 29 | 62 | 4.88 | 0 | 26 | 30 | 17 | 48.2646 | 0
2024-09-02 06:00 | 28.9 | 70 | 4.95 | 0 | 26 | 30 | 17 | 30.9936 | 0
2024-09-02 07:00 | 29.8 | 63 | 4.27 | 47 | 26 | 30 | 17 | 26.1961 | 0
2024-09-02 08:00 | 32.3 | 52 | 3.58 | 220 | 26 | 30 | 17 | 0 | 0
2024-09-02 09:00 | 35.7 | 38 | 3.33 | 436 | 26 | 30 | 17 | 0 | 0
2024-09-02 10:00 | 38.4 | 26 | 2.13 | 639 | 26 | 30 | 17 | 0 | 22.0172
2024-09-02 11:00 | 40.1 | 21 | 1.17 | 795 | 26 | 30 | 17 | 0 | 66.9933
2024-09-02 12:00 | 41.9 | 18 | 1.42 | 889 | 26 | 30 | 17 | 0 | 75.9735
2024-09-02 13:00 | 42.6 | 19 | 3.89 | 911 | 26 | 30 | 17 | 0 | 35.5643
2024-09-02 14:00 | 41.7 | 26 | 6.13 | 857 | 26 | 30 | 17 | 0 | 23.8516
2024-09-02 15:00 | 40 | 33 | 7.66 | 732 | 26 | 30 | 17 | 0 | 8.1889
2024-09-02 16:00 | 38.9 | 37 | 7.88 | 529 | 26 | 30 | 17 | 0 | 0
2024-09-02 17:00 | 37.6 | 38 | 6.64 | 348 | 26 | 30 | 17 | 0 | 0
2024-09-02 18:00 | 36.4 | 42 | 6.07 | 141 | 26 | 30 | 17 | 0 | 0
2024-09-02 19:00 | 34.9 | 53 | 4.9 | 14 | 26 | 30 | 17 | 0 | 0
2024-09-02 20:00 | 34.1 | 59 | 3.14 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-02 21:00 | 33.6 | 61 | 2.64 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-02 22:00 | 32.9 | 63 | 2.55 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-02 23:00 | 32.1 | 66 | 2.25 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-03 | 31.2 | 69 | 1.92 | 0 | 26 | 30 | 17 | 1.689 | 0
2024-09-03 01:00 | 30.7 | 72 | 2.55 | 0 | 26 | 30 | 17 | 1.3752 | 0
2024-09-03 02:00 | 30.4 | 77 | 2.91 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-03 03:00 | 30 | 83 | 3.54 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-03 04:00 | 29.6 | 82 | 3.64 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-03 05:00 | 29.9 | 74 | 3.91 | 0 | 26 | 30 | 17 | 6.3581 | 0
2024-09-03 06:00 | 29.6 | 68 | 3.8 | 0 | 26 | 30 | 17 | 22.6326 | 0
2024-09-03 07:00 | 30.2 | 60 | 4.16 | 46 | 26 | 30 | 17 | 27.6538 | 0
2024-09-03 08:00 | 32.7 | 56 | 4.81 | 217 | 26 | 30 | 17 | 0 | 0
2024-09-03 09:00 | 36.7 | 28 | 6.55 | 432 | 26 | 30 | 17 | 7.958 | 0
2024-09-03 10:00 | 38.3 | 30 | 5.95 | 634 | 26 | 30 | 17 | 0 | 0
2024-09-03 11:00 | 40.1 | 27 | 4.43 | 790 | 26 | 30 | 17 | 0 | 20.2699
2024-09-03 12:00 | 41.5 | 23 | 2.82 | 884 | 26 | 30 | 17 | 0 | 55.7555
2024-09-03 13:00 | 42.9 | 18 | 2.61 | 907 | 26 | 30 | 17 | 0 | 56.789
2024-09-03 14:00 | 44 | 14 | 2.92 | 855 | 26 | 30 | 17 | 0 | 36.8246
2024-09-03 15:00 | 42.3 | 23 | 4.3 | 736 | 26 | 30 | 17 | 0 | 20.5867
2024-09-03 16:00 | 38.7 | 41 | 8.05 | 554 | 26 | 30 | 17 | 0 | 4.7638
2024-09-03 17:00 | 37.8 | 43 | 7.07 | 342 | 26 | 30 | 17 | 0 | 0
2024-09-03 18:00 | 36.2 | 46 | 5.77 | 138 | 26 | 30 | 17 | 0 | 0
2024-09-03 19:00 | 35.1 | 52 | 4.61 | 13 | 26 | 30 | 17 | 0 | 0
2024-09-03 20:00 | 34.7 | 55 | 4.08 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-03 21:00 | 34.4 | 53 | 2.72 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-03 22:00 | 33.7 | 47 | 2.6 | 0 | 26 | 30 | 17 | 17.9932 | 0
2024-09-03 23:00 | 32.6 | 47 | 3.21 | 0 | 26 | 30 | 17 | 31.5093 | 0
2024-09-04 | 31.6 | 48 | 3.8 | 0 | 26 | 30 | 17 | 43.2877 | 0
2024-09-04 01:00 | 30.8 | 52 | 3.95 | 0 | 26 | 30 | 17 | 43.8243 | 0
2024-09-04 02:00 | 29.8 | 57 | 3.5 | 0 | 26 | 30 | 17 | 41.0306 | 0
2024-09-04 03:00 | 29 | 59 | 3.78 | 0 | 26 | 30 | 17 | 47.6639 | 0
2024-09-04 04:00 | 29 | 57 | 3.91 | 0 | 26 | 30 | 17 | 52.6671 | 0
2024-09-04 05:00 | 29.3 | 54 | 4.3 | 0 | 26 | 30 | 17 | 58.8229 | 0
2024-09-04 06:00 | 28.9 | 64 | 4.59 | 0 | 26 | 30 | 17 | 43.3745 | 0
2024-09-04 07:00 | 30.2 | 54 | 3.47 | 46 | 26 | 30 | 17 | 36.4012 | 0
2024-09-04 08:00 | 32.6 | 50 | 3.89 | 217 | 26 | 30 | 17 | 0 | 0
2024-09-04 09:00 | 34.3 | 49 | 5.65 | 431 | 26 | 30 | 17 | 0 | 0
2024-09-04 10:00 | 36.4 | 41 | 6.44 | 630 | 26 | 30 | 17 | 0 | 0
2024-09-04 11:00 | 38.2 | 35 | 6.1 | 785 | 26 | 30 | 17 | 0 | 11.0959
2024-09-04 12:00 | 39.8 | 30 | 5 | 880 | 26 | 30 | 17 | 0 | 34.5872
2024-09-04 13:00 | 41 | 26 | 3.82 | 904 | 26 | 30 | 17 | 0 | 49.2797
2024-09-04 14:00 | 42 | 23 | 2.4 | 853 | 26 | 30 | 17 | 0 | 62.6813
2024-09-04 15:00 | 42.3 | 20 | 2.14 | 732 | 26 | 30 | 17 | 0 | 44.7907
2024-09-04 16:00 | 39.4 | 37 | 7.22 | 544 | 26 | 30 | 17 | 0 | 0
2024-09-04 17:00 | 37.6 | 41 | 6.94 | 332 | 26 | 30 | 17 | 0 | 0
2024-09-04 18:00 | 36 | 50 | 5.42 | 136 | 26 | 30 | 17 | 0 | 0
2024-09-04 19:00 | 34.6 | 56 | 4.1 | 12 | 26 | 30 | 17 | 0 | 0
2024-09-04 20:00 | 34.4 | 55 | 3.94 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-04 21:00 | 34.1 | 54 | 3.34 | 0 | 26 | 30 | 17 | 0.0962 | 0
2024-09-04 22:00 | 33.4 | 57 | 2.34 | 0 | 26 | 30 | 17 | 1.0479 | 0
2024-09-04 23:00 | 32.7 | 60 | 1.58 | 0 | 26 | 30 | 17 | 1.8812 | 0
2024-09-05 | 31.9 | 63 | 1.8 | 0 | 26 | 30 | 17 | 4.1881 | 0
2024-09-05 01:00 | 30.9 | 67 | 1.39 | 0 | 26 | 30 | 17 | 6.2629 | 0
2024-09-05 02:00 | 30.3 | 69 | 1.7 | 0 | 26 | 30 | 17 | 8.9538 | 0
2024-09-05 03:00 | 29.7 | 71 | 1.84 | 0 | 26 | 30 | 17 | 11.5881 | 0
2024-09-05 04:00 | 29 | 74 | 1.84 | 0 | 26 | 30 | 17 | 13.6542 | 0
2024-09-05 05:00 | 29.1 | 75 | 1.96 | 0 | 26 | 30 | 17 | 11.8695 | 0
2024-09-05 06:00 | 28.6 | 74 | 2.36 | 0 | 26 | 30 | 17 | 18.7491 | 0
2024-09-05 07:00 | 29.9 | 64 | 4.62 | 46 | 26 | 30 | 17 | 23.9987 | 0
2024-09-05 08:00 | 32.5 | 50 | 5.72 | 218 | 26 | 30 | 17 | 7.0411 | 0
2024-09-05 09:00 | 34.8 | 45 | 6.9 | 434 | 26 | 30 | 17 | 0 | 0
2024-09-05 10:00 | 37.3 | 37 | 7.26 | 635 | 26 | 30 | 17 | 0 | 0
2024-09-05 11:00 | 39.2 | 31 | 6.56 | 792 | 26 | 30 | 17 | 0 | 2.2991
2024-09-05 12:00 | 40.8 | 25 | 5.58 | 887 | 26 | 30 | 17 | 0 | 17.2556
2024-09-05 13:00 | 42 | 20 | 4.85 | 908 | 26 | 30 | 17 | 0 | 18.8916
2024-09-05 14:00 | 39.8 | 36 | 7.94 | 855 | 26 | 30 | 17 | 0 | 37.4219
2024-09-05 15:00 | 38.1 | 41 | 8.4 | 727 | 26 | 30 | 17 | 0 | 14.2325
2024-09-05 16:00 | 37 | 41 | 7.94 | 554 | 26 | 30 | 17 | 0 | 0
2024-09-05 17:00 | 35.5 | 53 | 5.94 | 347 | 26 | 30 | 17 | 0 | 0
2024-09-05 18:00 | 33.8 | 59 | 4.94 | 138 | 26 | 30 | 17 | 0 | 0
2024-09-05 19:00 | 32.7 | 70 | 3.58 | 12 | 26 | 30 | 17 | 0 | 0
2024-09-05 20:00 | 32.4 | 71 | 2.28 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-05 21:00 | 31.6 | 75 | 1.4 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-05 22:00 | 31.1 | 78 | 0.5 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-05 23:00 | 29.7 | 85 | 1.24 | 0 | 26 | 30 | 17 | 0.9647 | 0
2024-09-06 | 28.9 | 87 | 1.78 | 0 | 26 | 30 | 17 | 2.2183 | 0
2024-09-06 01:00 | 28.2 | 90 | 2.05 | 0 | 26 | 30 | 17 | 3.9876 | 0
2024-09-06 02:00 | 27.4 | 93 | 1.92 | 0 | 26 | 30 | 17 | 6.635 | 0
2024-09-06 03:00 | 26.7 | 93 | 1.79 | 0 | 26 | 30 | 17 | 11.8777 | 0
2024-09-06 04:00 | 26.4 | 91 | 2.01 | 0 | 26 | 30 | 17 | 16.9787 | 0
2024-09-06 05:00 | 26.8 | 83 | 2.15 | 0 | 26 | 30 | 17 | 22.9105 | 0
2024-09-06 06:00 | 26.3 | 80 | 2.16 | 0 | 26 | 30 | 17 | 30.8232 | 0
2024-09-06 07:00 | 26.9 | 73 | 1.92 | 47 | 26 | 30 | 17 | 25.6284 | 0
2024-09-06 08:00 | 29.8 | 56 | 1.7 | 224 | 26 | 30 | 17 | 0 | 0
2024-09-06 09:00 | 33.3 | 41 | 1.56 | 447 | 26 | 30 | 17 | 0 | 2.8703
2024-09-06 10:00 | 36 | 32 | 1.75 | 652 | 26 | 30 | 17 | 0 | 28.9056
2024-09-06 11:00 | 37.6 | 29 | 2.62 | 810 | 26 | 30 | 17 | 0 | 36.3216
2024-09-06 12:00 | 37.4 | 38 | 4.53 | 901 | 26 | 30 | 17 | 0 | 45.2388
2024-09-06 13:00 | 37.2 | 40 | 5.37 | 916 | 26 | 30 | 17 | 0 | 43.4
2024-09-06 14:00 | 36.9 | 45 | 5.38 | 864 | 26 | 30 | 17 | 0 | 51.8759
2024-09-06 15:00 | 36.9 | 44 | 4.82 | 741 | 26 | 30 | 17 | 0 | 36.0581
2024-09-06 16:00 | 36.5 | 45 | 4.53 | 563 | 26 | 30 | 17 | 0 | 12.7534
2024-09-06 17:00 | 35.4 | 50 | 4.24 | 348 | 26 | 30 | 17 | 0 | 0
2024-09-06 18:00 | 33.8 | 62 | 3.72 | 137 | 26 | 30 | 17 | 0 | 0
2024-09-06 19:00 | 32.8 | 68 | 2.37 | 11 | 26 | 30 | 17 | 0 | 0
2024-09-06 20:00 | 32.2 | 72 | 1.84 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-06 21:00 | 31.3 | 78 | 0.82 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-06 22:00 | 30.4 | 83 | 1 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-06 23:00 | 29.4 | 85 | 1.22 | 0 | 26 | 30 | 17 | 1.8235 | 0
2024-09-07 | 28.6 | 88 | 1.44 | 0 | 26 | 30 | 17 | 3.6506 | 0
2024-09-07 01:00 | 28.1 | 89 | 2.32 | 0 | 26 | 30 | 17 | 3.9707 | 0
2024-09-07 02:00 | 27.5 | 90 | 2.11 | 0 | 26 | 30 | 17 | 8.0335 | 0
2024-09-07 03:00 | 27.3 | 88 | 2.33 | 0 | 26 | 30 | 17 | 12.5491 | 0
2024-09-07 04:00 | 26.9 | 90 | 2.5 | 0 | 26 | 30 | 17 | 14.2057 | 0
2024-09-07 05:00 | 27.3 | 90 | 2.31 | 0 | 26 | 30 | 17 | 9.9889 | 0
2024-09-07 06:00 | 26.8 | 90 | 2.65 | 0 | 26 | 30 | 17 | 15.4611 | 0
2024-09-07 07:00 | 27.4 | 81 | 1.5 | 46 | 26 | 30 | 17 | 11.2464 | 0
2024-09-07 08:00 | 30 | 64 | 1.41 | 222 | 26 | 30 | 17 | 0 | 0
2024-09-07 09:00 | 33.7 | 46 | 1.26 | 442 | 26 | 30 | 17 | 0 | 17.7807
2024-09-07 10:00 | 36.8 | 36 | 0.58 | 643 | 26 | 30 | 17 | 0 | 65.7894
2024-09-07 11:00 | 38.9 | 30 | 1.12 | 798 | 26 | 30 | 17 | 0 | 76.6244
2024-09-07 12:00 | 39.8 | 29 | 2.87 | 889 | 26 | 30 | 17 | 0 | 60.3294
2024-09-07 13:00 | 39.6 | 35 | 4.12 | 908 | 26 | 30 | 17 | 0 | 65.8077
2024-09-07 14:00 | 39.7 | 33 | 5.2 | 852 | 26 | 30 | 17 | 0 | 40.765
2024-09-07 15:00 | 39.1 | 36 | 5.81 | 726 | 26 | 30 | 17 | 0 | 23.6867
2024-09-07 16:00 | 38.3 | 39 | 5.61 | 544 | 26 | 30 | 17 | 0 | 2.6519
2024-09-07 17:00 | 36.7 | 46 | 5.56 | 327 | 26 | 30 | 17 | 0 | 0
2024-09-07 18:00 | 35.1 | 59 | 4.26 | 116 | 26 | 30 | 17 | 0 | 0
2024-09-07 19:00 | 34.1 | 64 | 3.98 | 10 | 26 | 30 | 17 | 0 | 0
2024-09-07 20:00 | 33.5 | 67 | 2.82 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-07 21:00 | 32.9 | 69 | 1.66 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-07 22:00 | 32 | 76 | 2.09 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-07 23:00 | 31 | 83 | 1.24 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-08 | 30.3 | 87 | 1.24 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-08 01:00 | 29.8 | 88 | 2.01 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-08 02:00 | 29.5 | 91 | 2.42 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-08 03:00 | 29.2 | 93 | 2.7 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-08 04:00 | 28.5 | 95 | 3.2 | 0 | 26 | 30 | 17 | 1.333 | 0
2024-09-08 05:00 | 28.7 | 81 | 2.94 | 0 | 26 | 30 | 17 | 8.1151 | 0
2024-09-08 06:00 | 28.4 | 74 | 2.66 | 0 | 26 | 30 | 17 | 21.732 | 0
2024-09-08 07:00 | 29.4 | 64 | 3.48 | 45 | 26 | 30 | 17 | 25.5979 | 0
2024-09-08 08:00 | 32.4 | 51 | 4.39 | 218 | 26 | 30 | 17 | 0.48 | 0
2024-09-08 09:00 | 35.7 | 33 | 6.86 | 437 | 26 | 30 | 17 | 0.402 | 0
2024-09-08 10:00 | 37.7 | 32 | 6.45 | 640 | 26 | 30 | 17 | 0 | 0
2024-09-08 11:00 | 39.7 | 28 | 5.9 | 795 | 26 | 30 | 17 | 0 | 1.937
2024-09-08 12:00 | 41.3 | 24 | 4.84 | 887 | 26 | 30 | 17 | 0 | 27.7647
2024-09-08 13:00 | 42.6 | 20 | 3.67 | 907 | 26 | 30 | 17 | 0 | 42.8146
2024-09-08 14:00 | 43.3 | 18 | 2.47 | 854 | 26 | 30 | 17 | 0 | 55.1626
2024-09-08 15:00 | 40.7 | 31 | 5.85 | 699 | 26 | 30 | 17 | 0 | 18.182
2024-09-08 16:00 | 38.8 | 38 | 5.92 | 474 | 26 | 30 | 17 | 0 | 0
2024-09-08 17:00 | 37.1 | 44 | 5.5 | 284 | 26 | 30 | 17 | 0 | 0
2024-09-08 18:00 | 35.1 | 56 | 5.15 | 116 | 26 | 30 | 17 | 0 | 0
2024-09-08 19:00 | 34 | 65 | 4.08 | 8 | 26 | 30 | 17 | 0 | 0
2024-09-08 20:00 | 33.5 | 68 | 4 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-08 21:00 | 32.8 | 70 | 2.41 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-08 22:00 | 31.9 | 73 | 1.24 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-08 23:00 | 31.1 | 75 | 1.46 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-09 | 30.4 | 78 | 2.04 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-09 01:00 | 30.2 | 77 | 3.11 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-09 02:00 | 29.8 | 78 | 2.8 | 0 | 26 | 30 | 17 | 0.7583 | 0
2024-09-09 03:00 | 29.1 | 84 | 2.76 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-09 04:00 | 28.1 | 85 | 3.03 | 0 | 26 | 30 | 17 | 8.5692 | 0
2024-09-09 05:00 | 27.4 | 81 | 1.84 | 0 | 26 | 30 | 17 | 18.7854 | 0
2024-09-09 06:00 | 27.2 | 77 | 2.66 | 0 | 26 | 30 | 17 | 29.2733 | 0
2024-09-09 07:00 | 28.1 | 70 | 2 | 44 | 26 | 30 | 17 | 20.5701 | 0
2024-09-09 08:00 | 31 | 58 | 3.21 | 220 | 26 | 30 | 17 | 0 | 0
2024-09-09 09:00 | 34.9 | 42 | 3.1 | 441 | 26 | 30 | 17 | 0 | 0
2024-09-09 10:00 | 38.1 | 29 | 3 | 645 | 26 | 30 | 17 | 0 | 10.8884
2024-09-09 11:00 | 40.2 | 22 | 2.69 | 802 | 26 | 30 | 17 | 0 | 34.3083
2024-09-09 12:00 | 41.2 | 20 | 3.07 | 896 | 26 | 30 | 17 | 0 | 40.5677
2024-09-09 13:00 | 40.8 | 24 | 4.74 | 917 | 26 | 30 | 17 | 0 | 27.7603
2024-09-09 14:00 | 40.5 | 21 | 5.3 | 862 | 26 | 30 | 17 | 0 | 0
2024-09-09 15:00 | 39.2 | 29 | 5.48 | 742 | 26 | 30 | 17 | 0 | 0
2024-09-09 16:00 | 37.7 | 35 | 5.52 | 558 | 26 | 30 | 17 | 0 | 0
2024-09-09 17:00 | 36.3 | 45 | 4.66 | 340 | 26 | 30 | 17 | 0 | 0
2024-09-09 18:00 | 34.5 | 59 | 3.92 | 126 | 26 | 30 | 17 | 0 | 0
2024-09-09 19:00 | 33.2 | 72 | 3.26 | 8 | 26 | 30 | 17 | 0 | 0
2024-09-09 20:00 | 32.6 | 77 | 2.77 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-09 21:00 | 32 | 81 | 2.36 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-09 22:00 | 31.1 | 87 | 1.71 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-09 23:00 | 30.1 | 93 | 1.2 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-10 | 30 | 93 | 0.81 | 0 | 26 | 30 | 17 | 1.1609 | 0
2024-09-10 01:00 | 29.8 | 94 | 0.82 | 0 | 26 | 30 | 17 | 1.6347 | 0
2024-09-10 02:00 | 28.8 | 98 | 2.22 | 0 | 26 | 30 | 17 | 1.7937 | 0
2024-09-10 03:00 | 28 | 99 | 1.77 | 0 | 26 | 30 | 17 | 4.9546 | 0
2024-09-10 04:00 | 27.5 | 99 | 1.8 | 0 | 26 | 30 | 17 | 6.4322 | 0
2024-09-10 05:00 | 28 | 100 | 2.62 | 0 | 26 | 30 | 17 | 3.9499 | 0
2024-09-10 06:00 | 28.2 | 100 | 3.41 | 0 | 26 | 30 | 17 | 2.2194 | 0
2024-09-10 07:00 | 28.7 | 99 | 3.41 | 29 | 26 | 30 | 17 | 0 | 0
2024-09-10 08:00 | 29.3 | 97 | 3.52 | 148 | 26 | 30 | 17 | 0 | 0
2024-09-10 09:00 | 31.9 | 79 | 3.65 | 346 | 26 | 30 | 17 | 0 | 20.0861
2024-09-10 10:00 | 34.7 | 62 | 2.79 | 631 | 26 | 30 | 17 | 0 | 59.9489
2024-09-10 11:00 | 37.1 | 51 | 2.28 | 780 | 26 | 30 | 17 | 0 | 83.9339
2024-09-10 12:00 | 38.6 | 43 | 4.34 | 876 | 26 | 30 | 17 | 0 | 77.3152
2024-09-10 13:00 | 38.8 | 38 | 5.25 | 893 | 26 | 30 | 17 | 0 | 55.5896
2024-09-10 14:00 | 38.2 | 42 | 5.35 | 852 | 26 | 30 | 17 | 0 | 57.6796
2024-09-10 15:00 | 37.6 | 48 | 5.63 | 729 | 26 | 30 | 17 | 0 | 55.4456
2024-09-10 16:00 | 36.9 | 53 | 5.13 | 548 | 26 | 30 | 17 | 0 | 41.8219
2024-09-10 17:00 | 35.6 | 59 | 4.62 | 336 | 26 | 30 | 17 | 0 | 15.7778
2024-09-10 18:00 | 34.6 | 64 | 3.85 | 125 | 26 | 30 | 17 | 0 | 0
2024-09-10 19:00 | 33.9 | 67 | 3.31 | 8 | 26 | 30 | 17 | 0 | 0
2024-09-10 20:00 | 33.3 | 69 | 2.6 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-10 21:00 | 32.5 | 74 | 2.33 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-10 22:00 | 31.6 | 78 | 3.04 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-10 23:00 | 30.9 | 81 | 3.54 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-11 | 29.8 | 86 | 1.17 | 0 | 26 | 30 | 17 | 0.8486 | 0
2024-09-11 01:00 | 29.1 | 88 | 2.38 | 0 | 26 | 30 | 17 | 0.5116 | 0
2024-09-11 02:00 | 28.3 | 91 | 2.79 | 0 | 26 | 30 | 17 | 2.6634 | 0
2024-09-11 03:00 | 28.5 | 89 | 3.22 | 0 | 26 | 30 | 17 | 1.3035 | 0
2024-09-11 04:00 | 28.1 | 89 | 3.84 | 0 | 26 | 30 | 17 | 2.0842 | 0
2024-09-11 05:00 | 28.4 | 90 | 3.25 | 0 | 26 | 30 | 17 | 1.6488 | 0
2024-09-11 06:00 | 28.1 | 89 | 2.83 | 0 | 26 | 30 | 17 | 3.3377 | 0
2024-09-11 07:00 | 28.5 | 84 | 1.63 | 44 | 26 | 30 | 17 | 0.2455 | 0
2024-09-11 08:00 | 30.8 | 71 | 1.55 | 220 | 26 | 30 | 17 | 0 | 0
2024-09-11 09:00 | 33.9 | 52 | 1.88 | 438 | 26 | 30 | 17 | 0 | 16.0671
2024-09-11 10:00 | 36.9 | 39 | 2.48 | 637 | 26 | 30 | 17 | 0 | 33.6618
2024-09-11 11:00 | 39.6 | 30 | 2.83 | 792 | 26 | 30 | 17 | 0 | 49.0895
2024-09-11 12:00 | 43.6 | 12 | 3.28 | 884 | 26 | 30 | 17 | 0 | 22.4391
2024-09-11 13:00 | 41.9 | 23 | 4.88 | 916 | 26 | 30 | 17 | 0 | 33.001
2024-09-11 14:00 | 40.7 | 33 | 5.69 | 856 | 26 | 30 | 17 | 0 | 50.8882
2024-09-11 15:00 | 41.6 | 27 | 4.01 | 731 | 26 | 30 | 17 | 0 | 33.6043
2024-09-11 16:00 | 40.2 | 33 | 3.26 | 551 | 26 | 30 | 17 | 0 | 25.8713
2024-09-11 17:00 | 35.3 | 58 | 7.24 | 328 | 26 | 30 | 17 | 0 | 0
2024-09-11 18:00 | 34.2 | 61 | 6.22 | 122 | 26 | 30 | 17 | 0 | 0
2024-09-11 19:00 | 33.1 | 72 | 4.48 | 7 | 26 | 30 | 17 | 0 | 0
2024-09-11 20:00 | 32.6 | 77 | 3.14 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-11 21:00 | 32.1 | 73 | 1.71 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-11 22:00 | 31.6 | 44 | 2.1 | 0 | 26 | 30 | 17 | 35.9694 | 0
2024-09-11 23:00 | 31 | 28 | 2.01 | 0 | 26 | 30 | 17 | 61.9012 | 0
2024-09-12 | 29.7 | 28 | 2.16 | 0 | 26 | 30 | 17 | 72.1953 | 0
2024-09-12 01:00 | 28.6 | 28 | 2.44 | 0 | 26 | 30 | 17 | 84.4946 | 0
2024-09-12 02:00 | 28.2 | 25 | 3.1 | 0 | 26 | 30 | 17 | 106.0487 | 0
2024-09-12 03:00 | 27.4 | 27 | 3.05 | 0 | 26 | 30 | 17 | 106.7061 | 0
2024-09-12 04:00 | 26.8 | 35 | 3.96 | 0 | 26 | 30 | 17 | 116.135 | 0
2024-09-12 05:00 | 29.1 | 30 | 4.61 | 0 | 26 | 30 | 17 | 118.6246 | 0
2024-09-12 06:00 | 28.6 | 41 | 4.61 | 0 | 26 | 30 | 17 | 98.4931 | 0
2024-09-12 07:00 | 29.3 | 46 | 4.82 | 44 | 26 | 30 | 17 | 76.1853 | 0
2024-09-12 08:00 | 31.6 | 52 | 5.07 | 224 | 26 | 30 | 17 | 10.0894 | 0
2024-09-12 09:00 | 34.7 | 45 | 5.22 | 449 | 26 | 30 | 17 | 0 | 0
2024-09-12 10:00 | 38.7 | 25 | 4.44 | 656 | 26 | 30 | 17 | 0 | 0
2024-09-12 11:00 | 40.9 | 16 | 3.01 | 814 | 26 | 30 | 17 | 0 | 15.341
2024-09-12 12:00 | 42 | 14 | 2.61 | 906 | 26 | 30 | 17 | 0 | 37.9609
2024-09-12 13:00 | 43 | 12 | 2.12 | 924 | 26 | 30 | 17 | 0 | 52.7873
2024-09-12 14:00 | 43.9 | 10 | 1.66 | 867 | 26 | 30 | 17 | 0 | 57.5128
2024-09-12 15:00 | 43.6 | 11 | 3 | 741 | 26 | 30 | 17 | 0 | 5.7458
2024-09-12 16:00 | 40 | 31 | 6.26 | 554 | 26 | 30 | 17 | 0 | 0
2024-09-12 17:00 | 38.7 | 31 | 5.22 | 334 | 26 | 30 | 17 | 0 | 0
2024-09-12 18:00 | 37.3 | 35 | 4.34 | 122 | 26 | 30 | 17 | 3.8639 | 0
2024-09-12 19:00 | 34.9 | 54 | 2.51 | 7 | 26 | 30 | 17 | 0 | 0
2024-09-12 20:00 | 34.9 | 48 | 2.64 | 0 | 26 | 30 | 17 | 5.133 | 0
2024-09-12 21:00 | 34.5 | 38 | 2.83 | 0 | 26 | 30 | 17 | 31.3825 | 0
2024-09-12 22:00 | 33 | 38 | 2.25 | 0 | 26 | 30 | 17 | 37.4698 | 0
2024-09-12 23:00 | 32 | 32 | 2.5 | 0 | 26 | 30 | 17 | 58.2061 | 0
2024-09-13 | 31.1 | 39 | 3.18 | 0 | 26 | 30 | 17 | 61.2669 | 0
2024-09-13 01:00 | 29.9 | 52 | 3.19 | 0 | 26 | 30 | 17 | 47.1341 | 0
2024-09-13 02:00 | 30.1 | 51 | 0.1 | 0 | 26 | 30 | 17 | 18.6939 | 0
2024-09-13 03:00 | 28.3 | 58 | 2.75 | 0 | 26 | 30 | 17 | 47.4101 | 0
2024-09-13 04:00 | 27.7 | 66 | 2.56 | 0 | 26 | 30 | 17 | 39.2784 | 0
2024-09-13 05:00 | 27.6 | 53 | 3.78 | 0 | 26 | 30 | 17 | 73.6263 | 0
2024-09-13 06:00 | 28.3 | 36 | 3.54 | 0 | 26 | 30 | 17 | 94.9104 | 0
2024-09-13 07:00 | 30.1 | 35 | 4.42 | 43 | 26 | 30 | 17 | 89.3001 | 0
2024-09-13 08:00 | 32.1 | 42 | 5.2 | 220 | 26 | 30 | 17 | 33.9185 | 0
2024-09-13 09:00 | 34.4 | 39 | 7.07 | 440 | 26 | 30 | 17 | 0 | 0
2024-09-13 10:00 | 37.4 | 28 | 7.2 | 645 | 26 | 30 | 17 | 0 | 0
2024-09-13 11:00 | 40 | 20 | 7.13 | 803 | 26 | 30 | 17 | 0 | 0
2024-09-13 12:00 | 41.5 | 18 | 6.38 | 895 | 26 | 30 | 17 | 0 | 0
2024-09-13 13:00 | 42.3 | 17 | 5.35 | 912 | 26 | 30 | 17 | 0 | 0
2024-09-13 14:00 | 41.6 | 23 | 5.1 | 853 | 26 | 30 | 17 | 0 | 18.2722
2024-09-13 15:00 | 39.3 | 37 | 6.26 | 723 | 26 | 30 | 17 | 0 | 27.6745
2024-09-13 16:00 | 37.6 | 40 | 6.3 | 538 | 26 | 30 | 17 | 0 | 0
2024-09-13 17:00 | 36.5 | 42 | 5.22 | 328 | 26 | 30 | 17 | 0 | 0
2024-09-13 18:00 | 34.6 | 49 | 4.19 | 118 | 26 | 30 | 17 | 0 | 0
2024-09-13 19:00 | 33.4 | 61 | 3.26 | 6 | 26 | 30 | 17 | 0 | 0
2024-09-13 20:00 | 32.8 | 66 | 2.21 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-13 21:00 | 32 | 68 | 1.93 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-13 22:00 | 31.1 | 67 | 1.77 | 0 | 26 | 30 | 17 | 5.2156 | 0
2024-09-13 23:00 | 31.4 | 62 | 0.58 | 0 | 26 | 30 | 17 | 5.3329 | 0
2024-09-14 | 29.6 | 71 | 2.51 | 0 | 26 | 30 | 17 | 13.9993 | 0
2024-09-14 01:00 | 28.6 | 81 | 2.39 | 0 | 26 | 30 | 17 | 9.0289 | 0
2024-09-14 02:00 | 27.8 | 85 | 2.1 | 0 | 26 | 30 | 17 | 11.2793 | 0
2024-09-14 03:00 | 27.5 | 88 | 2.33 | 0 | 26 | 30 | 17 | 10.5587 | 0
2024-09-14 04:00 | 27 | 94 | 2 | 0 | 26 | 30 | 17 | 8.1356 | 0
2024-09-14 05:00 | 28.9 | 77 | 0.85 | 0 | 26 | 30 | 17 | 8.9316 | 0
2024-09-14 06:00 | 27 | 72 | 4.55 | 0 | 26 | 30 | 17 | 50.9938 | 0
2024-09-14 07:00 | 28.3 | 53 | 2.82 | 42 | 26 | 30 | 17 | 50.1784 | 0
2024-09-14 08:00 | 31.6 | 34 | 3.57 | 218 | 26 | 30 | 17 | 43.1184 | 0
2024-09-14 09:00 | 34.3 | 34 | 5.51 | 440 | 26 | 30 | 17 | 5.7307 | 0
2024-09-14 10:00 | 37.4 | 28 | 6.75 | 642 | 26 | 30 | 17 | 0 | 0
2024-09-14 11:00 | 39.6 | 23 | 6.37 | 798 | 26 | 30 | 17 | 0 | 0
2024-09-14 12:00 | 41.1 | 20 | 5.44 | 888 | 26 | 30 | 17 | 0 | 0
2024-09-14 13:00 | 42.1 | 18 | 4.92 | 905 | 26 | 30 | 17 | 0 | 8.6383
2024-09-14 14:00 | 39.4 | 33 | 7.3 | 846 | 26 | 30 | 17 | 0 | 16.3761
2024-09-14 15:00 | 38.4 | 34 | 7.12 | 700 | 26 | 30 | 17 | 0 | 0
2024-09-14 16:00 | 36.8 | 46 | 6.82 | 513 | 26 | 30 | 17 | 0 | 0
2024-09-14 17:00 | 34.7 | 65 | 4.95 | 319 | 26 | 30 | 17 | 0 | 17.6581
2024-09-14 18:00 | 33.3 | 69 | 3.61 | 113 | 26 | 30 | 17 | 0 | 0
2024-09-14 19:00 | 32.8 | 75 | 3.16 | 5 | 26 | 30 | 17 | 0 | 0
2024-09-14 20:00 | 31.9 | 81 | 2.72 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-14 21:00 | 31.2 | 85 | 2.9 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-14 22:00 | 30.9 | 88 | 3.67 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-14 23:00 | 30.4 | 92 | 2.43 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-15 | 29.7 | 95 | 1.55 | 0 | 26 | 30 | 17 | 0.2868 | 0
2024-09-15 01:00 | 29.2 | 97 | 2.55 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-15 02:00 | 28.6 | 99 | 2.76 | 0 | 26 | 30 | 17 | 1.6223 | 0
2024-09-15 03:00 | 28.3 | 98 | 2.66 | 0 | 26 | 30 | 17 | 2.8402 | 0
2024-09-15 04:00 | 27.9 | 98 | 2.11 | 0 | 26 | 30 | 17 | 4.8741 | 0
2024-09-15 05:00 | 28.1 | 97 | 2.2 | 0 | 26 | 30 | 17 | 4.1196 | 0
2024-09-15 06:00 | 28.1 | 94 | 3.03 | 0 | 26 | 30 | 17 | 3.0895 | 0
2024-09-15 07:00 | 29.2 | 82 | 3.32 | 41 | 26 | 30 | 17 | 0 | 0
2024-09-15 08:00 | 31.8 | 66 | 3.01 | 212 | 26 | 30 | 17 | 0 | 0
2024-09-15 09:00 | 34.6 | 49 | 4.3 | 431 | 26 | 30 | 17 | 0 | 0
2024-09-15 10:00 | 37.1 | 36 | 4.57 | 634 | 26 | 30 | 17 | 0 | 0
2024-09-15 11:00 | 39.2 | 24 | 3.69 | 790 | 26 | 30 | 17 | 0 | 11.8933
2024-09-15 12:00 | 40.4 | 18 | 3.32 | 883 | 26 | 30 | 17 | 0 | 20.8978
2024-09-15 13:00 | 41 | 15 | 4.53 | 903 | 26 | 30 | 17 | 0 | 0
2024-09-15 14:00 | 40.7 | 15 | 5.47 | 850 | 26 | 30 | 17 | 0 | 0
2024-09-15 15:00 | 40 | 15 | 5.16 | 726 | 26 | 30 | 17 | 0 | 0
2024-09-15 16:00 | 38.9 | 19 | 4.84 | 542 | 26 | 30 | 17 | 0 | 0
2024-09-15 17:00 | 36.6 | 36 | 5.45 | 324 | 26 | 30 | 17 | 0 | 0
2024-09-15 18:00 | 34.7 | 49 | 5.14 | 114 | 26 | 30 | 17 | 0 | 0
2024-09-15 19:00 | 33.5 | 58 | 4.04 | 5 | 26 | 30 | 17 | 0 | 0
2024-09-15 20:00 | 32.7 | 64 | 2.95 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-15 21:00 | 31.9 | 69 | 2.65 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-15 22:00 | 31.2 | 74 | 2.75 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-15 23:00 | 30.4 | 78 | 2.19 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-16 | 30.8 | 75 | 0.51 | 0 | 26 | 30 | 17 | 0.4203 | 0
2024-09-16 01:00 | 28.7 | 83 | 4.05 | 0 | 26 | 30 | 17 | 4.0561 | 0
2024-09-16 02:00 | 28.2 | 81 | 2.92 | 0 | 26 | 30 | 17 | 13.7265 | 0
2024-09-16 03:00 | 27.7 | 81 | 2.33 | 0 | 26 | 30 | 17 | 17.7092 | 0
2024-09-16 04:00 | 27.4 | 78 | 2.75 | 0 | 26 | 30 | 17 | 26.2875 | 0
2024-09-16 05:00 | 27.1 | 81 | 3.11 | 0 | 26 | 30 | 17 | 26.4572 | 0
2024-09-16 06:00 | 26.5 | 81 | 2.78 | 0 | 26 | 30 | 17 | 31.3507 | 0
2024-09-16 07:00 | 27.3 | 73 | 2.68 | 42 | 26 | 30 | 17 | 28.3567 | 0
2024-09-16 08:00 | 30.4 | 53 | 2.48 | 220 | 26 | 30 | 17 | 5.1157 | 0
2024-09-16 09:00 | 34 | 37 | 1.77 | 441 | 26 | 30 | 17 | 0 | 0
2024-09-16 10:00 | 36.7 | 26 | 1.6 | 646 | 26 | 30 | 17 | 0 | 25.7918
2024-09-16 11:00 | 38.4 | 20 | 0.45 | 802 | 26 | 30 | 17 | 0 | 78.5842
2024-09-16 12:00 | 39.5 | 19 | 3.02 | 893 | 26 | 30 | 17 | 0 | 25.5402
2024-09-16 13:00 | 38.5 | 29 | 5.23 | 908 | 26 | 30 | 17 | 0 | 15.4668
2024-09-16 14:00 | 38.3 | 24 | 5.59 | 846 | 26 | 30 | 17 | 0 | 0
2024-09-16 15:00 | 37.5 | 29 | 5.73 | 724 | 26 | 30 | 17 | 0 | 0
2024-09-16 16:00 | 36.3 | 36 | 5.98 | 539 | 26 | 30 | 17 | 0 | 0
2024-09-16 17:00 | 35.3 | 39 | 4.7 | 320 | 26 | 30 | 17 | 0 | 0
2024-09-16 18:00 | 34 | 44 | 4.02 | 110 | 26 | 30 | 17 | 13.6708 | 0
2024-09-16 19:00 | 32.7 | 55 | 3 | 4 | 26 | 30 | 17 | 12.0864 | 0
2024-09-16 20:00 | 31.7 | 63 | 2.8 | 0 | 26 | 30 | 17 | 6.8544 | 0
2024-09-16 21:00 | 30.9 | 69 | 2.52 | 0 | 26 | 30 | 17 | 4.3287 | 0
2024-09-16 22:00 | 30.1 | 73 | 2.33 | 0 | 26 | 30 | 17 | 5.8808 | 0
2024-09-16 23:00 | 29.3 | 77 | 2.87 | 0 | 26 | 30 | 17 | 7.9539 | 0
2024-09-17 | 28.3 | 82 | 2.9 | 0 | 26 | 30 | 17 | 11.0117 | 0
2024-09-17 01:00 | 27.6 | 85 | 2.56 | 0 | 26 | 30 | 17 | 13.7748 | 0
2024-09-17 02:00 | 27 | 87 | 1.9 | 0 | 26 | 30 | 17 | 15.8017 | 0
2024-09-17 03:00 | 26.6 | 87 | 2.04 | 0 | 26 | 30 | 17 | 19.6963 | 0
2024-09-17 04:00 | 26 | 87 | 2.02 | 0 | 26 | 30 | 17 | 24.8664 | 0
2024-09-17 05:00 | 25.9 | 90 | 1.73 | 0 | 26 | 30 | 17 | 21.3578 | 0
2024-09-17 06:00 | 25.4 | 87 | 2.08 | 0 | 26 | 30 | 17 | 30.3705 | 0
2024-09-17 07:00 | 26.1 | 73 | 2.13 | 41 | 26 | 30 | 17 | 34.6182 | 0
2024-09-17 08:00 | 29.3 | 53 | 1.73 | 221 | 26 | 30 | 17 | 5.5979 | 0
2024-09-17 09:00 | 32.8 | 38 | 2.2 | 445 | 26 | 30 | 17 | 0 | 0
2024-09-17 10:00 | 35.3 | 28 | 1.53 | 650 | 26 | 30 | 17 | 0 | 23.9081
2024-09-17 11:00 | 37.4 | 25 | 2.47 | 807 | 26 | 30 | 17 | 0 | 27.9955
2024-09-17 12:00 | 38.8 | 21 | 3.45 | 894 | 26 | 30 | 17 | 0 | 17.3196
2024-09-17 13:00 | 38.7 | 26 | 5.06 | 906 | 26 | 30 | 17 | 0 | 7.3552
2024-09-17 14:00 | 38 | 27 | 6.64 | 841 | 26 | 30 | 17 | 0 | 0
2024-09-17 15:00 | 37.1 | 34 | 6.46 | 714 | 26 | 30 | 17 | 0 | 0
2024-09-17 16:00 | 36.2 | 41 | 6.53 | 529 | 26 | 30 | 17 | 0 | 0
2024-09-17 17:00 | 34.7 | 45 | 5.55 | 311 | 26 | 30 | 17 | 0 | 0
2024-09-17 18:00 | 33.4 | 56 | 4.74 | 106 | 26 | 30 | 17 | 0 | 0
2024-09-17 19:00 | 32.3 | 65 | 3.34 | 4 | 26 | 30 | 17 | 0 | 0
2024-09-17 20:00 | 31.7 | 71 | 2.69 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-17 21:00 | 31.2 | 72 | 2.34 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-17 22:00 | 30.4 | 73 | 1.86 | 0 | 26 | 30 | 17 | 3.2007 | 0
2024-09-17 23:00 | 29.3 | 76 | 1.56 | 0 | 26 | 30 | 17 | 8.4395 | 0
2024-09-18 | 28.6 | 78 | 1.08 | 0 | 26 | 30 | 17 | 10.539 | 0
2024-09-18 01:00 | 27.5 | 82 | 1.6 | 0 | 26 | 30 | 17 | 16.1044 | 0
2024-09-18 02:00 | 27.6 | 81 | 1 | 0 | 26 | 30 | 17 | 14.0948 | 0
2024-09-18 03:00 | 27.5 | 83 | 1.08 | 0 | 26 | 30 | 17 | 13.5269 | 0
2024-09-18 04:00 | 26.3 | 89 | 1.8 | 0 | 26 | 30 | 17 | 19.3395 | 0
2024-09-18 05:00 | 26.7 | 86 | 1.94 | 0 | 26 | 30 | 17 | 19.5862 | 0
2024-09-18 06:00 | 26.4 | 90 | 2.18 | 0 | 26 | 30 | 17 | 18.5211 | 0
2024-09-18 07:00 | 27 | 89 | 1.92 | 40 | 26 | 30 | 17 | 8.2556 | 0
2024-09-18 08:00 | 29.7 | 77 | 2.16 | 212 | 26 | 30 | 17 | 0 | 0
2024-09-18 09:00 | 32.2 | 63 | 2.42 | 429 | 26 | 30 | 17 | 0 | 11.4998
2024-09-18 10:00 | 34.6 | 43 | 2.33 | 631 | 26 | 30 | 17 | 0 | 24.6073
2024-09-18 11:00 | 36.5 | 36 | 1.84 | 786 | 26 | 30 | 17 | 0 | 55.3992
2024-09-18 12:00 | 38.2 | 30 | 2.24 | 879 | 26 | 30 | 17 | 0 | 59.8666
2024-09-18 13:00 | 39 | 27 | 3.47 | 896 | 26 | 30 | 17 | 0 | 38.3326
2024-09-18 14:00 | 38.1 | 34 | 5.4 | 836 | 26 | 30 | 17 | 0 | 19.7676
2024-09-18 15:00 | 37.5 | 31 | 6.37 | 705 | 26 | 30 | 17 | 0 | 0
2024-09-18 16:00 | 36.7 | 35 | 6.23 | 524 | 26 | 30 | 17 | 0 | 0
2024-09-18 17:00 | 35.7 | 35 | 5.94 | 308 | 26 | 30 | 17 | 4.8683 | 0
2024-09-18 18:00 | 34 | 49 | 5.19 | 103 | 26 | 30 | 17 | 2.9793 | 0
2024-09-18 19:00 | 33.1 | 59 | 4.88 | 3 | 26 | 30 | 17 | 0 | 0
2024-09-18 20:00 | 32.8 | 59 | 3.12 | 0 | 26 | 30 | 17 | 3.2516 | 0
2024-09-18 21:00 | 32.2 | 65 | 2.42 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-18 22:00 | 31.2 | 71 | 1.2 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-18 23:00 | 30.5 | 74 | 1.41 | 0 | 26 | 30 | 17 | 1.5379 | 0
2024-09-19 | 30 | 76 | 2 | 0 | 26 | 30 | 17 | 2.6579 | 0
2024-09-19 01:00 | 29.2 | 77 | 2.2 | 0 | 26 | 30 | 17 | 8.6592 | 0
2024-09-19 02:00 | 28.7 | 78 | 1.89 | 0 | 26 | 30 | 17 | 11.4828 | 0
2024-09-19 03:00 | 28.3 | 78 | 1.94 | 0 | 26 | 30 | 17 | 14.9979 | 0
2024-09-19 04:00 | 27.8 | 77 | 2.08 | 0 | 26 | 30 | 17 | 20.9805 | 0
2024-09-19 05:00 | 28.6 | 74 | 1.43 | 0 | 26 | 30 | 17 | 15.2939 | 0
2024-09-19 06:00 | 28.3 | 76 | 1.52 | 0 | 26 | 30 | 17 | 15.8225 | 0
2024-09-19 07:00 | 29.4 | 72 | 1.51 | 39 | 26 | 30 | 17 | 6.6218 | 0
2024-09-19 08:00 | 31.5 | 67 | 1.41 | 211 | 26 | 30 | 17 | 0 | 0
2024-09-19 09:00 | 32.9 | 63 | 1.39 | 428 | 26 | 30 | 17 | 0 | 29.1897
2024-09-19 10:00 | 34.8 | 52 | 1.75 | 628 | 26 | 30 | 17 | 0 | 50.5252
2024-09-19 11:00 | 36.6 | 43 | 1.86 | 782 | 26 | 30 | 17 | 0 | 68.1247
2024-09-19 12:00 | 37.8 | 39 | 2.92 | 870 | 26 | 30 | 17 | 0 | 67.3667
2024-09-19 13:00 | 37.2 | 49 | 5.41 | 882 | 26 | 30 | 17 | 0 | 74.7891
2024-09-19 14:00 | 36.8 | 45 | 6.63 | 814 | 26 | 30 | 17 | 0 | 34.1672
2024-09-19 15:00 | 36.5 | 46 | 6.55 | 674 | 26 | 30 | 17 | 0 | 15.184
2024-09-19 16:00 | 35.6 | 52 | 6.88 | 510 | 26 | 30 | 17 | 0 | 1.1684
2024-09-19 17:00 | 34.7 | 55 | 5.86 | 296 | 26 | 30 | 17 | 0 | 0
2024-09-19 18:00 | 33.2 | 61 | 5.74 | 98 | 26 | 30 | 17 | 0 | 0
2024-09-19 19:00 | 33 | 64 | 3.64 | 3 | 26 | 30 | 17 | 0 | 0
2024-09-19 20:00 | 32.6 | 66 | 2.58 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-19 21:00 | 31.9 | 70 | 1.34 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-19 22:00 | 31.4 | 71 | 2.3 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-19 23:00 | 30.8 | 72 | 1.84 | 0 | 26 | 30 | 17 | 1.1067 | 0
2024-09-20 | 30.1 | 74 | 1.84 | 0 | 26 | 30 | 17 | 4.4763 | 0
2024-09-20 01:00 | 29.7 | 76 | 1.77 | 0 | 26 | 30 | 17 | 5.3637 | 0
2024-09-20 02:00 | 28.9 | 80 | 1.27 | 0 | 26 | 30 | 17 | 7.1221 | 0
2024-09-20 03:00 | 28.7 | 80 | 1.2 | 0 | 26 | 30 | 17 | 8.4355 | 0
2024-09-20 04:00 | 28.6 | 80 | 1.97 | 0 | 26 | 30 | 17 | 10.0345 | 0
2024-09-20 05:00 | 29 | 78 | 2.14 | 0 | 26 | 30 | 17 | 9.1274 | 0
2024-09-20 06:00 | 28.3 | 82 | 1.8 | 0 | 26 | 30 | 17 | 10.095 | 0
2024-09-20 07:00 | 29 | 78 | 1.2 | 39 | 26 | 30 | 17 | 2.9148 | 0
2024-09-20 08:00 | 30.9 | 69 | 1.12 | 211 | 26 | 30 | 17 | 0 | 0
2024-09-20 09:00 | 32.5 | 64 | 0.51 | 428 | 26 | 30 | 17 | 0 | 38.3997
2024-09-20 10:00 | 34.1 | 54 | 0.4 | 629 | 26 | 30 | 17 | 0 | 65.7627
2024-09-20 11:00 | 35.8 | 45 | 0.85 | 782 | 26 | 30 | 17 | 0 | 82.5551
2024-09-20 12:00 | 37.2 | 40 | 1.22 | 870 | 26 | 30 | 17 | 0 | 89.2809
2024-09-20 13:00 | 37.9 | 39 | 3.19 | 881 | 26 | 30 | 17 | 0 | 66.6568
2024-09-20 14:00 | 37 | 43 | 5.94 | 819 | 26 | 30 | 17 | 0 | 34.6281
2024-09-20 15:00 | 36.1 | 47 | 6.24 | 689 | 26 | 30 | 17 | 0 | 17.095
2024-09-20 16:00 | 35.5 | 46 | 6.64 | 509 | 26 | 30 | 17 | 0 | 0
2024-09-20 17:00 | 34.3 | 53 | 6.5 | 295 | 26 | 30 | 17 | 0 | 0
2024-09-20 18:00 | 33.2 | 56 | 6.46 | 95 | 26 | 30 | 17 | 0 | 0
2024-09-20 19:00 | 33.1 | 58 | 4.44 | 2 | 26 | 30 | 17 | 1.4671 | 0
2024-09-20 20:00 | 32.5 | 61 | 3.53 | 0 | 26 | 30 | 17 | 2.2143 | 0
2024-09-20 21:00 | 32.2 | 62 | 1.96 | 0 | 26 | 30 | 17 | 3.2705 | 0
2024-09-20 22:00 | 31.6 | 64 | 1.25 | 0 | 26 | 30 | 17 | 4.4932 | 0
2024-09-20 23:00 | 30.9 | 67 | 1.08 | 0 | 26 | 30 | 17 | 5.6994 | 0
2024-09-21 | 30.4 | 69 | 0.95 | 0 | 26 | 30 | 17 | 6.6675 | 0
2024-09-21 01:00 | 30 | 71 | 0.98 | 0 | 26 | 30 | 17 | 7.4495 | 0
2024-09-21 02:00 | 30.1 | 70 | 0.54 | 0 | 26 | 30 | 17 | 6.6338 | 0
2024-09-21 03:00 | 28.7 | 76 | 1.43 | 0 | 26 | 30 | 17 | 12.6202 | 0
2024-09-21 04:00 | 28.2 | 79 | 1.61 | 0 | 26 | 30 | 17 | 13.8043 | 0
2024-09-21 05:00 | 28.1 | 83 | 1.51 | 0 | 26 | 30 | 17 | 10.3177 | 0
2024-09-21 06:00 | 27.7 | 86 | 1.84 | 0 | 26 | 30 | 17 | 10.7672 | 0
2024-09-21 07:00 | 28.3 | 83 | 1.5 | 38 | 26 | 30 | 17 | 3.6485 | 0
2024-09-21 08:00 | 30.6 | 73 | 1.65 | 209 | 26 | 30 | 17 | 0 | 0
2024-09-21 09:00 | 32.8 | 62 | 1.91 | 426 | 26 | 30 | 17 | 0 | 20.7308
2024-09-21 10:00 | 34.9 | 51 | 1.9 | 626 | 26 | 30 | 17 | 0 | 47.4683
2024-09-21 11:00 | 36.5 | 45 | 2.88 | 777 | 26 | 30 | 17 | 0 | 58.1502
2024-09-21 12:00 | 36.8 | 48 | 4.44 | 863 | 26 | 30 | 17 | 0 | 68.3578
2024-09-21 13:00 | 37.1 | 44 | 5.2 | 876 | 26 | 30 | 17 | 0 | 53.9446
2024-09-21 14:00 | 37.2 | 43 | 5.1 | 818 | 26 | 30 | 17 | 0 | 44.486
2024-09-21 15:00 | 37.1 | 43 | 4.96 | 690 | 26 | 30 | 17 | 0 | 27.001
2024-09-21 16:00 | 36.4 | 43 | 5.26 | 462 | 26 | 30 | 17 | 0 | 0
2024-09-21 17:00 | 35.8 | 42 | 4.84 | 293 | 26 | 30 | 17 | 0 | 0
2024-09-21 18:00 | 34.2 | 51 | 5.16 | 94 | 26 | 30 | 17 | 0 | 0
2024-09-21 19:00 | 33.2 | 60 | 3.62 | 2 | 26 | 30 | 17 | 0 | 0
2024-09-21 20:00 | 32.8 | 63 | 1.94 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-21 21:00 | 32.3 | 65 | 2.04 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-21 22:00 | 31.3 | 70 | 1.42 | 0 | 26 | 30 | 17 | 0.036 | 0
2024-09-21 23:00 | 30.7 | 74 | 0.89 | 0 | 26 | 30 | 17 | 0.86 | 0
2024-09-22 | 30 | 76 | 0.98 | 0 | 26 | 30 | 17 | 3.375 | 0
2024-09-22 01:00 | 29.2 | 78 | 1.51 | 0 | 26 | 30 | 17 | 7.0241 | 0
2024-09-22 02:00 | 28.8 | 78 | 2.04 | 0 | 26 | 30 | 17 | 10.8375 | 0
2024-09-22 03:00 | 28.1 | 81 | 2.32 | 0 | 26 | 30 | 17 | 13.8552 | 0
2024-09-22 04:00 | 27.5 | 84 | 2.21 | 0 | 26 | 30 | 17 | 15.4809 | 0
2024-09-22 05:00 | 27.7 | 83 | 2.12 | 0 | 26 | 30 | 17 | 14.6776 | 0
2024-09-22 06:00 | 27.2 | 84 | 2.56 | 0 | 26 | 30 | 17 | 19.2506 | 0
2024-09-22 07:00 | 27.7 | 80 | 2.7 | 38 | 26 | 30 | 17 | 15.0067 | 0
2024-09-22 08:00 | 30.7 | 65 | 2.81 | 211 | 26 | 30 | 17 | 0 | 0
2024-09-22 09:00 | 34.1 | 48 | 2.73 | 430 | 26 | 30 | 17 | 0 | 0
2024-09-22 10:00 | 37.1 | 35 | 2.51 | 631 | 26 | 30 | 17 | 0 | 24.7363
2024-09-22 11:00 | 39.3 | 28 | 3.5 | 785 | 26 | 30 | 17 | 0 | 28.8958
2024-09-22 12:00 | 40 | 29 | 4.97 | 875 | 26 | 30 | 17 | 0 | 32.269
2024-09-22 13:00 | 39.9 | 28 | 5.54 | 890 | 26 | 30 | 17 | 0 | 21.6557
2024-09-22 14:00 | 39.8 | 29 | 5.48 | 830 | 26 | 30 | 17 | 0 | 17.7248
2024-09-22 15:00 | 38.9 | 34 | 5.19 | 700 | 26 | 30 | 17 | 0 | 14.2169
2024-09-22 16:00 | 37.9 | 38 | 4.56 | 503 | 26 | 30 | 17 | 0 | 0
2024-09-22 17:00 | 36.7 | 42 | 4.71 | 293 | 26 | 30 | 17 | 0 | 0
2024-09-22 18:00 | 35.2 | 49 | 4.2 | 92 | 26 | 30 | 17 | 0 | 0
2024-09-22 19:00 | 34 | 58 | 2.79 | 2 | 26 | 30 | 17 | 0 | 0
2024-09-22 20:00 | 33 | 65 | 1.91 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-22 21:00 | 31.8 | 71 | 1.48 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-22 22:00 | 31.2 | 72 | 0.99 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-22 23:00 | 30.5 | 74 | 1.24 | 0 | 26 | 30 | 17 | 1.7134 | 0
2024-09-23 | 29.8 | 74 | 2.59 | 0 | 26 | 30 | 17 | 7.4028 | 0
2024-09-23 01:00 | 29 | 72 | 2.81 | 0 | 26 | 30 | 17 | 19.2375 | 0
2024-09-23 02:00 | 28.4 | 69 | 2.62 | 0 | 26 | 30 | 17 | 28.9802 | 0
2024-09-23 03:00 | 28 | 66 | 2.62 | 0 | 26 | 30 | 17 | 37.0696 | 0
2024-09-23 04:00 | 27.6 | 64 | 2.73 | 0 | 26 | 30 | 17 | 44.5073 | 0
2024-09-23 05:00 | 27.8 | 59 | 3.2 | 0 | 26 | 30 | 17 | 54.9023 | 0
2024-09-23 06:00 | 27.5 | 56 | 3.26 | 0 | 26 | 30 | 17 | 63.2821 | 0
2024-09-23 07:00 | 28.3 | 46 | 3.26 | 37 | 26 | 30 | 17 | 67.9347 | 0
2024-09-23 08:00 | 31.4 | 33 | 2.64 | 213 | 26 | 30 | 17 | 33.9471 | 0
2024-09-23 09:00 | 35.7 | 23 | 2.83 | 434 | 26 | 30 | 17 | 0 | 0
2024-09-23 10:00 | 38.3 | 19 | 2.75 | 637 | 26 | 30 | 17 | 0 | 0
2024-09-23 11:00 | 39.8 | 16 | 1.48 | 791 | 26 | 30 | 17 | 0 | 46.8894
2024-09-23 12:00 | 41.1 | 14 | 2.42 | 879 | 26 | 30 | 17 | 0 | 33.8326
2024-09-23 13:00 | 41.5 | 15 | 4.13 | 893 | 26 | 30 | 17 | 0 | 2.4487
2024-09-23 14:00 | 40.8 | 19 | 5.3 | 831 | 26 | 30 | 17 | 0 | 0
2024-09-23 15:00 | 39.6 | 23 | 5.71 | 701 | 26 | 30 | 17 | 0 | 0
2024-09-23 16:00 | 38 | 32 | 5.52 | 513 | 26 | 30 | 17 | 0 | 0
2024-09-23 17:00 | 36.6 | 38 | 4.61 | 293 | 26 | 30 | 17 | 0 | 0
2024-09-23 18:00 | 34.8 | 49 | 3.78 | 89 | 26 | 30 | 17 | 0 | 0
2024-09-23 19:00 | 33.7 | 59 | 2.87 | 1 | 26 | 30 | 17 | 0 | 0
2024-09-23 20:00 | 32.9 | 68 | 1.97 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-23 21:00 | 31.9 | 76 | 1.36 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-23 22:00 | 31.2 | 81 | 1.14 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-23 23:00 | 30.5 | 83 | 1.2 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-24 | 29.7 | 86 | 1.72 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-24 01:00 | 29.1 | 87 | 2.19 | 0 | 26 | 30 | 17 | 0.8597 | 0
2024-09-24 02:00 | 28.6 | 89 | 2.47 | 0 | 26 | 30 | 17 | 2.0679 | 0
2024-09-24 03:00 | 28 | 91 | 2.66 | 0 | 26 | 30 | 17 | 3.9027 | 0
2024-09-24 04:00 | 27.6 | 92 | 2.82 | 0 | 26 | 30 | 17 | 5.1655 | 0
2024-09-24 05:00 | 28.1 | 86 | 3.61 | 0 | 26 | 30 | 17 | 6.7453 | 0
2024-09-24 06:00 | 28 | 82 | 4.01 | 0 | 26 | 30 | 17 | 15.7797 | 0
2024-09-24 07:00 | 28.8 | 73 | 4.21 | 36 | 26 | 30 | 17 | 18.7118 | 0
2024-09-24 08:00 | 31.5 | 59 | 3.51 | 208 | 26 | 30 | 17 | 0 | 0
2024-09-24 09:00 | 34.9 | 46 | 4.57 | 425 | 26 | 30 | 17 | 0 | 0
2024-09-24 10:00 | 37 | 38 | 3.89 | 624 | 26 | 30 | 17 | 0 | 10.8839
2024-09-24 11:00 | 38.5 | 35 | 3.94 | 775 | 26 | 30 | 17 | 0 | 37.2495
2024-09-24 12:00 | 39.5 | 33 | 4.37 | 862 | 26 | 30 | 17 | 0 | 48.1169
2024-09-24 13:00 | 39.6 | 35 | 5.38 | 875 | 26 | 30 | 17 | 0 | 49.9591
2024-09-24 14:00 | 38.3 | 43 | 5.95 | 814 | 26 | 30 | 17 | 0 | 54.6689
2024-09-24 15:00 | 37.6 | 48 | 5.66 | 685 | 26 | 30 | 17 | 0 | 49.3643
2024-09-24 16:00 | 36.6 | 53 | 5.33 | 501 | 26 | 30 | 17 | 0 | 29.7619
2024-09-24 17:00 | 35.3 | 60 | 4.92 | 286 | 26 | 30 | 17 | 0 | 6.4817
2024-09-24 18:00 | 33.9 | 70 | 4.22 | 86 | 26 | 30 | 17 | 0 | 0
2024-09-24 19:00 | 33.1 | 76 | 3.52 | 1 | 26 | 30 | 17 | 0 | 0
2024-09-24 20:00 | 32.8 | 76 | 2.69 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-24 21:00 | 32.2 | 76 | 2.41 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-24 22:00 | 31.2 | 77 | 1.8 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-24 23:00 | 31.9 | 72 | 0.71 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-25 | 30.9 | 75 | 1.02 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-25 01:00 | 29.1 | 82 | 2.01 | 0 | 26 | 30 | 17 | 3.0111 | 0
2024-09-25 02:00 | 28.6 | 83 | 2.4 | 0 | 26 | 30 | 17 | 6.2194 | 0
2024-09-25 03:00 | 28 | 85 | 2.77 | 0 | 26 | 30 | 17 | 9.6647 | 0
2024-09-25 04:00 | 27.4 | 87 | 2.8 | 0 | 26 | 30 | 17 | 13.3503 | 0
2024-09-25 05:00 | 27.8 | 86 | 2.62 | 0 | 26 | 30 | 17 | 10.3153 | 0
2024-09-25 06:00 | 27.3 | 87 | 2.79 | 0 | 26 | 30 | 17 | 14.4408 | 0
2024-09-25 07:00 | 28 | 83 | 2.95 | 36 | 26 | 30 | 17 | 7.9974 | 0
2024-09-25 08:00 | 31.1 | 69 | 3 | 209 | 26 | 30 | 17 | 0 | 0
2024-09-25 09:00 | 33.9 | 58 | 3.41 | 427 | 26 | 30 | 17 | 0 | 9.2957
2024-09-25 10:00 | 36 | 48 | 2.84 | 626 | 26 | 30 | 17 | 0 | 40.5235
2024-09-25 11:00 | 37.9 | 41 | 3.01 | 777 | 26 | 30 | 17 | 0 | 60.2783
2024-09-25 12:00 | 39.4 | 35 | 3.67 | 863 | 26 | 30 | 17 | 0 | 62.0223
2024-09-25 13:00 | 39.5 | 35 | 5 | 878 | 26 | 30 | 17 | 0 | 52.3197
2024-09-25 14:00 | 38.4 | 44 | 6.14 | 817 | 26 | 30 | 17 | 0 | 60.3485
2024-09-25 15:00 | 37.4 | 51 | 6.29 | 688 | 26 | 30 | 17 | 0 | 56.9672
2024-09-25 16:00 | 36.2 | 58 | 5.8 | 502 | 26 | 30 | 17 | 0 | 41.0842
2024-09-25 17:00 | 34.8 | 63 | 5.73 | 285 | 26 | 30 | 17 | 0 | 5.5494
2024-09-25 18:00 | 33.2 | 77 | 4.83 | 84 | 26 | 30 | 17 | 0 | 0
2024-09-25 19:00 | 32.4 | 84 | 3.74 | 1 | 26 | 30 | 17 | 0 | 0
2024-09-25 20:00 | 32.1 | 87 | 3.04 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-25 21:00 | 31.6 | 90 | 2.53 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-25 22:00 | 30.9 | 95 | 2.06 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-25 23:00 | 30.3 | 98 | 1.73 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-26 | 29.8 | 99 | 1.2 | 0 | 26 | 30 | 17 | 0.7813 | 0
2024-09-26 01:00 | 29.9 | 99 | 0.93 | 0 | 26 | 30 | 17 | 1.1325 | 0
2024-09-26 02:00 | 30.1 | 99 | 0.4 | 0 | 26 | 30 | 17 | 1.9059 | 0
2024-09-26 03:00 | 29 | 100 | 1.42 | 0 | 26 | 30 | 17 | 2.553 | 0
2024-09-26 04:00 | 29.7 | 100 | 2.37 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-26 05:00 | 29.2 | 97 | 2.67 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-26 06:00 | 28.6 | 98 | 2.33 | 0 | 26 | 30 | 17 | 2.2831 | 0
2024-09-26 07:00 | 28.5 | 95 | 3.03 | 35 | 26 | 30 | 17 | 0 | 0
2024-09-26 08:00 | 30.3 | 79 | 3.46 | 206 | 26 | 30 | 17 | 0 | 0
2024-09-26 09:00 | 33.4 | 58 | 2.56 | 428 | 26 | 30 | 17 | 0 | 12.3373
2024-09-26 10:00 | 36.1 | 43 | 2.13 | 631 | 26 | 30 | 17 | 0 | 39.9218
2024-09-26 11:00 | 38.2 | 34 | 1.68 | 783 | 26 | 30 | 17 | 0 | 65.7161
2024-09-26 12:00 | 38.8 | 36 | 3.21 | 867 | 26 | 30 | 17 | 0 | 64.6793
2024-09-26 13:00 | 37.4 | 50 | 5.44 | 876 | 26 | 30 | 17 | 0 | 81.1747
2024-09-26 14:00 | 37.4 | 42 | 5.8 | 811 | 26 | 30 | 17 | 0 | 36.6197
2024-09-26 15:00 | 36.2 | 53 | 6.05 | 684 | 26 | 30 | 17 | 0 | 44.3594
2024-09-26 16:00 | 35.4 | 53 | 5.59 | 497 | 26 | 30 | 17 | 0 | 8.0897
2024-09-26 17:00 | 34.4 | 60 | 4.71 | 281 | 26 | 30 | 17 | 0 | 0
2024-09-26 18:00 | 32.8 | 74 | 3.37 | 81 | 26 | 30 | 17 | 0 | 0
2024-09-26 19:00 | 32 | 81 | 2.57 | 1 | 26 | 30 | 17 | 0 | 0
2024-09-26 20:00 | 31.5 | 85 | 1.68 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-26 21:00 | 30.7 | 90 | 0.63 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-26 22:00 | 30 | 93 | 1.37 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-26 23:00 | 29.3 | 95 | 1.62 | 0 | 26 | 30 | 17 | 1.3147 | 0
2024-09-27 | 28.5 | 98 | 1.46 | 0 | 26 | 30 | 17 | 3.9039 | 0
2024-09-27 01:00 | 28.2 | 99 | 1.68 | 0 | 26 | 30 | 17 | 4.4687 | 0
2024-09-27 02:00 | 27.9 | 100 | 1.9 | 0 | 26 | 30 | 17 | 5.1099 | 0
2024-09-27 03:00 | 28.1 | 99 | 1.64 | 0 | 26 | 30 | 17 | 4.8146 | 0
2024-09-27 04:00 | 28.4 | 97 | 1.7 | 0 | 26 | 30 | 17 | 3.8473 | 0
2024-09-27 05:00 | 27.2 | 99 | 1.88 | 0 | 26 | 30 | 17 | 7.2811 | 0
2024-09-27 06:00 | 27.1 | 99 | 2.06 | 0 | 26 | 30 | 17 | 7.4703 | 0
2024-09-27 07:00 | 26.9 | 99 | 1.6 | 24 | 26 | 30 | 17 | 5.1081 | 0
2024-09-27 08:00 | 27.8 | 94 | 1.77 | 145 | 26 | 30 | 17 | 0 | 0
2024-09-27 09:00 | 30.2 | 81 | 2.16 | 352 | 26 | 30 | 17 | 0 | 12.4878
2024-09-27 10:00 | 32.5 | 66 | 1.2 | 619 | 26 | 30 | 17 | 0 | 57.8686
2024-09-27 11:00 | 34.7 | 52 | 0.47 | 775 | 26 | 30 | 17 | 0 | 86.8897
2024-09-27 12:00 | 36.7 | 41 | 0.47 | 861 | 26 | 30 | 17 | 0 | 98.5842
2024-09-27 13:00 | 38.1 | 37 | 1.75 | 874 | 26 | 30 | 17 | 0 | 81.8422
2024-09-27 14:00 | 38.1 | 42 | 3.46 | 813 | 26 | 30 | 17 | 0 | 65.8843
2024-09-27 15:00 | 37.4 | 45 | 4.39 | 679 | 26 | 30 | 17 | 0 | 41.5715
2024-09-27 16:00 | 36.8 | 43 | 4.48 | 491 | 26 | 30 | 17 | 0 | 0.5321
2024-09-27 17:00 | 35 | 52 | 4.79 | 270 | 26 | 30 | 17 | 0 | 0
2024-09-27 18:00 | 33.2 | 63 | 4.44 | 77 | 26 | 30 | 17 | 0 | 0
2024-09-27 19:00 | 32.1 | 70 | 3.69 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-27 20:00 | 31.6 | 74 | 2.8 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-27 21:00 | 31 | 80 | 2 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-27 22:00 | 30.2 | 87 | 1.2 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-27 23:00 | 30.2 | 88 | 0.57 | 0 | 26 | 30 | 17 | 1.2596 | 0
2024-09-28 | 29.2 | 94 | 1.03 | 0 | 26 | 30 | 17 | 2.7252 | 0
2024-09-28 01:00 | 29 | 95 | 1.06 | 0 | 26 | 30 | 17 | 3.1912 | 0
2024-09-28 02:00 | 29.2 | 93 | 0.92 | 0 | 26 | 30 | 17 | 2.9333 | 0
2024-09-28 03:00 | 29.4 | 93 | 0.72 | 0 | 26 | 30 | 17 | 2.8282 | 0
2024-09-28 04:00 | 29.2 | 94 | 0.59 | 0 | 26 | 30 | 17 | 3.5573 | 0
2024-09-28 05:00 | 29.8 | 91 | 1.11 | 0 | 26 | 30 | 17 | 0.9834 | 0
2024-09-28 06:00 | 29.5 | 91 | 1.71 | 0 | 26 | 30 | 17 | 0.5384 | 0
2024-09-28 07:00 | 29.2 | 90 | 2.19 | 30 | 26 | 30 | 17 | 0 | 0
2024-09-28 08:00 | 29.9 | 84 | 1.68 | 202 | 26 | 30 | 17 | 0 | 0
2024-09-28 09:00 | 31.7 | 72 | 1.92 | 423 | 26 | 30 | 17 | 0 | 25.4042
2024-09-28 10:00 | 33.6 | 59 | 1.66 | 622 | 26 | 30 | 17 | 0 | 52.1379
2024-09-28 11:00 | 35.6 | 49 | 1.56 | 771 | 26 | 30 | 17 | 0 | 73.5655
2024-09-28 12:00 | 37.4 | 40 | 1.53 | 854 | 26 | 30 | 17 | 0 | 83.2058
2024-09-28 13:00 | 38.6 | 35 | 2.27 | 865 | 26 | 30 | 17 | 0 | 72.1981
2024-09-28 14:00 | 37.3 | 50 | 4.71 | 801 | 26 | 30 | 17 | 0 | 72.7132
2024-09-28 15:00 | 36.9 | 48 | 5.66 | 661 | 26 | 30 | 17 | 0 | 34.6339
2024-09-28 16:00 | 36 | 52 | 5.27 | 466 | 26 | 30 | 17 | 0 | 11.8522
2024-09-28 17:00 | 34.3 | 59 | 5.05 | 270 | 26 | 30 | 17 | 0 | 0
2024-09-28 18:00 | 32.9 | 70 | 4.26 | 74 | 26 | 30 | 17 | 0 | 0
2024-09-28 19:00 | 32.1 | 76 | 3.59 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-28 20:00 | 32 | 78 | 2.79 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-28 21:00 | 31.7 | 79 | 1.86 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-28 22:00 | 31.2 | 81 | 1.71 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-28 23:00 | 30.4 | 84 | 1.25 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-29 | 29.4 | 90 | 0.78 | 0 | 26 | 30 | 17 | 2.7076 | 0
2024-09-29 01:00 | 29.4 | 90 | 0.25 | 0 | 26 | 30 | 17 | 3.7726 | 0
2024-09-29 02:00 | 28.6 | 94 | 0.76 | 0 | 26 | 30 | 17 | 4.6955 | 0
2024-09-29 03:00 | 28.2 | 97 | 1.7 | 0 | 26 | 30 | 17 | 4.4427 | 0
2024-09-29 04:00 | 28.3 | 97 | 1.84 | 0 | 26 | 30 | 17 | 3.9548 | 0
2024-09-29 05:00 | 28.6 | 95 | 2.22 | 0 | 26 | 30 | 17 | 2.4521 | 0
2024-09-29 06:00 | 28.3 | 94 | 2.3 | 0 | 26 | 30 | 17 | 3.3295 | 0
2024-09-29 07:00 | 28.8 | 88 | 2.27 | 32 | 26 | 30 | 17 | 0 | 0
2024-09-29 08:00 | 30.8 | 77 | 3.53 | 197 | 26 | 30 | 17 | 0 | 0
2024-09-29 09:00 | 33.5 | 46 | 7.48 | 410 | 26 | 30 | 17 | 0 | 0
2024-09-29 10:00 | 35.3 | 39 | 6.63 | 609 | 26 | 30 | 17 | 0 | 0
2024-09-29 11:00 | 37.1 | 35 | 5.87 | 758 | 26 | 30 | 17 | 0 | 0
2024-09-29 12:00 | 38.5 | 32 | 4.84 | 840 | 26 | 30 | 17 | 0 | 23.8122
2024-09-29 13:00 | 39.4 | 30 | 3.97 | 849 | 26 | 30 | 17 | 0 | 38.6946
2024-09-29 14:00 | 40 | 27 | 3.18 | 786 | 26 | 30 | 17 | 0 | 37.087
2024-09-29 15:00 | 37.4 | 42 | 4.29 | 566 | 26 | 30 | 17 | 0 | 16.6541
2024-09-29 16:00 | 35.7 | 47 | 6.15 | 426 | 26 | 30 | 17 | 0 | 0
2024-09-29 17:00 | 35.1 | 52 | 6.61 | 231 | 26 | 30 | 17 | 0 | 0
2024-09-29 18:00 | 35.6 | 44 | 4.76 | 67 | 26 | 30 | 17 | 2.1317 | 0
2024-09-29 19:00 | 35.1 | 47 | 3.74 | 0 | 26 | 30 | 17 | 6.9718 | 0
2024-09-29 20:00 | 34.6 | 48 | 2.77 | 0 | 26 | 30 | 17 | 8.2181 | 0
2024-09-29 21:00 | 33.5 | 56 | 4.48 | 0 | 26 | 30 | 17 | 1.8905 | 0
2024-09-29 22:00 | 32.4 | 63 | 4.65 | 0 | 26 | 30 | 17 | 0 | 0
2024-09-29 23:00 | 31.5 | 66 | 5.78 | 0 | 26 | 30 | 17 | 1.893 | 0
2024-09-30 | 31 | 68 | 5.81 | 0 | 26 | 30 | 17 | 4.3116 | 0
2024-09-30 01:00 | 30.4 | 71 | 5.5 | 0 | 26 | 30 | 17 | 5.8622 | 0
2024-09-30 02:00 | 29.8 | 74 | 5.56 | 0 | 26 | 30 | 17 | 7.6216 | 0
2024-09-30 03:00 | 29.3 | 76 | 5.59 | 0 | 26 | 30 | 17 | 10.6951 | 0
2024-09-30 04:00 | 29.1 | 78 | 5.45 | 0 | 26 | 30 | 17 | 8.8356 | 0
2024-09-30 05:00 | 29.6 | 75 | 4.12 | 0 | 26 | 30 | 17 | 8.2815 | 0
2024-09-30 06:00 | 29.7 | 71 | 3.86 | 0 | 26 | 30 | 17 | 15.2838 | 0
2024-09-30 07:00 | 30.8 | 53 | 4.84 | 32 | 26 | 30 | 17 | 42.5576 | 0
2024-09-30 08:00 | 31.5 | 51 | 6.64 | 197 | 26 | 30 | 17 | 25.4269 | 0
2024-09-30 09:00 | 33 | 47 | 6.89 | 409 | 26 | 30 | 17 | 0 | 0
2024-09-30 10:00 | 34.5 | 43 | 6.83 | 602 | 26 | 30 | 17 | 0 | 0
2024-09-30 11:00 | 35.8 | 39 | 6.16 | 749 | 26 | 30 | 17 | 0 | 0
2024-09-30 12:00 | 36.7 | 37 | 5.12 | 832 | 26 | 30 | 17 | 0 | 16.4238
2024-09-30 13:00 | 37.6 | 35 | 3.59 | 839 | 26 | 30 | 17 | 0 | 40.8453
2024-09-30 14:00 | 37.6 | 33 | 2.09 | 705 | 26 | 30 | 17 | 0 | 41.5103
2024-09-30 15:00 | 37.7 | 32 | 4.55 | 587 | 26 | 30 | 17 | 0 | 0
2024-09-30 16:00 | 34.3 | 42 | 5.59 | 352 | 26 | 30 | 17 | 0 | 0
2024-09-30 17:00 | 33.7 | 48 | 4.55 | 208 | 26 | 30 | 17 | 0 | 0
2024-09-30 18:00 | 34.3 | 46 | 4.11 | 61 | 26 | 30 | 17 | 11.5949 | 0
2024-09-30 19:00 | 34.3 | 44 | 3.15 | 0 | 26 | 30 | 17 | 21.4774 | 0
2024-09-30 20:00 | 33.6 | 47 | 3.91 | 0 | 26 | 30 | 17 | 24.5017 | 0
2024-09-30 21:00 | 32.7 | 54 | 3.75 | 0 | 26 | 30 | 17 | 16.6369 | 0
2024-09-30 22:00 | 31.9 | 57 | 3.37 | 0 | 26 | 30 | 17 | 17.8389 | 0
2024-09-30 23:00 | 31.2 | 58 | 3.02 | 0 | 26 | 30 | 17 | 22.0019 | 0
2024-10-01 | 30.6 | 61 | 2.97 | 0 | 26 | 30 | 17 | 22.2666 | 0
2024-10-01 01:00 | 29.9 | 65 | 3.14 | 0 | 26 | 30 | 17 | 22.8876 | 0
2024-10-01 02:00 | 29.4 | 68 | 3.72 | 0 | 26 | 30 | 17 | 24.8229 | 0
2024-10-01 03:00 | 29.2 | 67 | 3.98 | 0 | 26 | 30 | 17 | 30.2401 | 0
2024-10-01 04:00 | 28.9 | 68 | 3.8 | 0 | 26 | 30 | 17 | 31.135 | 0
2024-10-01 05:00 | 28.8 | 68 | 3.36 | 0 | 26 | 30 | 17 | 30.3248 | 0
2024-10-01 06:00 | 28.6 | 68 | 2.9 | 0 | 26 | 30 | 17 | 30.1195 | 0
2024-10-01 07:00 | 29.1 | 65 | 2.12 | 31 | 26 | 30 | 17 | 21.2686 | 0
2024-10-01 08:00 | 30.8 | 57 | 1.87 | 196 | 26 | 30 | 17 | 0 | 0
2024-10-01 09:00 | 33.2 | 45 | 2.07 | 408 | 26 | 30 | 17 | 0 | 0
2024-10-01 10:00 | 34.9 | 38 | 1.66 | 603 | 26 | 30 | 17 | 0 | 27.2564
2024-10-01 11:00 | 36 | 36 | 1.54 | 751 | 26 | 30 | 17 | 0 | 53.6017
2024-10-01 12:00 | 36.8 | 34 | 1.23 | 834 | 26 | 30 | 17 | 0 | 73.4479
2024-10-01 13:00 | 37.4 | 32 | 2.16 | 843 | 26 | 30 | 17 | 0 | 55.2401
2024-10-01 14:00 | 37.2 | 35 | 4.8 | 759 | 26 | 30 | 17 | 0 | 9.3576
2024-10-01 15:00 | 36.1 | 39 | 5.76 | 573 | 26 | 30 | 17 | 0 | 0
2024-10-01 16:00 | 35.2 | 43 | 5.62 | 428 | 26 | 30 | 17 | 0 | 0
2024-10-01 17:00 | 35 | 47 | 4.31 | 223 | 26 | 30 | 17 | 0 | 0
2024-10-01 18:00 | 33.8 | 53 | 4.76 | 63 | 26 | 30 | 17 | 0 | 0
2024-10-01 19:00 | 33.2 | 56 | 4.52 | 0 | 26 | 30 | 17 | 5.9984 | 0
2024-10-01 20:00 | 32.9 | 60 | 4.41 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-01 21:00 | 32.5 | 63 | 3.9 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-01 22:00 | 32.2 | 65 | 2.6 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-01 23:00 | 31.7 | 68 | 2.01 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-02 | 31.3 | 71 | 1.88 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-02 01:00 | 30.7 | 73 | 2.01 | 0 | 26 | 30 | 17 | 0.4308 | 0
2024-10-02 02:00 | 30.1 | 76 | 1.97 | 0 | 26 | 30 | 17 | 1.7856 | 0
2024-10-02 03:00 | 29.5 | 78 | 2.15 | 0 | 26 | 30 | 17 | 4.4599 | 0
2024-10-02 04:00 | 29 | 80 | 2.55 | 0 | 26 | 30 | 17 | 6.4205 | 0
2024-10-02 05:00 | 28.9 | 80 | 2.5 | 0 | 26 | 30 | 17 | 7.4583 | 0
2024-10-02 06:00 | 28.7 | 81 | 2.75 | 0 | 26 | 30 | 17 | 8.092 | 0
2024-10-02 07:00 | 29.2 | 79 | 2.81 | 31 | 26 | 30 | 17 | 1.5892 | 0
2024-10-02 08:00 | 31.2 | 69 | 3.25 | 195 | 26 | 30 | 17 | 0 | 0
2024-10-02 09:00 | 33.2 | 55 | 3.91 | 407 | 26 | 30 | 17 | 0 | 0
2024-10-02 10:00 | 35.2 | 40 | 3.7 | 600 | 26 | 30 | 17 | 0 | 0
2024-10-02 11:00 | 36.4 | 35 | 2.87 | 750 | 26 | 30 | 17 | 0 | 28.798
2024-10-02 12:00 | 37.2 | 33 | 1.79 | 834 | 26 | 30 | 17 | 0 | 62.0186
2024-10-02 13:00 | 38 | 30 | 1.22 | 845 | 26 | 30 | 17 | 0 | 75.8565
2024-10-02 14:00 | 38.5 | 29 | 1.53 | 781 | 26 | 30 | 17 | 0 | 61.163
2024-10-02 15:00 | 38.5 | 30 | 3.26 | 650 | 26 | 30 | 17 | 0 | 13.5372
2024-10-02 16:00 | 37.6 | 33 | 5.21 | 463 | 26 | 30 | 17 | 0 | 0
2024-10-02 17:00 | 35.8 | 38 | 5.97 | 252 | 26 | 30 | 17 | 0 | 0
2024-10-02 18:00 | 34.6 | 44 | 5.81 | 63 | 26 | 30 | 17 | 18.4157 | 0
2024-10-02 19:00 | 33.7 | 49 | 5.48 | 0 | 26 | 30 | 17 | 21.685 | 0
2024-10-02 20:00 | 33 | 55 | 4.88 | 0 | 26 | 30 | 17 | 11.886 | 0
2024-10-02 21:00 | 32.6 | 62 | 3.34 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-02 22:00 | 32.2 | 66 | 2.41 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-02 23:00 | 31.6 | 71 | 2.17 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-03 | 30.9 | 75 | 1.36 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-03 01:00 | 30.7 | 76 | 0.76 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-03 02:00 | 30.4 | 78 | 0.75 | 0 | 26 | 30 | 17 | 0.3221 | 0
2024-10-03 03:00 | 30.4 | 78 | 0.57 | 0 | 26 | 30 | 17 | 0.7902 | 0
2024-10-03 04:00 | 29.1 | 83 | 1.18 | 0 | 26 | 30 | 17 | 3.0836 | 0
2024-10-03 05:00 | 28.5 | 81 | 2.16 | 0 | 26 | 30 | 17 | 9.8526 | 0
2024-10-03 06:00 | 28.1 | 82 | 2.32 | 0 | 26 | 30 | 17 | 12.5205 | 0
2024-10-03 07:00 | 28.8 | 79 | 2.36 | 31 | 26 | 30 | 17 | 5.6553 | 0
2024-10-03 08:00 | 31.2 | 69 | 3.06 | 197 | 26 | 30 | 17 | 0 | 0
2024-10-03 09:00 | 33.3 | 59 | 2.73 | 412 | 26 | 30 | 17 | 0 | 9.3255
2024-10-03 10:00 | 35.7 | 41 | 2.44 | 611 | 26 | 30 | 17 | 0 | 25.0732
2024-10-03 11:00 | 37.7 | 30 | 3.36 | 761 | 26 | 30 | 17 | 0 | 19.6561
2024-10-03 12:00 | 38.6 | 27 | 4.48 | 846 | 26 | 30 | 17 | 0 | 11.2579
2024-10-03 13:00 | 38.3 | 28 | 5.35 | 856 | 26 | 30 | 17 | 0 | 0.1288
2024-10-03 14:00 | 37.4 | 33 | 5.68 | 791 | 26 | 30 | 17 | 0 | 0
2024-10-03 15:00 | 36.2 | 44 | 6.35 | 659 | 26 | 30 | 17 | 0 | 1.045
2024-10-03 16:00 | 35.2 | 51 | 6.37 | 471 | 26 | 30 | 17 | 0 | 0
2024-10-03 17:00 | 34.1 | 53 | 6.29 | 256 | 26 | 30 | 17 | 0 | 0
2024-10-03 18:00 | 33.3 | 56 | 5.82 | 63 | 26 | 30 | 17 | 0 | 0
2024-10-03 19:00 | 32.7 | 59 | 5.08 | 0 | 26 | 30 | 17 | 4.3647 | 0
2024-10-03 20:00 | 32.3 | 61 | 3.78 | 0 | 26 | 30 | 17 | 4.6356 | 0
2024-10-03 21:00 | 31.8 | 64 | 3.15 | 0 | 26 | 30 | 17 | 3.9436 | 0
2024-10-03 22:00 | 31.1 | 67 | 2.47 | 0 | 26 | 30 | 17 | 5.6518 | 0
2024-10-03 23:00 | 30.3 | 71 | 1.99 | 0 | 26 | 30 | 17 | 6.7533 | 0
2024-10-04 | 29.7 | 74 | 2.12 | 0 | 26 | 30 | 17 | 8.0959 | 0
2024-10-04 01:00 | 29.2 | 77 | 2.23 | 0 | 26 | 30 | 17 | 8.6801 | 0
2024-10-04 02:00 | 28.6 | 80 | 2.32 | 0 | 26 | 30 | 17 | 10.3697 | 0
2024-10-04 03:00 | 28 | 83 | 3.07 | 0 | 26 | 30 | 17 | 12.9787 | 0
2024-10-04 04:00 | 27.5 | 84 | 3.8 | 0 | 26 | 30 | 17 | 18.4143 | 0
2024-10-04 05:00 | 27.8 | 83 | 3.85 | 0 | 26 | 30 | 17 | 16.367 | 0
2024-10-04 06:00 | 27.6 | 84 | 3.92 | 0 | 26 | 30 | 17 | 17.2667 | 0
2024-10-04 07:00 | 28 | 83 | 3.99 | 31 | 26 | 30 | 17 | 9.6317 | 0
2024-10-04 08:00 | 30 | 73 | 4.09 | 198 | 26 | 30 | 17 | 0 | 0
2024-10-04 09:00 | 32.8 | 62 | 4.86 | 415 | 26 | 30 | 17 | 0 | 0
2024-10-04 10:00 | 35.1 | 53 | 5.42 | 613 | 26 | 30 | 17 | 0 | 20.0891
2024-10-04 11:00 | 37.2 | 42 | 5.89 | 761 | 26 | 30 | 17 | 0 | 26.0448
2024-10-04 12:00 | 38.1 | 36 | 6.96 | 845 | 26 | 30 | 17 | 0 | 14.1164
2024-10-04 13:00 | 37.7 | 40 | 7.8 | 858 | 26 | 30 | 17 | 0 | 22.7786
2024-10-04 14:00 | 37 | 48 | 8.25 | 794 | 26 | 30 | 17 | 0 | 40.517
2024-10-04 15:00 | 36.4 | 52 | 8.2 | 657 | 26 | 30 | 17 | 0 | 30.4996
2024-10-04 16:00 | 35.7 | 55 | 7.91 | 471 | 26 | 30 | 17 | 0 | 6.514
2024-10-04 17:00 | 34.8 | 52 | 6.75 | 257 | 26 | 30 | 17 | 0 | 0
2024-10-04 18:00 | 33.3 | 61 | 6.02 | 62 | 26 | 30 | 17 | 0 | 0
2024-10-04 19:00 | 32.5 | 66 | 5.06 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-04 20:00 | 32 | 68 | 4.36 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-04 21:00 | 31.8 | 64 | 4.08 | 0 | 26 | 30 | 17 | 3.7939 | 0
2024-10-04 22:00 | 31.3 | 65 | 4.08 | 0 | 26 | 30 | 17 | 8.0212 | 0
2024-10-04 23:00 | 30.6 | 73 | 3.99 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-05 | 30.1 | 74 | 3.89 | 0 | 26 | 30 | 17 | 3.6832 | 0
2024-10-05 01:00 | 29.9 | 76 | 3.97 | 0 | 26 | 30 | 17 | 2.0349 | 0
2024-10-05 02:00 | 30 | 75 | 4.16 | 0 | 26 | 30 | 17 | 2.6802 | 0
2024-10-05 03:00 | 29.7 | 80 | 4.06 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-05 04:00 | 29.4 | 78 | 3.66 | 0 | 26 | 30 | 17 | 4.8249 | 0
2024-10-05 05:00 | 29.1 | 71 | 3.26 | 0 | 26 | 30 | 17 | 21.1965 | 0
2024-10-05 06:00 | 28.4 | 72 | 2.82 | 0 | 26 | 30 | 17 | 25.4224 | 0
2024-10-05 07:00 | 28.7 | 69 | 2.48 | 31 | 26 | 30 | 17 | 21.2397 | 0
2024-10-05 08:00 | 30.6 | 61 | 2.83 | 200 | 26 | 30 | 17 | 0 | 0
2024-10-05 09:00 | 32.1 | 53 | 3.8 | 419 | 26 | 30 | 17 | 0 | 0
2024-10-05 10:00 | 33.3 | 48 | 4.19 | 618 | 26 | 30 | 17 | 0 | 0
2024-10-05 11:00 | 34.4 | 43 | 4.46 | 766 | 26 | 30 | 17 | 0 | 8.0637
2024-10-05 12:00 | 35.4 | 39 | 4.94 | 847 | 26 | 30 | 17 | 0 | 11.6198
2024-10-05 13:00 | 36 | 38 | 5.72 | 853 | 26 | 30 | 17 | 0 | 6.3422
2024-10-05 14:00 | 36 | 36 | 6.15 | 784 | 26 | 30 | 17 | 0 | 0
2024-10-05 15:00 | 35.7 | 37 | 6.25 | 652 | 26 | 30 | 17 | 0 | 0
2024-10-05 16:00 | 34.9 | 42 | 6.21 | 465 | 26 | 30 | 17 | 0 | 0
2024-10-05 17:00 | 33.9 | 48 | 6.15 | 248 | 26 | 30 | 17 | 0 | 0
2024-10-05 18:00 | 33 | 50 | 5.45 | 58 | 26 | 30 | 17 | 20.5761 | 0
2024-10-05 19:00 | 32.5 | 51 | 4.03 | 0 | 26 | 30 | 17 | 27.2957 | 0
2024-10-05 20:00 | 31.8 | 53 | 3.49 | 0 | 26 | 30 | 17 | 28.0816 | 0
2024-10-05 21:00 | 31 | 57 | 3.25 | 0 | 26 | 30 | 17 | 27.0223 | 0
2024-10-05 22:00 | 30.1 | 61 | 3.02 | 0 | 26 | 30 | 17 | 27.5549 | 0
2024-10-05 23:00 | 29.3 | 64 | 2.83 | 0 | 26 | 30 | 17 | 29.3203 | 0
2024-10-06 | 28.6 | 69 | 2.47 | 0 | 26 | 30 | 17 | 26.2935 | 0
2024-10-06 01:00 | 27.7 | 73 | 2.1 | 0 | 26 | 30 | 17 | 26.7981 | 0
2024-10-06 02:00 | 27.2 | 73 | 2.18 | 0 | 26 | 30 | 17 | 31.5316 | 0
2024-10-06 03:00 | 26.5 | 74 | 2.62 | 0 | 26 | 30 | 17 | 39.759 | 0
2024-10-06 04:00 | 26 | 77 | 2.46 | 0 | 26 | 30 | 17 | 39.2195 | 0
2024-10-06 05:00 | 25.8 | 79 | 2.34 | 0 | 26 | 30 | 17 | 37.6386 | 0
2024-10-06 06:00 | 25.5 | 81 | 2.49 | 0 | 26 | 30 | 17 | 39.1318 | 0
2024-10-06 07:00 | 26.1 | 78 | 2.5 | 30 | 26 | 30 | 17 | 33.3312 | 0
2024-10-06 08:00 | 28.7 | 67 | 2.38 | 198 | 26 | 30 | 17 | 0.9947 | 0
2024-10-06 09:00 | 30.7 | 59 | 1.95 | 416 | 26 | 30 | 17 | 0 | 0
2024-10-06 10:00 | 32.3 | 49 | 1.77 | 615 | 26 | 30 | 17 | 0 | 25.4986
2024-10-06 11:00 | 33.8 | 43 | 1.2 | 763 | 26 | 30 | 17 | 0 | 59.4751
2024-10-06 12:00 | 35.1 | 38 | 1.42 | 843 | 26 | 30 | 17 | 0 | 66.249
2024-10-06 13:00 | 35.9 | 35 | 2.89 | 851 | 26 | 30 | 17 | 0 | 37.8088
2024-10-06 14:00 | 34.7 | 46 | 5.69 | 784 | 26 | 30 | 17 | 0 | 9.1757
2024-10-06 15:00 | 34 | 44 | 6.34 | 646 | 26 | 30 | 17 | 0 | 0
2024-10-06 16:00 | 33.7 | 51 | 5.62 | 460 | 26 | 30 | 17 | 0 | 0
2024-10-06 17:00 | 32.1 | 50 | 5.85 | 244 | 26 | 30 | 17 | 9.8531 | 0
2024-10-06 18:00 | 32 | 54 | 3.91 | 56 | 26 | 30 | 17 | 17.733 | 0
2024-10-06 19:00 | 31.1 | 56 | 3.65 | 0 | 26 | 30 | 17 | 29.9058 | 0
2024-10-06 20:00 | 30.8 | 58 | 2.26 | 0 | 26 | 30 | 17 | 22.1032 | 0
2024-10-06 21:00 | 30.2 | 62 | 1.45 | 0 | 26 | 30 | 17 | 16.7583 | 0
2024-10-06 22:00 | 29.6 | 66 | 1.74 | 0 | 26 | 30 | 17 | 18.0906 | 0
2024-10-06 23:00 | 29.1 | 68 | 2.3 | 0 | 26 | 30 | 17 | 22.3424 | 0
2024-10-07 | 28.5 | 71 | 1.94 | 0 | 26 | 30 | 17 | 21.7252 | 0
2024-10-07 01:00 | 27.9 | 74 | 1.7 | 0 | 26 | 30 | 17 | 21.7216 | 0
2024-10-07 02:00 | 27.3 | 76 | 1.5 | 0 | 26 | 30 | 17 | 22.8806 | 0
2024-10-07 03:00 | 27.1 | 76 | 2.21 | 0 | 26 | 30 | 17 | 28.943 | 0
2024-10-07 04:00 | 26.8 | 77 | 2.88 | 0 | 26 | 30 | 17 | 34.5 | 0
2024-10-07 05:00 | 27.5 | 75 | 2.63 | 0 | 26 | 30 | 17 | 28.9913 | 0
2024-10-07 06:00 | 27.2 | 78 | 2.75 | 0 | 26 | 30 | 17 | 28.3144 | 0
2024-10-07 07:00 | 27.7 | 69 | 1.96 | 28 | 26 | 30 | 17 | 26.791 | 0
2024-10-07 08:00 | 30.3 | 41 | 1.92 | 194 | 26 | 30 | 17 | 20.3347 | 0
2024-10-07 09:00 | 32.2 | 32 | 2.51 | 411 | 26 | 30 | 17 | 1.5289 | 0
2024-10-07 10:00 | 34.3 | 33 | 3.92 | 605 | 26 | 30 | 17 | 0 | 0
2024-10-07 11:00 | 36.1 | 29 | 4.31 | 746 | 26 | 30 | 17 | 0 | 0
2024-10-07 12:00 | 37.6 | 24 | 4.04 | 823 | 26 | 30 | 17 | 0 | 0
2024-10-07 13:00 | 38.2 | 23 | 2.09 | 826 | 26 | 30 | 17 | 0 | 40.2718
2024-10-07 14:00 | 38.7 | 22 | 1.24 | 757 | 26 | 30 | 17 | 0 | 54.7596
2024-10-07 15:00 | 38.6 | 21 | 3.67 | 574 | 26 | 30 | 17 | 0 | 0
2024-10-07 16:00 | 37.5 | 27 | 7.65 | 438 | 26 | 30 | 17 | 7.4496 | 0
2024-10-07 17:00 | 36.2 | 32 | 6.79 | 187 | 26 | 30 | 17 | 31.1925 | 0
2024-10-07 18:00 | 34.1 | 40 | 7.58 | 49 | 26 | 30 | 17 | 49.9845 | 0
2024-10-07 19:00 | 33.5 | 44 | 4.35 | 0 | 26 | 30 | 17 | 35.7847 | 0
2024-10-07 20:00 | 32.5 | 49 | 3.05 | 0 | 26 | 30 | 17 | 27.2863 | 0
2024-10-07 21:00 | 31.8 | 54 | 3.12 | 0 | 26 | 30 | 17 | 24.2549 | 0
2024-10-07 22:00 | 31 | 58 | 3.2 | 0 | 26 | 30 | 17 | 24.8106 | 0
2024-10-07 23:00 | 29.9 | 64 | 2.89 | 0 | 26 | 30 | 17 | 23.6763 | 0
2024-10-08 | 29.1 | 68 | 3.1 | 0 | 26 | 30 | 17 | 25.9156 | 0
2024-10-08 01:00 | 28.9 | 63 | 3.61 | 0 | 26 | 30 | 17 | 39.8454 | 0
2024-10-08 02:00 | 28.5 | 63 | 3.48 | 0 | 26 | 30 | 17 | 43.3307 | 0
2024-10-08 03:00 | 27.9 | 69 | 3.18 | 0 | 26 | 30 | 17 | 37.3012 | 0
2024-10-08 04:00 | 27 | 74 | 2.43 | 0 | 26 | 30 | 17 | 33.7841 | 0
2024-10-08 05:00 | 27 | 73 | 3.81 | 0 | 26 | 30 | 17 | 44.4397 | 0
2024-10-08 06:00 | 26.8 | 69 | 4.52 | 0 | 26 | 30 | 17 | 59.3265 | 0
2024-10-08 07:00 | 27.4 | 68 | 5.13 | 28 | 26 | 30 | 17 | 53.9981 | 0
2024-10-08 08:00 | 29.5 | 68 | 6.31 | 193 | 26 | 30 | 17 | 4.3941 | 0
2024-10-08 09:00 | 32 | 59 | 7.07 | 409 | 26 | 30 | 17 | 0 | 0
2024-10-08 10:00 | 34.5 | 44 | 6.18 | 605 | 26 | 30 | 17 | 0 | 0
2024-10-08 11:00 | 36.5 | 31 | 4.63 | 751 | 26 | 30 | 17 | 0 | 0
2024-10-08 12:00 | 37.8 | 25 | 3.4 | 832 | 26 | 30 | 17 | 0 | 14.3797
2024-10-08 13:00 | 38.7 | 20 | 2.8 | 780 | 26 | 30 | 17 | 0 | 12.7218
2024-10-08 14:00 | 39.1 | 18 | 2.54 | 724 | 26 | 30 | 17 | 0 | 8.7383
2024-10-08 15:00 | 38.3 | 23 | 5.53 | 543 | 26 | 30 | 17 | 0 | 0
2024-10-08 16:00 | 37.3 | 22 | 6.6 | 303 | 26 | 30 | 17 | 45.8067 | 0
2024-10-08 17:00 | 36.7 | 22 | 5.38 | 222 | 26 | 30 | 17 | 51.8945 | 0
2024-10-08 18:00 | 33.7 | 47 | 5.35 | 50 | 26 | 30 | 17 | 21.2682 | 0
2024-10-08 19:00 | 32.8 | 53 | 3.9 | 0 | 26 | 30 | 17 | 18.3016 | 0
2024-10-08 20:00 | 31.7 | 64 | 4.15 | 0 | 26 | 30 | 17 | 5.1194 | 0
2024-10-08 21:00 | 31.1 | 68 | 3.41 | 0 | 26 | 30 | 17 | 3.8405 | 0
2024-10-08 22:00 | 30.3 | 67 | 2.51 | 0 | 26 | 30 | 17 | 13.4849 | 0
2024-10-08 23:00 | 29.3 | 65 | 2.25 | 0 | 26 | 30 | 17 | 24.5472 | 0
2024-10-09 | 28.5 | 65 | 2.33 | 0 | 26 | 30 | 17 | 31.9057 | 0
2024-10-09 01:00 | 27.6 | 69 | 2.09 | 0 | 26 | 30 | 17 | 32.3922 | 0
2024-10-09 02:00 | 26.7 | 71 | 1.78 | 0 | 26 | 30 | 17 | 34.344 | 0
2024-10-09 03:00 | 26.9 | 67 | 1.03 | 0 | 26 | 30 | 17 | 28.2676 | 0
2024-10-09 04:00 | 26.1 | 70 | 1.14 | 0 | 26 | 30 | 17 | 31.9125 | 0
2024-10-09 05:00 | 26.5 | 68 | 2.57 | 0 | 26 | 30 | 17 | 47.1979 | 0
2024-10-09 06:00 | 26 | 66 | 3.08 | 0 | 26 | 30 | 17 | 59.8647 | 0
2024-10-09 07:00 | 26.8 | 61 | 3.47 | 27 | 26 | 30 | 17 | 60.4986 | 0
2024-10-09 08:00 | 29.8 | 45 | 3.77 | 191 | 26 | 30 | 17 | 41.8887 | 0
2024-10-09 09:00 | 32.2 | 41 | 5.53 | 405 | 26 | 30 | 17 | 13.2668 | 0
2024-10-09 10:00 | 33.5 | 41 | 5.66 | 598 | 26 | 30 | 17 | 0 | 0
2024-10-09 11:00 | 35.2 | 36 | 5.16 | 742 | 26 | 30 | 17 | 0 | 0
2024-10-09 12:00 | 36.5 | 30 | 4.09 | 822 | 26 | 30 | 17 | 0 | 3.8592
2024-10-09 13:00 | 37.5 | 25 | 2.64 | 830 | 26 | 30 | 17 | 0 | 27.9204
2024-10-09 14:00 | 37.9 | 22 | 2.8 | 701 | 26 | 30 | 17 | 0 | 1.9542
2024-10-09 15:00 | 35.7 | 38 | 6.83 | 542 | 26 | 30 | 17 | 0 | 0
2024-10-09 16:00 | 34.8 | 37 | 6.48 | 309 | 26 | 30 | 17 | 11.7104 | 0
2024-10-09 17:00 | 33.3 | 46 | 6.55 | 218 | 26 | 30 | 17 | 11.8173 | 0
2024-10-09 18:00 | 32.3 | 54 | 5.99 | 48 | 26 | 30 | 17 | 20.7321 | 0
2024-10-09 19:00 | 31.6 | 56 | 5.27 | 0 | 26 | 30 | 17 | 29.6459 | 0
2024-10-09 20:00 | 31.3 | 61 | 3.46 | 0 | 26 | 30 | 17 | 16.236 | 0
2024-10-09 21:00 | 30.7 | 65 | 2.16 | 0 | 26 | 30 | 17 | 12.0381 | 0
2024-10-09 22:00 | 30.1 | 69 | 1.75 | 0 | 26 | 30 | 17 | 10.6349 | 0
2024-10-09 23:00 | 29.4 | 74 | 1.66 | 0 | 26 | 30 | 17 | 10.0381 | 0
2024-10-10 | 28.7 | 76 | 1.79 | 0 | 26 | 30 | 17 | 13.6178 | 0
2024-10-10 01:00 | 27.9 | 77 | 2.16 | 0 | 26 | 30 | 17 | 20.4311 | 0
2024-10-10 02:00 | 27.2 | 79 | 1.86 | 0 | 26 | 30 | 17 | 22.6765 | 0
2024-10-10 03:00 | 26.6 | 81 | 1.54 | 0 | 26 | 30 | 17 | 23.479 | 0
2024-10-10 04:00 | 26.2 | 84 | 1.39 | 0 | 26 | 30 | 17 | 22.7601 | 0
2024-10-10 05:00 | 27.2 | 80 | 2.2 | 0 | 26 | 30 | 17 | 23.1332 | 0
2024-10-10 06:00 | 26.9 | 82 | 1.93 | 0 | 26 | 30 | 17 | 22.21 | 0
2024-10-10 07:00 | 27.3 | 80 | 1.73 | 26 | 26 | 30 | 17 | 16.6844 | 0
2024-10-10 08:00 | 29.8 | 69 | 1.73 | 187 | 26 | 30 | 17 | 0 | 0
2024-10-10 09:00 | 31.6 | 61 | 1.84 | 400 | 26 | 30 | 17 | 0 | 6.8221
2024-10-10 10:00 | 33.7 | 46 | 2.53 | 592 | 26 | 30 | 17 | 0 | 14.2771
2024-10-10 11:00 | 35.1 | 37 | 2.61 | 738 | 26 | 30 | 17 | 0 | 25.7158
2024-10-10 12:00 | 36.1 | 32 | 1.39 | 818 | 26 | 30 | 17 | 0 | 60.6686
2024-10-10 13:00 | 36.9 | 31 | 2.64 | 827 | 26 | 30 | 17 | 0 | 37.7306
2024-10-10 14:00 | 36 | 35 | 4.49 | 758 | 26 | 30 | 17 | 0 | 0
2024-10-10 15:00 | 35.2 | 36 | 4.32 | 485 | 26 | 30 | 17 | 0 | 0
2024-10-10 16:00 | 34.6 | 41 | 5.45 | 407 | 26 | 30 | 17 | 0 | 0
2024-10-10 17:00 | 33.6 | 48 | 5.66 | 218 | 26 | 30 | 17 | 0 | 0
2024-10-10 18:00 | 32.4 | 58 | 5.46 | 47 | 26 | 30 | 17 | 5.7253 | 0
2024-10-10 19:00 | 32 | 61 | 5.4 | 0 | 26 | 30 | 17 | 9.0745 | 0
2024-10-10 20:00 | 31.8 | 62 | 4.17 | 0 | 26 | 30 | 17 | 8.7444 | 0
2024-10-10 21:00 | 31.4 | 64 | 2.83 | 0 | 26 | 30 | 17 | 8.1411 | 0
2024-10-10 22:00 | 30.7 | 67 | 2.55 | 0 | 26 | 30 | 17 | 9.6584 | 0
2024-10-10 23:00 | 30 | 70 | 2.08 | 0 | 26 | 30 | 17 | 10.8691 | 0
2024-10-11 | 29.2 | 74 | 1.81 | 0 | 26 | 30 | 17 | 11.9438 | 0
2024-10-11 01:00 | 28.5 | 77 | 2.11 | 0 | 26 | 30 | 17 | 14.9263 | 0
2024-10-11 02:00 | 27.8 | 80 | 2.62 | 0 | 26 | 30 | 17 | 18.884 | 0
2024-10-11 03:00 | 27 | 84 | 2.54 | 0 | 26 | 30 | 17 | 21.2088 | 0
2024-10-11 04:00 | 26.6 | 86 | 2.14 | 0 | 26 | 30 | 17 | 21.1785 | 0
2024-10-11 05:00 | 26.7 | 82 | 1.26 | 0 | 26 | 30 | 17 | 20.2597 | 0
2024-10-11 06:00 | 26.3 | 83 | 1.64 | 0 | 26 | 30 | 17 | 24.4344 | 0
2024-10-11 07:00 | 27.2 | 76 | 1.5 | 26 | 26 | 30 | 17 | 20.0713 | 0
2024-10-11 08:00 | 29.5 | 66 | 1.47 | 187 | 26 | 30 | 17 | 0 | 0
2024-10-11 09:00 | 31.9 | 58 | 1.98 | 400 | 26 | 30 | 17 | 0 | 2.7591
2024-10-11 10:00 | 34.3 | 43 | 2.84 | 593 | 26 | 30 | 17 | 0 | 8.2913
2024-10-11 11:00 | 36 | 32 | 3.62 | 738 | 26 | 30 | 17 | 0 | 2.2529
2024-10-11 12:00 | 36.9 | 29 | 4.55 | 819 | 26 | 30 | 17 | 0 | 0
2024-10-11 13:00 | 37.1 | 27 | 5.41 | 818 | 26 | 30 | 17 | 0 | 0
2024-10-11 14:00 | 36.9 | 26 | 5.4 | 690 | 26 | 30 | 17 | 0 | 0
2024-10-11 15:00 | 36.5 | 26 | 4.7 | 541 | 26 | 30 | 17 | 0 | 0
2024-10-11 16:00 | 35.8 | 30 | 4.78 | 399 | 26 | 30 | 17 | 2.6143 | 0
2024-10-11 17:00 | 34.1 | 42 | 5.15 | 214 | 26 | 30 | 17 | 9.5017 | 0
2024-10-11 18:00 | 32.3 | 53 | 4.38 | 43 | 26 | 30 | 17 | 19.9953 | 0
2024-10-11 19:00 | 31.7 | 60 | 2.97 | 0 | 26 | 30 | 17 | 12.8363 | 0
2024-10-11 20:00 | 31.1 | 63 | 3.04 | 0 | 26 | 30 | 17 | 13.5152 | 0
2024-10-11 21:00 | 29.9 | 71 | 1.68 | 0 | 26 | 30 | 17 | 9.644 | 0
2024-10-11 22:00 | 29.2 | 76 | 1.32 | 0 | 26 | 30 | 17 | 8.8329 | 0
2024-10-11 23:00 | 28.6 | 78 | 1.92 | 0 | 26 | 30 | 17 | 12.3901 | 0
2024-10-12 | 29 | 76 | 1.01 | 0 | 26 | 30 | 17 | 9.4928 | 0
2024-10-12 01:00 | 28.6 | 78 | 1.14 | 0 | 26 | 30 | 17 | 10.6912 | 0
2024-10-12 02:00 | 27.7 | 82 | 1.54 | 0 | 26 | 30 | 17 | 14.4004 | 0
2024-10-12 03:00 | 27.2 | 83 | 2.21 | 0 | 26 | 30 | 17 | 19.5052 | 0
2024-10-12 04:00 | 27 | 83 | 2.7 | 0 | 26 | 30 | 17 | 23.1049 | 0
2024-10-12 05:00 | 26 | 86 | 2.38 | 0 | 26 | 30 | 17 | 27.7613 | 0
2024-10-12 06:00 | 25.5 | 89 | 2.51 | 0 | 26 | 30 | 17 | 29.6032 | 0
2024-10-12 07:00 | 25.9 | 87 | 2.71 | 25 | 26 | 30 | 17 | 25.6994 | 0
2024-10-12 08:00 | 28.7 | 74 | 2.36 | 186 | 26 | 30 | 17 | 0 | 0
2024-10-12 09:00 | 31 | 62 | 1.25 | 398 | 26 | 30 | 17 | 0 | 13.1783
2024-10-12 10:00 | 32.9 | 50 | 0.9 | 591 | 26 | 30 | 17 | 0 | 45.5971
2024-10-12 11:00 | 35 | 35 | 1.32 | 738 | 26 | 30 | 17 | 0 | 49.8061
2024-10-12 12:00 | 36.3 | 28 | 2.86 | 817 | 26 | 30 | 17 | 0 | 19.9226
2024-10-12 13:00 | 36.8 | 25 | 4.74 | 824 | 26 | 30 | 17 | 0 | 0
2024-10-12 14:00 | 36.1 | 29 | 6.4 | 759 | 26 | 30 | 17 | 0 | 0
2024-10-12 15:00 | 34.9 | 39 | 6.37 | 626 | 26 | 30 | 17 | 0 | 0
2024-10-12 16:00 | 34 | 45 | 5.94 | 419 | 26 | 30 | 17 | 0 | 0
2024-10-12 17:00 | 33.2 | 49 | 5.19 | 220 | 26 | 30 | 17 | 0 | 0
2024-10-12 18:00 | 32.1 | 55 | 4.72 | 43 | 26 | 30 | 17 | 18.1849 | 0
2024-10-12 19:00 | 31.5 | 59 | 3.55 | 0 | 26 | 30 | 17 | 18.4765 | 0
2024-10-12 20:00 | 30.8 | 61 | 1.92 | 0 | 26 | 30 | 17 | 16.0525 | 0
2024-10-12 21:00 | 30.2 | 64 | 1.06 | 0 | 26 | 30 | 17 | 12.5024 | 0
2024-10-12 22:00 | 30.2 | 63 | 0.74 | 0 | 26 | 30 | 17 | 11.2028 | 0
2024-10-12 23:00 | 28.6 | 70 | 1.85 | 0 | 26 | 30 | 17 | 21.6361 | 0
2024-10-13 | 28 | 72 | 1.81 | 0 | 26 | 30 | 17 | 23.7807 | 0
2024-10-13 01:00 | 27.3 | 75 | 1.96 | 0 | 26 | 30 | 17 | 26.8742 | 0
2024-10-13 02:00 | 26.6 | 77 | 2.44 | 0 | 26 | 30 | 17 | 33.6391 | 0
2024-10-13 03:00 | 25.9 | 80 | 2.63 | 0 | 26 | 30 | 17 | 37.6652 | 0
2024-10-13 04:00 | 25.1 | 84 | 2.62 | 0 | 26 | 30 | 17 | 40.2382 | 0
2024-10-13 05:00 | 25.1 | 81 | 2.45 | 0 | 26 | 30 | 17 | 42.4336 | 0
2024-10-13 06:00 | 24.4 | 84 | 2.32 | 0 | 26 | 30 | 17 | 44.0851 | 0
2024-10-13 07:00 | 24.8 | 82 | 2.07 | 26 | 26 | 30 | 17 | 36.9637 | 0
2024-10-13 08:00 | 27.9 | 68 | 1.31 | 192 | 26 | 30 | 17 | 0 | 0
2024-10-13 09:00 | 31 | 53 | 1.08 | 410 | 26 | 30 | 17 | 0 | 9.599
2024-10-13 10:00 | 32.7 | 45 | 0.9 | 606 | 26 | 30 | 17 | 0 | 42.1081
2024-10-13 11:00 | 34.6 | 31 | 1.96 | 751 | 26 | 30 | 17 | 0 | 26.7085
2024-10-13 12:00 | 35.6 | 25 | 3.3 | 832 | 26 | 30 | 17 | 0 | 0
2024-10-13 13:00 | 35.7 | 24 | 4.17 | 840 | 26 | 30 | 17 | 0 | 0
2024-10-13 14:00 | 35.3 | 27 | 4.85 | 772 | 26 | 30 | 17 | 0 | 0
2024-10-13 15:00 | 34.6 | 31 | 4.8 | 636 | 26 | 30 | 17 | 0 | 0
2024-10-13 16:00 | 33.9 | 35 | 4.53 | 445 | 26 | 30 | 17 | 0 | 0
2024-10-13 17:00 | 33.3 | 37 | 4.65 | 227 | 26 | 30 | 17 | 29.5022 | 0
2024-10-13 18:00 | 32.5 | 42 | 3.78 | 43 | 26 | 30 | 17 | 42.239 | 0
2024-10-13 19:00 | 31.9 | 46 | 3.47 | 0 | 26 | 30 | 17 | 42.3227 | 0
2024-10-13 20:00 | 31.2 | 49 | 2.55 | 0 | 26 | 30 | 17 | 35.367 | 0
2024-10-13 21:00 | 30.3 | 54 | 2.15 | 0 | 26 | 30 | 17 | 31.2934 | 0
2024-10-13 22:00 | 29.2 | 59 | 1.6 | 0 | 26 | 30 | 17 | 27.9087 | 0
2024-10-13 23:00 | 28.3 | 62 | 1.55 | 0 | 26 | 30 | 17 | 30.1941 | 0
2024-10-14 | 27.5 | 62 | 2.01 | 0 | 26 | 30 | 17 | 40.6987 | 0
2024-10-14 01:00 | 26.5 | 65 | 1.66 | 0 | 26 | 30 | 17 | 40.3399 | 0
2024-10-14 02:00 | 25.9 | 68 | 1.55 | 0 | 26 | 30 | 17 | 40.0569 | 0
2024-10-14 03:00 | 25.7 | 70 | 1.55 | 0 | 26 | 30 | 17 | 39.5858 | 0
2024-10-14 04:00 | 25.4 | 73 | 1.87 | 0 | 26 | 30 | 17 | 42.746 | 0
2024-10-14 05:00 | 25.5 | 71 | 3.07 | 0 | 26 | 30 | 17 | 57.4216 | 0
2024-10-14 06:00 | 25.2 | 73 | 3.2 | 0 | 26 | 30 | 17 | 58.8987 | 0
2024-10-14 07:00 | 25.8 | 74 | 3.14 | 24 | 26 | 30 | 17 | 47.6496 | 0
2024-10-14 08:00 | 27.8 | 61 | 2.85 | 185 | 26 | 30 | 17 | 23.3085 | 0
2024-10-14 09:00 | 30.7 | 46 | 3.21 | 401 | 26 | 30 | 17 | 0 | 0
2024-10-14 10:00 | 34 | 41 | 4.5 | 594 | 26 | 30 | 17 | 0 | 0
2024-10-14 11:00 | 35.9 | 25 | 3.63 | 736 | 26 | 30 | 17 | 0 | 0
2024-10-14 12:00 | 36.9 | 25 | 2.62 | 817 | 26 | 30 | 17 | 0 | 22.4116
2024-10-14 13:00 | 38.4 | 22 | 3.71 | 820 | 26 | 30 | 17 | 0 | 1.9637
2024-10-14 14:00 | 38.5 | 20 | 4.85 | 623 | 26 | 30 | 17 | 0 | 0
2024-10-14 15:00 | 38.7 | 19 | 3.83 | 569 | 26 | 30 | 17 | 0 | 0
2024-10-14 16:00 | 38.4 | 19 | 4.48 | 407 | 26 | 30 | 17 | 13.2071 | 0
2024-10-14 17:00 | 34.2 | 46 | 7.63 | 206 | 26 | 30 | 17 | 1.3031 | 0
2024-10-14 18:00 | 33.4 | 52 | 5.07 | 37 | 26 | 30 | 17 | 10.5906 | 0
2024-10-14 19:00 | 33.6 | 38 | 3.99 | 0 | 26 | 30 | 17 | 48.8317 | 0
2024-10-14 20:00 | 32.5 | 30 | 4.05 | 0 | 26 | 30 | 17 | 80.6372 | 0
2024-10-14 21:00 | 31.2 | 34 | 3.88 | 0 | 26 | 30 | 17 | 80.1117 | 0
2024-10-14 22:00 | 29.7 | 42 | 3.5 | 0 | 26 | 30 | 17 | 71.3681 | 0
2024-10-14 23:00 | 28.4 | 50 | 2.7 | 0 | 26 | 30 | 17 | 58.1261 | 0
2024-10-15 | 27.5 | 53 | 2.76 | 0 | 26 | 30 | 17 | 61.6949 | 0
2024-10-15 01:00 | 27.2 | 58 | 3.6 | 0 | 26 | 30 | 17 | 66.6511 | 0
2024-10-15 02:00 | 27 | 64 | 4.55 | 0 | 26 | 30 | 17 | 67.0381 | 0
2024-10-15 03:00 | 26.7 | 69 | 4.95 | 0 | 26 | 30 | 17 | 63.8808 | 0
2024-10-15 04:00 | 26.3 | 73 | 5.36 | 0 | 26 | 30 | 17 | 63.8998 | 0
2024-10-15 05:00 | 26.5 | 73 | 5.07 | 0 | 26 | 30 | 17 | 59.0857 | 0
2024-10-15 06:00 | 26.3 | 75 | 5.09 | 0 | 26 | 30 | 17 | 57.8481 | 0
2024-10-15 07:00 | 26.7 | 73 | 5.41 | 24 | 26 | 30 | 17 | 55.169 | 0
2024-10-15 08:00 | 28.6 | 66 | 5.09 | 185 | 26 | 30 | 17 | 20.3992 | 0
2024-10-15 09:00 | 30.7 | 55 | 5.48 | 399 | 26 | 30 | 17 | 0 | 0
2024-10-15 10:00 | 32.6 | 50 | 4.8 | 590 | 26 | 30 | 17 | 0 | 0
2024-10-15 11:00 | 35.2 | 38 | 4.88 | 731 | 26 | 30 | 17 | 0 | 0
2024-10-15 12:00 | 37 | 28 | 5.5 | 806 | 26 | 30 | 17 | 0 | 0
2024-10-15 13:00 | 37.8 | 26 | 6 | 796 | 26 | 30 | 17 | 0 | 0
2024-10-15 14:00 | 37.2 | 26 | 6.25 | 392 | 26 | 30 | 17 | 14.0706 | 0
2024-10-15 15:00 | 37.7 | 24 | 5.88 | 554 | 26 | 30 | 17 | 0 | 0
2024-10-15 16:00 | 36.4 | 27 | 6.41 | 371 | 26 | 30 | 17 | 23.4314 | 0
2024-10-15 17:00 | 33.3 | 50 | 5.52 | 136 | 26 | 30 | 17 | 5.8947 | 0
2024-10-15 18:00 | 32.8 | 50 | 3.47 | 32 | 26 | 30 | 17 | 19.7818 | 0
2024-10-15 19:00 | 32 | 44 | 4.79 | 0 | 26 | 30 | 17 | 56.0307 | 0
2024-10-15 20:00 | 30.1 | 55 | 4.95 | 0 | 26 | 30 | 17 | 51.381 | 0
2024-10-15 21:00 | 29.1 | 57 | 4.72 | 0 | 26 | 30 | 17 | 57.6709 | 0
2024-10-15 22:00 | 28.3 | 57 | 3.39 | 0 | 26 | 30 | 17 | 55.3504 | 0
2024-10-15 23:00 | 27.4 | 59 | 3.32 | 0 | 26 | 30 | 17 | 59.9689 | 0
2024-10-16 | 26.9 | 59 | 3.9 | 0 | 26 | 30 | 17 | 71.2603 | 0
2024-10-16 01:00 | 26.4 | 61 | 4.01 | 0 | 26 | 30 | 17 | 74.1973 | 0
2024-10-16 02:00 | 25.9 | 66 | 3.79 | 0 | 26 | 30 | 17 | 68.5747 | 0
2024-10-16 03:00 | 25.6 | 73 | 3.48 | 0 | 26 | 30 | 17 | 57.5318 | 0
2024-10-16 04:00 | 25.4 | 77 | 3.55 | 0 | 26 | 30 | 17 | 54.1865 | 0
2024-10-16 05:00 | 26.7 | 70 | 4.44 | 0 | 26 | 30 | 17 | 58.0257 | 0
2024-10-16 06:00 | 26.6 | 71 | 4.78 | 0 | 26 | 30 | 17 | 59.8368 | 0
2024-10-16 07:00 | 27 | 69 | 4.72 | 23 | 26 | 30 | 17 | 55.1235 | 0
2024-10-16 08:00 | 28.7 | 63 | 4.78 | 181 | 26 | 30 | 17 | 24.9008 | 0
2024-10-16 09:00 | 30.6 | 54 | 6.03 | 393 | 26 | 30 | 17 | 0.2241 | 0
2024-10-16 10:00 | 32.6 | 46 | 6.05 | 584 | 26 | 30 | 17 | 0 | 0
2024-10-16 11:00 | 34 | 41 | 5.78 | 726 | 26 | 30 | 17 | 0 | 0
2024-10-16 12:00 | 35.4 | 36 | 5.93 | 801 | 26 | 30 | 17 | 0 | 0
2024-10-16 13:00 | 36.3 | 31 | 6.15 | 711 | 26 | 30 | 17 | 0 | 0
2024-10-16 14:00 | 36.4 | 30 | 5.83 | 683 | 26 | 30 | 17 | 0 | 0
2024-10-16 15:00 | 35.7 | 34 | 5.8 | 573 | 26 | 30 | 17 | 0 | 0
2024-10-16 16:00 | 34.7 | 37 | 5.56 | 353 | 26 | 30 | 17 | 2.2858 | 0
2024-10-16 17:00 | 32.7 | 55 | 5.7 | 186 | 26 | 30 | 17 | 0 | 0
2024-10-16 18:00 | 31.9 | 56 | 4.66 | 35 | 26 | 30 | 17 | 19.0517 | 0
2024-10-16 19:00 | 31.6 | 53 | 3.91 | 0 | 26 | 30 | 17 | 32.2944 | 0
2024-10-16 20:00 | 30.8 | 50 | 3.63 | 0 | 26 | 30 | 17 | 45.923 | 0
2024-10-16 21:00 | 29.8 | 54 | 3.63 | 0 | 26 | 30 | 17 | 47.9569 | 0
2024-10-16 22:00 | 28.9 | 58 | 3.77 | 0 | 26 | 30 | 17 | 50.6479 | 0
2024-10-16 23:00 | 28.3 | 62 | 3.7 | 0 | 26 | 30 | 17 | 48.9477 | 0
2024-10-17 | 27.7 | 64 | 3.48 | 0 | 26 | 30 | 17 | 50.0212 | 0
2024-10-17 01:00 | 27.3 | 68 | 3.65 | 0 | 26 | 30 | 17 | 48.7066 | 0
2024-10-17 02:00 | 27 | 72 | 4.01 | 0 | 26 | 30 | 17 | 47.5315 | 0
2024-10-17 03:00 | 26.9 | 74 | 4.38 | 0 | 26 | 30 | 17 | 47.3133 | 0
2024-10-17 04:00 | 26.9 | 75 | 4.33 | 0 | 26 | 30 | 17 | 45.0904 | 0
2024-10-17 05:00 | 26.9 | 73 | 3.94 | 0 | 26 | 30 | 17 | 46.4612 | 0
2024-10-17 06:00 | 26.7 | 74 | 3.16 | 0 | 26 | 30 | 17 | 41.7983 | 0
2024-10-17 07:00 | 26.8 | 74 | 2.15 | 22 | 26 | 30 | 17 | 30.4957 | 0
2024-10-17 08:00 | 28.9 | 65 | 1.26 | 176 | 26 | 30 | 17 | 0 | 0
2024-10-17 09:00 | 30.7 | 57 | 0.8 | 384 | 26 | 30 | 17 | 0 | 14.7264
2024-10-17 10:00 | 31.9 | 53 | 0.92 | 573 | 26 | 30 | 17 | 0 | 40.2041
2024-10-17 11:00 | 33.1 | 48 | 1.89 | 715 | 26 | 30 | 17 | 0 | 40.9204
2024-10-17 12:00 | 34.1 | 44 | 2.64 | 792 | 26 | 30 | 17 | 0 | 38.864
2024-10-17 13:00 | 34.7 | 42 | 3.54 | 795 | 26 | 30 | 17 | 0 | 25.9005
2024-10-17 14:00 | 34.8 | 42 | 5.19 | 719 | 26 | 30 | 17 | 0 | 0
2024-10-17 15:00 | 33.9 | 46 | 6.78 | 569 | 26 | 30 | 17 | 0 | 0
2024-10-17 16:00 | 33.1 | 46 | 6.49 | 378 | 26 | 30 | 17 | 0 | 0
2024-10-17 17:00 | 32.3 | 53 | 5.81 | 195 | 26 | 30 | 17 | 3.7061 | 0
2024-10-17 18:00 | 31.2 | 60 | 4.99 | 33 | 26 | 30 | 17 | 18.9393 | 0
2024-10-17 19:00 | 30.9 | 63 | 4.04 | 0 | 26 | 30 | 17 | 17.8586 | 0
2024-10-17 20:00 | 30.7 | 65 | 3.27 | 0 | 26 | 30 | 17 | 14.4682 | 0
2024-10-17 21:00 | 30.1 | 69 | 2.25 | 0 | 26 | 30 | 17 | 11.7314 | 0
2024-10-17 22:00 | 29.3 | 74 | 1.8 | 0 | 26 | 30 | 17 | 11.1057 | 0
2024-10-17 23:00 | 28.7 | 77 | 1.81 | 0 | 26 | 30 | 17 | 12.5087 | 0
2024-10-18 | 28 | 81 | 1.72 | 0 | 26 | 30 | 17 | 13.5394 | 0
2024-10-18 01:00 | 27.5 | 83 | 1.95 | 0 | 26 | 30 | 17 | 16.0631 | 0
2024-10-18 02:00 | 27.1 | 86 | 2.1 | 0 | 26 | 30 | 17 | 16.5157 | 0
2024-10-18 03:00 | 26.6 | 89 | 2 | 0 | 26 | 30 | 17 | 17.3603 | 0
2024-10-18 04:00 | 26.3 | 92 | 2.23 | 0 | 26 | 30 | 17 | 17.2622 | 0
2024-10-18 05:00 | 27 | 83 | 2.07 | 0 | 26 | 30 | 17 | 20.8132 | 0
2024-10-18 06:00 | 26.7 | 82 | 2.05 | 0 | 26 | 30 | 17 | 24.4766 | 0
2024-10-18 07:00 | 27.3 | 75 | 2.07 | 20 | 26 | 30 | 17 | 24.8674 | 0
2024-10-18 08:00 | 30.2 | 57 | 2.87 | 162 | 26 | 30 | 17 | 10.9426 | 0
2024-10-18 09:00 | 32.1 | 52 | 4.5 | 359 | 26 | 30 | 17 | 0 | 0
2024-10-18 10:00 | 33.6 | 48 | 4.35 | 564 | 26 | 30 | 17 | 0 | 0
2024-10-18 11:00 | 34.7 | 45 | 3.82 | 702 | 26 | 30 | 17 | 0 | 17.4329
2024-10-18 12:00 | 35.6 | 42 | 3.13 | 770 | 26 | 30 | 17 | 0 | 37.5913
2024-10-18 13:00 | 36.1 | 41 | 3.45 | 765 | 26 | 30 | 17 | 0 | 34.9227
2024-10-18 14:00 | 34.1 | 49 | 4.52 | 689 | 26 | 30 | 17 | 0 | 11.2552
2024-10-18 15:00 | 34.2 | 49 | 3.35 | 312 | 26 | 30 | 17 | 0 | 0
2024-10-18 16:00 | 33.8 | 51 | 4.07 | 344 | 26 | 30 | 17 | 0 | 0
2024-10-18 17:00 | 33.5 | 51 | 4.32 | 195 | 26 | 30 | 17 | 0 | 0
2024-10-18 18:00 | 32.1 | 57 | 3.8 | 32 | 26 | 30 | 17 | 12.3039 | 0
2024-10-18 19:00 | 31.5 | 63 | 3.43 | 0 | 26 | 30 | 17 | 9.6189 | 0
2024-10-18 20:00 | 31.2 | 66 | 2.2 | 0 | 26 | 30 | 17 | 6.1332 | 0
2024-10-18 21:00 | 30.5 | 75 | 0.96 | 0 | 26 | 30 | 17 | 1.1492 | 0
2024-10-18 22:00 | 29.8 | 80 | 0.86 | 0 | 26 | 30 | 17 | 1.637 | 0
2024-10-18 23:00 | 29 | 82 | 1.33 | 0 | 26 | 30 | 17 | 4.5297 | 0
2024-10-19 | 28.8 | 83 | 0.96 | 0 | 26 | 30 | 17 | 5.2911 | 0
2024-10-19 01:00 | 28.2 | 85 | 1.06 | 0 | 26 | 30 | 17 | 7.5192 | 0
2024-10-19 02:00 | 27.5 | 87 | 1.77 | 0 | 26 | 30 | 17 | 11.317 | 0
2024-10-19 03:00 | 27.2 | 88 | 2.32 | 0 | 26 | 30 | 17 | 13.5262 | 0
2024-10-19 04:00 | 26.7 | 92 | 2.42 | 0 | 26 | 30 | 17 | 13.5958 | 0
2024-10-19 05:00 | 27.1 | 89 | 2.23 | 0 | 26 | 30 | 17 | 13.147 | 0
2024-10-19 06:00 | 26.7 | 91 | 2.23 | 0 | 26 | 30 | 17 | 14.5919 | 0
2024-10-19 07:00 | 27 | 89 | 2.02 | 21 | 26 | 30 | 17 | 10.9708 | 0
2024-10-19 08:00 | 29.2 | 78 | 2.06 | 173 | 26 | 30 | 17 | 0 | 0
2024-10-19 09:00 | 31.6 | 65 | 2.34 | 380 | 26 | 30 | 17 | 0 | 3.4604
2024-10-19 10:00 | 33.9 | 46 | 1.87 | 570 | 26 | 30 | 17 | 0 | 24.4217
2024-10-19 11:00 | 35.8 | 35 | 1.11 | 712 | 26 | 30 | 17 | 0 | 55.9198
2024-10-19 12:00 | 37.2 | 29 | 1.76 | 789 | 26 | 30 | 17 | 0 | 49.1928
2024-10-19 13:00 | 37.9 | 27 | 3.52 | 794 | 26 | 30 | 17 | 0 | 13.9158
2024-10-19 14:00 | 37.7 | 27 | 5.13 | 725 | 26 | 30 | 17 | 0 | 0
2024-10-19 15:00 | 37.3 | 25 | 5.58 | 591 | 26 | 30 | 17 | 0 | 0
2024-10-19 16:00 | 36.1 | 30 | 5.24 | 408 | 26 | 30 | 17 | 1.5313 | 0
2024-10-19 17:00 | 33.5 | 50 | 4.81 | 198 | 26 | 30 | 17 | 0 | 0
2024-10-19 18:00 | 32 | 63 | 4.45 | 31 | 26 | 30 | 17 | 0 | 0
2024-10-19 19:00 | 31.5 | 70 | 3.89 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-19 20:00 | 31.3 | 72 | 3.33 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-19 21:00 | 31 | 73 | 2.26 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-19 22:00 | 30.5 | 76 | 1.23 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-19 23:00 | 29.9 | 79 | 1.32 | 0 | 26 | 30 | 17 | 0.8986 | 0
2024-10-20 | 29.4 | 80 | 1.44 | 0 | 26 | 30 | 17 | 3.4343 | 0
2024-10-20 01:00 | 29 | 82 | 1.33 | 0 | 26 | 30 | 17 | 4.5297 | 0
2024-10-20 02:00 | 28.9 | 81 | 1.06 | 0 | 26 | 30 | 17 | 6.1951 | 0
2024-10-20 03:00 | 28.7 | 82 | 0.97 | 0 | 26 | 30 | 17 | 6.6529 | 0
2024-10-20 04:00 | 27.9 | 87 | 1.63 | 0 | 26 | 30 | 17 | 7.9292 | 0
2024-10-20 05:00 | 28.2 | 84 | 1.72 | 0 | 26 | 30 | 17 | 8.655 | 0
2024-10-20 06:00 | 27.8 | 86 | 2.07 | 0 | 26 | 30 | 17 | 10.0393 | 0
2024-10-20 07:00 | 27.8 | 86 | 2.19 | 20 | 26 | 30 | 17 | 7.4049 | 0
2024-10-20 08:00 | 30.3 | 73 | 2.05 | 168 | 26 | 30 | 17 | 0 | 0
2024-10-20 09:00 | 32.1 | 63 | 0.96 | 373 | 26 | 30 | 17 | 0 | 22.4236
2024-10-20 10:00 | 34 | 49 | 1.09 | 561 | 26 | 30 | 17 | 0 | 42.5149
2024-10-20 11:00 | 35.7 | 39 | 2.87 | 703 | 26 | 30 | 17 | 0 | 26.0595
2024-10-20 12:00 | 36.4 | 35 | 4.15 | 781 | 26 | 30 | 17 | 0 | 12.3403
2024-10-20 13:00 | 36.3 | 36 | 5.04 | 787 | 26 | 30 | 17 | 0 | 2.6452
2024-10-20 14:00 | 35.7 | 40 | 5.2 | 721 | 26 | 30 | 17 | 0 | 0
2024-10-20 15:00 | 34.9 | 46 | 5.06 | 590 | 26 | 30 | 17 | 0 | 0
2024-10-20 16:00 | 34 | 51 | 5.09 | 405 | 26 | 30 | 17 | 0 | 0
2024-10-20 17:00 | 32.6 | 60 | 5.02 | 195 | 26 | 30 | 17 | 0 | 0
2024-10-20 18:00 | 31.5 | 66 | 5.05 | 30 | 26 | 30 | 17 | 0 | 0
2024-10-20 19:00 | 31.2 | 69 | 3.98 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-20 20:00 | 30.9 | 72 | 2.48 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-20 21:00 | 30.4 | 74 | 1.98 | 0 | 26 | 30 | 17 | 1.7824 | 0
2024-10-20 22:00 | 29.8 | 77 | 1.84 | 0 | 26 | 30 | 17 | 3.2571 | 0
2024-10-20 23:00 | 29.3 | 82 | 1.76 | 0 | 26 | 30 | 17 | 1.5912 | 0
2024-10-21 | 28.7 | 86 | 1.41 | 0 | 26 | 30 | 17 | 3.4155 | 0
2024-10-21 01:00 | 28.5 | 87 | 1.14 | 0 | 26 | 30 | 17 | 4.3767 | 0
2024-10-21 02:00 | 28 | 89 | 1.15 | 0 | 26 | 30 | 17 | 5.6875 | 0
2024-10-21 03:00 | 27.3 | 91 | 1.76 | 0 | 26 | 30 | 17 | 8.7819 | 0
2024-10-21 04:00 | 26.8 | 92 | 1.93 | 0 | 26 | 30 | 17 | 12.1697 | 0
2024-10-21 05:00 | 27.3 | 90 | 2.19 | 0 | 26 | 30 | 17 | 9.9585 | 0
2024-10-21 06:00 | 26.5 | 93 | 2.58 | 0 | 26 | 30 | 17 | 14.57 | 0
2024-10-21 07:00 | 26.9 | 90 | 2.69 | 20 | 26 | 30 | 17 | 11.738 | 0
2024-10-21 08:00 | 29.2 | 78 | 3.98 | 172 | 26 | 30 | 17 | 0 | 0
2024-10-21 09:00 | 32.1 | 58 | 4.25 | 379 | 26 | 30 | 17 | 0 | 0
2024-10-21 10:00 | 35.6 | 32 | 3.57 | 572 | 26 | 30 | 17 | 0 | 0
2024-10-21 11:00 | 37.4 | 24 | 3.02 | 717 | 26 | 30 | 17 | 0 | 0.8604
2024-10-21 12:00 | 38.3 | 22 | 3.07 | 794 | 26 | 30 | 17 | 0 | 11.2525
2024-10-21 13:00 | 37.9 | 30 | 4.73 | 797 | 26 | 30 | 17 | 0 | 4.7476
2024-10-21 14:00 | 35.6 | 52 | 7.22 | 715 | 26 | 30 | 17 | 0 | 26.8104
2024-10-21 15:00 | 34.9 | 47 | 6.49 | 559 | 26 | 30 | 17 | 0 | 0
2024-10-21 16:00 | 34.1 | 57 | 5.5 | 396 | 26 | 30 | 17 | 0 | 0
2024-10-21 17:00 | 32.6 | 62 | 6.03 | 186 | 26 | 30 | 17 | 0 | 0
2024-10-21 18:00 | 31.3 | 72 | 6.15 | 29 | 26 | 30 | 17 | 0 | 0
2024-10-21 19:00 | 31.2 | 70 | 4.78 | 0 | 26 | 30 | 17 | 0 | 0
2024-10-21 20:00 | 30.6 | 74 | 1.74 | 0 | 26 | 30 | 17 | 0.3344 | 0
2024-10-21 21:00 | 30 | 76 | 2.04 | 0 | 26 | 30 | 17 | 2.6235 | 0
2024-10-21 22:00 | 29.2 | 80 | 2 | 0 | 26 | 30 | 17 | 4.6649 | 0
2024-10-21 23:00 | 28.3 | 84 | 2.34 | 0 | 26 | 30 | 17 | 7.8709 | 0
2024-10-22 | 27.6 | 88 | 2.14 | 0 | 26 | 30 | 17 | 9.5107 | 0
2024-10-22 01:00 | 27.2 | 90 | 2.9 | 0 | 26 | 30 | 17 | 11.2626 | 0
2024-10-22 02:00 | 26.5 | 93 | 3.28 | 0 | 26 | 30 | 17 | 15.3432 | 0
2024-10-22 03:00 | 26.1 | 95 | 3.35 | 0 | 26 | 30 | 17 | 17.3231 | 0
2024-10-22 04:00 | 25.9 | 95 | 3.36 | 0 | 26 | 30 | 17 | 19.8385 | 0
2024-10-22 05:00 | 25.9 | 95 | 2.93 | 0 | 26 | 30 | 17 | 19.0358 | 0
2024-10-22 06:00 | 25.8 | 95 | 3.01 | 0 | 26 | 30 | 17 | 20.3478 | 0
2024-10-22 07:00 | 26 | 94 | 3.01 | 19 | 26 | 30 | 17 | 16.8741 | 0
2024-10-22 08:00 | 28.3 | 82 | 2.96 | 171 | 26 | 30 | 17 | 0 | 0
2024-10-22 09:00 | 30.9 | 70 | 4.42 | 379 | 26 | 30 | 17 | 0 | 0
2024-10-22 10:00 | 32.4 | 61 | 4.3 | 566 | 26 | 30 | 17 | 0 | 8.147
2024-10-22 11:00 | 34.2 | 48 | 3.63 | 705 | 26 | 30 | 17 | 0 | 22.755
2024-10-22 12:00 | 35.7 | 39 | 3.29 | 783 | 26 | 30 | 17 | 0 | 30.2244
2024-10-22 13:00 | 36.8 | 34 | 3.47 | 790 | 26 | 30 | 17 | 0 | 25.1406
2024-10-22 14:00 | 37.1 | 35 | 4.4 | 722 | 26 | 30 | 17 | 0 | 8.521
2024-10-22 15:00 | 34.9 | 56 | 6.27 | 581 | 26 | 30 | 17 | 0 | 18.1592
2024-10-22 16:00 | 33.8 | 54 | 6.65 | 387 | 26 | 30 | 17 | 0 | 0
2024-10-22 17:00 | 31.9 | 66 | 6.88 | 190 | 26 | 30 | 17 | 0 | 0
2024-10-22 18:00 | 31.3 | 69 | 5.36 | 28 | 26 | 30 | 17 | 0 | 0
2024-10-22 19:00 | 30.6 | 71 | 3.95 | 0 | 26 | 30 | 17 | 3.5159 | 0
2024-10-22 20:00 | 29.9 | 74 | 2.69 | 0 | 26 | 30 | 17 | 6.3844 | 0
2024-10-22 21:00 | 28.9 | 78 | 2.12 | 0 | 26 | 30 | 17 | 10.0292 | 0
2024-10-22 22:00 | 28.2 | 82 | 1.87 | 0 | 26 | 30 | 17 | 11.0243 | 0
2024-10-22 23:00 | 27.2 | 88 | 1.95 | 0 | 26 | 30 | 17 | 13.0378 | 0
2024-10-23 | 26.1 | 93 | 1.69 | 0 | 26 | 30 | 17 | 16.7463 | 0
2024-10-23 01:00 | 25.6 | 94 | 1.88 | 0 | 26 | 30 | 17 | 20.5115 | 0
2024-10-23 02:00 | 25.1 | 96 | 1.8 | 0 | 26 | 30 | 17 | 22.5161 | 0
2024-10-23 03:00 | 24.6 | 97 | 1.8 | 0 | 26 | 30 | 17 | 25.7365 | 0
2024-10-23 04:00 | 24.4 | 97 | 2.14 | 0 | 26 | 30 | 17 | 29.2025 | 0
2024-10-23 05:00 | 24.7 | 96 | 2.01 | 0 | 26 | 30 | 17 | 26.8706 | 0
2024-10-23 06:00 | 24.5 | 95 | 2.44 | 0 | 26 | 30 | 17 | 32.0073 | 0
2024-10-23 07:00 | 25 | 92 | 2.64 | 19 | 26 | 30 | 17 | 29.0442 | 0
2024-10-23 08:00 | 27.9 | 71 | 4.31 | 170 | 26 | 30 | 17 | 16.988 | 0
2024-10-23 09:00 | 31.5 | 51 | 5.31 | 379 | 26 | 30 | 17 | 0 | 0
2024-10-23 10:00 | 33.9 | 46 | 7.12 | 566 | 26 | 30 | 17 | 0 | 0
2024-10-23 11:00 | 35.7 | 39 | 6.84 | 704 | 26 | 30 | 17 | 0 | 0
2024-10-23 12:00 | 37.2 | 33 | 5.78 | 778 | 26 | 30 | 17 | 0 | 0
2024-10-23 13:00 | 37.9 | 26 | 4.22 | 672 | 26 | 30 | 17 | 0 | 0
2024-10-23 14:00 | 37.8 | 25 | 2.38 | 625 | 26 | 30 | 17 | 0 | 8.2088
2024-10-23 15:00 | 34.8 | 50 | 6.09 | 515 | 26 | 30 | 17 | 0 | 0
2024-10-23 16:00 | 33.9 | 49 | 5.1 | 316 | 26 | 30 | 17 | 0 | 0
2024-10-23 17:00 | 33.1 | 54 | 4.83 | 179 | 26 | 30 | 17 | 0 | 0
2024-10-23 18:00 | 31.9 | 57 | 3.74 | 26 | 26 | 30 | 17 | 15.3351 | 0
2024-10-23 19:00 | 31.1 | 64 | 3.65 | 0 | 26 | 30 | 17 | 12.4777 | 0
2024-10-23 20:00 | 30.8 | 66 | 3.11 | 0 | 26 | 30 | 17 | 11.1491 | 0
2024-10-23 21:00 | 30.3 | 64 | 3.25 | 0 | 26 | 30 | 17 | 20.8083 | 0
2024-10-23 22:00 | 29.8 | 66 | 3.43 | 0 | 26 | 30 | 17 | 23.1237 | 0
2024-10-23 23:00 | 29.3 | 68 | 3.67 | 0 | 26 | 30 | 17 | 25.8511 | 0
2024-10-24 | 28.9 | 68 | 3.7 | 0 | 26 | 30 | 17 | 30.7075 | 0
2024-10-24 01:00 | 28.4 | 77 | 4.32 | 0 | 26 | 30 | 17 | 20.86 | 0
2024-10-24 02:00 | 28 | 78 | 4.23 | 0 | 26 | 30 | 17 | 24.1149 | 0
2024-10-24 03:00 | 27.7 | 76 | 4.43 | 0 | 26 | 30 | 17 | 32.9036 | 0
2024-10-24 04:00 | 27.6 | 72 | 4.27 | 0 | 26 | 30 | 17 | 41.5897 | 0
2024-10-24 05:00 | 27.9 | 72 | 3.98 | 0 | 26 | 30 | 17 | 36.348 | 0
2024-10-24 06:00 | 27.8 | 67 | 4.08 | 0 | 26 | 30 | 17 | 47.8179 | 0
2024-10-24 07:00 | 28.1 | 62 | 3.96 | 17 | 26 | 30 | 17 | 50.8832 | 0
2024-10-24 08:00 | 30 | 53 | 4.08 | 165 | 26 | 30 | 17 | 29.1227 | 0
2024-10-24 09:00 | 33 | 43 | 7.48 | 370 | 26 | 30 | 17 | 11.5064 | 0
2024-10-24 10:00 | 34.6 | 41 | 7.8 | 557 | 26 | 30 | 17 | 0 | 0
2024-10-24 11:00 | 36 | 36 | 7.03 | 695 | 26 | 30 | 17 | 0 | 0
2024-10-24 12:00 | 37.3 | 31 | 5.68 | 770 | 26 | 30 | 17 | 0 | 0
2024-10-24 13:00 | 38.1 | 26 | 3.96 | 721 | 26 | 30 | 17 | 0 | 0
2024-10-24 14:00 | 38.3 | 24 | 3.53 | 650 | 26 | 30 | 17 | 0 | 0
2024-10-24 15:00 | 38.2 | 24 | 1.8 | 537 | 26 | 30 | 17 | 0 | 10.6078
2024-10-24 16:00 | 34 | 57 | 6.61 | 318 | 26 | 30 | 17 | 0 | 0
2024-10-24 17:00 | 33.1 | 56 | 5.61 | 171 | 26 | 30 | 17 | 0 | 0
2024-10-24 18:00 | 31.4 | 65 | 5.46 | 25 | 26 | 30 | 17 | 3.3192 | 0
2024-10-24 19:00 | 31.5 | 62 | 5.02 | 0 | 26 | 30 | 17 | 13.567 | 0
2024-10-24 20:00 | 31.1 | 63 | 3.18 | 0 | 26 | 30 | 17 | 13.7918 | 0
2024-10-24 21:00 | 30.5 | 64 | 2.46 | 0 | 26 | 30 | 17 | 16.2493 | 0
2024-10-24 22:00 | 29.7 | 66 | 2.06 | 0 | 26 | 30 | 17 | 18.8255 | 0
2024-10-24 23:00 | 28.9 | 68 | 1.94 | 0 | 26 | 30 | 17 | 22.1684 | 0
2024-10-25 | 28 | 71 | 1.76 | 0 | 26 | 30 | 17 | 24.567 | 0
2024-10-25 01:00 | 27.5 | 70 | 2.28 | 0 | 26 | 30 | 17 | 33.4515 | 0
2024-10-25 02:00 | 27.1 | 70 | 2.49 | 0 | 26 | 30 | 17 | 38.5766 | 0
2024-10-25 03:00 | 26.8 | 69 | 2.59 | 0 | 26 | 30 | 17 | 43.4306 | 0
2024-10-25 04:00 | 26.2 | 69 | 2.3 | 0 | 26 | 30 | 17 | 45.6813 | 0
2024-10-25 05:00 | 26.7 | 68 | 2.3 | 0 | 26 | 30 | 17 | 42.8052 | 0
2024-10-25 06:00 | 26.1 | 72 | 1.71 | 0 | 26 | 30 | 17 | 36.9288 | 0
2024-10-25 07:00 | 26.7 | 66 | 1.71 | 17 | 26 | 30 | 17 | 36.3383 | 0
2024-10-25 08:00 | 29.6 | 45 | 3.14 | 161 | 26 | 30 | 17 | 40.3312 | 0
2024-10-25 09:00 | 32.1 | 35 | 5.4 | 331 | 26 | 30 | 17 | 41.6793 | 0
2024-10-25 10:00 | 34.5 | 31 | 6.55 | 554 | 26 | 30 | 17 | 7.0622 | 0
2024-10-25 11:00 | 35 | 31 | 5.99 | 621 | 26 | 30 | 17 | 0 | 0
2024-10-25 12:00 | 35.3 | 33 | 4.73 | 767 | 26 | 30 | 17 | 0 | 0
2024-10-25 13:00 | 34.9 | 41 | 5.23 | 765 | 26 | 30 | 17 | 0 | 0
2024-10-25 14:00 | 33.9 | 54 | 5.71 | 695 | 26 | 30 | 17 | 0 | 13.2448
2024-10-25 15:00 | 33.4 | 57 | 5.06 | 539 | 26 | 30 | 17 | 0 | 0.1898
2024-10-25 16:00 | 32.9 | 59 | 4.88 | 358 | 26 | 30 | 17 | 0 | 0
2024-10-25 17:00 | 31.7 | 66 | 5.59 | 166 | 26 | 30 | 17 | 0 | 0
2024-10-25 18:00 | 31.3 | 66 | 4.79 | 23 | 26 | 30 | 17 | 2.4453 | 0
2024-10-25 19:00 | 31.2 | 66 | 4.48 | 0 | 26 | 30 | 17 | 7.021 | 0
2024-10-25 20:00 | 30.9 | 67 | 3.6 | 0 | 26 | 30 | 17 | 8.4062 | 0
2024-10-25 21:00 | 30.6 | 69 | 3.04 | 0 | 26 | 30 | 17 | 7.6414 | 0
2024-10-25 22:00 | 30 | 72 | 2.78 | 0 | 26 | 30 | 17 | 8.6944 | 0
2024-10-25 23:00 | 29.3 | 77 | 1.96 | 0 | 26 | 30 | 17 | 7.6019 | 0
2024-10-26 | 29.1 | 78 | 0.76 | 0 | 26 | 30 | 17 | 6.9921 | 0
2024-10-26 01:00 | 29 | 78 | 0.47 | 0 | 26 | 30 | 17 | 7.4458 | 0
2024-10-26 02:00 | 27.5 | 86 | 1.42 | 0 | 26 | 30 | 17 | 11.8469 | 0
2024-10-26 03:00 | 27.4 | 86 | 2.06 | 0 | 26 | 30 | 17 | 13.7026 | 0
2024-10-26 04:00 | 27 | 88 | 2.3 | 0 | 26 | 30 | 17 | 15.4546 | 0
2024-10-26 05:00 | 26.9 | 87 | 2.65 | 0 | 26 | 30 | 17 | 18.4867 | 0
2024-10-26 06:00 | 26.6 | 87 | 2.65 | 0 | 26 | 30 | 17 | 21.6178 | 0
2024-10-26 07:00 | 26.7 | 86 | 2.45 | 16 | 26 | 30 | 17 | 19.1321 | 0
2024-10-26 08:00 | 29.2 | 74 | 2.21 | 158 | 26 | 30 | 17 | 0 | 0
2024-10-26 09:00 | 31.3 | 64 | 3.66 | 360 | 26 | 30 | 17 | 0 | 0
2024-10-26 10:00 | 32.4 | 58 | 2.51 | 544 | 26 | 30 | 17 | 0 | 18.94
2024-10-26 11:00 | 33.7 | 51 | 2.61 | 683 | 26 | 30 | 17 | 0 | 35.2259
2024-10-26 12:00 | 34.5 | 46 | 2.84 | 696 | 26 | 30 | 17 | 0 | 30.6613
2024-10-26 13:00 | 35 | 44 | 3.99 | 732 | 26 | 30 | 17 | 0 | 19.8335
2024-10-26 14:00 | 34.1 | 49 | 5.87 | 651 | 26 | 30 | 17 | 0 | 0
2024-10-26 15:00 | 33.5 | 47 | 5.51 | 505 | 26 | 30 | 17 | 0 | 0
2024-10-26 16:00 | 33.1 | 48 | 5.2 | 352 | 26 | 30 | 17 | 0 | 0
2024-10-26 17:00 | 31.9 | 53 | 6.2 | 159 | 26 | 30 | 17 | 15.8771 | 0
2024-10-26 18:00 | 31.4 | 55 | 5.24 | 22 | 26 | 30 | 17 | 32.2917 | 0
2024-10-26 19:00 | 30.8 | 58 | 4.01 | 0 | 26 | 30 | 17 | 30.4983 | 0
2024-10-26 20:00 | 30.2 | 61 | 3.43 | 0 | 26 | 30 | 17 | 28.4494 | 0
2024-10-26 21:00 | 29.7 | 63 | 2.77 | 0 | 26 | 30 | 17 | 26.7732 | 0
2024-10-26 22:00 | 29.1 | 65 | 2.49 | 0 | 26 | 30 | 17 | 27.6918 | 0
2024-10-26 23:00 | 28.2 | 69 | 1.94 | 0 | 26 | 30 | 17 | 26.5092 | 0
2024-10-27 | 29.1 | 62 | 0.25 | 0 | 26 | 30 | 17 | 16.117 | 0
2024-10-27 01:00 | 28.1 | 67 | 1 | 0 | 26 | 30 | 17 | 21.4607 | 0
2024-10-27 02:00 | 26.4 | 76 | 1.89 | 0 | 26 | 30 | 17 | 32.4 | 0
2024-10-27 03:00 | 26.2 | 76 | 2.51 | 0 | 26 | 30 | 17 | 39.0575 | 0
2024-10-27 04:00 | 25.3 | 80 | 2.8 | 0 | 26 | 30 | 17 | 44.7475 | 0
2024-10-27 05:00 | 25.2 | 76 | 2.5 | 0 | 26 | 30 | 17 | 47.8846 | 0
2024-10-27 06:00 | 24.6 | 79 | 2.56 | 0 | 26 | 30 | 17 | 50.2714 | 0
2024-10-27 07:00 | 24.7 | 78 | 2.6 | 16 | 26 | 30 | 17 | 48.8031 | 0
2024-10-27 08:00 | 27.6 | 66 | 2.35 | 162 | 26 | 30 | 17 | 16.4704 | 0
2024-10-27 09:00 | 30.4 | 56 | 2.31 | 370 | 26 | 30 | 17 | 0 | 0
2024-10-27 10:00 | 32.1 | 51 | 2.2 | 560 | 26 | 30 | 17 | 0 | 11.3562
2024-10-27 11:00 | 33.6 | 46 | 3.35 | 702 | 26 | 30 | 17 | 0 | 14.9834
2024-10-27 12:00 | 33.8 | 50 | 5.51 | 775 | 26 | 30 | 17 | 0 | 10.7088
2024-10-27 13:00 | 33.7 | 53 | 6.44 | 774 | 26 | 30 | 17 | 0 | 10.3134
2024-10-27 14:00 | 33.5 | 54 | 6.63 | 700 | 26 | 30 | 17 | 0 | 0
2024-10-27 15:00 | 33.3 | 53 | 6.5 | 554 | 26 | 30 | 17 | 0 | 0
2024-10-27 16:00 | 32.7 | 53 | 6.22 | 375 | 26 | 30 | 17 | 0 | 0
2024-10-27 17:00 | 31.4 | 58 | 5.23 | 177 | 26 | 30 | 17 | 2.7781 | 0
2024-10-27 18:00 | 30.2 | 68 | 5.05 | 22 | 26 | 30 | 17 | 13.94 | 0
2024-10-27 19:00 | 29.8 | 70 | 4.44 | 0 | 26 | 30 | 17 | 16.9925 | 0
2024-10-27 20:00 | 29.8 | 68 | 3.82 | 0 | 26 | 30 | 17 | 20.2135 | 0
2024-10-27 21:00 | 29.5 | 69 | 3.41 | 0 | 26 | 30 | 17 | 20.753 | 0
2024-10-27 22:00 | 29.1 | 68 | 3.25 | 0 | 26 | 30 | 17 | 26.5395 | 0
2024-10-27 23:00 | 28.8 | 70 | 3.41 | 0 | 26 | 30 | 17 | 26.9177 | 0
2024-10-28 | 28.6 | 69 | 3.49 | 0 | 26 | 30 | 17 | 31.3583 | 0
2024-10-28 01:00 | 28.3 | 73 | 3.89 | 0 | 26 | 30 | 17 | 29.0562 | 0
2024-10-28 02:00 | 28 | 77 | 3.99 | 0 | 26 | 30 | 17 | 25.4541 | 0
2024-10-28 03:00 | 27.9 | 76 | 4.02 | 0 | 26 | 30 | 17 | 28.7853 | 0
2024-10-28 04:00 | 27.6 | 75 | 3.84 | 0 | 26 | 30 | 17 | 33.756 | 0
2024-10-28 05:00 | 27.8 | 72 | 3.2 | 0 | 26 | 30 | 17 | 33.5471 | 0
2024-10-28 06:00 | 27.4 | 70 | 3.03 | 0 | 26 | 30 | 17 | 39.841 | 0
2024-10-28 07:00 | 27.5 | 69 | 2.79 | 15 | 26 | 30 | 17 | 36.6063 | 0
2024-10-28 08:00 | 29.5 | 61 | 2.82 | 159 | 26 | 30 | 17 | 10.8282 | 0
2024-10-28 09:00 | 31 | 53 | 4.57 | 364 | 26 | 30 | 17 | 0 | 0
2024-10-28 10:00 | 31.8 | 49 | 5.48 | 550 | 26 | 30 | 17 | 0 | 0
2024-10-28 11:00 | 32.4 | 45 | 5.91 | 687 | 26 | 30 | 17 | 0 | 0
2024-10-28 12:00 | 32.8 | 41 | 6.21 | 765 | 26 | 30 | 17 | 0 | 0
2024-10-28 13:00 | 32.8 | 41 | 6.78 | 773 | 26 | 30 | 17 | 0 | 0
2024-10-28 14:00 | 32.7 | 40 | 7.21 | 704 | 26 | 30 | 17 | 0 | 0
2024-10-28 15:00 | 32.2 | 40 | 7.31 | 570 | 26 | 30 | 17 | 7.5654 | 0
2024-10-28 16:00 | 31.5 | 42 | 7.15 | 385 | 26 | 30 | 17 | 34.4134 | 0
2024-10-28 17:00 | 30.4 | 46 | 6.38 | 178 | 26 | 30 | 17 | 58.8633 | 0
2024-10-28 18:00 | 29.5 | 51 | 5.21 | 21 | 26 | 30 | 17 | 68.2929 | 0
2024-10-28 19:00 | 29 | 54 | 4.62 | 0 | 26 | 30 | 17 | 64.997 | 0
2024-10-28 20:00 | 28.6 | 55 | 4.43 | 0 | 26 | 30 | 17 | 65.7744 | 0
2024-10-28 21:00 | 28.2 | 55 | 4.3 | 0 | 26 | 30 | 17 | 69.0772 | 0
2024-10-28 22:00 | 27.7 | 58 | 3.95 | 0 | 26 | 30 | 17 | 65.1586 | 0
2024-10-28 23:00 | 27.2 | 62 | 3.57 | 0 | 26 | 30 | 17 | 59.4692 | 0
2024-10-29 | 26.8 | 64 | 3.49 | 0 | 26 | 30 | 17 | 59.4227 | 0
2024-10-29 01:00 | 26.6 | 65 | 3.49 | 0 | 26 | 30 | 17 | 59.8293 | 0
2024-10-29 02:00 | 26.1 | 67 | 3.23 | 0 | 26 | 30 | 17 | 59.058 | 0
2024-10-29 03:00 | 25.5 | 71 | 2.86 | 0 | 26 | 30 | 17 | 55.201 | 0
2024-10-29 04:00 | 25 | 73 | 2.71 | 0 | 26 | 30 | 17 | 55.5229 | 0
2024-10-29 05:00 | 24.6 | 70 | 3.1 | 0 | 26 | 30 | 17 | 67.6372 | 0
2024-10-29 06:00 | 24.4 | 70 | 3.5 | 0 | 26 | 30 | 17 | 74.5293 | 0
2024-10-29 07:00 | 24.6 | 69 | 3.69 | 15 | 26 | 30 | 17 | 74.2753 | 0
2024-10-29 08:00 | 27.1 | 59 | 2.95 | 157 | 26 | 30 | 17 | 37.4217 | 0
2024-10-29 09:00 | 30.1 | 50 | 2.14 | 362 | 26 | 30 | 17 | 0 | 0
2024-10-29 10:00 | 31.5 | 46 | 4.63 | 549 | 26 | 30 | 17 | 0 | 0
2024-10-29 11:00 | 32.3 | 43 | 5.22 | 687 | 26 | 30 | 17 | 0 | 0
2024-10-29 12:00 | 32.8 | 40 | 5.64 | 763 | 26 | 30 | 17 | 0 | 0
2024-10-29 13:00 | 32.9 | 40 | 6.64 | 770 | 26 | 30 | 17 | 0 | 0
2024-10-29 14:00 | 32.6 | 41 | 7.26 | 702 | 26 | 30 | 17 | 0 | 0
2024-10-29 15:00 | 31.9 | 46 | 7.96 | 568 | 26 | 30 | 17 | 0 | 0
2024-10-29 16:00 | 31.1 | 48 | 7.84 | 382 | 26 | 30 | 17 | 23.8117 | 0
2024-10-29 17:00 | 30.3 | 51 | 6.73 | 174 | 26 | 30 | 17 | 47.6687 | 0
2024-10-29 18:00 | 29.4 | 53 | 5.32 | 20 | 26 | 30 | 17 | 65.4737 | 0
2024-10-29 19:00 | 28.7 | 56 | 4.57 | 0 | 26 | 30 | 17 | 63.6325 | 0
2024-10-29 20:00 | 28.2 | 62 | 4.99 | 0 | 26 | 30 | 17 | 59.584 | 0
2024-10-29 21:00 | 27.8 | 65 | 5.14 | 0 | 26 | 30 | 17 | 59.1149 | 0
2024-10-29 22:00 | 27.7 | 62 | 4.86 | 0 | 26 | 30 | 17 | 65.0959 | 0
2024-10-29 23:00 | 27.3 | 61 | 4.37 | 0 | 26 | 30 | 17 | 67.8309 | 0
2024-10-30 | 26.9 | 60 | 4.14 | 0 | 26 | 30 | 17 | 72.0043 | 0
2024-10-30 01:00 | 26.5 | 61 | 3.95 | 0 | 26 | 30 | 17 | 72.4697 | 0
2024-10-30 02:00 | 26 | 66 | 3.8 | 0 | 26 | 30 | 17 | 67.6144 | 0
2024-10-30 03:00 | 25.6 | 68 | 3.54 | 0 | 26 | 30 | 17 | 65.8325 | 0
2024-10-30 04:00 | 25.2 | 72 | 3.24 | 0 | 26 | 30 | 17 | 60.7314 | 0
2024-10-30 05:00 | 24.2 | 63 | 2.66 | 0 | 26 | 30 | 17 | 73.5803 | 0
2024-10-30 06:00 | 24 | 62 | 3.27 | 0 | 26 | 30 | 17 | 86.1035 | 0
2024-10-30 07:00 | 24.2 | 62 | 3.59 | 14 | 26 | 30 | 17 | 87.2804 | 0
2024-10-30 08:00 | 26.7 | 57 | 3.16 | 157 | 26 | 30 | 17 | 46.5567 | 0
2024-10-30 09:00 | 29.7 | 50 | 2.62 | 362 | 26 | 30 | 17 | 0 | 0
2024-10-30 10:00 | 31.5 | 44 | 3.99 | 548 | 26 | 30 | 17 | 0 | 0
2024-10-30 11:00 | 32.1 | 42 | 4.91 | 685 | 26 | 30 | 17 | 0 | 0
2024-10-30 12:00 | 32.5 | 40 | 5.03 | 759 | 26 | 30 | 17 | 0 | 0
2024-10-30 13:00 | 32.7 | 39 | 5.52 | 762 | 26 | 30 | 17 | 0 | 0
2024-10-30 14:00 | 32.5 | 39 | 5.8 | 693 | 26 | 30 | 17 | 0 | 0
2024-10-30 15:00 | 32.2 | 40 | 5.85 | 560 | 26 | 30 | 17 | 0 | 0
2024-10-30 16:00 | 31.6 | 40 | 5.64 | 377 | 26 | 30 | 17 | 28.455 | 0
2024-10-30 17:00 | 30 | 50 | 5.29 | 172 | 26 | 30 | 17 | 44.8325 | 0
2024-10-30 18:00 | 29.2 | 56 | 4.4 | 19 | 26 | 30 | 17 | 53.7823 | 0
2024-10-30 19:00 | 28.7 | 59 | 3.75 | 0 | 26 | 30 | 17 | 50.7018 | 0
2024-10-30 20:00 | 28.2 | 60 | 3.26 | 0 | 26 | 30 | 17 | 49.9282 | 0
2024-10-30 21:00 | 27.5 | 63 | 2.55 | 0 | 26 | 30 | 17 | 45.0875 | 0
2024-10-30 22:00 | 26.4 | 68 | 1.86 | 0 | 26 | 30 | 17 | 40.4347 | 0
2024-10-30 23:00 | 26 | 71 | 1.56 | 0 | 26 | 30 | 17 | 36.8627 | 0
2024-10-31 | 25.4 | 73 | 2.23 | 0 | 26 | 30 | 17 | 46.8064 | 0
2024-10-31 01:00 | 24.9 | 73 | 2.87 | 0 | 26 | 30 | 17 | 58.2203 | 0
2024-10-31 02:00 | 23.9 | 76 | 3.35 | 0 | 26 | 30 | 17 | 69.3897 | 0
2024-10-31 03:00 | 23.3 | 78 | 3.29 | 0 | 26 | 30 | 17 | 72.0047 | 0
2024-10-31 04:00 | 23 | 80 | 3.14 | 0 | 26 | 30 | 17 | 70.5599 | 0
2024-10-31 05:00 | 22.8 | 79 | 2.84 | 0 | 26 | 30 | 17 | 69.6742 | 0
2024-10-31 06:00 | 22.6 | 80 | 2.85 | 0 | 26 | 30 | 17 | 70.4811 | 0
2024-10-31 07:00 | 22.9 | 78 | 2.91 | 13 | 26 | 30 | 17 | 69.1054 | 0
2024-10-31 08:00 | 25.1 | 69 | 2.78 | 142 | 26 | 30 | 17 | 41.3059 | 0
2024-10-31 09:00 | 28.2 | 57 | 2.44 | 331 | 26 | 30 | 17 | 1.7597 | 0
2024-10-31 10:00 | 30.1 | 51 | 1.7 | 535 | 26 | 30 | 17 | 0 | 3.9745
2024-10-31 11:00 | 31.5 | 44 | 0.96 | 684 | 26 | 30 | 17 | 0 | 44.2594
2024-10-31 12:00 | 32.9 | 34 | 0.85 | 760 | 26 | 30 | 17 | 0 | 55.6105
2024-10-31 13:00 | 33.8 | 29 | 0.71 | 765 | 26 | 30 | 17 | 0 | 60.8398
2024-10-31 14:00 | 34.2 | 29 | 2.2 | 691 | 26 | 30 | 17 | 0 | 6.295
2024-10-31 15:00 | 33.1 | 40 | 4.31 | 559 | 26 | 30 | 17 | 0 | 0
2024-10-31 16:00 | 32.2 | 40 | 5.1 | 373 | 26 | 30 | 17 | 17.1578 | 0
2024-10-31 17:00 | 31 | 52 | 4.77 | 168 | 26 | 30 | 17 | 23.8707 | 0
2024-10-31 18:00 | 29.7 | 61 | 4.23 | 18 | 26 | 30 | 17 | 35.666 | 0
2024-10-31 19:00 | 29.2 | 66 | 2.81 | 0 | 26 | 30 | 17 | 26.923 | 0
2024-10-31 20:00 | 28.5 | 73 | 1.76 | 0 | 26 | 30 | 17 | 18.5184 | 0
2024-10-31 21:00 | 27.7 | 78 | 1.49 | 0 | 26 | 30 | 17 | 18.0865 | 0
2024-10-31 22:00 | 27.3 | 75 | 2.2 | 0 | 26 | 30 | 17 | 28.3709 | 0
2024-10-31 23:00 | 26.5 | 76 | 2.27 | 0 | 26 | 30 | 17 | 34.5503 | 0
2024-11-01 | 25.5 | 81 | 1.73 | 0 | 26 | 30 | 17 | 32.9467 | 0
2024-11-01 01:00 | 25 | 83 | 1.43 | 0 | 26 | 30 | 17 | 32.0299 | 0
2024-11-01 02:00 | 24.1 | 86 | 1.57 | 0 | 26 | 30 | 17 | 37.174 | 0
2024-11-01 03:00 | 23.5 | 86 | 1.72 | 0 | 26 | 30 | 17 | 43.0661 | 0
2024-11-01 04:00 | 23.2 | 84 | 2.03 | 0 | 26 | 30 | 17 | 50.7471 | 0
2024-11-01 05:00 | 23.9 | 79 | 2.29 | 0 | 26 | 30 | 17 | 53.2261 | 0
2024-11-01 06:00 | 23.5 | 79 | 2.26 | 0 | 26 | 30 | 17 | 56.0745 | 0
2024-11-01 07:00 | 23.6 | 78 | 2.37 | 13 | 26 | 30 | 17 | 55.9509 | 0
2024-11-01 08:00 | 26.1 | 67 | 1.55 | 150 | 26 | 30 | 17 | 19.4169 | 0
2024-11-01 09:00 | 28.9 | 56 | 1.46 | 353 | 26 | 30 | 17 | 0 | 0
2024-11-01 10:00 | 31 | 47 | 1.59 | 539 | 26 | 30 | 17 | 0 | 8.093
2024-11-01 11:00 | 32.7 | 40 | 1.7 | 677 | 26 | 30 | 17 | 0 | 25.4363
2024-11-01 12:00 | 33.8 | 36 | 2.33 | 750 | 26 | 30 | 17 | 0 | 21.2587
2024-11-01 13:00 | 34 | 38 | 4.11 | 752 | 26 | 30 | 17 | 0 | 0
2024-11-01 14:00 | 33.4 | 41 | 5.88 | 682 | 26 | 30 | 17 | 0 | 0
2024-11-01 15:00 | 32.5 | 46 | 5.91 | 549 | 26 | 30 | 17 | 0 | 0
2024-11-01 16:00 | 31.7 | 52 | 5.49 | 367 | 26 | 30 | 17 | 0 | 0
2024-11-01 17:00 | 30.4 | 59 | 4.96 | 164 | 26 | 30 | 17 | 15.011 | 0
2024-11-01 18:00 | 29.4 | 66 | 4.41 | 18 | 26 | 30 | 17 | 29.0633 | 0
2024-11-01 19:00 | 29.2 | 67 | 3.15 | 0 | 26 | 30 | 17 | 26.8121 | 0
2024-11-01 20:00 | 28.7 | 69 | 2.01 | 0 | 26 | 30 | 17 | 22.9307 | 0
2024-11-01 21:00 | 27.7 | 76 | 1.4 | 0 | 26 | 30 | 17 | 19.4982 | 0
2024-11-01 22:00 | 27.6 | 75 | 0.85 | 0 | 26 | 30 | 17 | 17.313 | 0
2024-11-01 23:00 | 27.8 | 73 | 0.21 | 0 | 26 | 30 | 17 | 15.8099 | 0
2024-11-02 | 27.5 | 74 | 0.3 | 0 | 26 | 30 | 17 | 16.5002 | 0
2024-11-02 01:00 | 27 | 77 | 0.2 | 0 | 26 | 30 | 17 | 17.2378 | 0
2024-11-02 02:00 | 24.9 | 87 | 1.5 | 0 | 26 | 30 | 17 | 30.1204 | 0
2024-11-02 03:00 | 24.3 | 89 | 2.26 | 0 | 26 | 30 | 17 | 39.1385 | 0
2024-11-02 04:00 | 23.5 | 92 | 1.99 | 0 | 26 | 30 | 17 | 40.6541 | 0
2024-11-02 05:00 | 23.7 | 90 | 1.79 | 0 | 26 | 30 | 17 | 38.9679 | 0
2024-11-02 06:00 | 23.4 | 92 | 2.21 | 0 | 26 | 30 | 17 | 43.5173 | 0
2024-11-02 07:00 | 23.4 | 91 | 2.06 | 12 | 26 | 30 | 17 | 41.4336 | 0
2024-11-02 08:00 | 25.7 | 80 | 1.43 | 148 | 26 | 30 | 17 | 9.7991 | 0
2024-11-02 09:00 | 28.3 | 68 | 1.35 | 352 | 26 | 30 | 17 | 0 | 0
2024-11-02 10:00 | 30.5 | 53 | 1.19 | 539 | 26 | 30 | 17 | 0 | 21.5429
2024-11-02 11:00 | 32.4 | 41 | 1.74 | 678 | 26 | 30 | 17 | 0 | 24.1038
2024-11-02 12:00 | 33.5 | 36 | 2.67 | 753 | 26 | 30 | 17 | 0 | 11.8086
2024-11-02 13:00 | 33.8 | 37 | 3.89 | 755 | 26 | 30 | 17 | 0 | 0
2024-11-02 14:00 | 33.5 | 37 | 4.82 | 682 | 26 | 30 | 17 | 0 | 0
2024-11-02 15:00 | 32.6 | 42 | 5.37 | 557 | 26 | 30 | 17 | 0 | 0
2024-11-02 16:00 | 31.6 | 48 | 4.81 | 373 | 26 | 30 | 17 | 0 | 0
2024-11-02 17:00 | 30.3 | 58 | 4.36 | 166 | 26 | 30 | 17 | 15.7922 | 0
2024-11-02 18:00 | 29.1 | 68 | 3.65 | 17 | 26 | 30 | 17 | 25.8496 | 0
2024-11-02 19:00 | 28.5 | 73 | 2.75 | 0 | 26 | 30 | 17 | 22.5773 | 0
2024-11-02 20:00 | 27.8 | 78 | 2.06 | 0 | 26 | 30 | 17 | 19.6888 | 0
2024-11-02 21:00 | 26.9 | 84 | 1.33 | 0 | 26 | 30 | 17 | 17.6226 | 0
2024-11-02 22:00 | 27.6 | 79 | 0.25 | 0 | 26 | 30 | 17 | 13.6146 | 0
2024-11-02 23:00 | 25.5 | 89 | 1.82 | 0 | 26 | 30 | 17 | 25.983 | 0
2024-11-03 | 24.8 | 92 | 2.93 | 0 | 26 | 30 | 17 | 35.238 | 0
2024-11-03 01:00 | 23.6 | 96 | 2.48 | 0 | 26 | 30 | 17 | 39.8303 | 0
2024-11-03 02:00 | 23.3 | 96 | 2.26 | 0 | 26 | 30 | 17 | 40.9038 | 0
2024-11-03 03:00 | 22.9 | 96 | 2.33 | 0 | 26 | 30 | 17 | 45.0862 | 0
2024-11-03 04:00 | 22.5 | 97 | 2.39 | 0 | 26 | 30 | 17 | 48.2666 | 0
2024-11-03 05:00 | 22.4 | 96 | 2.18 | 0 | 26 | 30 | 17 | 47.9921 | 0
2024-11-03 06:00 | 22.1 | 96 | 2.36 | 0 | 26 | 30 | 17 | 52.4849 | 0
2024-11-03 07:00 | 22.2 | 96 | 2.53 | 12 | 26 | 30 | 17 | 51.7714 | 0
2024-11-03 08:00 | 24.7 | 83 | 2.15 | 151 | 26 | 30 | 17 | 20.6292 | 0
2024-11-03 09:00 | 27.6 | 70 | 2.07 | 359 | 26 | 30 | 17 | 0 | 0
2024-11-03 10:00 | 29.8 | 60 | 1.68 | 551 | 26 | 30 | 17 | 0 | 15.278
2024-11-03 11:00 | 32 | 45 | 0.93 | 693 | 26 | 30 | 17 | 0 | 49.6315
2024-11-03 12:00 | 33.7 | 35 | 1.37 | 769 | 26 | 30 | 17 | 0 | 45.6063
2024-11-03 13:00 | 34.4 | 35 | 2.85 | 772 | 26 | 30 | 17 | 0 | 15.4973
2024-11-03 14:00 | 33.5 | 47 | 4.36 | 700 | 26 | 30 | 17 | 0 | 1.4357
2024-11-03 15:00 | 32.9 | 45 | 5.1 | 561 | 26 | 30 | 17 | 0 | 0
2024-11-03 16:00 | 31.6 | 51 | 5.18 | 377 | 26 | 30 | 17 | 0 | 0
2024-11-03 17:00 | 30 | 63 | 4.51 | 166 | 26 | 30 | 17 | 8.4598 | 0
2024-11-03 18:00 | 29.1 | 69 | 3.59 | 17 | 26 | 30 | 17 | 23.6939 | 0
2024-11-03 19:00 | 28.5 | 72 | 2.22 | 0 | 26 | 30 | 17 | 21.8209 | 0
2024-11-03 20:00 | 27.5 | 77 | 1.78 | 0 | 26 | 30 | 17 | 22.0336 | 0
2024-11-03 21:00 | 27.3 | 78 | 0.9 | 0 | 26 | 30 | 17 | 17.3345 | 0
2024-11-03 22:00 | 27 | 79 | 0.82 | 0 | 26 | 30 | 17 | 17.7529 | 0
2024-11-03 23:00 | 24.9 | 89 | 2.44 | 0 | 26 | 30 | 17 | 34.9695 | 0
2024-11-04 | 23.8 | 94 | 2.41 | 0 | 26 | 30 | 17 | 39.5605 | 0
2024-11-04 01:00 | 22.9 | 97 | 2.04 | 0 | 26 | 30 | 17 | 41.5291 | 0
2024-11-04 02:00 | 22.4 | 98 | 2.15 | 0 | 26 | 30 | 17 | 45.8783 | 0
2024-11-04 03:00 | 21.9 | 98 | 2.02 | 0 | 26 | 30 | 17 | 48.6619 | 0
2024-11-04 04:00 | 21.6 | 97 | 2.24 | 0 | 26 | 30 | 17 | 54.5149 | 0
2024-11-04 05:00 | 22 | 98 | 2.04 | 0 | 26 | 30 | 17 | 48.0718 | 0
2024-11-04 06:00 | 21.6 | 98 | 2.21 | 0 | 26 | 30 | 17 | 53.2852 | 0
2024-11-04 07:00 | 21.4 | 98 | 2.2 | 11 | 26 | 30 | 17 | 53.3554 | 0
2024-11-04 08:00 | 23.8 | 87 | 1.91 | 145 | 26 | 30 | 17 | 22.461 | 0
2024-11-04 09:00 | 26.9 | 71 | 1.56 | 353 | 26 | 30 | 17 | 0 | 0
2024-11-04 10:00 | 29.4 | 58 | 1.13 | 543 | 26 | 30 | 17 | 0 | 21.9881
2024-11-04 11:00 | 31.6 | 45 | 0.36 | 684 | 26 | 30 | 17 | 0 | 56.5296
2024-11-04 12:00 | 33.3 | 36 | 1.44 | 758 | 26 | 30 | 17 | 0 | 41.2886
2024-11-04 13:00 | 33.9 | 36 | 2.9 | 760 | 26 | 30 | 17 | 0 | 10.9696
2024-11-04 14:00 | 33.5 | 41 | 4.11 | 688 | 26 | 30 | 17 | 0 | 0
2024-11-04 15:00 | 32.8 | 39 | 4.69 | 553 | 26 | 30 | 17 | 0 | 0
2024-11-04 16:00 | 31.5 | 47 | 4.53 | 370 | 26 | 30 | 17 | 2.0256 | 0
2024-11-04 17:00 | 30.2 | 58 | 3.57 | 163 | 26 | 30 | 17 | 13.1832 | 0
2024-11-04 18:00 | 28.9 | 71 | 2.67 | 16 | 26 | 30 | 17 | 19.1961 | 0
2024-11-04 19:00 | 28.3 | 77 | 1.84 | 0 | 26 | 30 | 17 | 15.8754 | 0
2024-11-04 20:00 | 27.4 | 83 | 1.72 | 0 | 26 | 30 | 17 | 16.2492 | 0
2024-11-04 21:00 | 26.7 | 88 | 1.01 | 0 | 26 | 30 | 17 | 14.6355 | 0
2024-11-04 22:00 | 26.9 | 88 | 0.25 | 0 | 26 | 30 | 17 | 12.3497 | 0
2024-11-04 23:00 | 25.7 | 92 | 0.99 | 0 | 26 | 30 | 17 | 17.9515 | 0
2024-11-05 | 24.5 | 95 | 1.8 | 0 | 26 | 30 | 17 | 28.3663 | 0
2024-11-05 01:00 | 24.2 | 95 | 2.23 | 0 | 26 | 30 | 17 | 33.5843 | 0
2024-11-05 02:00 | 23.6 | 96 | 2.27 | 0 | 26 | 30 | 17 | 38.284 | 0
2024-11-05 03:00 | 22.9 | 98 | 2.06 | 0 | 26 | 30 | 17 | 40.8074 | 0
2024-11-05 04:00 | 22.6 | 97 | 2.06 | 0 | 26 | 30 | 17 | 44.2133 | 0
2024-11-05 05:00 | 23 | 92 | 2.41 | 0 | 26 | 30 | 17 | 48.9401 | 0
2024-11-05 06:00 | 22.3 | 94 | 2.54 | 0 | 26 | 30 | 17 | 54.5864 | 0
2024-11-05 07:00 | 22.2 | 93 | 2.72 | 11 | 26 | 30 | 17 | 57.02 | 0
2024-11-05 08:00 | 24.8 | 77 | 2.33 | 145 | 26 | 30 | 17 | 28.8177 | 0
2024-11-05 09:00 | 28.2 | 61 | 2.42 | 351 | 26 | 30 | 17 | 0 | 0
2024-11-05 10:00 | 31.4 | 41 | 2.1 | 540 | 26 | 30 | 17 | 0 | 0
2024-11-05 11:00 | 33.9 | 26 | 1.11 | 681 | 26 | 30 | 17 | 0 | 32.1752
2024-11-05 12:00 | 35.3 | 20 | 0.65 | 759 | 26 | 30 | 17 | 0 | 60.5925
2024-11-05 13:00 | 35.4 | 26 | 3.35 | 764 | 26 | 30 | 17 | 0 | 0
2024-11-05 14:00 | 34.1 | 36 | 5.1 | 690 | 26 | 30 | 17 | 0 | 0
2024-11-05 15:00 | 33.7 | 29 | 5.52 | 553 | 26 | 30 | 17 | 14.5 | 0
2024-11-05 16:00 | 32.5 | 40 | 5.15 | 370 | 26 | 30 | 17 | 14.4379 | 0
2024-11-05 17:00 | 31.4 | 42 | 3.96 | 162 | 26 | 30 | 17 | 38.7661 | 0
2024-11-05 18:00 | 29.7 | 55 | 2.86 | 15 | 26 | 30 | 17 | 38.7729 | 0
2024-11-05 19:00 | 28.5 | 65 | 1.98 | 0 | 26 | 30 | 17 | 29.2689 | 0
2024-11-05 20:00 | 27.3 | 72 | 1.54 | 0 | 26 | 30 | 17 | 26.9647 | 0
2024-11-05 21:00 | 26.4 | 77 | 1.45 | 0 | 26 | 30 | 17 | 27.795 | 0
2024-11-05 22:00 | 25.9 | 76 | 2.5 | 0 | 26 | 30 | 17 | 41.682 | 0
2024-11-05 23:00 | 24.7 | 75 | 1.72 | 0 | 26 | 30 | 17 | 44.0213 | 0
2024-11-06 | 25.7 | 67 | 0.41 | 0 | 26 | 30 | 17 | 27.1709 | 0
2024-11-06 01:00 | 25.3 | 68 | 0.74 | 0 | 26 | 30 | 17 | 31.0315 | 0
2024-11-06 02:00 | 23 | 76 | 1.62 | 0 | 26 | 30 | 17 | 53.0103 | 0
2024-11-06 03:00 | 22.6 | 74 | 1.55 | 0 | 26 | 30 | 17 | 55.7877 | 0
2024-11-06 04:00 | 22.3 | 74 | 2.5 | 0 | 26 | 30 | 17 | 74.0725 | 0
2024-11-06 05:00 | 22.8 | 72 | 2.47 | 0 | 26 | 30 | 17 | 71.6992 | 0
2024-11-06 06:00 | 22.5 | 71 | 2.77 | 0 | 26 | 30 | 17 | 80.0119 | 0
2024-11-06 07:00 | 22.3 | 69 | 2.36 | 10 | 26 | 30 | 17 | 75.1965 | 0
2024-11-06 08:00 | 24.7 | 58 | 1.51 | 142 | 26 | 30 | 17 | 35.8876 | 0
2024-11-06 09:00 | 28.2 | 47 | 1.53 | 345 | 26 | 30 | 17 | 0 | 0
2024-11-06 10:00 | 30.7 | 42 | 2.03 | 532 | 26 | 30 | 17 | 0 | 0
2024-11-06 11:00 | 32.8 | 36 | 1.87 | 671 | 26 | 30 | 17 | 0 | 15.1017
2024-11-06 12:00 | 34.4 | 31 | 1.9 | 745 | 26 | 30 | 17 | 0 | 26.2257
2024-11-06 13:00 | 34.7 | 36 | 3.37 | 747 | 26 | 30 | 17 | 0 | 6.85
2024-11-06 14:00 | 33.6 | 50 | 5.19 | 674 | 26 | 30 | 17 | 0 | 0
2024-11-06 15:00 | 32.9 | 47 | 5.92 | 517 | 26 | 30 | 17 | 0 | 0
2024-11-06 16:00 | 32.1 | 46 | 5.54 | 359 | 26 | 30 | 17 | 5.3638 | 0
2024-11-06 17:00 | 30.4 | 62 | 5.21 | 158 | 26 | 30 | 17 | 8.7882 | 0
2024-11-06 18:00 | 29.1 | 71 | 4.54 | 15 | 26 | 30 | 17 | 22.6442 | 0
2024-11-06 19:00 | 28.6 | 74 | 3.76 | 0 | 26 | 30 | 17 | 22.9626 | 0
2024-11-06 20:00 | 28.1 | 74 | 3.32 | 0 | 26 | 30 | 17 | 27.44 | 0
2024-11-06 21:00 | 27.2 | 76 | 1.95 | 0 | 26 | 30 | 17 | 26.494 | 0
2024-11-06 22:00 | 26 | 81 | 1.49 | 0 | 26 | 30 | 17 | 27.3881 | 0
2024-11-06 23:00 | 25.6 | 83 | 1.28 | 0 | 26 | 30 | 17 | 26.7586 | 0
2024-11-07 | 25 | 85 | 1.23 | 0 | 26 | 30 | 17 | 28.6518 | 0
2024-11-07 01:00 | 24.6 | 87 | 1.2 | 0 | 26 | 30 | 17 | 29.4601 | 0
2024-11-07 02:00 | 24.4 | 86 | 1.3 | 0 | 26 | 30 | 17 | 32.3966 | 0
2024-11-07 03:00 | 24 | 88 | 1.44 | 0 | 26 | 30 | 17 | 34.968 | 0
2024-11-07 04:00 | 23.5 | 91 | 1.61 | 0 | 26 | 30 | 17 | 37.8469 | 0
2024-11-07 05:00 | 23.9 | 91 | 2.35 | 0 | 26 | 30 | 17 | 41.3417 | 0
2024-11-07 06:00 | 23.4 | 94 | 2.55 | 0 | 26 | 30 | 17 | 44.4327 | 0
2024-11-07 07:00 | 23.2 | 96 | 2.44 | 9 | 26 | 30 | 17 | 42.0784 | 0
2024-11-07 08:00 | 25.4 | 86 | 1.87 | 138 | 26 | 30 | 17 | 11.3864 | 0
2024-11-07 09:00 | 28.1 | 72 | 2.21 | 339 | 26 | 30 | 17 | 0 | 0
2024-11-07 10:00 | 30 | 59 | 2.16 | 524 | 26 | 30 | 17 | 0 | 2.4575
2024-11-07 11:00 | 31.5 | 48 | 0.76 | 661 | 26 | 30 | 17 | 0 | 50.2857
2024-11-07 12:00 | 32.8 | 42 | 1.1 | 737 | 26 | 30 | 17 | 0 | 52.0079
2024-11-07 13:00 | 33.4 | 43 | 2.83 | 741 | 26 | 30 | 17 | 0 | 20.4524
2024-11-07 14:00 | 33 | 49 | 4.45 | 671 | 26 | 30 | 17 | 0 | 0
2024-11-07 15:00 | 32.6 | 44 | 5.04 | 537 | 26 | 30 | 17 | 0 | 0
2024-11-07 16:00 | 31.6 | 50 | 4.77 | 358 | 26 | 30 | 17 | 0 | 0
2024-11-07 17:00 | 30.2 | 62 | 4.58 | 157 | 26 | 30 | 17 | 9.6663 | 0
2024-11-07 18:00 | 29.3 | 64 | 3.19 | 14 | 26 | 30 | 17 | 29.3831 | 0
2024-11-07 19:00 | 28.6 | 68 | 2.48 | 0 | 26 | 30 | 17 | 27.7865 | 0
2024-11-07 20:00 | 27.7 | 72 | 2.26 | 0 | 26 | 30 | 17 | 29.0396 | 0
2024-11-07 21:00 | 26.7 | 78 | 1.87 | 0 | 26 | 30 | 17 | 27.8003 | 0
2024-11-07 22:00 | 26.1 | 80 | 1.57 | 0 | 26 | 30 | 17 | 28.1872 | 0
2024-11-07 23:00 | 25.9 | 81 | 1.25 | 0 | 26 | 30 | 17 | 26.1183 | 0
2024-11-08 | 25.1 | 85 | 1.29 | 0 | 26 | 30 | 17 | 28.5557 | 0
2024-11-08 01:00 | 24.1 | 90 | 1.65 | 0 | 26 | 30 | 17 | 34.6811 | 0
2024-11-08 02:00 | 23.8 | 90 | 2.27 | 0 | 26 | 30 | 17 | 42.5822 | 0
2024-11-08 03:00 | 23.5 | 92 | 2.78 | 0 | 26 | 30 | 17 | 47.6221 | 0
2024-11-08 04:00 | 22.7 | 96 | 2.53 | 0 | 26 | 30 | 17 | 48.7537 | 0
2024-11-08 05:00 | 22.6 | 95 | 2.23 | 0 | 26 | 30 | 17 | 47.7212 | 0
2024-11-08 06:00 | 22.4 | 95 | 2.51 | 0 | 26 | 30 | 17 | 52.3512 | 0
2024-11-08 07:00 | 22.3 | 96 | 2.47 | 9 | 26 | 30 | 17 | 50.6416 | 0
2024-11-08 08:00 | 24.4 | 86 | 1.78 | 137 | 26 | 30 | 17 | 18.5771 | 0
2024-11-08 09:00 | 27.3 | 70 | 1.73 | 339 | 26 | 30 | 17 | 0 | 0
2024-11-08 10:00 | 28.9 | 62 | 0.96 | 527 | 26 | 30 | 17 | 0 | 24.6321
2024-11-08 11:00 | 30.3 | 54 | 0.61 | 665 | 26 | 30 | 17 | 0 | 54.0417
2024-11-08 12:00 | 31.8 | 43 | 1.52 | 740 | 26 | 30 | 17 | 0 | 36.9631
2024-11-08 13:00 | 32.4 | 40 | 2.73 | 743 | 26 | 30 | 17 | 0 | 8.3653
2024-11-08 14:00 | 32.1 | 43 | 4.1 | 675 | 26 | 30 | 17 | 0 | 0
2024-11-08 15:00 | 31.6 | 41 | 4.56 | 541 | 26 | 30 | 17 | 0 | 0
2024-11-08 16:00 | 30.9 | 42 | 4.36 | 359 | 26 | 30 | 17 | 21.241 | 0
2024-11-08 17:00 | 29.3 | 56 | 4.22 | 155 | 26 | 30 | 17 | 32.8845 | 0
2024-11-08 18:00 | 28.4 | 61 | 3.16 | 14 | 26 | 30 | 17 | 43.5196 | 0
2024-11-08 19:00 | 27.8 | 65 | 2.04 | 0 | 26 | 30 | 17 | 35.1944 | 0
2024-11-08 20:00 | 26.9 | 70 | 1.98 | 0 | 26 | 30 | 17 | 35.8004 | 0
2024-11-08 21:00 | 26 | 76 | 1.91 | 0 | 26 | 30 | 17 | 35.6591 | 0
2024-11-08 22:00 | 25 | 80 | 1.68 | 0 | 26 | 30 | 17 | 37.0261 | 0
2024-11-08 23:00 | 24.2 | 84 | 1.87 | 0 | 26 | 30 | 17 | 41.2774 | 0
2024-11-09 | 23.4 | 89 | 2.17 | 0 | 26 | 30 | 17 | 46.0402 | 0
2024-11-09 01:00 | 22.8 | 93 | 2.6 | 0 | 26 | 30 | 17 | 51.6155 | 0
2024-11-09 02:00 | 21.9 | 96 | 2.65 | 0 | 26 | 30 | 17 | 57.4572 | 0
2024-11-09 03:00 | 21.3 | 98 | 2.56 | 0 | 26 | 30 | 17 | 59.9997 | 0
2024-11-09 04:00 | 20.9 | 98 | 2.52 | 0 | 26 | 30 | 17 | 63.0998 | 0
2024-11-09 05:00 | 20.9 | 96 | 2.34 | 0 | 26 | 30 | 17 | 62.5362 | 0
2024-11-09 06:00 | 20.6 | 96 | 2.55 | 0 | 26 | 30 | 17 | 67.9669 | 0
2024-11-09 07:00 | 20.5 | 96 | 2.69 | 9 | 26 | 30 | 17 | 69.5747 | 0
2024-11-09 08:00 | 22.8 | 85 | 2.32 | 138 | 26 | 30 | 17 | 37.9753 | 0
2024-11-09 09:00 | 26.2 | 69 | 2.27 | 344 | 26 | 30 | 17 | 0 | 0
2024-11-09 10:00 | 28.5 | 55 | 1.61 | 533 | 26 | 30 | 17 | 0 | 0.1887
2024-11-09 11:00 | 30.1 | 43 | 1.05 | 674 | 26 | 30 | 17 | 0 | 32.5585
2024-11-09 12:00 | 31.6 | 34 | 1.53 | 749 | 26 | 30 | 17 | 0 | 25.7256
2024-11-09 13:00 | 32.3 | 32 | 2.27 | 752 | 26 | 30 | 17 | 0 | 5.7774
2024-11-09 14:00 | 32 | 38 | 3.54 | 681 | 26 | 30 | 17 | 0 | 0
2024-11-09 15:00 | 31.1 | 40 | 4.67 | 543 | 26 | 30 | 17 | 2.4853 | 0
2024-11-09 16:00 | 30.4 | 39 | 4.7 | 359 | 26 | 30 | 17 | 37.5643 | 0
2024-11-09 17:00 | 29.1 | 50 | 4.24 | 154 | 26 | 30 | 17 | 48.4169 | 0
2024-11-09 18:00 | 28 | 57 | 2.22 | 13 | 26 | 30 | 17 | 43.741 | 0
2024-11-09 19:00 | 26.9 | 66 | 1.21 | 0 | 26 | 30 | 17 | 31.3018 | 0
2024-11-09 20:00 | 27.3 | 60 | 0.64 | 0 | 26 | 30 | 17 | 24.8027 | 0
2024-11-09 21:00 | 26 | 67 | 1.04 | 0 | 26 | 30 | 17 | 33.1497 | 0
2024-11-09 22:00 | 24.6 | 71 | 2.21 | 0 | 26 | 30 | 17 | 55.001 | 0
2024-11-09 23:00 | 23.5 | 77 | 1.91 | 0 | 26 | 30 | 17 | 53.2179 | 0
2024-11-10 | 22.9 | 80 | 1.42 | 0 | 26 | 30 | 17 | 47.5174 | 0
2024-11-10 01:00 | 22.7 | 81 | 1.3 | 0 | 26 | 30 | 17 | 46.1277 | 0
2024-11-10 02:00 | 22.3 | 82 | 1.39 | 0 | 26 | 30 | 17 | 49.2998 | 0
2024-11-10 03:00 | 21.7 | 85 | 1.59 | 0 | 26 | 30 | 17 | 54.2481 | 0
2024-11-10 04:00 | 21.1 | 86 | 2.15 | 0 | 26 | 30 | 17 | 66.6812 | 0
2024-11-10 05:00 | 21.5 | 82 | 2.36 | 0 | 26 | 30 | 17 | 70.4522 | 0
2024-11-10 06:00 | 21.1 | 85 | 2.62 | 0 | 26 | 30 | 17 | 74.9749 | 0
2024-11-10 07:00 | 21.1 | 85 | 2.61 | 8 | 26 | 30 | 17 | 73.7398 | 0
2024-11-10 08:00 | 23.6 | 72 | 2.14 | 133 | 26 | 30 | 17 | 42.5451 | 0
2024-11-10 09:00 | 27.2 | 56 | 1.96 | 333 | 26 | 30 | 17 | 4.1084 | 0
2024-11-10 10:00 | 29.6 | 46 | 1.81 | 519 | 26 | 30 | 17 | 0 | 0
2024-11-10 11:00 | 31.4 | 37 | 0.99 | 656 | 26 | 30 | 17 | 0 | 32.8661
2024-11-10 12:00 | 32.8 | 31 | 1.27 | 730 | 26 | 30 | 17 | 0 | 33.9468
2024-11-10 13:00 | 33.4 | 31 | 2.62 | 733 | 26 | 30 | 17 | 0 | 0
2024-11-10 14:00 | 33 | 36 | 4.26 | 664 | 26 | 30 | 17 | 0 | 0
2024-11-10 15:00 | 32.2 | 36 | 5.08 | 531 | 26 | 30 | 17 | 7.3503 | 0
2024-11-10 16:00 | 31.2 | 44 | 4.88 | 350 | 26 | 30 | 17 | 18.8506 | 0
2024-11-10 17:00 | 29.8 | 59 | 4.53 | 149 | 26 | 30 | 17 | 22.8851 | 0
2024-11-10 18:00 | 28.9 | 62 | 3.84 | 12 | 26 | 30 | 17 | 41.6218 | 0
2024-11-10 19:00 | 28.3 | 64 | 3.12 | 0 | 26 | 30 | 17 | 41.0668 | 0
2024-11-10 20:00 | 27.4 | 69 | 2.15 | 0 | 26 | 30 | 17 | 34.4983 | 0
2024-11-10 21:00 | 26.6 | 73 | 2.11 | 0 | 26 | 30 | 17 | 35.941 | 0
2024-11-10 22:00 | 25.7 | 76 | 2.42 | 0 | 26 | 30 | 17 | 42.746 | 0
2024-11-10 23:00 | 24.7 | 79 | 1.98 | 0 | 26 | 30 | 17 | 43.3412 | 0
2024-11-11 | 24 | 82 | 1.3 | 0 | 26 | 30 | 17 | 37.7141 | 0
2024-11-11 01:00 | 23.9 | 83 | 1.25 | 0 | 26 | 30 | 17 | 36.9969 | 0
2024-11-11 02:00 | 23 | 86 | 1.44 | 0 | 26 | 30 | 17 | 42.9792 | 0
2024-11-11 03:00 | 22.8 | 87 | 1.19 | 0 | 26 | 30 | 17 | 40.1106 | 0
2024-11-11 04:00 | 21.9 | 90 | 1.41 | 0 | 26 | 30 | 17 | 46.8158 | 0
2024-11-11 05:00 | 21.9 | 92 | 1.41 | 0 | 26 | 30 | 17 | 45.5141 | 0
2024-11-11 06:00 | 21.5 | 93 | 1.91 | 0 | 26 | 30 | 17 | 54.4586 | 0
2024-11-11 07:00 | 21.9 | 93 | 2.52 | 7 | 26 | 30 | 17 | 58.0106 | 0
2024-11-11 08:00 | 23.9 | 83 | 1.44 | 129 | 26 | 30 | 17 | 21.9508 | 0
2024-11-11 09:00 | 27.1 | 72 | 1.3 | 328 | 26 | 30 | 17 | 0 | 0
2024-11-11 10:00 | 29 | 66 | 0.93 | 512 | 26 | 30 | 17 | 0 | 26.8614
2024-11-11 11:00 | 30.9 | 53 | 1.8 | 649 | 26 | 30 | 17 | 0 | 25.0802
2024-11-11 12:00 | 32.4 | 41 | 2.9 | 723 | 26 | 30 | 17 | 0 | 3.9925
2024-11-11 13:00 | 32.9 | 38 | 3.88 | 726 | 26 | 30 | 17 | 0 | 0
2024-11-11 14:00 | 32.8 | 36 | 4.66 | 659 | 26 | 30 | 17 | 0 | 0
2024-11-11 15:00 | 32 | 41 | 4.98 | 528 | 26 | 30 | 17 | 0 | 0
2024-11-11 16:00 | 31.1 | 47 | 4.74 | 348 | 26 | 30 | 17 | 11.2207 | 0
2024-11-11 17:00 | 30 | 50 | 4.11 | 148 | 26 | 30 | 17 | 38.3138 | 0
2024-11-11 18:00 | 28.9 | 59 | 3.01 | 12 | 26 | 30 | 17 | 41.0943 | 0
2024-11-11 19:00 | 28.1 | 65 | 2.41 | 0 | 26 | 30 | 17 | 35.9426 | 0
2024-11-11 20:00 | 26.9 | 71 | 1.61 | 0 | 26 | 30 | 17 | 31.3057 | 0
2024-11-11 21:00 | 27.6 | 68 | 0.64 | 0 | 26 | 30 | 17 | 19.3427 | 0
2024-11-11 22:00 | 27.1 | 70 | 0.25 | 0 | 26 | 30 | 17 | 20.183 | 0
2024-11-11 23:00 | 24.6 | 81 | 1.84 | 0 | 26 | 30 | 17 | 40.7038 | 0
2024-11-12 | 24.1 | 81 | 2.66 | 0 | 26 | 30 | 17 | 53.495 | 0
2024-11-12 01:00 | 23.2 | 85 | 2.53 | 0 | 26 | 30 | 17 | 55.698 | 0
2024-11-12 02:00 | 22.5 | 88 | 2.21 | 0 | 26 | 30 | 17 | 54.8439 | 0
2024-11-12 03:00 | 21.9 | 91 | 1.85 | 0 | 26 | 30 | 17 | 52.2646 | 0
2024-11-12 04:00 | 21.9 | 90 | 1.7 | 0 | 26 | 30 | 17 | 50.9722 | 0
2024-11-12 05:00 | 22.5 | 90 | 1.66 | 0 | 26 | 30 | 17 | 46.2599 | 0
2024-11-12 06:00 | 22.2 | 90 | 2.26 | 0 | 26 | 30 | 17 | 56.0736 | 0
2024-11-12 07:00 | 22.3 | 90 | 2.41 | 7 | 26 | 30 | 17 | 56.1178 | 0
2024-11-12 08:00 | 24.3 | 80 | 1.74 | 128 | 26 | 30 | 17 | 25.3915 | 0
2024-11-12 09:00 | 27.2 | 69 | 1.54 | 328 | 26 | 30 | 17 | 0 | 0
2024-11-12 10:00 | 28.9 | 61 | 0.67 | 513 | 26 | 30 | 17 | 0 | 29.8391
2024-11-12 11:00 | 30.6 | 47 | 0.99 | 650 | 26 | 30 | 17 | 0 | 37.0186
2024-11-12 12:00 | 31.8 | 39 | 1.9 | 723 | 26 | 30 | 17 | 0 | 19.4786
2024-11-12 13:00 | 32.2 | 39 | 2.83 | 727 | 26 | 30 | 17 | 0 | 0.4613
2024-11-12 14:00 | 32.1 | 40 | 3.97 | 659 | 26 | 30 | 17 | 0 | 0
2024-11-12 15:00 | 31.7 | 39 | 4.56 | 528 | 26 | 30 | 17 | 0 | 0
2024-11-12 16:00 | 30.8 | 44 | 4.81 | 347 | 26 | 30 | 17 | 23.2425 | 0
2024-11-12 17:00 | 29.5 | 60 | 4.63 | 145 | 26 | 30 | 17 | 25.4505 | 0
2024-11-12 18:00 | 28.6 | 62 | 3.22 | 11 | 26 | 30 | 17 | 40.6965 | 0
2024-11-12 19:00 | 28.1 | 64 | 2.47 | 0 | 26 | 30 | 17 | 37.8197 | 0
2024-11-12 20:00 | 27.4 | 66 | 1.97 | 0 | 26 | 30 | 17 | 36.4098 | 0
2024-11-12 21:00 | 26.9 | 67 | 1.28 | 0 | 26 | 30 | 17 | 31.3573 | 0
2024-11-12 22:00 | 26.6 | 67 | 0.5 | 0 | 26 | 30 | 17 | 23.5431 | 0
2024-11-12 23:00 | 26.1 | 69 | 0.51 | 0 | 26 | 30 | 17 | 24.6612 | 0
2024-11-13 | 25.4 | 72 | 0.92 | 0 | 26 | 30 | 17 | 31.2706 | 0
2024-11-13 01:00 | 24.9 | 74 | 0.98 | 0 | 26 | 30 | 17 | 33.4973 | 0
2024-11-13 02:00 | 24.3 | 76 | 1.45 | 0 | 26 | 30 | 17 | 42.2479 | 0
2024-11-13 03:00 | 23.6 | 79 | 1.9 | 0 | 26 | 30 | 17 | 50.5855 | 0
2024-11-13 04:00 | 23 | 82 | 2.29 | 0 | 26 | 30 | 17 | 57.5151 | 0
2024-11-13 05:00 | 23.2 | 80 | 2.11 | 0 | 26 | 30 | 17 | 55.4685 | 0
2024-11-13 06:00 | 22.4 | 83 | 2.52 | 0 | 26 | 30 | 17 | 64.5442 | 0
2024-11-13 07:00 | 21.9 | 85 | 2.55 | 7 | 26 | 30 | 17 | 66.2508 | 0
2024-11-13 08:00 | 23.9 | 78 | 2.11 | 128 | 26 | 30 | 17 | 34.7239 | 0
2024-11-13 09:00 | 26.9 | 66 | 2.05 | 329 | 26 | 30 | 17 | 0 | 0
2024-11-13 10:00 | 28.7 | 58 | 2.09 | 515 | 26 | 30 | 17 | 0 | 0
2024-11-13 11:00 | 30.1 | 47 | 2.4 | 651 | 26 | 30 | 17 | 0 | 0
2024-11-13 12:00 | 31.2 | 40 | 2.72 | 725 | 26 | 30 | 17 | 0 | 0
2024-11-13 13:00 | 31.7 | 39 | 3.26 | 729 | 26 | 30 | 17 | 0 | 0
2024-11-13 14:00 | 31.4 | 44 | 4.03 | 660 | 26 | 30 | 17 | 0 | 0
2024-11-13 15:00 | 30.8 | 47 | 4.6 | 527 | 26 | 30 | 17 | 0 | 0
2024-11-13 16:00 | 29.9 | 55 | 4.68 | 346 | 26 | 30 | 17 | 5.487 | 0
2024-11-13 17:00 | 28.9 | 69 | 4.22 | 146 | 26 | 30 | 17 | 11.0452 | 0
2024-11-13 18:00 | 27.7 | 78 | 2.91 | 11 | 26 | 30 | 17 | 22.3158 | 0
2024-11-13 19:00 | 27.1 | 82 | 2.68 | 0 | 26 | 30 | 17 | 23.3982 | 0
2024-11-13 20:00 | 26.4 | 85 | 2.35 | 0 | 26 | 30 | 17 | 25.0549 | 0
2024-11-13 21:00 | 25.7 | 87 | 2.04 | 0 | 26 | 30 | 17 | 27.5547 | 0
2024-11-13 22:00 | 25.3 | 87 | 1.68 | 0 | 26 | 30 | 17 | 28.5534 | 0
2024-11-13 23:00 | 24.7 | 88 | 2.1 | 0 | 26 | 30 | 17 | 35.459 | 0
2024-11-14 | 24.1 | 92 | 3.1 | 0 | 26 | 30 | 17 | 43.8552 | 0
2024-11-14 01:00 | 23.4 | 96 | 3.63 | 0 | 26 | 30 | 17 | 50.2302 | 0
2024-11-14 02:00 | 23.1 | 97 | 3.59 | 0 | 26 | 30 | 17 | 52.1649 | 0
2024-11-14 03:00 | 22.9 | 96 | 3.37 | 0 | 26 | 30 | 17 | 54.0587 | 0
2024-11-14 04:00 | 22.8 | 95 | 3.35 | 0 | 26 | 30 | 17 | 56.2734 | 0
2024-11-14 05:00 | 22.7 | 95 | 2.9 | 0 | 26 | 30 | 17 | 53.2744 | 0
2024-11-14 06:00 | 22.4 | 96 | 3.03 | 0 | 26 | 30 | 17 | 56.4295 | 0
2024-11-14 07:00 | 22.3 | 96 | 3.16 | 6 | 26 | 30 | 17 | 57.9176 | 0
2024-11-14 08:00 | 24 | 88 | 2.7 | 123 | 26 | 30 | 17 | 30.0765 | 0
2024-11-14 09:00 | 26.6 | 77 | 3.18 | 321 | 26 | 30 | 17 | 0 | 0
2024-11-14 10:00 | 28.8 | 67 | 3.43 | 504 | 26 | 30 | 17 | 0 | 0
2024-11-14 11:00 | 30.2 | 60 | 2.65 | 640 | 26 | 30 | 17 | 0 | 12.6415
2024-11-14 12:00 | 31.1 | 56 | 2.55 | 713 | 26 | 30 | 17 | 0 | 25.6797
2024-11-14 13:00 | 31.8 | 52 | 2.93 | 714 | 26 | 30 | 17 | 0 | 18.5723
2024-11-14 14:00 | 31.7 | 52 | 3.87 | 644 | 26 | 30 | 17 | 0 | 0
2024-11-14 15:00 | 31 | 54 | 4.61 | 519 | 26 | 30 | 17 | 0 | 0
2024-11-14 16:00 | 30.2 | 58 | 4.6 | 343 | 26 | 30 | 17 | 0 | 0
2024-11-14 17:00 | 29.6 | 65 | 4.54 | 145 | 26 | 30 | 17 | 12.0308 | 0
2024-11-14 18:00 | 28.3 | 69 | 3.63 | 11 | 26 | 30 | 17 | 33.9956 | 0
2024-11-14 19:00 | 27.7 | 72 | 3.26 | 0 | 26 | 30 | 17 | 34.9558 | 0
2024-11-14 20:00 | 27.3 | 75 | 2.98 | 0 | 26 | 30 | 17 | 32.8938 | 0
2024-11-14 21:00 | 26.9 | 76 | 2.99 | 0 | 26 | 30 | 17 | 35.5959 | 0
2024-11-14 22:00 | 26.4 | 78 | 2.8 | 0 | 26 | 30 | 17 | 36.6103 | 0
2024-11-14 23:00 | 25.8 | 80 | 2.52 | 0 | 26 | 30 | 17 | 37.8104 | 0
2024-11-15 | 25.4 | 81 | 2.29 | 0 | 26 | 30 | 17 | 38.4367 | 0
2024-11-15 01:00 | 25.3 | 79 | 1.57 | 0 | 26 | 30 | 17 | 34.6772 | 0
2024-11-15 02:00 | 25.2 | 78 | 0.96 | 0 | 26 | 30 | 17 | 29.2339 | 0
2024-11-15 03:00 | 24.8 | 78 | 1.95 | 0 | 26 | 30 | 17 | 43.2258 | 0
2024-11-15 04:00 | 24.4 | 82 | 2.4 | 0 | 26 | 30 | 17 | 47.0274 | 0
2024-11-15 05:00 | 24.8 | 78 | 2.91 | 0 | 26 | 30 | 17 | 53.1553 | 0
2024-11-15 06:00 | 24.5 | 79 | 2.65 | 0 | 26 | 30 | 17 | 52.0995 | 0
2024-11-15 07:00 | 24.7 | 78 | 2.17 | 6 | 26 | 30 | 17 | 45.5996 | 0
2024-11-15 08:00 | 26.8 | 71 | 1.84 | 120 | 26 | 30 | 17 | 17.9767 | 0
2024-11-15 09:00 | 29 | 58 | 2.06 | 315 | 26 | 30 | 17 | 0 | 0
2024-11-15 10:00 | 30.3 | 46 | 3.53 | 497 | 26 | 30 | 17 | 0 | 0
2024-11-15 11:00 | 30.7 | 44 | 4.09 | 635 | 26 | 30 | 17 | 0 | 0
2024-11-15 12:00 | 30.8 | 44 | 4.68 | 710 | 26 | 30 | 17 | 0 | 0
2024-11-15 13:00 | 30.7 | 45 | 5.12 | 715 | 26 | 30 | 17 | 0 | 0
2024-11-15 14:00 | 30.5 | 46 | 5.42 | 648 | 26 | 30 | 17 | 0 | 0
2024-11-15 15:00 | 30.1 | 47 | 5.2 | 518 | 26 | 30 | 17 | 4.0562 | 0
2024-11-15 16:00 | 29.4 | 49 | 4.9 | 340 | 26 | 30 | 17 | 28.6604 | 0
2024-11-15 17:00 | 28.9 | 54 | 4.36 | 142 | 26 | 30 | 17 | 44.7187 | 0
2024-11-15 18:00 | 27.8 | 59 | 3.4 | 10 | 26 | 30 | 17 | 55.5447 | 0
2024-11-15 19:00 | 27.2 | 62 | 3.18 | 0 | 26 | 30 | 17 | 55.593 | 0
2024-11-15 20:00 | 26.5 | 66 | 3.12 | 0 | 26 | 30 | 17 | 55.5484 | 0
2024-11-15 21:00 | 26 | 69 | 3.04 | 0 | 26 | 30 | 17 | 55.1419 | 0
2024-11-15 22:00 | 25.6 | 72 | 3.23 | 0 | 26 | 30 | 17 | 56.6376 | 0
2024-11-15 23:00 | 25.2 | 78 | 3.08 | 0 | 26 | 30 | 17 | 50.7957 | 0
2024-11-16 | 24.8 | 80 | 2.86 | 0 | 26 | 30 | 17 | 50.1193 | 0
2024-11-16 01:00 | 24.2 | 82 | 2.69 | 0 | 26 | 30 | 17 | 51.7179 | 0
2024-11-16 02:00 | 23.8 | 82 | 2.5 | 0 | 26 | 30 | 17 | 53.3159 | 0
2024-11-16 03:00 | 23.6 | 81 | 2 | 0 | 26 | 30 | 17 | 50.0673 | 0
2024-11-16 04:00 | 23.3 | 81 | 1.77 | 0 | 26 | 30 | 17 | 49.2505 | 0
2024-11-16 05:00 | 23.1 | 76 | 2.37 | 0 | 26 | 30 | 17 | 63.7683 | 0
2024-11-16 06:00 | 22.6 | 77 | 2.42 | 0 | 26 | 30 | 17 | 67.469 | 0
2024-11-16 07:00 | 22.3 | 78 | 2.29 | 5 | 26 | 30 | 17 | 66.1756 | 0
2024-11-16 08:00 | 24.2 | 71 | 2.15 | 121 | 26 | 30 | 17 | 40.8603 | 0
2024-11-16 09:00 | 26.5 | 60 | 2.51 | 319 | 26 | 30 | 17 | 13.8011 | 0
2024-11-16 10:00 | 28 | 49 | 3.6 | 504 | 26 | 30 | 17 | 6.8035 | 0
2024-11-16 11:00 | 28.7 | 47 | 4.55 | 641 | 26 | 30 | 17 | 0 | 0
2024-11-16 12:00 | 29.1 | 44 | 5.33 | 715 | 26 | 30 | 17 | 0 | 0
2024-11-16 13:00 | 29.3 | 43 | 5.76 | 722 | 26 | 30 | 17 | 2.4975 | 0
2024-11-16 14:00 | 29.2 | 44 | 5.95 | 656 | 26 | 30 | 17 | 11.9741 | 0
2024-11-16 15:00 | 28.9 | 45 | 5.81 | 524 | 26 | 30 | 17 | 29.3021 | 0
2024-11-16 16:00 | 28.4 | 47 | 5.61 | 343 | 26 | 30 | 17 | 52.4857 | 0
2024-11-16 17:00 | 27.6 | 49 | 4.88 | 143 | 26 | 30 | 17 | 75.5882 | 0
2024-11-16 18:00 | 26.7 | 54 | 3.89 | 10 | 26 | 30 | 17 | 80.7102 | 0
2024-11-16 19:00 | 26.2 | 56 | 3.65 | 0 | 26 | 30 | 17 | 80.3466 | 0
2024-11-16 20:00 | 25.9 | 57 | 3.69 | 0 | 26 | 30 | 17 | 82.1169 | 0
2024-11-16 21:00 | 25.5 | 57 | 3.4 | 0 | 26 | 30 | 17 | 81.7806 | 0
2024-11-16 22:00 | 24.9 | 58 | 3.37 | 0 | 26 | 30 | 17 | 85.2293 | 0
2024-11-16 23:00 | 24.5 | 60 | 3.26 | 0 | 26 | 30 | 17 | 84.2662 | 0
2024-11-17 | 24.3 | 63 | 3.32 | 0 | 26 | 30 | 17 | 82.8393 | 0
2024-11-17 01:00 | 24 | 65 | 3.12 | 0 | 26 | 30 | 17 | 79.8783 | 0
2024-11-17 02:00 | 23.8 | 67 | 2.84 | 0 | 26 | 30 | 17 | 74.9016 | 0
2024-11-17 03:00 | 23.6 | 69 | 2.78 | 0 | 26 | 30 | 17 | 73.3191 | 0
2024-11-17 04:00 | 23.5 | 71 | 2.45 | 0 | 26 | 30 | 17 | 66.9544 | 0
2024-11-17 05:00 | 21.2 | 75 | 2.7 | 0 | 26 | 30 | 17 | 85.1821 | 0
2024-11-17 06:00 | 20.8 | 77 | 3.63 | 0 | 26 | 30 | 17 | 102.4991 | 0
2024-11-17 07:00 | 20.1 | 81 | 4.41 | 5 | 26 | 30 | 17 | 116.8569 | 0
2024-11-17 08:00 | 21.7 | 76 | 4.33 | 115 | 26 | 30 | 17 | 90.0134 | 0
2024-11-17 09:00 | 24.9 | 65 | 3.92 | 306 | 26 | 30 | 17 | 40.9188 | 0
2024-11-17 10:00 | 27.7 | 57 | 3.2 | 486 | 26 | 30 | 17 | 0 | 0
2024-11-17 11:00 | 29.6 | 51 | 2.88 | 611 | 26 | 30 | 17 | 0 | 0
2024-11-17 12:00 | 30.3 | 43 | 4.83 | 666 | 26 | 30 | 17 | 0 | 0
2024-11-17 13:00 | 30.6 | 38 | 5.13 | 710 | 26 | 30 | 17 | 0 | 0
2024-11-17 14:00 | 30.5 | 34 | 4.82 | 650 | 26 | 30 | 17 | 11.4087 | 0
2024-11-17 15:00 | 30.2 | 33 | 4.61 | 525 | 26 | 30 | 17 | 30.7605 | 0
2024-11-17 16:00 | 29.5 | 33 | 4.4 | 346 | 26 | 30 | 17 | 58.1916 | 0
2024-11-17 17:00 | 29.3 | 32 | 3.42 | 144 | 26 | 30 | 17 | 73.1127 | 0
2024-11-17 18:00 | 27.4 | 38 | 2.65 | 10 | 26 | 30 | 17 | 80.7515 | 0
2024-11-17 19:00 | 26.3 | 43 | 2.13 | 0 | 26 | 30 | 17 | 72.4851 | 0
2024-11-17 20:00 | 25.7 | 46 | 1.95 | 0 | 26 | 30 | 17 | 69.1361 | 0
2024-11-17 21:00 | 25.3 | 48 | 1.77 | 0 | 26 | 30 | 17 | 65.6996 | 0
2024-11-17 22:00 | 24.8 | 50 | 1.67 | 0 | 26 | 30 | 17 | 64.5281 | 0
2024-11-17 23:00 | 24.6 | 52 | 1.08 | 0 | 26 | 30 | 17 | 50.5563 | 0
2024-11-18 | 23.1 | 56 | 2.36 | 0 | 26 | 30 | 17 | 83.704 | 0
2024-11-18 01:00 | 21 | 62 | 3.57 | 0 | 26 | 30 | 17 | 117.2986 | 0
2024-11-18 02:00 | 20 | 65 | 2.72 | 0 | 26 | 30 | 17 | 104.1246 | 0
2024-11-18 03:00 | 19.6 | 66 | 2.4 | 0 | 26 | 30 | 17 | 98.7428 | 0
2024-11-18 04:00 | 19.3 | 68 | 2.9 | 0 | 26 | 30 | 17 | 110.4493 | 0
2024-11-18 05:00 | 19.4 | 66 | 2.92 | 0 | 26 | 30 | 17 | 112.0041 | 0
2024-11-18 06:00 | 19 | 68 | 2.77 | 0 | 26 | 30 | 17 | 109.7052 | 0
2024-11-18 07:00 | 18.6 | 70 | 2.48 | 4 | 26 | 30 | 17 | 103.5264 | 0
2024-11-18 08:00 | 20.9 | 62 | 1.8 | 117 | 26 | 30 | 17 | 63.9493 | 0
2024-11-18 09:00 | 24.8 | 50 | 1.43 | 315 | 26 | 30 | 17 | 16.6772 | 0
2024-11-18 10:00 | 27.9 | 39 | 1.45 | 502 | 26 | 30 | 17 | 0 | 0
2024-11-18 11:00 | 29.4 | 32 | 0.76 | 641 | 26 | 30 | 17 | 0 | 27.7926
2024-11-18 12:00 | 30.4 | 28 | 0.22 | 717 | 26 | 30 | 17 | 0 | 46.3052
2024-11-18 13:00 | 31.2 | 25 | 0.41 | 722 | 26 | 30 | 17 | 0 | 47.7485
2024-11-18 14:00 | 31.7 | 23 | 1.23 | 655 | 26 | 30 | 17 | 0 | 11.5427
2024-11-18 15:00 | 31.5 | 27 | 2.72 | 523 | 26 | 30 | 17 | 3.5194 | 0
2024-11-18 16:00 | 30.1 | 38 | 3.77 | 340 | 26 | 30 | 17 | 33.6194 | 0
2024-11-18 17:00 | 28.8 | 39 | 3.64 | 140 | 26 | 30 | 17 | 67.9694 | 0
2024-11-18 18:00 | 27.5 | 51 | 2.69 | 10 | 26 | 30 | 17 | 62.2659 | 0
2024-11-18 19:00 | 26.7 | 57 | 2.25 | 0 | 26 | 30 | 17 | 55.5442 | 0
2024-11-18 20:00 | 25.9 | 59 | 1.73 | 0 | 26 | 30 | 17 | 50.9689 | 0
2024-11-18 21:00 | 25.2 | 59 | 2.11 | 0 | 26 | 30 | 17 | 61.7699 | 0
2024-11-18 22:00 | 24.2 | 61 | 2.05 | 0 | 26 | 30 | 17 | 65.4811 | 0
2024-11-18 23:00 | 23.3 | 65 | 2.07 | 0 | 26 | 30 | 17 | 68.0769 | 0
2024-11-19 | 22.5 | 70 | 2.42 | 0 | 26 | 30 | 17 | 75.1584 | 0
2024-11-19 01:00 | 21.7 | 75 | 2.01 | 0 | 26 | 30 | 17 | 69.1066 | 0
2024-11-19 02:00 | 21.1 | 77 | 2.07 | 0 | 26 | 30 | 17 | 72.6928 | 0
2024-11-19 03:00 | 20.7 | 75 | 2.08 | 0 | 26 | 30 | 17 | 77.2172 | 0
2024-11-19 04:00 | 20.2 | 74 | 2.28 | 0 | 26 | 30 | 17 | 85.4882 | 0
2024-11-19 05:00 | 20.8 | 69 | 2.39 | 0 | 26 | 30 | 17 | 87.8235 | 0
2024-11-19 06:00 | 20.3 | 70 | 2.33 | 0 | 26 | 30 | 17 | 89.1649 | 0
2024-11-19 07:00 | 20.2 | 70 | 2.32 | 4 | 26 | 30 | 17 | 89.0926 | 0
2024-11-19 08:00 | 22.4 | 62 | 1.96 | 112 | 26 | 30 | 17 | 59.2984 | 0
2024-11-19 09:00 | 25.2 | 53 | 1.26 | 307 | 26 | 30 | 17 | 9.6972 | 0
2024-11-19 10:00 | 28.3 | 44 | 2.42 | 490 | 26 | 30 | 17 | 0 | 0
2024-11-19 11:00 | 30.2 | 35 | 3.03 | 625 | 26 | 30 | 17 | 0 | 0
2024-11-19 12:00 | 31.2 | 31 | 2.15 | 701 | 26 | 30 | 17 | 0 | 0
2024-11-19 13:00 | 31.7 | 29 | 1.69 | 706 | 26 | 30 | 17 | 0 | 8.9841
2024-11-19 14:00 | 31.9 | 27 | 1.14 | 641 | 26 | 30 | 17 | 0 | 18.1228
2024-11-19 15:00 | 31.2 | 33 | 2.62 | 512 | 26 | 30 | 17 | 0 | 0
2024-11-19 16:00 | 29.7 | 44 | 4.55 | 333 | 26 | 30 | 17 | 34.6143 | 0
2024-11-19 17:00 | 29.1 | 44 | 4.79 | 136 | 26 | 30 | 17 | 70.3625 | 0
2024-11-19 18:00 | 27.8 | 52 | 3 | 9 | 26 | 30 | 17 | 62.6443 | 0
2024-11-19 19:00 | 26.8 | 60 | 1.64 | 0 | 26 | 30 | 17 | 42.9594 | 0
2024-11-19 20:00 | 26.2 | 62 | 1.78 | 0 | 26 | 30 | 17 | 46.8727 | 0
2024-11-19 21:00 | 25.6 | 62 | 1.79 | 0 | 26 | 30 | 17 | 50.9612 | 0
2024-11-19 22:00 | 24.6 | 64 | 2.1 | 0 | 26 | 30 | 17 | 60.6097 | 0
2024-11-19 23:00 | 23.7 | 68 | 2.78 | 0 | 26 | 30 | 17 | 73.6498 | 0
2024-11-20 | 22.7 | 71 | 2.35 | 0 | 26 | 30 | 17 | 71.4904 | 0
2024-11-20 01:00 | 22.1 | 72 | 1.99 | 0 | 26 | 30 | 17 | 68.5276 | 0
2024-11-20 02:00 | 22.1 | 70 | 1.44 | 0 | 26 | 30 | 17 | 59.3563 | 0
2024-11-20 03:00 | 21.9 | 69 | 1.15 | 0 | 26 | 30 | 17 | 54.7539 | 0
2024-11-20 04:00 | 21.3 | 70 | 1.45 | 0 | 26 | 30 | 17 | 63.9765 | 0
2024-11-20 05:00 | 21.3 | 75 | 1.33 | 0 | 26 | 30 | 17 | 58.2771 | 0
2024-11-20 06:00 | 20.9 | 75 | 1.77 | 0 | 26 | 30 | 17 | 69.6933 | 0
2024-11-20 07:00 | 20.6 | 76 | 2.32 | 4 | 26 | 30 | 17 | 81.2469 | 0
2024-11-20 08:00 | 22.6 | 67 | 1.74 | 112 | 26 | 30 | 17 | 49.5314 | 0
2024-11-20 09:00 | 25.7 | 56 | 1.24 | 309 | 26 | 30 | 17 | 4.2646 | 0
2024-11-20 10:00 | 28 | 49 | 0.85 | 495 | 26 | 30 | 17 | 0 | 10.145
2024-11-20 11:00 | 29.7 | 34 | 0.54 | 634 | 26 | 30 | 17 | 0 | 36.3115
2024-11-20 12:00 | 30.7 | 27 | 1.61 | 711 | 26 | 30 | 17 | 0 | 4.8656
2024-11-20 13:00 | 31.2 | 25 | 2.36 | 718 | 26 | 30 | 17 | 0 | 0
2024-11-20 14:00 | 30.9 | 29 | 3.63 | 652 | 26 | 30 | 17 | 1.9333 | 0
2024-11-20 15:00 | 30.2 | 30 | 4.53 | 518 | 26 | 30 | 17 | 37.7809 | 0
2024-11-20 16:00 | 29.4 | 31 | 4.24 | 339 | 26 | 30 | 17 | 61.9123 | 0
2024-11-20 17:00 | 28.8 | 40 | 3.82 | 140 | 26 | 30 | 17 | 68.705 | 0
2024-11-20 18:00 | 27.3 | 47 | 3.01 | 9 | 26 | 30 | 17 | 74.6413 | 0
2024-11-20 19:00 | 26.3 | 50 | 2.44 | 0 | 26 | 30 | 17 | 69.9569 | 0
2024-11-20 20:00 | 25.5 | 52 | 2.37 | 0 | 26 | 30 | 17 | 71.9159 | 0
2024-11-20 21:00 | 25 | 55 | 1.61 | 0 | 26 | 30 | 17 | 57.8306 | 0
2024-11-20 22:00 | 24.6 | 57 | 1.06 | 0 | 26 | 30 | 17 | 46.934 | 0
2024-11-20 23:00 | 23.8 | 61 | 1.15 | 0 | 26 | 30 | 17 | 50.2153 | 0
2024-11-21 | 22.1 | 67 | 2.6 | 0 | 26 | 30 | 17 | 84.3758 | 0
2024-11-21 01:00 | 21.1 | 70 | 2.93 | 0 | 26 | 30 | 17 | 95.228 | 0
2024-11-21 02:00 | 19.8 | 75 | 2.66 | 0 | 26 | 30 | 17 | 95.2749 | 0
2024-11-21 03:00 | 19 | 79 | 2.38 | 0 | 26 | 30 | 17 | 91.9763 | 0
2024-11-21 04:00 | 18.4 | 81 | 2.58 | 0 | 26 | 30 | 17 | 98.995 | 0
2024-11-21 05:00 | 18.6 | 78 | 2.51 | 0 | 26 | 30 | 17 | 98.4183 | 0
2024-11-21 06:00 | 18.1 | 80 | 2.57 | 0 | 26 | 30 | 17 | 101.7648 | 0
2024-11-21 07:00 | 17.8 | 81 | 2.59 | 3 | 26 | 30 | 17 | 103.2042 | 0
2024-11-21 08:00 | 19.8 | 71 | 2 | 111 | 26 | 30 | 17 | 69.4016 | 0
2024-11-21 09:00 | 24.3 | 54 | 1.68 | 308 | 26 | 30 | 17 | 22.5019 | 0
2024-11-21 10:00 | 27.4 | 43 | 1.88 | 492 | 26 | 30 | 17 | 0 | 0
2024-11-21 11:00 | 28.8 | 37 | 0.59 | 629 | 26 | 30 | 17 | 0 | 34.1644
2024-11-21 12:00 | 29.7 | 35 | 0.98 | 704 | 26 | 30 | 17 | 0 | 30.6372
2024-11-21 13:00 | 30.2 | 37 | 1.9 | 706 | 26 | 30 | 17 | 0 | 4.63
2024-11-21 14:00 | 30.1 | 42 | 3.22 | 639 | 26 | 30 | 17 | 0 | 0
2024-11-21 15:00 | 29.4 | 48 | 4.24 | 508 | 26 | 30 | 17 | 1.7839 | 0
2024-11-21 16:00 | 28.4 | 51 | 4.39 | 330 | 26 | 30 | 17 | 31.6309 | 0
2024-11-21 17:00 | 28 | 58 | 4.26 | 134 | 26 | 30 | 17 | 46.7094 | 0
2024-11-21 18:00 | 27 | 64 | 2.91 | 9 | 26 | 30 | 17 | 50.4783 | 0
2024-11-21 19:00 | 26.5 | 67 | 2.53 | 0 | 26 | 30 | 17 | 48.0863 | 0
2024-11-21 20:00 | 26 | 69 | 2.52 | 0 | 26 | 30 | 17 | 49.7028 | 0
2024-11-21 21:00 | 25.4 | 71 | 2.35 | 0 | 26 | 30 | 17 | 50.4146 | 0
2024-11-21 22:00 | 24.8 | 74 | 2.02 | 0 | 26 | 30 | 17 | 47.9792 | 0
2024-11-21 23:00 | 24.6 | 75 | 1.37 | 0 | 26 | 30 | 17 | 40.0535 | 0
2024-11-22 | 24.4 | 77 | 0.88 | 0 | 26 | 30 | 17 | 32.7969 | 0
2024-11-22 01:00 | 24.1 | 79 | 0.14 | 0 | 26 | 30 | 17 | 28.1595 | 0
2024-11-22 02:00 | 23.4 | 81 | 0.75 | 0 | 26 | 30 | 17 | 33.4622 | 0
2024-11-22 03:00 | 22.3 | 86 | 2.09 | 0 | 26 | 30 | 17 | 56.6663 | 0
2024-11-22 04:00 | 21.4 | 89 | 2.98 | 0 | 26 | 30 | 17 | 73.4705 | 0
2024-11-22 05:00 | 21.5 | 89 | 2.98 | 0 | 26 | 30 | 17 | 72.5266 | 0
2024-11-22 06:00 | 20.5 | 93 | 2.93 | 0 | 26 | 30 | 17 | 77.0721 | 0
2024-11-22 07:00 | 20.3 | 93 | 2.53 | 3 | 26 | 30 | 17 | 72.5424 | 0
2024-11-22 08:00 | 22.5 | 83 | 2.08 | 105 | 26 | 30 | 17 | 43.4734 | 0
2024-11-22 09:00 | 25.7 | 69 | 2.08 | 297 | 26 | 30 | 17 | 7.0113 | 0
2024-11-22 10:00 | 27.5 | 61 | 2.02 | 479 | 26 | 30 | 17 | 0 | 0
2024-11-22 11:00 | 28.7 | 56 | 1.49 | 618 | 26 | 30 | 17 | 0 | 17.0296
2024-11-22 12:00 | 30 | 50 | 1.92 | 693 | 26 | 30 | 17 | 0 | 18.1056
2024-11-22 13:00 | 30.8 | 45 | 3.03 | 698 | 26 | 30 | 17 | 0 | 0
2024-11-22 14:00 | 30.6 | 46 | 4.02 | 633 | 26 | 30 | 17 | 0 | 0
2024-11-22 15:00 | 30.1 | 46 | 4.25 | 506 | 26 | 30 | 17 | 0 | 0
2024-11-22 16:00 | 29.4 | 50 | 4.07 | 331 | 26 | 30 | 17 | 19.6479 | 0
2024-11-22 17:00 | 28.4 | 66 | 3.8 | 135 | 26 | 30 | 17 | 22.6969 | 0
2024-11-22 18:00 | 27.5 | 73 | 2.93 | 9 | 26 | 30 | 17 | 32.3752 | 0
2024-11-22 19:00 | 26.9 | 78 | 2.94 | 0 | 26 | 30 | 17 | 32.3568 | 0
2024-11-22 20:00 | 26.1 | 83 | 2.41 | 0 | 26 | 30 | 17 | 30.6129 | 0
2024-11-22 21:00 | 25.2 | 87 | 1.73 | 0 | 26 | 30 | 17 | 29.6666 | 0
2024-11-22 22:00 | 24.9 | 88 | 1.23 | 0 | 26 | 30 | 17 | 27.1493 | 0
2024-11-22 23:00 | 24.3 | 90 | 1.64 | 0 | 26 | 30 | 17 | 33.1214 | 0
2024-11-23 | 23.5 | 93 | 2.8 | 0 | 26 | 30 | 17 | 46.6322 | 0
2024-11-23 01:00 | 22.4 | 98 | 2.94 | 0 | 26 | 30 | 17 | 53.3207 | 0
2024-11-23 02:00 | 21.7 | 99 | 2.63 | 0 | 26 | 30 | 17 | 56.1093 | 0
2024-11-23 03:00 | 21.3 | 98 | 2.4 | 0 | 26 | 30 | 17 | 58.0946 | 0
2024-11-23 04:00 | 20.8 | 99 | 2.47 | 0 | 26 | 30 | 17 | 62.4363 | 0
2024-11-23 05:00 | 20.9 | 100 | 2.58 | 0 | 26 | 30 | 17 | 61.992 | 0
2024-11-23 06:00 | 20.7 | 100 | 2.74 | 0 | 26 | 30 | 17 | 65.8063 | 0
2024-11-23 07:00 | 20.5 | 100 | 2.62 | 2 | 26 | 30 | 17 | 65.8604 | 0
2024-11-23 08:00 | 21 | 99 | 2.67 | 71 | 26 | 30 | 17 | 53.5267 | 0
2024-11-23 09:00 | 22 | 97 | 2.55 | 205 | 26 | 30 | 17 | 26.7741 | 0
2024-11-23 10:00 | 25.4 | 81 | 2.4 | 387 | 26 | 30 | 17 | 0 | 0
2024-11-23 11:00 | 28.6 | 64 | 2.07 | 607 | 26 | 30 | 17 | 0 | 10.9188
2024-11-23 12:00 | 30 | 59 | 1.98 | 686 | 26 | 30 | 17 | 0 | 27.7705
2024-11-23 13:00 | 31 | 52 | 3.02 | 690 | 26 | 30 | 17 | 0 | 6.1799
2024-11-23 14:00 | 31.1 | 49 | 3.96 | 621 | 26 | 30 | 17 | 0 | 0
2024-11-23 15:00 | 30.6 | 49 | 4.36 | 494 | 26 | 30 | 17 | 0 | 0
2024-11-23 16:00 | 29.8 | 51 | 4.38 | 317 | 26 | 30 | 17 | 17.7658 | 0
2024-11-23 17:00 | 29.1 | 56 | 4.11 | 127 | 26 | 30 | 17 | 38.081 | 0
2024-11-23 18:00 | 27.8 | 61 | 2.87 | 9 | 26 | 30 | 17 | 47.2625 | 0
2024-11-23 19:00 | 26.8 | 65 | 2.75 | 0 | 26 | 30 | 17 | 50.4392 | 0
2024-11-23 20:00 | 25.8 | 69 | 2.45 | 0 | 26 | 30 | 17 | 50.6168 | 0
2024-11-23 21:00 | 25.1 | 75 | 2.41 | 0 | 26 | 30 | 17 | 48.979 | 0
2024-11-23 22:00 | 24.9 | 78 | 2.35 | 0 | 26 | 30 | 17 | 46.6518 | 0
2024-11-23 23:00 | 24.6 | 77 | 2.22 | 0 | 26 | 30 | 17 | 48.818 | 0
2024-11-24 | 23.9 | 80 | 2.22 | 0 | 26 | 30 | 17 | 51.3682 | 0
2024-11-24 01:00 | 23.5 | 81 | 2.55 | 0 | 26 | 30 | 17 | 57.596 | 0
2024-11-24 02:00 | 22.7 | 86 | 2.93 | 0 | 26 | 30 | 17 | 63.8149 | 0
2024-11-24 03:00 | 22.3 | 88 | 2.82 | 0 | 26 | 30 | 17 | 64.0589 | 0
2024-11-24 04:00 | 21.9 | 89 | 3.05 | 0 | 26 | 30 | 17 | 69.5885 | 0
2024-11-24 05:00 | 21.4 | 87 | 3.3 | 0 | 26 | 30 | 17 | 80.0147 | 0
2024-11-24 06:00 | 21.1 | 89 | 3.29 | 0 | 26 | 30 | 17 | 80.5849 | 0
2024-11-24 07:00 | 20.7 | 91 | 3.4 | 2 | 26 | 30 | 17 | 83.6009 | 0
2024-11-24 08:00 | 22.5 | 81 | 3.36 | 98 | 26 | 30 | 17 | 63.809 | 0
2024-11-24 09:00 | 25.4 | 68 | 3.15 | 285 | 26 | 30 | 17 | 24.9874 | 0
2024-11-24 10:00 | 27.8 | 60 | 3.28 | 464 | 26 | 30 | 17 | 0 | 0
2024-11-24 11:00 | 29.2 | 57 | 2.67 | 599 | 26 | 30 | 17 | 0 | 0
2024-11-24 12:00 | 30.1 | 54 | 3.27 | 672 | 26 | 30 | 17 | 0 | 0
2024-11-24 13:00 | 30.1 | 53 | 4.25 | 677 | 26 | 30 | 17 | 0 | 0
2024-11-24 14:00 | 29.9 | 51 | 4.25 | 617 | 26 | 30 | 17 | 0 | 0
2024-11-24 15:00 | 29.5 | 53 | 4.01 | 495 | 26 | 30 | 17 | 0 | 0
2024-11-24 16:00 | 28.8 | 57 | 3.96 | 322 | 26 | 30 | 17 | 11.8016 | 0
2024-11-24 17:00 | 28.3 | 56 | 4.27 | 131 | 26 | 30 | 17 | 47.9194 | 0
2024-11-24 18:00 | 27.3 | 59 | 3.05 | 8 | 26 | 30 | 17 | 56.8812 | 0
2024-11-24 19:00 | 26.6 | 61 | 2.67 | 0 | 26 | 30 | 17 | 56.7484 | 0
2024-11-24 20:00 | 25.8 | 65 | 2.23 | 0 | 26 | 30 | 17 | 52.642 | 0
2024-11-24 21:00 | 25.2 | 70 | 1.66 | 0 | 26 | 30 | 17 | 44.3006 | 0
2024-11-24 22:00 | 24.7 | 75 | 1.57 | 0 | 26 | 30 | 17 | 42.0955 | 0
2024-11-24 23:00 | 23.8 | 79 | 2.55 | 0 | 26 | 30 | 17 | 57.1852 | 0
2024-11-25 | 22.6 | 82 | 2.67 | 0 | 26 | 30 | 17 | 65.8817 | 0
2024-11-25 01:00 | 21.8 | 84 | 2.57 | 0 | 26 | 30 | 17 | 69.3113 | 0
2024-11-25 02:00 | 21.1 | 88 | 2.58 | 0 | 26 | 30 | 17 | 71.5154 | 0
2024-11-25 03:00 | 20.5 | 90 | 2.57 | 0 | 26 | 30 | 17 | 74.5741 | 0
2024-11-25 04:00 | 20 | 91 | 2.57 | 0 | 26 | 30 | 17 | 77.8575 | 0
2024-11-25 05:00 | 20 | 89 | 2.4 | 0 | 26 | 30 | 17 | 76.7587 | 0
2024-11-25 06:00 | 19.6 | 91 | 2.37 | 0 | 26 | 30 | 17 | 77.7297 | 0
2024-11-25 07:00 | 19.2 | 93 | 2.24 | 2 | 26 | 30 | 17 | 76.673 | 0
2024-11-25 08:00 | 21.1 | 84 | 1.59 | 97 | 26 | 30 | 17 | 45.6465 | 0
2024-11-25 09:00 | 25 | 66 | 1.46 | 285 | 26 | 30 | 17 | 7.5099 | 0
2024-11-25 10:00 | 27.7 | 56 | 2.67 | 466 | 26 | 30 | 17 | 0 | 0
2024-11-25 11:00 | 29.5 | 46 | 2.22 | 603 | 26 | 30 | 17 | 0 | 0
2024-11-25 12:00 | 30.8 | 37 | 1.23 | 678 | 26 | 30 | 17 | 0 | 24.9999
2024-11-25 13:00 | 31.7 | 33 | 1.76 | 684 | 26 | 30 | 17 | 0 | 9.1644
2024-11-25 14:00 | 31.6 | 38 | 3.41 | 621 | 26 | 30 | 17 | 0 | 0
2024-11-25 15:00 | 30.6 | 50 | 4.52 | 494 | 26 | 30 | 17 | 0 | 0
2024-11-25 16:00 | 29.2 | 54 | 5.32 | 320 | 26 | 30 | 17 | 25.0219 | 0
2024-11-25 17:00 | 28.5 | 61 | 4.09 | 129 | 26 | 30 | 17 | 34.1543 | 0
2024-11-25 18:00 | 27.8 | 66 | 3.05 | 8 | 26 | 30 | 17 | 41.1819 | 0
2024-11-25 19:00 | 27.3 | 68 | 2.92 | 0 | 26 | 30 | 17 | 43.0359 | 0
2024-11-25 20:00 | 26.7 | 67 | 2.81 | 0 | 26 | 30 | 17 | 49.1427 | 0
2024-11-25 21:00 | 26.3 | 66 | 2.88 | 0 | 26 | 30 | 17 | 54.908 | 0
2024-11-25 22:00 | 25.8 | 71 | 3 | 0 | 26 | 30 | 17 | 53.8295 | 0
2024-11-25 23:00 | 25.1 | 75 | 3.46 | 0 | 26 | 30 | 17 | 59.6269 | 0
2024-11-26 | 24.6 | 74 | 3.57 | 0 | 26 | 30 | 17 | 67.4969 | 0
2024-11-26 01:00 | 24.1 | 72 | 3.43 | 0 | 26 | 30 | 17 | 73.8265 | 0
2024-11-26 02:00 | 23.5 | 72 | 3.2 | 0 | 26 | 30 | 17 | 76.5785 | 0
2024-11-26 03:00 | 22.6 | 74 | 2.67 | 0 | 26 | 30 | 17 | 74.3774 | 0
2024-11-26 04:00 | 22 | 73 | 1.88 | 0 | 26 | 30 | 17 | 66.3434 | 0
2024-11-26 05:00 | 21.4 | 74 | 1.87 | 0 | 26 | 30 | 17 | 69.2626 | 0
2024-11-26 06:00 | 20.8 | 77 | 2.33 | 0 | 26 | 30 | 17 | 79.6669 | 0
2024-11-26 07:00 | 20.6 | 77 | 2.8 | 2 | 26 | 30 | 17 | 89.5723 | 0
2024-11-26 08:00 | 22.8 | 61 | 2.44 | 94 | 26 | 30 | 17 | 69.6282 | 0
2024-11-26 09:00 | 26.1 | 49 | 2.16 | 280 | 26 | 30 | 17 | 29.7393 | 0
2024-11-26 10:00 | 27.9 | 46 | 2.27 | 460 | 26 | 30 | 17 | 0 | 0
2024-11-26 11:00 | 29.8 | 42 | 2.52 | 595 | 26 | 30 | 17 | 0 | 0
2024-11-26 12:00 | 31.3 | 37 | 2.9 | 671 | 26 | 30 | 17 | 0 | 0
2024-11-26 13:00 | 32.1 | 34 | 3.08 | 679 | 26 | 30 | 17 | 0 | 0
2024-11-26 14:00 | 32.2 | 34 | 3.41 | 618 | 26 | 30 | 17 | 0 | 0
2024-11-26 15:00 | 31.3 | 39 | 4.12 | 493 | 26 | 30 | 17 | 3.8392 | 0
2024-11-26 16:00 | 30.2 | 42 | 4.21 | 321 | 26 | 30 | 17 | 31.9158 | 0
2024-11-26 17:00 | 29 | 46 | 3.52 | 131 | 26 | 30 | 17 | 52.5178 | 0
2024-11-26 18:00 | 27.5 | 58 | 2.32 | 8 | 26 | 30 | 17 | 48.1379 | 0
2024-11-26 19:00 | 26.5 | 64 | 1.9 | 0 | 26 | 30 | 17 | 44.3846 | 0
2024-11-26 20:00 | 25.7 | 69 | 1.57 | 0 | 26 | 30 | 17 | 40.7218 | 0
2024-11-26 21:00 | 24.9 | 70 | 1.66 | 0 | 26 | 30 | 17 | 46.2728 | 0
2024-11-26 22:00 | 23.9 | 69 | 2.53 | 0 | 26 | 30 | 17 | 67.1459 | 0
2024-11-26 23:00 | 23 | 67 | 2.64 | 0 | 26 | 30 | 17 | 78.1798 | 0
2024-11-27 | 22.4 | 68 | 2.52 | 0 | 26 | 30 | 17 | 79.6571 | 0
2024-11-27 01:00 | 21.7 | 70 | 2.46 | 0 | 26 | 30 | 17 | 81.8199 | 0
2024-11-27 02:00 | 21 | 74 | 2.06 | 0 | 26 | 30 | 17 | 75.6032 | 0
2024-11-27 03:00 | 20.2 | 82 | 1.97 | 0 | 26 | 30 | 17 | 73.0687 | 0
2024-11-27 04:00 | 19.5 | 92 | 2.28 | 0 | 26 | 30 | 17 | 76.1406 | 0
2024-11-27 05:00 | 19.4 | 94 | 1.9 | 0 | 26 | 30 | 17 | 68.6912 | 0
2024-11-27 06:00 | 19 | 95 | 1.68 | 0 | 26 | 30 | 17 | 66.6653 | 0
2024-11-27 07:00 | 19.1 | 94 | 1.46 | 2 | 26 | 30 | 17 | 62.1079 | 0
2024-11-27 08:00 | 21.1 | 85 | 1.28 | 94 | 26 | 30 | 17 | 39.7932 | 0
2024-11-27 09:00 | 24.6 | 67 | 1.16 | 282 | 26 | 30 | 17 | 4.3758 | 0
2024-11-27 10:00 | 27.7 | 51 | 1.09 | 463 | 26 | 30 | 17 | 0 | 0
2024-11-27 11:00 | 29.6 | 42 | 0.9 | 600 | 26 | 30 | 17 | 0 | 24.5766
2024-11-27 12:00 | 31.2 | 34 | 1.5 | 676 | 26 | 30 | 17 | 0 | 14.7182
2024-11-27 13:00 | 32.2 | 30 | 2.28 | 684 | 26 | 30 | 17 | 0 | 0
2024-11-27 14:00 | 32.4 | 30 | 3.15 | 623 | 26 | 30 | 17 | 0 | 0
2024-11-27 15:00 | 31.9 | 32 | 3.82 | 498 | 26 | 30 | 17 | 10.6618 | 0
2024-11-27 16:00 | 31 | 35 | 3.74 | 324 | 26 | 30 | 17 | 33.9828 | 0
2024-11-27 17:00 | 29.8 | 39 | 3.47 | 132 | 26 | 30 | 17 | 58.1421 | 0
2024-11-27 18:00 | 27.7 | 53 | 2.27 | 8 | 26 | 30 | 17 | 52.423 | 0
2024-11-27 19:00 | 26.5 | 65 | 1.8 | 0 | 26 | 30 | 17 | 42.0978 | 0
2024-11-27 20:00 | 25.8 | 74 | 1.84 | 0 | 26 | 30 | 17 | 38.5049 | 0
2024-11-27 21:00 | 25.3 | 80 | 1.81 | 0 | 26 | 30 | 17 | 36.101 | 0
2024-11-27 22:00 | 24.9 | 85 | 1.65 | 0 | 26 | 30 | 17 | 33.0694 | 0
2024-11-27 23:00 | 24.4 | 88 | 1.39 | 0 | 26 | 30 | 17 | 31.8057 | 0
2024-11-28 | 23.8 | 90 | 1.66 | 0 | 26 | 30 | 17 | 36.9723 | 0
2024-11-28 01:00 | 23.1 | 92 | 2.3 | 0 | 26 | 30 | 17 | 46.9729 | 0
2024-11-28 02:00 | 22.6 | 93 | 2.72 | 0 | 26 | 30 | 17 | 54.7115 | 0
2024-11-28 03:00 | 21.9 | 95 | 2.95 | 0 | 26 | 30 | 17 | 61.7956 | 0
2024-11-28 04:00 | 21 | 98 | 2.85 | 0 | 26 | 30 | 17 | 66.28 | 0
2024-11-28 05:00 | 20.7 | 96 | 2.28 | 0 | 26 | 30 | 17 | 63.37 | 0
2024-11-28 06:00 | 20.2 | 96 | 2.15 | 0 | 26 | 30 | 17 | 65.4637 | 0
2024-11-28 07:00 | 19.9 | 97 | 2.2 | 1 | 26 | 30 | 17 | 67.6547 | 0
2024-11-28 08:00 | 21.7 | 88 | 1.66 | 90 | 26 | 30 | 17 | 41.0666 | 0
2024-11-28 09:00 | 25.4 | 71 | 1.32 | 274 | 26 | 30 | 17 | 0.6081 | 0
2024-11-28 10:00 | 28 | 61 | 1.42 | 453 | 26 | 30 | 17 | 0 | 0
2024-11-28 11:00 | 29.5 | 56 | 3.94 | 585 | 26 | 30 | 17 | 0 | 0
2024-11-28 12:00 | 29.6 | 56 | 5.39 | 600 | 26 | 30 | 17 | 0 | 0
2024-11-28 13:00 | 29.4 | 59 | 5.22 | 549 | 26 | 30 | 17 | 0 | 0
2024-11-28 14:00 | 29.2 | 56 | 5.4 | 478 | 26 | 30 | 17 | 0 | 0
2024-11-28 15:00 | 28.7 | 63 | 5.53 | 454 | 26 | 30 | 17 | 0 | 0
2024-11-28 16:00 | 28.1 | 65 | 5.42 | 303 | 26 | 30 | 17 | 15.7993 | 0
2024-11-28 17:00 | 27.5 | 65 | 4.72 | 121 | 26 | 30 | 17 | 43.7766 | 0
2024-11-28 18:00 | 26.8 | 71 | 4.58 | 8 | 26 | 30 | 17 | 54.7185 | 0
2024-11-28 19:00 | 26.6 | 72 | 3.67 | 0 | 26 | 30 | 17 | 49.806 | 0
2024-11-28 20:00 | 26.9 | 70 | 4.56 | 0 | 26 | 30 | 17 | 56.3614 | 0
2024-11-28 21:00 | 26.1 | 73 | 5.17 | 0 | 26 | 30 | 17 | 65.3762 | 0
2024-11-28 22:00 | 25.4 | 78 | 6 | 0 | 26 | 30 | 17 | 70.9659 | 0
2024-11-28 23:00 | 25.3 | 75 | 4.88 | 0 | 26 | 30 | 17 | 70.0095 | 0
2024-11-29 | 25.5 | 72 | 5.01 | 0 | 26 | 30 | 17 | 74.2727 | 0
2024-11-29 01:00 | 25.3 | 71 | 5.08 | 0 | 26 | 30 | 17 | 79.5178 | 0
2024-11-29 02:00 | 25.2 | 67 | 4.71 | 0 | 26 | 30 | 17 | 84.6486 | 0
2024-11-29 03:00 | 24.6 | 71 | 4.99 | 0 | 26 | 30 | 17 | 87.689 | 0
2024-11-29 04:00 | 24.3 | 69 | 4.43 | 0 | 26 | 30 | 17 | 88.5025 | 0
2024-11-29 05:00 | 25.3 | 63 | 4.6 | 0 | 26 | 30 | 17 | 89.5705 | 0
2024-11-29 06:00 | 24.6 | 65 | 3.71 | 0 | 26 | 30 | 17 | 82.5754 | 0
2024-11-29 07:00 | 24.4 | 64 | 3.48 | 1 | 26 | 30 | 17 | 82.6958 | 0
2024-11-29 08:00 | 25.6 | 57 | 4.48 | 84 | 26 | 30 | 17 | 84.3555 | 0
2024-11-29 09:00 | 26.4 | 51 | 5.81 | 266 | 26 | 30 | 17 | 80.0898 | 0
2024-11-29 10:00 | 26.8 | 50 | 6.06 | 446 | 26 | 30 | 17 | 56.2769 | 0
2024-11-29 11:00 | 27.1 | 48 | 6.39 | 583 | 26 | 30 | 17 | 42.9498 | 0
2024-11-29 12:00 | 27.1 | 48 | 6.78 | 660 | 26 | 30 | 17 | 37.2553 | 0
2024-11-29 13:00 | 27 | 49 | 7.12 | 673 | 26 | 30 | 17 | 38.1757 | 0
2024-11-29 14:00 | 26.6 | 51 | 7.32 | 615 | 26 | 30 | 17 | 48.5496 | 0
2024-11-29 15:00 | 26.1 | 54 | 7.2 | 491 | 26 | 30 | 17 | 63.1334 | 0
2024-11-29 16:00 | 25.3 | 58 | 7.02 | 319 | 26 | 30 | 17 | 85.747 | 0
2024-11-29 17:00 | 25 | 59 | 6.44 | 127 | 26 | 30 | 17 | 106.5905 | 0
2024-11-29 18:00 | 24.4 | 62 | 5.66 | 8 | 26 | 30 | 17 | 114.398 | 0
2024-11-29 19:00 | 24 | 64 | 5.29 | 0 | 26 | 30 | 17 | 111.7724 | 0
2024-11-29 20:00 | 23.7 | 65 | 4.94 | 0 | 26 | 30 | 17 | 108.844 | 0
2024-11-29 21:00 | 23.3 | 67 | 4.89 | 0 | 26 | 30 | 17 | 109.3708 | 0
2024-11-29 22:00 | 23 | 68 | 4.99 | 0 | 26 | 30 | 17 | 112.58 | 0
2024-11-29 23:00 | 22.8 | 68 | 4.85 | 0 | 26 | 30 | 17 | 112.9155 | 0
2024-11-30 | 22.6 | 70 | 4.86 | 0 | 26 | 30 | 17 | 112.1186 | 0
2024-11-30 01:00 | 22.4 | 70 | 4.59 | 0 | 26 | 30 | 17 | 110.4723 | 0
2024-11-30 02:00 | 22.2 | 71 | 4.37 | 0 | 26 | 30 | 17 | 107.8817 | 0
2024-11-30 03:00 | 22.2 | 71 | 4.35 | 0 | 26 | 30 | 17 | 107.5806 | 0
2024-11-30 04:00 | 22.3 | 70 | 4.44 | 0 | 26 | 30 | 17 | 109.3314 | 0
2024-11-30 05:00 | 22.2 | 67 | 4.33 | 0 | 26 | 30 | 17 | 113.0947 | 0
2024-11-30 06:00 | 21.8 | 68 | 3.84 | 0 | 26 | 30 | 17 | 107.6285 | 0
2024-11-30 07:00 | 21.3 | 68 | 3.24 | 1 | 26 | 30 | 17 | 101.3801 | 0
2024-11-30 08:00 | 23.1 | 61 | 3.04 | 89 | 26 | 30 | 17 | 79.1147 | 0
2024-11-30 09:00 | 25 | 52 | 4.75 | 275 | 26 | 30 | 17 | 77.9198 | 0
2024-11-30 10:00 | 25.8 | 47 | 5.94 | 456 | 26 | 30 | 17 | 72.5014 | 0
2024-11-30 11:00 | 26.4 | 45 | 6.54 | 595 | 26 | 30 | 17 | 59.7366 | 0
2024-11-30 12:00 | 26.7 | 44 | 7.08 | 673 | 26 | 30 | 17 | 55.3162 | 0
2024-11-30 13:00 | 26.7 | 43 | 7.47 | 682 | 26 | 30 | 17 | 62.0639 | 0
2024-11-30 14:00 | 26.6 | 43 | 7.69 | 622 | 26 | 30 | 17 | 74.4699 | 0
2024-11-30 15:00 | 26.1 | 46 | 7.9 | 496 | 26 | 30 | 17 | 92.7971 | 0
2024-11-30 16:00 | 25.5 | 48 | 7.88 | 321 | 26 | 30 | 17 | 119.2038 | 0
2024-11-30 17:00 | 24.9 | 53 | 7.42 | 129 | 26 | 30 | 17 | 134.5349 | 0
2024-11-30 18:00 | 24.4 | 56 | 6.71 | 8 | 26 | 30 | 17 | 141.0878 | 0
2024-11-30 19:00 | 24.1 | 58 | 6.39 | 0 | 26 | 30 | 17 | 137.3647 | 0
2024-11-30 20:00 | 23.8 | 58 | 6.26 | 0 | 26 | 30 | 17 | 139.4323 | 0
2024-11-30 21:00 | 23.6 | 59 | 5.99 | 0 | 26 | 30 | 17 | 136.0464 | 0
2024-11-30 22:00 | 23.4 | 62 | 6 | 0 | 26 | 30 | 17 | 132.79 | 0
2024-11-30 23:00 | 23.2 | 63 | 5.86 | 0 | 26 | 30 | 17 | 131.4081 | 0
2024-12-01 | 23.1 | 60 | 5.75 | 0 | 26 | 30 | 12 | 137.6306 | 0
2024-12-01 01:00 | 23 | 57 | 5.74 | 0 | 26 | 30 | 12 | 144.3122 | 0
2024-12-01 02:00 | 22.8 | 56 | 5.73 | 0 | 26 | 30 | 12 | 148.3386 | 0
2024-12-01 03:00 | 22.7 | 56 | 5.7 | 0 | 26 | 30 | 12 | 148.9881 | 0
2024-12-01 04:00 | 22.5 | 56 | 5.56 | 0 | 26 | 30 | 12 | 148.8809 | 0
2024-12-01 05:00 | 22.4 | 57 | 5.4 | 0 | 26 | 30 | 12 | 145.4914 | 0
2024-12-01 06:00 | 22.2 | 61 | 5.18 | 0 | 26 | 30 | 12 | 137.1847 | 0
2024-12-01 07:00 | 22 | 61 | 4.83 | 1 | 26 | 30 | 12 | 133.2436 | 0
2024-12-01 08:00 | 23.2 | 55 | 4.87 | 85 | 26 | 30 | 12 | 119.7989 | 0
2024-12-01 09:00 | 24.4 | 49 | 5.55 | 271 | 26 | 30 | 12 | 104.1774 | 0
2024-12-01 10:00 | 25.1 | 47 | 5.86 | 448 | 26 | 30 | 12 | 81.5147 | 0
2024-12-01 11:00 | 25.5 | 46 | 6.21 | 581 | 26 | 30 | 12 | 66.5 | 0
2024-12-01 12:00 | 25.7 | 46 | 6.48 | 662 | 26 | 30 | 12 | 57.1596 | 0
2024-12-01 13:00 | 25.9 | 45 | 6.84 | 646 | 26 | 30 | 12 | 64.5082 | 0
2024-12-01 14:00 | 25.7 | 45 | 7.04 | 591 | 26 | 30 | 12 | 77.3829 | 0
2024-12-01 15:00 | 25.3 | 47 | 7.01 | 477 | 26 | 30 | 12 | 92.4886 | 0
2024-12-01 16:00 | 24.6 | 48 | 6.47 | 301 | 26 | 30 | 12 | 114.5598 | 0
2024-12-01 17:00 | 23.8 | 51 | 6.01 | 129 | 26 | 30 | 12 | 133.6027 | 0
2024-12-01 18:00 | 23.1 | 53 | 5.13 | 8 | 26 | 30 | 12 | 139.149 | 0
2024-12-01 19:00 | 22.8 | 54 | 4.9 | 0 | 26 | 30 | 12 | 137.5861 | 0
2024-12-01 20:00 | 22.5 | 56 | 4.38 | 0 | 26 | 30 | 12 | 128.0181 | 0
2024-12-01 21:00 | 22.1 | 58 | 3.99 | 0 | 26 | 30 | 12 | 121.641 | 0
2024-12-01 22:00 | 21.7 | 60 | 3.77 | 0 | 26 | 30 | 12 | 118.374 | 0
2024-12-01 23:00 | 21.5 | 62 | 3.78 | 0 | 26 | 30 | 12 | 117.772 | 0
2024-12-02 | 21.4 | 62 | 3.7 | 0 | 26 | 30 | 12 | 117.1275 | 0
2024-12-02 01:00 | 21.3 | 63 | 3.69 | 0 | 26 | 30 | 12 | 116.57 | 0
2024-12-02 02:00 | 21 | 64 | 3.31 | 0 | 26 | 30 | 12 | 110.5116 | 0
2024-12-02 03:00 | 20.5 | 66 | 2.8 | 0 | 26 | 30 | 12 | 101.8705 | 0
2024-12-02 04:00 | 20.3 | 66 | 2.66 | 0 | 26 | 30 | 12 | 100.3365 | 0
2024-12-02 05:00 | 20.3 | 61 | 1.65 | 0 | 26 | 30 | 12 | 80.4454 | 0
2024-12-02 06:00 | 19.7 | 63 | 2.44 | 0 | 26 | 30 | 12 | 102.0955 | 0
2024-12-02 07:00 | 19.5 | 65 | 2.85 | 1 | 26 | 30 | 12 | 111.1334 | 0
2024-12-02 08:00 | 21 | 59 | 3.01 | 63 | 26 | 30 | 12 | 101.231 | 0
2024-12-02 09:00 | 23.5 | 50 | 2.9 | 221 | 26 | 30 | 12 | 69.3653 | 0
2024-12-02 10:00 | 25.1 | 41 | 3.15 | 406 | 26 | 30 | 12 | 49.6497 | 0
2024-12-02 11:00 | 25.8 | 39 | 2.91 | 571 | 26 | 30 | 12 | 20.2912 | 0
2024-12-02 12:00 | 26 | 38 | 2.32 | 647 | 26 | 30 | 12 | 0 | 0
2024-12-02 13:00 | 26.3 | 36 | 1.92 | 663 | 26 | 30 | 12 | 0 | 0
2024-12-02 14:00 | 26.6 | 34 | 1.9 | 622 | 26 | 30 | 12 | 0 | 0
2024-12-02 15:00 | 26.4 | 34 | 2.59 | 492 | 26 | 30 | 12 | 26.9211 | 0
2024-12-02 16:00 | 25.7 | 38 | 3.49 | 325 | 26 | 30 | 12 | 67.5125 | 0
2024-12-02 17:00 | 25 | 43 | 3.18 | 132 | 26 | 30 | 12 | 85.1808 | 0
2024-12-02 18:00 | 23.9 | 48 | 2.06 | 8 | 26 | 30 | 12 | 79.5572 | 0
2024-12-02 19:00 | 23 | 52 | 1.84 | 0 | 26 | 30 | 12 | 77.123 | 0
2024-12-02 20:00 | 22.5 | 55 | 1.46 | 0 | 26 | 30 | 12 | 68.2887 | 0
2024-12-02 21:00 | 22.1 | 57 | 0.5 | 0 | 26 | 30 | 12 | 44.7192 | 0
2024-12-02 22:00 | 20.9 | 60 | 2.85 | 0 | 26 | 30 | 12 | 105.9545 | 0
2024-12-02 23:00 | 19.7 | 63 | 2.76 | 0 | 26 | 30 | 12 | 109.6163 | 0
2024-12-03 | 19 | 66 | 1.95 | 0 | 26 | 30 | 12 | 92.0121 | 0
2024-12-03 01:00 | 18.2 | 71 | 2.53 | 0 | 26 | 30 | 12 | 107.7645 | 0
2024-12-03 02:00 | 17.3 | 76 | 2.62 | 0 | 26 | 30 | 12 | 112.281 | 0
2024-12-03 03:00 | 16.6 | 79 | 2.58 | 0 | 26 | 30 | 12 | 113.9418 | 0
2024-12-03 04:00 | 15.8 | 83 | 2.51 | 0 | 26 | 30 | 12 | 114.8832 | 0
2024-12-03 05:00 | 15.8 | 75 | 1.88 | 0 | 26 | 30 | 12 | 102.6486 | 0
2024-12-03 06:00 | 15.6 | 73 | 2.16 | 0 | 26 | 30 | 12 | 112.9982 | 0
2024-12-03 07:00 | 15.3 | 72 | 2.12 | 1 | 26 | 30 | 12 | 114.0111 | 0
2024-12-03 08:00 | 17.3 | 62 | 1.55 | 82 | 26 | 30 | 12 | 81.0314 | 0
2024-12-03 09:00 | 20.8 | 48 | 1.13 | 268 | 26 | 30 | 12 | 34.73 | 0
2024-12-03 10:00 | 23.8 | 39 | 1.02 | 452 | 26 | 30 | 12 | 0 | 0
2024-12-03 11:00 | 25.9 | 34 | 2.42 | 593 | 26 | 30 | 12 | 12.3614 | 0
2024-12-03 12:00 | 26.7 | 32 | 2.21 | 673 | 26 | 30 | 12 | 0 | 0
2024-12-03 13:00 | 27.1 | 31 | 1.88 | 684 | 26 | 30 | 12 | 0 | 0
2024-12-03 14:00 | 27.2 | 32 | 2.62 | 623 | 26 | 30 | 12 | 7.7214 | 0
2024-12-03 15:00 | 26.8 | 36 | 4.14 | 498 | 26 | 30 | 12 | 51.3284 | 0
2024-12-03 16:00 | 25.9 | 40 | 5.17 | 323 | 26 | 30 | 12 | 93.4356 | 0
2024-12-03 17:00 | 24.8 | 34 | 4.4 | 135 | 26 | 30 | 12 | 125.4273 | 0
2024-12-03 18:00 | 23.6 | 42 | 3.68 | 9 | 26 | 30 | 12 | 124.0681 | 0
2024-12-03 19:00 | 22.9 | 45 | 3.3 | 0 | 26 | 30 | 12 | 118.2472 | 0
2024-12-03 20:00 | 21.9 | 48 | 2.62 | 0 | 26 | 30 | 12 | 106.012 | 0
2024-12-03 21:00 | 21 | 50 | 2.16 | 0 | 26 | 30 | 12 | 98.0811 | 0
2024-12-03 22:00 | 20 | 53 | 2.8 | 0 | 26 | 30 | 12 | 117.8411 | 0
2024-12-03 23:00 | 18.8 | 55 | 2.71 | 0 | 26 | 30 | 12 | 121.4914 | 0
2024-12-04 | 18 | 57 | 1.98 | 0 | 26 | 30 | 12 | 104.4258 | 0
2024-12-04 01:00 | 17.6 | 57 | 2.05 | 0 | 26 | 30 | 12 | 108.612 | 0
2024-12-04 02:00 | 16.6 | 59 | 2.52 | 0 | 26 | 30 | 12 | 126.6126 | 0
2024-12-04 03:00 | 15.8 | 61 | 2.55 | 0 | 26 | 30 | 12 | 130.8369 | 0
2024-12-04 04:00 | 15.2 | 64 | 2.27 | 0 | 26 | 30 | 12 | 123.9375 | 0
2024-12-04 05:00 | 15.6 | 62 | 2.69 | 0 | 26 | 30 | 12 | 135.4696 | 0
2024-12-04 06:00 | 15.1 | 69 | 2.68 | 0 | 26 | 30 | 12 | 133.5 | 0
2024-12-04 07:00 | 14.7 | 75 | 2.77 | 1 | 26 | 30 | 12 | 134.4782 | 0
2024-12-04 08:00 | 16.6 | 73 | 2.42 | 82 | 26 | 30 | 12 | 102.9907 | 0
2024-12-04 09:00 | 20.4 | 59 | 2.01 | 270 | 26 | 30 | 12 | 54.0379 | 0
2024-12-04 10:00 | 23.7 | 45 | 1.7 | 456 | 26 | 30 | 12 | 14.2564 | 0
2024-12-04 11:00 | 25.7 | 33 | 1.73 | 598 | 26 | 30 | 12 | 0 | 0
2024-12-04 12:00 | 26.8 | 28 | 2.3 | 679 | 26 | 30 | 12 | 0.1997 | 0
2024-12-04 13:00 | 27.3 | 27 | 2.96 | 690 | 26 | 30 | 12 | 12.9825 | 0
2024-12-04 14:00 | 27.2 | 29 | 4.23 | 630 | 26 | 30 | 12 | 45.3589 | 0
2024-12-04 15:00 | 26.5 | 33 | 4.94 | 504 | 26 | 30 | 12 | 73.8016 | 0
2024-12-04 16:00 | 25.7 | 35 | 4.44 | 329 | 26 | 30 | 12 | 90.8826 | 0
2024-12-04 17:00 | 24.9 | 40 | 3.96 | 134 | 26 | 30 | 12 | 105.7237 | 0
2024-12-04 18:00 | 23.3 | 45 | 2.88 | 9 | 26 | 30 | 12 | 104.8958 | 0
2024-12-04 19:00 | 22.1 | 48 | 2.48 | 0 | 26 | 30 | 12 | 101.3806 | 0
2024-12-04 20:00 | 21.4 | 50 | 2.2 | 0 | 26 | 30 | 12 | 96.809 | 0
2024-12-04 21:00 | 20.8 | 50 | 2.23 | 0 | 26 | 30 | 12 | 101.0534 | 0
2024-12-04 22:00 | 19.7 | 49 | 2.75 | 0 | 26 | 30 | 12 | 122.1949 | 0
2024-12-04 23:00 | 18.4 | 51 | 2.93 | 0 | 26 | 30 | 12 | 133.4052 | 0
2024-12-05 | 17.3 | 54 | 2.8 | 0 | 26 | 30 | 12 | 134.1615 | 0
2024-12-05 01:00 | 16.5 | 58 | 2.69 | 0 | 26 | 30 | 12 | 132.8484 | 0
2024-12-05 02:00 | 16 | 63 | 2.65 | 0 | 26 | 30 | 12 | 131.1542 | 0
2024-12-05 03:00 | 15.7 | 65 | 2.64 | 0 | 26 | 30 | 12 | 131.3247 | 0
2024-12-05 04:00 | 15.4 | 65 | 2.64 | 0 | 26 | 30 | 12 | 133.1748 | 0
2024-12-05 05:00 | 15 | 61 | 2.27 | 0 | 26 | 30 | 12 | 126.8312 | 0
2024-12-05 06:00 | 14.9 | 61 | 2.37 | 0 | 26 | 30 | 12 | 130.5154 | 0
2024-12-05 07:00 | 15.2 | 57 | 2.63 | 0 | 26 | 30 | 12 | 139.445 | 0
2024-12-05 08:00 | 17.5 | 48 | 2.23 | 78 | 26 | 30 | 12 | 110.0933 | 0
2024-12-05 09:00 | 21.1 | 38 | 1.5 | 261 | 26 | 30 | 12 | 52.1875 | 0
2024-12-05 10:00 | 24 | 31 | 1.61 | 436 | 26 | 30 | 12 | 24.6002 | 0
2024-12-05 11:00 | 25.3 | 35 | 1 | 574 | 26 | 30 | 12 | 0 | 0
2024-12-05 12:00 | 26 | 39 | 0.81 | 652 | 26 | 30 | 12 | 0 | 18.3754
2024-12-05 13:00 | 26.7 | 39 | 2.23 | 670 | 26 | 30 | 12 | 0 | 0
2024-12-05 14:00 | 26.7 | 45 | 3.54 | 613 | 26 | 30 | 12 | 10.307 | 0
2024-12-05 15:00 | 26.3 | 49 | 3.86 | 490 | 26 | 30 | 12 | 28.7097 | 0
2024-12-05 16:00 | 25.7 | 51 | 3.61 | 319 | 26 | 30 | 12 | 50.0109 | 0
2024-12-05 17:00 | 25.1 | 55 | 3.31 | 131 | 26 | 30 | 12 | 69.7866 | 0
2024-12-05 18:00 | 23.8 | 63 | 2.12 | 9 | 26 | 30 | 12 | 66.6794 | 0
2024-12-05 19:00 | 22.9 | 69 | 1.79 | 0 | 26 | 30 | 12 | 62.4818 | 0
2024-12-05 20:00 | 22.4 | 72 | 1.55 | 0 | 26 | 30 | 12 | 58.7428 | 0
2024-12-05 21:00 | 21.9 | 74 | 1.23 | 0 | 26 | 30 | 12 | 53.8627 | 0
2024-12-05 22:00 | 21.4 | 76 | 0.97 | 0 | 26 | 30 | 12 | 49.6648 | 0
2024-12-05 23:00 | 20.5 | 79 | 1.81 | 0 | 26 | 30 | 12 | 70.5158 | 0
2024-12-06 | 19.3 | 81 | 2.62 | 0 | 26 | 30 | 12 | 93.5395 | 0
2024-12-06 01:00 | 18.3 | 83 | 2.8 | 0 | 26 | 30 | 12 | 103.293 | 0
2024-12-06 02:00 | 17.6 | 85 | 2.48 | 0 | 26 | 30 | 12 | 100.0993 | 0
2024-12-06 03:00 | 17.3 | 87 | 2.24 | 0 | 26 | 30 | 12 | 95.3738 | 0
2024-12-06 04:00 | 17.2 | 86 | 1.88 | 0 | 26 | 30 | 12 | 88.1895 | 0
2024-12-06 05:00 | 17.6 | 82 | 1.52 | 0 | 26 | 30 | 12 | 79.1544 | 0
2024-12-06 06:00 | 17.3 | 84 | 2.19 | 0 | 26 | 30 | 12 | 96.2405 | 0
2024-12-06 07:00 | 16.7 | 86 | 2.56 | 0 | 26 | 30 | 12 | 107.7081 | 0
2024-12-06 08:00 | 17.9 | 78 | 1.67 | 77 | 26 | 30 | 12 | 73.1609 | 0
2024-12-06 09:00 | 21.5 | 63 | 1.07 | 259 | 26 | 30 | 12 | 23.29 | 0
2024-12-06 10:00 | 24.3 | 59 | 0.85 | 437 | 26 | 30 | 12 | 0 | 0
2024-12-06 11:00 | 25.9 | 59 | 1.38 | 571 | 26 | 30 | 12 | 0 | 0
2024-12-06 12:00 | 27.3 | 55 | 2.5 | 651 | 26 | 30 | 12 | 0 | 0
2024-12-06 13:00 | 28 | 51 | 3.85 | 660 | 26 | 30 | 12 | 0 | 0
2024-12-06 14:00 | 27.9 | 52 | 4.22 | 602 | 26 | 30 | 12 | 0 | 0
2024-12-06 15:00 | 27.5 | 55 | 3.76 | 482 | 26 | 30 | 12 | 6.2416 | 0
2024-12-06 16:00 | 27.2 | 56 | 3.74 | 314 | 26 | 30 | 12 | 29.8954 | 0
2024-12-06 17:00 | 26.9 | 55 | 4.05 | 128 | 26 | 30 | 12 | 63.5869 | 0
2024-12-06 18:00 | 25.7 | 62 | 2.44 | 8 | 26 | 30 | 12 | 59.063 | 0
2024-12-06 19:00 | 24.9 | 65 | 1.89 | 0 | 26 | 30 | 12 | 54.6038 | 0
2024-12-06 20:00 | 24.4 | 65 | 2.04 | 0 | 26 | 30 | 12 | 60.4207 | 0
2024-12-06 21:00 | 24.1 | 65 | 2.67 | 0 | 26 | 30 | 12 | 72.6637 | 0
2024-12-06 22:00 | 23.9 | 68 | 2.98 | 0 | 26 | 30 | 12 | 75.3753 | 0
2024-12-06 23:00 | 23.5 | 73 | 2.88 | 0 | 26 | 30 | 12 | 71.3626 | 0
2024-12-07 | 23 | 77 | 2.79 | 0 | 26 | 30 | 12 | 69.8719 | 0
2024-12-07 01:00 | 22.8 | 78 | 2.69 | 0 | 26 | 30 | 12 | 69.1028 | 0
2024-12-07 02:00 | 22.7 | 78 | 2.71 | 0 | 26 | 30 | 12 | 70.2488 | 0
2024-12-07 03:00 | 22.7 | 77 | 2.82 | 0 | 26 | 30 | 12 | 72.9313 | 0
2024-12-07 04:00 | 22.6 | 77 | 2.77 | 0 | 26 | 30 | 12 | 73.0747 | 0
2024-12-07 05:00 | 22.6 | 75 | 2.18 | 0 | 26 | 30 | 12 | 66.0134 | 0
2024-12-07 06:00 | 22.4 | 77 | 1.69 | 0 | 26 | 30 | 12 | 57.5503 | 0
2024-12-07 07:00 | 22.3 | 78 | 1.32 | 0 | 26 | 30 | 12 | 50.941 | 0
2024-12-07 08:00 | 23.6 | 75 | 0.55 | 72 | 26 | 30 | 12 | 22.6748 | 0
2024-12-07 09:00 | 25.8 | 65 | 0.45 | 248 | 26 | 30 | 12 | 0 | 0
2024-12-07 10:00 | 27.3 | 58 | 1.97 | 413 | 26 | 30 | 12 | 0 | 0
2024-12-07 11:00 | 28.2 | 52 | 2.77 | 550 | 26 | 30 | 12 | 0 | 0
2024-12-07 12:00 | 28.7 | 47 | 2.87 | 649 | 26 | 30 | 12 | 0 | 0
2024-12-07 13:00 | 29 | 44 | 3.14 | 666 | 26 | 30 | 12 | 0 | 0
2024-12-07 14:00 | 29 | 44 | 3.69 | 612 | 26 | 30 | 12 | 0 | 0
2024-12-07 15:00 | 28.1 | 49 | 4.74 | 489 | 26 | 30 | 12 | 22.4118 | 0
2024-12-07 16:00 | 27.2 | 53 | 4.25 | 319 | 26 | 30 | 12 | 40.92 | 0
2024-12-07 17:00 | 27 | 52 | 3.76 | 131 | 26 | 30 | 12 | 63.9172 | 0
2024-12-07 18:00 | 25.9 | 55 | 3.01 | 9 | 26 | 30 | 12 | 74.8159 | 0
2024-12-07 19:00 | 24.9 | 55 | 2.32 | 0 | 26 | 30 | 12 | 72.2513 | 0
2024-12-07 20:00 | 23.7 | 56 | 1.84 | 0 | 26 | 30 | 12 | 69.6183 | 0
2024-12-07 21:00 | 22.9 | 58 | 1.6 | 0 | 26 | 30 | 12 | 67.3164 | 0
2024-12-07 22:00 | 22 | 58 | 1.51 | 0 | 26 | 30 | 12 | 70.0066 | 0
2024-12-07 23:00 | 21 | 60 | 1.38 | 0 | 26 | 30 | 12 | 70.4569 | 0
2024-12-08 | 20.2 | 64 | 1.29 | 0 | 26 | 30 | 12 | 69.6114 | 0
2024-12-08 01:00 | 19.7 | 67 | 0.64 | 0 | 26 | 30 | 12 | 51.3518 | 0
2024-12-08 02:00 | 18.8 | 73 | 1.25 | 0 | 26 | 30 | 12 | 70.5244 | 0
2024-12-08 03:00 | 17.7 | 82 | 2.15 | 0 | 26 | 30 | 12 | 94.0055 | 0
2024-12-08 04:00 | 17 | 88 | 2.58 | 0 | 26 | 30 | 12 | 104.5103 | 0
2024-12-08 05:00 | 16.5 | 91 | 2.39 | 0 | 26 | 30 | 12 | 101.69 | 0
2024-12-08 06:00 | 16.3 | 92 | 2.84 | 0 | 26 | 30 | 12 | 112.703 | 0
2024-12-08 07:00 | 16.4 | 89 | 3.74 | 0 | 26 | 30 | 12 | 134.0513 | 0
2024-12-08 08:00 | 18.9 | 72 | 3.17 | 74 | 26 | 30 | 12 | 106.3395 | 0
2024-12-08 09:00 | 22.5 | 59 | 3.01 | 258 | 26 | 30 | 12 | 63.4726 | 0
2024-12-08 10:00 | 25.7 | 49 | 3.65 | 441 | 26 | 30 | 12 | 37.3853 | 0
2024-12-08 11:00 | 28 | 31 | 5.6 | 585 | 26 | 30 | 12 | 65.0843 | 0
2024-12-08 12:00 | 29 | 26 | 5.58 | 668 | 26 | 30 | 12 | 56.794 | 0
2024-12-08 13:00 | 29.4 | 24 | 5.6 | 681 | 26 | 30 | 12 | 57.0468 | 0
2024-12-08 14:00 | 29.4 | 22 | 5.95 | 622 | 26 | 30 | 12 | 76.6813 | 0
2024-12-08 15:00 | 29 | 21 | 5.93 | 502 | 26 | 30 | 12 | 98.8643 | 0
2024-12-08 16:00 | 28.4 | 21 | 5.71 | 330 | 26 | 30 | 12 | 123.1049 | 0
2024-12-08 17:00 | 28.1 | 26 | 2.87 | 133 | 26 | 30 | 12 | 82.8198 | 0
2024-12-08 18:00 | 26.1 | 26 | 4.1 | 9 | 26 | 30 | 12 | 140.1991 | 0
2024-12-08 19:00 | 24.7 | 29 | 5.69 | 0 | 26 | 30 | 12 | 180.9331 | 0
2024-12-08 20:00 | 23.6 | 35 | 5.47 | 0 | 26 | 30 | 12 | 174.4069 | 0
2024-12-08 21:00 | 22.6 | 40 | 4.98 | 0 | 26 | 30 | 12 | 164.2561 | 0
2024-12-08 22:00 | 21.6 | 43 | 4.44 | 0 | 26 | 30 | 12 | 156.3922 | 0
2024-12-08 23:00 | 20.9 | 44 | 4.14 | 0 | 26 | 30 | 12 | 153.7794 | 0
2024-12-09 | 19.9 | 44 | 3.69 | 0 | 26 | 30 | 12 | 150.2819 | 0
2024-12-09 01:00 | 19.1 | 43 | 3.54 | 0 | 26 | 30 | 12 | 153.0005 | 0
2024-12-09 02:00 | 18.7 | 40 | 3.9 | 0 | 26 | 30 | 12 | 168.649 | 0
2024-12-09 03:00 | 18.3 | 42 | 3.97 | 0 | 26 | 30 | 12 | 171.1369 | 0
2024-12-09 04:00 | 17.8 | 46 | 3.86 | 0 | 26 | 30 | 12 | 167.4464 | 0
2024-12-09 05:00 | 16.9 | 56 | 3.52 | 0 | 26 | 30 | 12 | 154.9488 | 0
2024-12-09 06:00 | 16.3 | 60 | 3.48 | 0 | 26 | 30 | 12 | 154.5804 | 0
2024-12-09 07:00 | 15.9 | 63 | 3.53 | 0 | 26 | 30 | 12 | 156.2261 | 0
2024-12-09 08:00 | 17.6 | 55 | 3.41 | 74 | 26 | 30 | 12 | 138.0009 | 0
2024-12-09 09:00 | 21.1 | 44 | 2.73 | 261 | 26 | 30 | 12 | 82.5414 | 0
2024-12-09 10:00 | 24.5 | 38 | 3.81 | 448 | 26 | 30 | 12 | 66.5848 | 0
2024-12-09 11:00 | 26.9 | 31 | 4.41 | 593 | 26 | 30 | 12 | 52.3658 | 0
2024-12-09 12:00 | 28.4 | 24 | 3.93 | 676 | 26 | 30 | 12 | 33.9747 | 0
2024-12-09 13:00 | 29.2 | 21 | 2.75 | 687 | 26 | 30 | 12 | 6.8265 | 0
2024-12-09 14:00 | 29.5 | 19 | 0.91 | 627 | 26 | 30 | 12 | 0 | 9.5555
2024-12-09 15:00 | 28.8 | 25 | 2.67 | 505 | 26 | 30 | 12 | 25.4989 | 0
2024-12-09 16:00 | 26.5 | 39 | 5.63 | 330 | 26 | 30 | 12 | 96.1879 | 0
2024-12-09 17:00 | 26 | 38 | 4.05 | 136 | 26 | 30 | 12 | 101.5507 | 0
2024-12-09 18:00 | 24.5 | 47 | 2.92 | 9 | 26 | 30 | 12 | 94.8857 | 0
2024-12-09 19:00 | 23.7 | 59 | 3.11 | 0 | 26 | 30 | 12 | 90.5133 | 0
2024-12-09 20:00 | 22.5 | 65 | 2.17 | 0 | 26 | 30 | 12 | 75.7933 | 0
2024-12-09 21:00 | 21.5 | 67 | 1.86 | 0 | 26 | 30 | 12 | 74.2402 | 0
2024-12-09 22:00 | 20.3 | 68 | 1.95 | 0 | 26 | 30 | 12 | 82.8329 | 0
2024-12-09 23:00 | 19.3 | 71 | 2.1 | 0 | 26 | 30 | 12 | 90.3082 | 0
2024-12-10 | 18.5 | 74 | 2.15 | 0 | 26 | 30 | 12 | 94.3967 | 0
2024-12-10 01:00 | 17.9 | 75 | 2.06 | 0 | 26 | 30 | 12 | 95.2688 | 0
2024-12-10 02:00 | 17.7 | 73 | 2.12 | 0 | 26 | 30 | 12 | 99.3563 | 0
2024-12-10 03:00 | 17.4 | 71 | 1.94 | 0 | 26 | 30 | 12 | 97.6912 | 0
2024-12-10 04:00 | 17.3 | 70 | 1.88 | 0 | 26 | 30 | 12 | 97.2253 | 0
2024-12-10 05:00 | 17.7 | 69 | 1.84 | 0 | 26 | 30 | 12 | 94.5123 | 0
2024-12-10 06:00 | 17.2 | 71 | 1.96 | 0 | 26 | 30 | 12 | 99.3777 | 0
2024-12-10 07:00 | 16.9 | 71 | 2.08 | 0 | 26 | 30 | 12 | 104.3944 | 0
2024-12-10 08:00 | 18.9 | 62 | 2 | 64 | 26 | 30 | 12 | 88.0237 | 0
2024-12-10 09:00 | 21.8 | 52 | 1.57 | 247 | 26 | 30 | 12 | 43.4068 | 0
2024-12-10 10:00 | 24.1 | 48 | 1.95 | 435 | 26 | 30 | 12 | 18.2482 | 0
2024-12-10 11:00 | 25.4 | 46 | 1.25 | 576 | 26 | 30 | 12 | 0 | 0
2024-12-10 12:00 | 26.3 | 44 | 1 | 657 | 26 | 30 | 12 | 0 | 15.2676
2024-12-10 13:00 | 26.9 | 44 | 2.24 | 669 | 26 | 30 | 12 | 0 | 0
2024-12-10 14:00 | 27 | 44 | 3.67 | 612 | 26 | 30 | 12 | 11.697 | 0
2024-12-10 15:00 | 26.6 | 46 | 4.39 | 490 | 26 | 30 | 12 | 39.4085 | 0
2024-12-10 16:00 | 25.9 | 49 | 4.15 | 322 | 26 | 30 | 12 | 59.6064 | 0
2024-12-10 17:00 | 25.1 | 55 | 3.53 | 135 | 26 | 30 | 12 | 72.7288 | 0
2024-12-10 18:00 | 24 | 62 | 2.17 | 9 | 26 | 30 | 12 | 67.181 | 0
2024-12-10 19:00 | 23.3 | 66 | 1.56 | 0 | 26 | 30 | 12 | 58.0884 | 0
2024-12-10 20:00 | 22.9 | 67 | 1.37 | 0 | 26 | 30 | 12 | 55.8483 | 0
2024-12-10 21:00 | 22.7 | 68 | 1.08 | 0 | 26 | 30 | 12 | 50.1174 | 0
2024-12-10 22:00 | 22.3 | 69 | 0.46 | 0 | 26 | 30 | 12 | 39.529 | 0
2024-12-10 23:00 | 21.6 | 72 | 0.65 | 0 | 26 | 30 | 12 | 42.8061 | 0
2024-12-11 | 20.5 | 77 | 1.88 | 0 | 26 | 30 | 12 | 73.3833 | 0
2024-12-11 01:00 | 19.5 | 82 | 2.97 | 0 | 26 | 30 | 12 | 97.777 | 0
2024-12-11 02:00 | 18.3 | 88 | 3.26 | 0 | 26 | 30 | 12 | 107.9958 | 0
2024-12-11 03:00 | 17.9 | 89 | 2.75 | 0 | 26 | 30 | 12 | 100.4374 | 0
2024-12-11 04:00 | 17.5 | 90 | 2.21 | 0 | 26 | 30 | 12 | 91.2682 | 0
2024-12-11 05:00 | 17.4 | 85 | 2.41 | 0 | 26 | 30 | 12 | 99.9588 | 0
2024-12-11 06:00 | 17.5 | 84 | 2.91 | 0 | 26 | 30 | 12 | 111.1133 | 0
2024-12-11 07:00 | 17.4 | 80 | 3.2 | 0 | 26 | 30 | 12 | 121.7277 | 0
2024-12-11 08:00 | 18.9 | 69 | 3.15 | 67 | 26 | 30 | 12 | 109.7243 | 0
2024-12-11 09:00 | 22 | 56 | 2.51 | 247 | 26 | 30 | 12 | 61.4724 | 0
2024-12-11 10:00 | 24.8 | 46 | 3.38 | 429 | 26 | 30 | 12 | 46.2536 | 0
2024-12-11 11:00 | 26.4 | 44 | 4.64 | 569 | 26 | 30 | 12 | 38.4768 | 0
2024-12-11 12:00 | 27.6 | 42 | 4.43 | 650 | 26 | 30 | 12 | 16.6816 | 0
2024-12-11 13:00 | 28.4 | 38 | 5.06 | 659 | 26 | 30 | 12 | 25.6713 | 0
2024-12-11 14:00 | 28.5 | 36 | 5.79 | 496 | 26 | 30 | 12 | 62.1844 | 0
2024-12-11 15:00 | 28.4 | 30 | 6.5 | 472 | 26 | 30 | 12 | 93.5529 | 0
2024-12-11 16:00 | 27.5 | 30 | 6.76 | 319 | 26 | 30 | 12 | 128.1036 | 0
2024-12-11 17:00 | 27 | 35 | 6.05 | 97 | 26 | 30 | 12 | 138.6846 | 0
2024-12-11 18:00 | 25 | 38 | 5.56 | 10 | 26 | 30 | 12 | 155.6352 | 0
2024-12-11 19:00 | 23.7 | 40 | 6.13 | 0 | 26 | 30 | 12 | 176.6665 | 0
2024-12-11 20:00 | 22.7 | 43 | 5.36 | 0 | 26 | 30 | 12 | 166.0548 | 0
2024-12-11 21:00 | 22.1 | 44 | 5.45 | 0 | 26 | 30 | 12 | 171.9283 | 0
2024-12-11 22:00 | 21.5 | 47 | 4.86 | 0 | 26 | 30 | 12 | 160.4685 | 0
2024-12-11 23:00 | 20.8 | 49 | 4.41 | 0 | 26 | 30 | 12 | 154.0521 | 0
2024-12-12 | 19.9 | 52 | 3.82 | 0 | 26 | 30 | 12 | 144.233 | 0
2024-12-12 01:00 | 19 | 55 | 3.37 | 0 | 26 | 30 | 12 | 136.9547 | 0
2024-12-12 02:00 | 18.3 | 58 | 3.18 | 0 | 26 | 30 | 12 | 134.3081 | 0
2024-12-12 03:00 | 17.8 | 60 | 3.18 | 0 | 26 | 30 | 12 | 136.0121 | 0
2024-12-12 04:00 | 17.5 | 64 | 3.27 | 0 | 26 | 30 | 12 | 136.8582 | 0
2024-12-12 05:00 | 17.6 | 67 | 3.43 | 0 | 26 | 30 | 12 | 137.2803 | 0
2024-12-12 06:00 | 17.3 | 70 | 3.38 | 0 | 26 | 30 | 12 | 135.6456 | 0
2024-12-12 07:00 | 17.1 | 73 | 3.22 | 0 | 26 | 30 | 12 | 130.6859 | 0
2024-12-12 08:00 | 18.6 | 69 | 2.55 | 66 | 26 | 30 | 12 | 98.2099 | 0
2024-12-12 09:00 | 21.4 | 59 | 1.3 | 246 | 26 | 30 | 12 | 33.8076 | 0
2024-12-12 10:00 | 24 | 50 | 2.17 | 429 | 26 | 30 | 12 | 22.5763 | 0
2024-12-12 11:00 | 25.7 | 43 | 1.52 | 571 | 26 | 30 | 12 | 0 | 0
2024-12-12 12:00 | 26.6 | 37 | 0.81 | 653 | 26 | 30 | 12 | 0 | 19.5784
2024-12-12 13:00 | 27.3 | 33 | 1.5 | 667 | 26 | 30 | 12 | 0 | 0
2024-12-12 14:00 | 27.6 | 31 | 2.49 | 613 | 26 | 30 | 12 | 5.1719 | 0
2024-12-12 15:00 | 27.3 | 33 | 3.66 | 493 | 26 | 30 | 12 | 44.4528 | 0
2024-12-12 16:00 | 26.2 | 39 | 3.83 | 324 | 26 | 30 | 12 | 68.6796 | 0
2024-12-12 17:00 | 25.1 | 42 | 3.17 | 136 | 26 | 30 | 12 | 85.1069 | 0
2024-12-12 18:00 | 23.4 | 48 | 3.48 | 10 | 26 | 30 | 12 | 112.9984 | 0
2024-12-12 19:00 | 22.8 | 56 | 3.7 | 0 | 26 | 30 | 12 | 112.7265 | 0
2024-12-12 20:00 | 22 | 64 | 3.51 | 0 | 26 | 30 | 12 | 105.7931 | 0
2024-12-12 21:00 | 21.2 | 66 | 3.38 | 0 | 26 | 30 | 12 | 107.9105 | 0
2024-12-12 22:00 | 20 | 63 | 3.07 | 0 | 26 | 30 | 12 | 114.4345 | 0
2024-12-12 23:00 | 19.3 | 65 | 3.04 | 0 | 26 | 30 | 12 | 117.0677 | 0
2024-12-13 | 18.3 | 70 | 2.68 | 0 | 26 | 30 | 12 | 111.4814 | 0
2024-12-13 01:00 | 17.5 | 74 | 2.36 | 0 | 26 | 30 | 12 | 105.9973 | 0
2024-12-13 02:00 | 16.7 | 77 | 2.4 | 0 | 26 | 30 | 12 | 110.1371 | 0
2024-12-13 03:00 | 16 | 80 | 2.23 | 0 | 26 | 30 | 12 | 108.2339 | 0
2024-12-13 04:00 | 15.2 | 82 | 2.13 | 0 | 26 | 30 | 12 | 109.2504 | 0
2024-12-13 05:00 | 15.7 | 76 | 2.07 | 0 | 26 | 30 | 12 | 108.0829 | 0
2024-12-13 06:00 | 15.3 | 76 | 1.93 | 0 | 26 | 30 | 12 | 106.32 | 0
2024-12-13 07:00 | 14.9 | 77 | 1.81 | 0 | 26 | 30 | 12 | 104.3924 | 0
2024-12-13 08:00 | 16.3 | 70 | 1.46 | 64 | 26 | 30 | 12 | 81.4293 | 0
2024-12-13 09:00 | 19.2 | 58 | 0.91 | 243 | 26 | 30 | 12 | 32.5995 | 0
2024-12-13 10:00 | 22.1 | 49 | 1.24 | 425 | 26 | 30 | 12 | 10.8136 | 0
2024-12-13 11:00 | 24.5 | 39 | 1.86 | 566 | 26 | 30 | 12 | 4.6351 | 0
2024-12-13 12:00 | 26 | 34 | 1.8 | 650 | 26 | 30 | 12 | 0 | 0
2024-12-13 13:00 | 26.8 | 33 | 2.1 | 666 | 26 | 30 | 12 | 0 | 0
2024-12-13 14:00 | 27 | 33 | 2.53 | 612 | 26 | 30 | 12 | 7.0684 | 0
2024-12-13 15:00 | 26.6 | 36 | 3.1 | 493 | 26 | 30 | 12 | 33.5229 | 0
2024-12-13 16:00 | 25.9 | 43 | 3.85 | 324 | 26 | 30 | 12 | 64.7446 | 0
2024-12-13 17:00 | 24.9 | 57 | 5.57 | 123 | 26 | 30 | 12 | 102.4528 | 0
2024-12-13 18:00 | 24.1 | 59 | 3.34 | 9 | 26 | 30 | 12 | 89.7757 | 0
2024-12-13 19:00 | 23.2 | 63 | 2.11 | 0 | 26 | 30 | 12 | 71.7816 | 0
2024-12-13 20:00 | 22.4 | 69 | 2.42 | 0 | 26 | 30 | 12 | 77.3414 | 0
2024-12-13 21:00 | 21.4 | 77 | 1.94 | 0 | 26 | 30 | 12 | 68.6119 | 0
2024-12-13 22:00 | 20.9 | 80 | 1.38 | 0 | 26 | 30 | 12 | 58.7847 | 0
2024-12-13 23:00 | 20 | 83 | 1.8 | 0 | 26 | 30 | 12 | 70.7092 | 0
2024-12-14 | 19 | 83 | 2.83 | 0 | 26 | 30 | 12 | 98.3051 | 0
2024-12-14 01:00 | 18.1 | 86 | 2.29 | 0 | 26 | 30 | 12 | 91.613 | 0
2024-12-14 02:00 | 17.7 | 88 | 2.28 | 0 | 26 | 30 | 12 | 92.7895 | 0
2024-12-14 03:00 | 17.1 | 91 | 2.34 | 0 | 26 | 30 | 12 | 96.2755 | 0
2024-12-14 04:00 | 16.6 | 92 | 2.54 | 0 | 26 | 30 | 12 | 103.6834 | 0
2024-12-14 05:00 | 16.9 | 86 | 2.21 | 0 | 26 | 30 | 12 | 98.0493 | 0
2024-12-14 06:00 | 16.5 | 86 | 2.26 | 0 | 26 | 30 | 12 | 101.9268 | 0
2024-12-14 07:00 | 16.3 | 86 | 2.44 | 0 | 26 | 30 | 12 | 107.6755 | 0
2024-12-14 08:00 | 17.7 | 80 | 2.13 | 60 | 26 | 30 | 12 | 86.7855 | 0
2024-12-14 09:00 | 20.6 | 68 | 1.67 | 234 | 26 | 30 | 12 | 42.9878 | 0
2024-12-14 10:00 | 23.2 | 59 | 1.65 | 420 | 26 | 30 | 12 | 9.2672 | 0
2024-12-14 11:00 | 24.7 | 53 | 1.98 | 562 | 26 | 30 | 12 | 0 | 0
2024-12-14 12:00 | 25.7 | 47 | 3.42 | 647 | 26 | 30 | 12 | 8.8276 | 0
2024-12-14 13:00 | 26.2 | 44 | 4.2 | 655 | 26 | 30 | 12 | 21.6521 | 0
2024-12-14 14:00 | 26.2 | 43 | 5.05 | 578 | 26 | 30 | 12 | 47.7948 | 0
2024-12-14 15:00 | 25.2 | 45 | 6.23 | 451 | 26 | 30 | 12 | 90.1727 | 0
2024-12-14 16:00 | 24.5 | 41 | 6.07 | 306 | 26 | 30 | 12 | 123.7033 | 0
2024-12-14 17:00 | 23.9 | 45 | 5.6 | 135 | 26 | 30 | 12 | 136.6381 | 0
2024-12-14 18:00 | 22.4 | 50 | 4.24 | 11 | 26 | 30 | 12 | 133.6758 | 0
2024-12-14 19:00 | 21.6 | 56 | 3.63 | 0 | 26 | 30 | 12 | 121.53 | 0
2024-12-14 20:00 | 20.7 | 65 | 3.12 | 0 | 26 | 30 | 12 | 108.0025 | 0
2024-12-14 21:00 | 19.9 | 67 | 3 | 0 | 26 | 30 | 12 | 109.6904 | 0
2024-12-14 22:00 | 19.4 | 66 | 3.18 | 0 | 26 | 30 | 12 | 118.4683 | 0
2024-12-14 23:00 | 18.8 | 70 | 2.8 | 0 | 26 | 30 | 12 | 110.7121 | 0
2024-12-15 | 18.3 | 76 | 2.42 | 0 | 26 | 30 | 12 | 100.5966 | 0
2024-12-15 01:00 | 17.6 | 77 | 2.62 | 0 | 26 | 30 | 12 | 109.3991 | 0
2024-12-15 02:00 | 17 | 77 | 2.82 | 0 | 26 | 30 | 12 | 118.4932 | 0
2024-12-15 03:00 | 16.5 | 75 | 3.08 | 0 | 26 | 30 | 12 | 130.1378 | 0
2024-12-15 04:00 | 16.2 | 74 | 3.42 | 0 | 26 | 30 | 12 | 141.6904 | 0
2024-12-15 05:00 | 15.8 | 70 | 3.6 | 0 | 26 | 30 | 12 | 152.7945 | 0
2024-12-15 06:00 | 15.5 | 73 | 3.65 | 0 | 26 | 30 | 12 | 153.8481 | 0
2024-12-15 07:00 | 15.4 | 74 | 3.67 | 0 | 26 | 30 | 12 | 154.2987 | 0
2024-12-15 08:00 | 16.8 | 70 | 3.59 | 59 | 26 | 30 | 12 | 136.7112 | 0
2024-12-15 09:00 | 19.8 | 61 | 3.55 | 230 | 26 | 30 | 12 | 97.6443 | 0
2024-12-15 10:00 | 22.7 | 55 | 3.83 | 392 | 26 | 30 | 12 | 64.4956 | 0
2024-12-15 11:00 | 24.5 | 54 | 3.85 | 533 | 26 | 30 | 12 | 31.1274 | 0
2024-12-15 12:00 | 24.7 | 53 | 5.6 | 592 | 26 | 30 | 12 | 50.1481 | 0
2024-12-15 13:00 | 24.3 | 55 | 6.31 | 575 | 26 | 30 | 12 | 63.4789 | 0
2024-12-15 14:00 | 23.5 | 61 | 6.87 | 495 | 26 | 30 | 12 | 79.7863 | 0
2024-12-15 15:00 | 23.5 | 58 | 6.66 | 432 | 26 | 30 | 12 | 91.8182 | 0
2024-12-15 16:00 | 22.7 | 57 | 6.35 | 302 | 26 | 30 | 12 | 116.9839 | 0
2024-12-15 17:00 | 22 | 61 | 5.19 | 132 | 26 | 30 | 12 | 121.7479 | 0
2024-12-15 18:00 | 21 | 64 | 3.96 | 11 | 26 | 30 | 12 | 121.6927 | 0
2024-12-15 19:00 | 20.3 | 67 | 3.65 | 0 | 26 | 30 | 12 | 119.7975 | 0
2024-12-15 20:00 | 19.6 | 70 | 3.26 | 0 | 26 | 30 | 12 | 114.5506 | 0
2024-12-15 21:00 | 18.9 | 74 | 2.8 | 0 | 26 | 30 | 12 | 106.4551 | 0
2024-12-15 22:00 | 18.7 | 75 | 2.67 | 0 | 26 | 30 | 12 | 104.2208 | 0
2024-12-15 23:00 | 18.3 | 76 | 2.4 | 0 | 26 | 30 | 12 | 100.1332 | 0
2024-12-16 | 18.3 | 77 | 2.12 | 0 | 26 | 30 | 12 | 92.8437 | 0
2024-12-16 01:00 | 18.1 | 78 | 2.38 | 0 | 26 | 30 | 12 | 99.5317 | 0
2024-12-16 02:00 | 17.9 | 76 | 2.21 | 0 | 26 | 30 | 12 | 98.2807 | 0
2024-12-16 03:00 | 17.6 | 76 | 2.12 | 0 | 26 | 30 | 12 | 97.963 | 0
2024-12-16 04:00 | 17.3 | 77 | 2.28 | 0 | 26 | 30 | 12 | 103.1921 | 0
2024-12-16 05:00 | 17.7 | 72 | 2.78 | 0 | 26 | 30 | 12 | 116.4834 | 0
2024-12-16 06:00 | 17.5 | 74 | 2.86 | 0 | 26 | 30 | 12 | 118.2156 | 0
2024-12-16 07:00 | 17.3 | 75 | 2.51 | 0 | 26 | 30 | 12 | 110.3324 | 0
2024-12-16 08:00 | 18.6 | 73 | 1.65 | 61 | 26 | 30 | 12 | 73.8521 | 0
2024-12-16 09:00 | 21 | 65 | 1.81 | 240 | 26 | 30 | 12 | 45.2474 | 0
2024-12-16 10:00 | 22.8 | 51 | 1.17 | 421 | 26 | 30 | 12 | 5.0691 | 0
2024-12-16 11:00 | 23.6 | 45 | 1.29 | 567 | 26 | 30 | 12 | 0 | 0
2024-12-16 12:00 | 24.2 | 42 | 1.56 | 655 | 26 | 30 | 12 | 0 | 0
2024-12-16 13:00 | 24.5 | 41 | 2.13 | 672 | 26 | 30 | 12 | 0 | 0
2024-12-16 14:00 | 24.8 | 40 | 2.94 | 619 | 26 | 30 | 12 | 19.9048 | 0
2024-12-16 15:00 | 24.5 | 41 | 3.46 | 501 | 26 | 30 | 12 | 47.6339 | 0
2024-12-16 16:00 | 23.9 | 42 | 3.27 | 334 | 26 | 30 | 12 | 69.1655 | 0
2024-12-16 17:00 | 22.8 | 51 | 2.88 | 142 | 26 | 30 | 12 | 83.4525 | 0
2024-12-16 18:00 | 21.1 | 59 | 2.31 | 11 | 26 | 30 | 12 | 91.9331 | 0
2024-12-16 19:00 | 20.5 | 60 | 2.23 | 0 | 26 | 30 | 12 | 94.472 | 0
2024-12-16 20:00 | 20.1 | 62 | 1.86 | 0 | 26 | 30 | 12 | 86.2228 | 0
2024-12-16 21:00 | 19.3 | 66 | 1.66 | 0 | 26 | 30 | 12 | 82.8214 | 0
2024-12-16 22:00 | 18.5 | 67 | 1.16 | 0 | 26 | 30 | 12 | 72.2342 | 0
2024-12-16 23:00 | 17.6 | 69 | 1.07 | 0 | 26 | 30 | 12 | 72.4894 | 0
2024-12-17 | 16.5 | 75 | 1.24 | 0 | 26 | 30 | 12 | 80.0769 | 0
2024-12-17 01:00 | 15.8 | 78 | 1.35 | 0 | 26 | 30 | 12 | 85.4078 | 0
2024-12-17 02:00 | 15.7 | 77 | 1.12 | 0 | 26 | 30 | 12 | 79.0069 | 0
2024-12-17 03:00 | 15.5 | 76 | 1.43 | 0 | 26 | 30 | 12 | 90.1857 | 0
2024-12-17 04:00 | 14.8 | 77 | 2.24 | 0 | 26 | 30 | 12 | 117.658 | 0
2024-12-17 05:00 | 15.3 | 78 | 2.51 | 0 | 26 | 30 | 12 | 121.5106 | 0
2024-12-17 06:00 | 14.7 | 80 | 2.32 | 0 | 26 | 30 | 12 | 118.7921 | 0
2024-12-17 07:00 | 14.2 | 82 | 2.01 | 0 | 26 | 30 | 12 | 111.6673 | 0
2024-12-17 08:00 | 15.5 | 80 | 1.97 | 60 | 26 | 30 | 12 | 96.046 | 0
2024-12-17 09:00 | 19.3 | 65 | 1.41 | 241 | 26 | 30 | 12 | 44.1585 | 0
2024-12-17 10:00 | 22.1 | 49 | 2.18 | 430 | 26 | 30 | 12 | 35.0644 | 0
2024-12-17 11:00 | 23.4 | 34 | 3.05 | 578 | 26 | 30 | 12 | 44.7203 | 0
2024-12-17 12:00 | 24.1 | 31 | 2.71 | 665 | 26 | 30 | 12 | 23.7891 | 0
2024-12-17 13:00 | 24.4 | 32 | 3.06 | 680 | 26 | 30 | 12 | 27.5205 | 0
2024-12-17 14:00 | 24.4 | 35 | 3.91 | 625 | 26 | 30 | 12 | 50.2433 | 0
2024-12-17 15:00 | 24 | 37 | 4.1 | 503 | 26 | 30 | 12 | 70.7598 | 0
2024-12-17 16:00 | 23.4 | 40 | 3.26 | 333 | 26 | 30 | 12 | 75.2365 | 0
2024-12-17 17:00 | 22.2 | 51 | 1.6 | 141 | 26 | 30 | 12 | 57.2038 | 0
2024-12-17 18:00 | 21.3 | 55 | 0.25 | 11 | 26 | 30 | 12 | 45.9419 | 0
2024-12-17 19:00 | 21 | 56 | 0.43 | 0 | 26 | 30 | 12 | 48.5644 | 0
2024-12-17 20:00 | 20.6 | 58 | 1 | 0 | 26 | 30 | 12 | 62.6861 | 0
2024-12-17 21:00 | 20.5 | 74 | 3.56 | 0 | 26 | 30 | 12 | 108.2094 | 0
2024-12-17 22:00 | 20 | 79 | 3.43 | 0 | 26 | 30 | 12 | 104.8657 | 0
2024-12-17 23:00 | 20.4 | 75 | 3.54 | 0 | 26 | 30 | 12 | 107.6226 | 0
2024-12-18 | 20.3 | 71 | 4.1 | 0 | 26 | 30 | 12 | 123.5675 | 0
2024-12-18 01:00 | 20.5 | 67 | 4.82 | 0 | 26 | 30 | 12 | 140.0758 | 0
2024-12-18 02:00 | 20 | 64 | 4.34 | 0 | 26 | 30 | 12 | 139.9599 | 0
2024-12-18 03:00 | 19.1 | 66 | 3.35 | 0 | 26 | 30 | 12 | 124.6023 | 0
2024-12-18 04:00 | 19.4 | 68 | 3.41 | 0 | 26 | 30 | 12 | 121.4234 | 0
2024-12-18 05:00 | 19.5 | 59 | 3 | 0 | 26 | 30 | 12 | 120.4297 | 0
2024-12-18 06:00 | 19.3 | 59 | 3.13 | 0 | 26 | 30 | 12 | 124.9697 | 0
2024-12-18 07:00 | 19.1 | 60 | 3.77 | 0 | 26 | 30 | 12 | 140.418 | 0
2024-12-18 08:00 | 19 | 61 | 4.22 | 44 | 26 | 30 | 12 | 144.3166 | 0
2024-12-18 09:00 | 21.1 | 54 | 3.07 | 137 | 26 | 30 | 12 | 97.1702 | 0
2024-12-18 10:00 | 22.8 | 50 | 3.9 | 272 | 26 | 30 | 12 | 88.1938 | 0
2024-12-18 11:00 | 23.2 | 50 | 6 | 329 | 26 | 30 | 12 | 115.3342 | 0
2024-12-18 12:00 | 23.7 | 43 | 6.17 | 493 | 26 | 30 | 12 | 104.6923 | 0
2024-12-18 13:00 | 24 | 40 | 6 | 631 | 26 | 30 | 12 | 85.9261 | 0
2024-12-18 14:00 | 23.8 | 41 | 5.94 | 612 | 26 | 30 | 12 | 87.414 | 0
2024-12-18 15:00 | 23.7 | 41 | 5.98 | 500 | 26 | 30 | 12 | 104.3195 | 0
2024-12-18 16:00 | 23.2 | 43 | 5.71 | 330 | 26 | 30 | 12 | 123.4029 | 0
2024-12-18 17:00 | 22.9 | 46 | 4.63 | 134 | 26 | 30 | 12 | 126.4988 | 0
2024-12-18 18:00 | 21.9 | 50 | 3.59 | 11 | 26 | 30 | 12 | 124.322 | 0
2024-12-18 19:00 | 21.6 | 52 | 3.05 | 0 | 26 | 30 | 12 | 113.7959 | 0
2024-12-18 20:00 | 20.6 | 54 | 2.62 | 0 | 26 | 30 | 12 | 108.5412 | 0
2024-12-18 21:00 | 19.6 | 58 | 2.47 | 0 | 26 | 30 | 12 | 107.6873 | 0
2024-12-18 22:00 | 19.4 | 61 | 2.59 | 0 | 26 | 30 | 12 | 109.3983 | 0
2024-12-18 23:00 | 19.4 | 62 | 2.89 | 0 | 26 | 30 | 12 | 115.6982 | 0
2024-12-19 | 19.8 | 60 | 2.93 | 0 | 26 | 30 | 12 | 115.6785 | 0
2024-12-19 01:00 | 19 | 64 | 2.69 | 0 | 26 | 30 | 12 | 111.9319 | 0
2024-12-19 02:00 | 18.4 | 67 | 2.36 | 0 | 26 | 30 | 12 | 105.3466 | 0
2024-12-19 03:00 | 17.9 | 68 | 2.06 | 0 | 26 | 30 | 12 | 99.9444 | 0
2024-12-19 04:00 | 17.7 | 67 | 1.63 | 0 | 26 | 30 | 12 | 89.7937 | 0
2024-12-19 05:00 | 16.2 | 70 | 2.12 | 0 | 26 | 30 | 12 | 110.194 | 0
2024-12-19 06:00 | 15.4 | 76 | 2.78 | 0 | 26 | 30 | 12 | 129.4954 | 0
2024-12-19 07:00 | 14.7 | 81 | 3.21 | 0 | 26 | 30 | 12 | 142.2741 | 0
2024-12-19 08:00 | 15.5 | 78 | 2.82 | 57 | 26 | 30 | 12 | 120.7533 | 0
2024-12-19 09:00 | 19.1 | 63 | 2.32 | 234 | 26 | 30 | 12 | 71.4096 | 0
2024-12-19 10:00 | 22 | 50 | 2.2 | 391 | 26 | 30 | 12 | 40.5074 | 0
2024-12-19 11:00 | 23.2 | 42 | 1.11 | 563 | 26 | 30 | 12 | 0 | 0
2024-12-19 12:00 | 23.9 | 41 | 2.34 | 645 | 26 | 30 | 12 | 7.1933 | 0
2024-12-19 13:00 | 24.3 | 40 | 3.55 | 663 | 26 | 30 | 12 | 30.5919 | 0
2024-12-19 14:00 | 24.4 | 37 | 4.22 | 620 | 26 | 30 | 12 | 54.3361 | 0
2024-12-19 15:00 | 24.2 | 38 | 4.25 | 501 | 26 | 30 | 12 | 71.004 | 0
2024-12-19 16:00 | 23.7 | 43 | 3.65 | 337 | 26 | 30 | 12 | 76.9599 | 0
2024-12-19 17:00 | 23.4 | 47 | 3.64 | 145 | 26 | 30 | 12 | 99.3916 | 0
2024-12-19 18:00 | 22.1 | 55 | 3.7 | 12 | 26 | 30 | 12 | 118.4269 | 0
2024-12-19 19:00 | 21.4 | 58 | 3.3 | 0 | 26 | 30 | 12 | 113.9288 | 0
2024-12-19 20:00 | 20.4 | 61 | 2.51 | 0 | 26 | 30 | 12 | 100.8414 | 0
2024-12-19 21:00 | 19.6 | 66 | 2.33 | 0 | 26 | 30 | 12 | 97.6619 | 0
2024-12-19 22:00 | 19.2 | 70 | 2.18 | 0 | 26 | 30 | 12 | 93.575 | 0
2024-12-19 23:00 | 18.7 | 74 | 2.33 | 0 | 26 | 30 | 12 | 97.3235 | 0
2024-12-20 | 17.8 | 77 | 2.74 | 0 | 26 | 30 | 12 | 110.7556 | 0
2024-12-20 01:00 | 17.1 | 79 | 3.03 | 0 | 26 | 30 | 12 | 121.0972 | 0
2024-12-20 02:00 | 16.3 | 83 | 3.15 | 0 | 26 | 30 | 12 | 126.8749 | 0
2024-12-20 03:00 | 15.9 | 85 | 3.02 | 0 | 26 | 30 | 12 | 125.337 | 0
2024-12-20 04:00 | 14.6 | 92 | 3.16 | 0 | 26 | 30 | 12 | 133.6774 | 0
2024-12-20 05:00 | 14.8 | 82 | 2.99 | 0 | 26 | 30 | 12 | 135.0482 | 0
2024-12-20 06:00 | 14.6 | 83 | 3.21 | 0 | 26 | 30 | 12 | 141.5487 | 0
2024-12-20 07:00 | 14.2 | 85 | 3.34 | 0 | 26 | 30 | 12 | 146.521 | 0
2024-12-20 08:00 | 15.1 | 80 | 2.84 | 56 | 26 | 30 | 12 | 122.8053 | 0
2024-12-20 09:00 | 18.1 | 66 | 2.19 | 233 | 26 | 30 | 12 | 72.1104 | 0
2024-12-20 10:00 | 21.2 | 55 | 1.9 | 420 | 26 | 30 | 12 | 29.5478 | 0
2024-12-20 11:00 | 22.7 | 46 | 1.19 | 569 | 26 | 30 | 12 | 0 | 0
2024-12-20 12:00 | 23.7 | 38 | 1.55 | 658 | 26 | 30 | 12 | 0 | 0
2024-12-20 13:00 | 24.6 | 30 | 1.68 | 679 | 26 | 30 | 12 | 0 | 0
2024-12-20 14:00 | 25.2 | 25 | 1.44 | 630 | 26 | 30 | 12 | 0 | 0
2024-12-20 15:00 | 25.5 | 23 | 0.56 | 515 | 26 | 30 | 12 | 0 | 1.1076
2024-12-20 16:00 | 24.9 | 27 | 2.33 | 345 | 26 | 30 | 12 | 57.1619 | 0
2024-12-20 17:00 | 22.8 | 51 | 4.63 | 149 | 26 | 30 | 12 | 117.4123 | 0
2024-12-20 18:00 | 21.7 | 51 | 3 | 13 | 26 | 30 | 12 | 111.3032 | 0
2024-12-20 19:00 | 21.1 | 51 | 2.31 | 0 | 26 | 30 | 12 | 100.4821 | 0
2024-12-20 20:00 | 20.5 | 53 | 1.75 | 0 | 26 | 30 | 12 | 87.5279 | 0
2024-12-20 21:00 | 19.7 | 56 | 2.37 | 0 | 26 | 30 | 12 | 106.1897 | 0
2024-12-20 22:00 | 18.8 | 60 | 2.49 | 0 | 26 | 30 | 12 | 111.596 | 0
2024-12-20 23:00 | 18 | 59 | 2.7 | 0 | 26 | 30 | 12 | 122.9932 | 0
2024-12-21 | 16.9 | 60 | 2.58 | 0 | 26 | 30 | 12 | 125.8048 | 0
2024-12-21 01:00 | 15.7 | 64 | 2.1 | 0 | 26 | 30 | 12 | 115.9943 | 0
2024-12-21 02:00 | 14.9 | 67 | 2 | 0 | 26 | 30 | 12 | 115.4732 | 0
2024-12-21 03:00 | 14.4 | 70 | 2.04 | 0 | 26 | 30 | 12 | 117.7749 | 0
2024-12-21 04:00 | 13.9 | 76 | 2.53 | 0 | 26 | 30 | 12 | 132.1874 | 0
2024-12-21 05:00 | 13.8 | 77 | 2.52 | 0 | 26 | 30 | 12 | 131.9147 | 0
2024-12-21 06:00 | 13.3 | 80 | 2.76 | 0 | 26 | 30 | 12 | 140.3414 | 0
2024-12-21 07:00 | 12.8 | 81 | 2.65 | 0 | 26 | 30 | 12 | 139.7083 | 0
2024-12-21 08:00 | 14 | 73 | 1.8 | 55 | 26 | 30 | 12 | 103.2664 | 0
2024-12-21 09:00 | 17.5 | 58 | 1.25 | 232 | 26 | 30 | 12 | 52.2383 | 0
2024-12-21 10:00 | 20.8 | 47 | 1.38 | 417 | 26 | 30 | 12 | 22.9996 | 0
2024-12-21 11:00 | 23.6 | 39 | 2.5 | 563 | 26 | 30 | 12 | 26.0773 | 0
2024-12-21 12:00 | 24.8 | 31 | 3.59 | 651 | 26 | 30 | 12 | 42.8094 | 0
2024-12-21 13:00 | 24.9 | 33 | 5.06 | 669 | 26 | 30 | 12 | 67.9324 | 0
2024-12-21 14:00 | 24.4 | 37 | 5.2 | 613 | 26 | 30 | 12 | 75.1016 | 0
2024-12-21 15:00 | 24 | 38 | 4.95 | 496 | 26 | 30 | 12 | 87.6969 | 0
2024-12-21 16:00 | 23.4 | 42 | 4.14 | 330 | 26 | 30 | 12 | 92.0148 | 0
2024-12-21 17:00 | 22.6 | 49 | 4.21 | 141 | 26 | 30 | 12 | 115.237 | 0
2024-12-21 18:00 | 21.4 | 54 | 3.86 | 13 | 26 | 30 | 12 | 128.744 | 0
2024-12-21 19:00 | 20.6 | 56 | 3.53 | 0 | 26 | 30 | 12 | 127.4896 | 0
2024-12-21 20:00 | 19.8 | 59 | 3.47 | 0 | 26 | 30 | 12 | 129.0943 | 0
2024-12-21 21:00 | 19.1 | 62 | 3.25 | 0 | 26 | 30 | 12 | 126.3297 | 0
2024-12-21 22:00 | 18.6 | 66 | 2.89 | 0 | 26 | 30 | 12 | 117.7818 | 0
2024-12-21 23:00 | 17.8 | 73 | 2.73 | 0 | 26 | 30 | 12 | 113.7584 | 0
2024-12-22 | 17.4 | 76 | 2.98 | 0 | 26 | 30 | 12 | 120.141 | 0
2024-12-22 01:00 | 16.9 | 79 | 3.22 | 0 | 26 | 30 | 12 | 127.077 | 0
2024-12-22 02:00 | 16.3 | 82 | 3.5 | 0 | 26 | 30 | 12 | 135.8763 | 0
2024-12-22 03:00 | 15.7 | 80 | 3.73 | 0 | 26 | 30 | 12 | 148.1166 | 0
2024-12-22 04:00 | 15.2 | 78 | 3.93 | 0 | 26 | 30 | 12 | 159.0021 | 0
2024-12-22 05:00 | 15.1 | 74 | 3.98 | 0 | 26 | 30 | 12 | 164.6392 | 0
2024-12-22 06:00 | 14.6 | 74 | 4.18 | 0 | 26 | 30 | 12 | 173.9596 | 0
2024-12-22 07:00 | 14.1 | 75 | 4.41 | 0 | 26 | 30 | 12 | 183.3141 | 0
2024-12-22 08:00 | 15 | 69 | 4.27 | 54 | 26 | 30 | 12 | 170.1635 | 0
2024-12-22 09:00 | 17.5 | 57 | 3.36 | 229 | 26 | 30 | 12 | 114.6146 | 0
2024-12-22 10:00 | 20.6 | 47 | 4.1 | 412 | 26 | 30 | 12 | 95.7108 | 0
2024-12-22 11:00 | 22.8 | 45 | 3.59 | 527 | 26 | 30 | 12 | 54.1893 | 0
2024-12-22 12:00 | 24 | 42 | 3.49 | 645 | 26 | 30 | 12 | 31.1455 | 0
2024-12-22 13:00 | 24.6 | 39 | 4.23 | 662 | 26 | 30 | 12 | 43.926 | 0
2024-12-22 14:00 | 25.1 | 36 | 5.05 | 567 | 26 | 30 | 12 | 73.9265 | 0
2024-12-22 15:00 | 23.3 | 51 | 6.71 | 221 | 26 | 30 | 12 | 138.6083 | 0
2024-12-22 16:00 | 22.5 | 56 | 6.13 | 258 | 26 | 30 | 12 | 123.6997 | 0
2024-12-22 17:00 | 22.3 | 57 | 5.85 | 138 | 26 | 30 | 12 | 135.6823 | 0
2024-12-22 18:00 | 21.5 | 60 | 4.63 | 13 | 26 | 30 | 12 | 134.688 | 0
2024-12-22 19:00 | 21.1 | 61 | 4.3 | 0 | 26 | 30 | 12 | 132.7089 | 0
2024-12-22 20:00 | 20.5 | 63 | 3.98 | 0 | 26 | 30 | 12 | 129.3915 | 0
2024-12-22 21:00 | 19.9 | 65 | 3.56 | 0 | 26 | 30 | 12 | 123.6635 | 0
2024-12-22 22:00 | 19.1 | 67 | 3.23 | 0 | 26 | 30 | 12 | 120.9306 | 0
2024-12-22 23:00 | 18.3 | 71 | 3.22 | 0 | 26 | 30 | 12 | 123.1482 | 0
2024-12-23 | 17.6 | 74 | 3.44 | 0 | 26 | 30 | 12 | 130.9519 | 0
2024-12-23 01:00 | 17.2 | 73 | 3.94 | 0 | 26 | 30 | 12 | 146.694 | 0
2024-12-23 02:00 | 16.7 | 73 | 3.44 | 0 | 26 | 30 | 12 | 139.1165 | 0
2024-12-23 03:00 | 16.8 | 71 | 2.98 | 0 | 26 | 30 | 12 | 128.6745 | 0
2024-12-23 04:00 | 16.5 | 70 | 3.13 | 0 | 26 | 30 | 12 | 135.4711 | 0
2024-12-23 05:00 | 16.1 | 63 | 2.98 | 0 | 26 | 30 | 12 | 139.8155 | 0
2024-12-23 06:00 | 15.6 | 65 | 2.96 | 0 | 26 | 30 | 12 | 141.0498 | 0
2024-12-23 07:00 | 14.6 | 71 | 3.32 | 0 | 26 | 30 | 12 | 153.4626 | 0
2024-12-23 08:00 | 15.2 | 69 | 3.11 | 48 | 26 | 30 | 12 | 138.4607 | 0
2024-12-23 09:00 | 17.6 | 60 | 2.47 | 218 | 26 | 30 | 12 | 89.0526 | 0
2024-12-23 10:00 | 20.3 | 50 | 2.87 | 400 | 26 | 30 | 12 | 66.508 | 0
2024-12-23 11:00 | 22.1 | 44 | 2.45 | 554 | 26 | 30 | 12 | 29.7782 | 0
2024-12-23 12:00 | 23.2 | 46 | 1.68 | 643 | 26 | 30 | 12 | 0 | 0
2024-12-23 13:00 | 23.8 | 45 | 1.45 | 665 | 26 | 30 | 12 | 0 | 0
2024-12-23 14:00 | 24.3 | 44 | 2.2 | 617 | 26 | 30 | 12 | 2.1754 | 0
2024-12-23 15:00 | 24.4 | 45 | 2.59 | 503 | 26 | 30 | 12 | 24.4963 | 0
2024-12-23 16:00 | 23.9 | 48 | 3 | 324 | 26 | 30 | 12 | 57.0638 | 0
2024-12-23 17:00 | 23.5 | 50 | 3.23 | 149 | 26 | 30 | 12 | 85.779 | 0
2024-12-23 18:00 | 22.1 | 56 | 2.24 | 14 | 26 | 30 | 12 | 86.2702 | 0
2024-12-23 19:00 | 21.1 | 60 | 1.74 | 0 | 26 | 30 | 12 | 79.0718 | 0
2024-12-23 20:00 | 20.5 | 63 | 2.94 | 0 | 26 | 30 | 12 | 107.8313 | 0
2024-12-23 21:00 | 20 | 68 | 2.9 | 0 | 26 | 30 | 12 | 105.8144 | 0
2024-12-23 22:00 | 19.3 | 73 | 2.91 | 0 | 26 | 30 | 12 | 106.6673 | 0
2024-12-23 23:00 | 18.4 | 79 | 2.42 | 0 | 26 | 30 | 12 | 97.5925 | 0
2024-12-24 | 17.7 | 83 | 1.7 | 0 | 26 | 30 | 12 | 82.5671 | 0
2024-12-24 01:00 | 16.9 | 87 | 1.78 | 0 | 26 | 30 | 12 | 86.9665 | 0
2024-12-24 02:00 | 16.2 | 89 | 1.77 | 0 | 26 | 30 | 12 | 89.7468 | 0
2024-12-24 03:00 | 15.6 | 91 | 1.63 | 0 | 26 | 30 | 12 | 88.4669 | 0
2024-12-24 04:00 | 14.9 | 93 | 1.75 | 0 | 26 | 30 | 12 | 94.6953 | 0
2024-12-24 05:00 | 14.8 | 91 | 2.07 | 0 | 26 | 30 | 12 | 104.9966 | 0
2024-12-24 06:00 | 14.2 | 92 | 2.3 | 0 | 26 | 30 | 12 | 114.4355 | 0
2024-12-24 07:00 | 14 | 90 | 2.67 | 0 | 26 | 30 | 12 | 126.9253 | 0
2024-12-24 08:00 | 15.4 | 81 | 2.52 | 50 | 26 | 30 | 12 | 112.4128 | 0
2024-12-24 09:00 | 18.6 | 64 | 1.76 | 222 | 26 | 30 | 12 | 60.5406 | 0
2024-12-24 10:00 | 21.8 | 48 | 1.52 | 404 | 26 | 30 | 12 | 23.6293 | 0
2024-12-24 11:00 | 24.6 | 38 | 2.64 | 544 | 26 | 30 | 12 | 27.0874 | 0
2024-12-24 12:00 | 25.7 | 38 | 2.32 | 628 | 26 | 30 | 12 | 1.726 | 0
2024-12-24 13:00 | 26.4 | 36 | 1.46 | 657 | 26 | 30 | 12 | 0 | 0
2024-12-24 14:00 | 26.8 | 34 | 2.01 | 560 | 26 | 30 | 12 | 2.1096 | 0
2024-12-24 15:00 | 26.3 | 35 | 2.21 | 397 | 26 | 30 | 12 | 30.4177 | 0
2024-12-24 16:00 | 25.4 | 43 | 2.97 | 234 | 26 | 30 | 12 | 64.316 | 0
2024-12-24 17:00 | 24.4 | 50 | 3.29 | 120 | 26 | 30 | 12 | 83.7997 | 0
2024-12-24 18:00 | 22.7 | 62 | 3.12 | 14 | 26 | 30 | 12 | 93.3322 | 0
2024-12-24 19:00 | 22 | 68 | 2.05 | 0 | 26 | 30 | 12 | 74.1353 | 0
2024-12-24 20:00 | 21.1 | 72 | 2.05 | 0 | 26 | 30 | 12 | 76.7711 | 0
2024-12-24 21:00 | 20.6 | 73 | 2.09 | 0 | 26 | 30 | 12 | 80.1118 | 0
2024-12-24 22:00 | 20.3 | 76 | 2.14 | 0 | 26 | 30 | 12 | 80.7708 | 0
2024-12-24 23:00 | 19.8 | 79 | 2.86 | 0 | 26 | 30 | 12 | 96.059 | 0
2024-12-25 | 19.2 | 83 | 2.96 | 0 | 26 | 30 | 12 | 99.1684 | 0
2024-12-25 01:00 | 18.6 | 86 | 2.57 | 0 | 26 | 30 | 12 | 93.7457 | 0
2024-12-25 02:00 | 18.2 | 86 | 2.47 | 0 | 26 | 30 | 12 | 94.718 | 0
2024-12-25 03:00 | 18.2 | 84 | 2.4 | 0 | 26 | 30 | 12 | 94.7574 | 0
2024-12-25 04:00 | 18.2 | 81 | 2.16 | 0 | 26 | 30 | 12 | 91.6224 | 0
2024-12-25 05:00 | 18.5 | 76 | 2.87 | 0 | 26 | 30 | 12 | 109.269 | 0
2024-12-25 06:00 | 18.1 | 79 | 2.53 | 0 | 26 | 30 | 12 | 102.1947 | 0
2024-12-25 07:00 | 18 | 79 | 1.65 | 0 | 26 | 30 | 12 | 81.9102 | 0
2024-12-25 08:00 | 18.8 | 78 | 0.75 | 49 | 26 | 30 | 12 | 47.7692 | 0
2024-12-25 09:00 | 20.7 | 69 | 1.12 | 220 | 26 | 30 | 12 | 30.3937 | 0
2024-12-25 10:00 | 22.4 | 62 | 1.33 | 402 | 26 | 30 | 12 | 6.673 | 0
2024-12-25 11:00 | 23.7 | 52 | 1.41 | 547 | 26 | 30 | 12 | 0 | 0
2024-12-25 12:00 | 24.6 | 43 | 2.06 | 598 | 26 | 30 | 12 | 0.7758 | 0
2024-12-25 13:00 | 25.1 | 39 | 2.5 | 607 | 26 | 30 | 12 | 11.0864 | 0
2024-12-25 14:00 | 25.2 | 39 | 3.1 | 591 | 26 | 30 | 12 | 25.7115 | 0
2024-12-25 15:00 | 24.7 | 41 | 3.8 | 498 | 26 | 30 | 12 | 53.4235 | 0
2024-12-25 16:00 | 23.9 | 44 | 4.22 | 338 | 26 | 30 | 12 | 85.228 | 0
2024-12-25 17:00 | 23.9 | 40 | 3.61 | 152 | 26 | 30 | 12 | 103.8472 | 0
2024-12-25 18:00 | 22.2 | 52 | 2.44 | 15 | 26 | 30 | 12 | 93.8464 | 0
2024-12-25 19:00 | 21.1 | 64 | 1.64 | 0 | 26 | 30 | 12 | 73.818 | 0
2024-12-25 20:00 | 20.5 | 70 | 1.33 | 0 | 26 | 30 | 12 | 65.7509 | 0
2024-12-25 21:00 | 20.2 | 73 | 1.48 | 0 | 26 | 30 | 12 | 69.1335 | 0
2024-12-25 22:00 | 19.9 | 76 | 1.7 | 0 | 26 | 30 | 12 | 73.9583 | 0
2024-12-25 23:00 | 19.3 | 79 | 2.02 | 0 | 26 | 30 | 12 | 82.6686 | 0
2024-12-26 | 18.5 | 82 | 1.98 | 0 | 26 | 30 | 12 | 84.888 | 0
2024-12-26 01:00 | 18 | 83 | 1.9 | 0 | 26 | 30 | 12 | 85.5627 | 0
2024-12-26 02:00 | 17.1 | 86 | 2.57 | 0 | 26 | 30 | 12 | 105.0267 | 0
2024-12-26 03:00 | 16 | 90 | 2.82 | 0 | 26 | 30 | 12 | 116.0713 | 0
2024-12-26 04:00 | 15.4 | 90 | 2.44 | 0 | 26 | 30 | 12 | 111.2595 | 0
2024-12-26 05:00 | 15.3 | 86 | 2.21 | 0 | 26 | 30 | 12 | 108.4601 | 0
2024-12-26 06:00 | 15.5 | 85 | 2.15 | 0 | 26 | 30 | 12 | 106.2 | 0
2024-12-26 07:00 | 15.5 | 85 | 2.24 | 0 | 26 | 30 | 12 | 108.5813 | 0
2024-12-26 08:00 | 16.8 | 77 | 2.1 | 44 | 26 | 30 | 12 | 95.7996 | 0
2024-12-26 09:00 | 19.8 | 64 | 1.14 | 204 | 26 | 30 | 12 | 39.7622 | 0
2024-12-26 10:00 | 22.2 | 56 | 0.97 | 385 | 26 | 30 | 12 | 4.1712 | 0
2024-12-26 11:00 | 23.7 | 52 | 1.8 | 481 | 26 | 30 | 12 | 7.3124 | 0
2024-12-26 12:00 | 24.4 | 48 | 2.07 | 568 | 26 | 30 | 12 | 1.2068 | 0
2024-12-26 13:00 | 25.3 | 44 | 2.25 | 648 | 26 | 30 | 12 | 0 | 0
2024-12-26 14:00 | 25.6 | 43 | 3.04 | 608 | 26 | 30 | 12 | 13.755 | 0
2024-12-26 15:00 | 25.3 | 46 | 3.65 | 459 | 26 | 30 | 12 | 43.136 | 0
2024-12-26 16:00 | 24.4 | 51 | 3.85 | 323 | 26 | 30 | 12 | 65.0218 | 0
2024-12-26 17:00 | 23.2 | 61 | 4.21 | 152 | 26 | 30 | 12 | 90.1327 | 0
2024-12-26 18:00 | 21.9 | 72 | 3.49 | 16 | 26 | 30 | 12 | 94.2445 | 0
2024-12-26 19:00 | 21.3 | 74 | 2.67 | 0 | 26 | 30 | 12 | 85.3241 | 0
2024-12-26 20:00 | 20.7 | 77 | 2.4 | 0 | 26 | 30 | 12 | 82.1588 | 0
2024-12-26 21:00 | 19.8 | 79 | 2.09 | 0 | 26 | 30 | 12 | 80.8176 | 0
2024-12-26 22:00 | 19.3 | 79 | 1.84 | 0 | 26 | 30 | 12 | 78.7187 | 0
2024-12-26 23:00 | 18.6 | 79 | 2.33 | 0 | 26 | 30 | 12 | 94.1911 | 0
2024-12-27 | 17.5 | 83 | 2.55 | 0 | 26 | 30 | 12 | 103.9005 | 0
2024-12-27 01:00 | 16.5 | 84 | 2.34 | 0 | 26 | 30 | 12 | 105.2097 | 0
2024-12-27 02:00 | 16 | 85 | 2.52 | 0 | 26 | 30 | 12 | 112.406 | 0
2024-12-27 03:00 | 15.5 | 87 | 2.8 | 0 | 26 | 30 | 12 | 121.5249 | 0
2024-12-27 04:00 | 14.9 | 90 | 2.47 | 0 | 26 | 30 | 12 | 115.4571 | 0
2024-12-27 05:00 | 14.8 | 90 | 2.41 | 0 | 26 | 30 | 12 | 114.5769 | 0
2024-12-27 06:00 | 14.7 | 90 | 2.85 | 0 | 26 | 30 | 12 | 126.5923 | 0
2024-12-27 07:00 | 14.5 | 89 | 2.85 | 0 | 26 | 30 | 12 | 128.7417 | 0
2024-12-27 08:00 | 15.8 | 81 | 2.52 | 48 | 26 | 30 | 12 | 110.005 | 0
2024-12-27 09:00 | 18.9 | 66 | 2.07 | 220 | 26 | 30 | 12 | 65.9646 | 0
2024-12-27 10:00 | 22.2 | 51 | 1.66 | 407 | 26 | 30 | 12 | 22.8511 | 0
2024-12-27 11:00 | 24.5 | 43 | 2.57 | 556 | 26 | 30 | 12 | 18.5937 | 0
2024-12-27 12:00 | 25.9 | 37 | 3.1 | 648 | 26 | 30 | 12 | 15.9867 | 0
2024-12-27 13:00 | 27.3 | 30 | 3.11 | 672 | 26 | 30 | 12 | 14.0865 | 0
2024-12-27 14:00 | 28.3 | 22 | 2.86 | 623 | 26 | 30 | 12 | 21.5442 | 0
2024-12-27 15:00 | 28 | 22 | 1.92 | 512 | 26 | 30 | 12 | 14.1005 | 0
2024-12-27 16:00 | 26.9 | 30 | 3.31 | 347 | 26 | 30 | 12 | 64.9214 | 0
2024-12-27 17:00 | 25.2 | 43 | 4.68 | 156 | 26 | 30 | 12 | 108.3602 | 0
2024-12-27 18:00 | 23.4 | 63 | 4.41 | 16 | 26 | 30 | 12 | 106.4486 | 0
2024-12-27 19:00 | 22.6 | 60 | 3.1 | 0 | 26 | 30 | 12 | 98.057 | 0
2024-12-27 20:00 | 21.6 | 59 | 2.56 | 0 | 26 | 30 | 12 | 95.6815 | 0
2024-12-27 21:00 | 21.1 | 54 | 3.05 | 0 | 26 | 30 | 12 | 115.2121 | 0
2024-12-27 22:00 | 20.3 | 55 | 3.62 | 0 | 26 | 30 | 12 | 133.0157 | 0
2024-12-27 23:00 | 19.5 | 61 | 3.52 | 0 | 26 | 30 | 12 | 130.4353 | 0
2024-12-28 | 18.6 | 67 | 2.92 | 0 | 26 | 30 | 12 | 117.6053 | 0
2024-12-28 01:00 | 17.8 | 67 | 2.8 | 0 | 26 | 30 | 12 | 120.3638 | 0
2024-12-28 02:00 | 17 | 68 | 2.36 | 0 | 26 | 30 | 12 | 113.4002 | 0
2024-12-28 03:00 | 16.2 | 68 | 2.35 | 0 | 26 | 30 | 12 | 117.9913 | 0
2024-12-28 04:00 | 15.6 | 65 | 2.67 | 0 | 26 | 30 | 12 | 132.8075 | 0
2024-12-28 05:00 | 15 | 66 | 2.47 | 0 | 26 | 30 | 12 | 129.9064 | 0
2024-12-28 06:00 | 14.3 | 67 | 2.41 | 0 | 26 | 30 | 12 | 131.5355 | 0
2024-12-28 07:00 | 13.7 | 69 | 2.41 | 0 | 26 | 30 | 12 | 133.8046 | 0
2024-12-28 08:00 | 14.7 | 65 | 1.88 | 47 | 26 | 30 | 12 | 107.3669 | 0
2024-12-28 09:00 | 18.1 | 52 | 1.2 | 219 | 26 | 30 | 12 | 52.6016 | 0
2024-12-28 10:00 | 22.1 | 41 | 0.47 | 404 | 26 | 30 | 12 | 0 | 0
2024-12-28 11:00 | 24.8 | 33 | 0.21 | 552 | 26 | 30 | 12 | 0 | 9.4928
2024-12-28 12:00 | 26.4 | 29 | 0.5 | 644 | 26 | 30 | 12 | 0 | 24.0922
2024-12-28 13:00 | 27 | 28 | 2.1 | 667 | 26 | 30 | 12 | 0 | 0
2024-12-28 14:00 | 26.9 | 31 | 3.2 | 622 | 26 | 30 | 12 | 23.8441 | 0
2024-12-28 15:00 | 26.5 | 33 | 4.05 | 510 | 26 | 30 | 12 | 55.9465 | 0
2024-12-28 16:00 | 25.2 | 39 | 4.66 | 346 | 26 | 30 | 12 | 89.7534 | 0
2024-12-28 17:00 | 24.1 | 49 | 3.79 | 156 | 26 | 30 | 12 | 92.1398 | 0
2024-12-28 18:00 | 22.5 | 65 | 2.77 | 17 | 26 | 30 | 12 | 84.7491 | 0
2024-12-28 19:00 | 21.7 | 62 | 2.58 | 0 | 26 | 30 | 12 | 92.4514 | 0
2024-12-28 20:00 | 20.9 | 68 | 2.58 | 0 | 26 | 30 | 12 | 92.4327 | 0
2024-12-28 21:00 | 20.4 | 76 | 1.88 | 0 | 26 | 30 | 12 | 74.759 | 0
2024-12-28 22:00 | 20.2 | 75 | 0.95 | 0 | 26 | 30 | 12 | 55.1566 | 0
2024-12-28 23:00 | 19.9 | 75 | 0.76 | 0 | 26 | 30 | 12 | 51.3712 | 0
2024-12-29 | 19.3 | 77 | 0.88 | 0 | 26 | 30 | 12 | 56.3844 | 0
2024-12-29 01:00 | 18.6 | 79 | 1.44 | 0 | 26 | 30 | 12 | 73.3538 | 0
2024-12-29 02:00 | 17.4 | 83 | 2.41 | 0 | 26 | 30 | 12 | 101.4035 | 0
2024-12-29 03:00 | 16.5 | 85 | 2.55 | 0 | 26 | 30 | 12 | 109.6207 | 0
2024-12-29 04:00 | 15.7 | 88 | 2.69 | 0 | 26 | 30 | 12 | 116.6533 | 0
2024-12-29 05:00 | 15.3 | 83 | 2.1 | 0 | 26 | 30 | 12 | 107.2437 | 0
2024-12-29 06:00 | 14.6 | 84 | 2.49 | 0 | 26 | 30 | 12 | 121.7321 | 0
2024-12-29 07:00 | 14.1 | 85 | 2.83 | 0 | 26 | 30 | 12 | 133.7341 | 0
2024-12-29 08:00 | 15.3 | 78 | 2.96 | 45 | 26 | 30 | 12 | 127.4613 | 0
2024-12-29 09:00 | 18.7 | 66 | 2.67 | 209 | 26 | 30 | 12 | 83.5853 | 0
2024-12-29 10:00 | 21.8 | 57 | 2.03 | 392 | 26 | 30 | 12 | 31.3972 | 0
2024-12-29 11:00 | 23.9 | 47 | 2.34 | 541 | 26 | 30 | 12 | 14.896 | 0
2024-12-29 12:00 | 25 | 44 | 2.51 | 623 | 26 | 30 | 12 | 3.8443 | 0
2024-12-29 13:00 | 25.5 | 42 | 3.1 | 639 | 26 | 30 | 12 | 12.8858 | 0
2024-12-29 14:00 | 25.7 | 42 | 3.73 | 593 | 26 | 30 | 12 | 29.585 | 0
2024-12-29 15:00 | 25.4 | 43 | 3.8 | 497 | 26 | 30 | 12 | 44.6863 | 0
2024-12-29 16:00 | 24.8 | 46 | 3.76 | 332 | 26 | 30 | 12 | 66.4727 | 0
2024-12-29 17:00 | 23.8 | 56 | 3.36 | 141 | 26 | 30 | 12 | 78.9551 | 0
2024-12-29 18:00 | 21.9 | 73 | 2.43 | 17 | 26 | 30 | 12 | 75.0813 | 0
2024-12-29 19:00 | 21 | 82 | 2.31 | 0 | 26 | 30 | 12 | 73.8734 | 0
2024-12-29 20:00 | 20.5 | 87 | 2.13 | 0 | 26 | 30 | 12 | 70.3549 | 0
2024-12-29 21:00 | 20 | 89 | 2.2 | 0 | 26 | 30 | 12 | 73.6951 | 0
2024-12-29 22:00 | 19.4 | 89 | 2.08 | 0 | 26 | 30 | 12 | 75.9126 | 0
2024-12-29 23:00 | 18.9 | 89 | 2.08 | 0 | 26 | 30 | 12 | 79.4508 | 0
2024-12-30 | 18.7 | 89 | 1.95 | 0 | 26 | 30 | 12 | 78.1992 | 0
2024-12-30 01:00 | 18.7 | 88 | 1.56 | 0 | 26 | 30 | 12 | 70.5559 | 0
2024-12-30 02:00 | 18.2 | 89 | 2.07 | 0 | 26 | 30 | 12 | 84.0943 | 0
2024-12-30 03:00 | 17.5 | 91 | 2.95 | 0 | 26 | 30 | 12 | 106.122 | 0
2024-12-30 04:00 | 16.2 | 96 | 3.02 | 0 | 26 | 30 | 12 | 114.3856 | 0
2024-12-30 05:00 | 16.2 | 94 | 2.23 | 0 | 26 | 30 | 12 | 98.0987 | 0
2024-12-30 06:00 | 16 | 93 | 2.44 | 0 | 26 | 30 | 12 | 105.0789 | 0
2024-12-30 07:00 | 15.5 | 94 | 2.48 | 0 | 26 | 30 | 12 | 108.9505 | 0
2024-12-30 08:00 | 16.4 | 90 | 2.39 | 43 | 26 | 30 | 12 | 97.2688 | 0
2024-12-30 09:00 | 19.5 | 75 | 2.11 | 197 | 26 | 30 | 12 | 59.6728 | 0
2024-12-30 10:00 | 22.4 | 64 | 1.84 | 347 | 26 | 30 | 12 | 23.8418 | 0
2024-12-30 11:00 | 24 | 60 | 1 | 491 | 26 | 30 | 12 | 0 | 0
2024-12-30 12:00 | 25.2 | 56 | 0.43 | 598 | 26 | 30 | 12 | 0 | 26.3851
2024-12-30 13:00 | 26.2 | 50 | 1.42 | 601 | 26 | 30 | 12 | 0 | 0
2024-12-30 14:00 | 26.5 | 48 | 1.82 | 531 | 26 | 30 | 12 | 0 | 0
2024-12-30 15:00 | 26.4 | 50 | 2.77 | 446 | 26 | 30 | 12 | 15.0533 | 0
2024-12-30 16:00 | 25.6 | 54 | 3.86 | 323 | 26 | 30 | 12 | 49.3433 | 0
2024-12-30 17:00 | 24 | 66 | 3.93 | 145 | 26 | 30 | 12 | 71.1133 | 0
2024-12-30 18:00 | 22.4 | 81 | 2.91 | 18 | 26 | 30 | 12 | 69.9661 | 0
2024-12-30 19:00 | 21.7 | 89 | 2.48 | 0 | 26 | 30 | 12 | 64.3796 | 0
2024-12-30 20:00 | 21.2 | 90 | 1.39 | 0 | 26 | 30 | 12 | 51.0523 | 0
2024-12-30 21:00 | 20.9 | 89 | 0.96 | 0 | 26 | 30 | 12 | 45.6311 | 0
2024-12-30 22:00 | 19.8 | 94 | 2.5 | 0 | 26 | 30 | 12 | 76.1581 | 0
2024-12-30 23:00 | 19 | 96 | 2.22 | 0 | 26 | 30 | 12 | 76.1998 | 0
2024-12-31 | 18.3 | 96 | 1.62 | 0 | 26 | 30 | 12 | 69.6308 | 0
2024-12-31 01:00 | 18.1 | 95 | 1.7 | 0 | 26 | 30 | 12 | 73.1326 | 0
2024-12-31 02:00 | 18 | 94 | 1.59 | 0 | 26 | 30 | 12 | 71.98 | 0
2024-12-31 03:00 | 17.6 | 95 | 1.28 | 0 | 26 | 30 | 12 | 66.7487 | 0
2024-12-31 04:00 | 17.2 | 97 | 1.07 | 0 | 26 | 30 | 12 | 62.8567 | 0
2024-12-31 05:00 | 18 | 97 | 1.06 | 0 | 26 | 30 | 12 | 58.6615 | 0
2024-12-31 06:00 | 17.7 | 97 | 2.19 | 0 | 26 | 30 | 12 | 84.6164 | 0
2024-12-31 07:00 | 17.3 | 97 | 1.83 | 0 | 26 | 30 | 12 | 79.8541 | 0
2024-12-31 08:00 | 17.5 | 96 | 1.59 | 42 | 26 | 30 | 12 | 68.2228 | 0
2024-12-31 09:00 | 19.8 | 84 | 1.57 | 169 | 26 | 30 | 12 | 43.8075 | 0
2024-12-31 10:00 | 22.3 | 71 | 1.41 | 335 | 26 | 30 | 12 | 12.0427 | 0
2024-12-31 11:00 | 24.2 | 64 | 1.54 | 502 | 26 | 30 | 12 | 0 | 0
2024-12-31 12:00 | 25.7 | 55 | 1.42 | 614 | 26 | 30 | 12 | 0 | 0
2024-12-31 13:00 | 26.8 | 47 | 1.58 | 642 | 26 | 30 | 12 | 0 | 0
2024-12-31 14:00 | 27.5 | 42 | 2.15 | 560 | 26 | 30 | 12 | 0 | 0
2024-12-31 15:00 | 27.4 | 44 | 2.66 | 493 | 26 | 30 | 12 | 7.8519 | 0
2024-12-31 16:00 | 26.3 | 53 | 3.68 | 299 | 26 | 30 | 12 | 45.0346 | 0
2024-12-31 17:00 | 25.2 | 60 | 3.72 | 148 | 26 | 30 | 12 | 65.1076 | 0
2024-12-31 18:00 | 23.3 | 67 | 2.76 | 18 | 26 | 30 | 12 | 75.8244 | 0
2024-12-31 19:00 | 22.2 | 75 | 1.43 | 0 | 26 | 30 | 12 | 55.5334 | 0
2024-12-31 20:00 | 21.8 | 78 | 0.47 | 0 | 26 | 30 | 12 | 38.1693 | 0
2024-12-31 21:00 | 21.2 | 80 | 0.51 | 0 | 26 | 30 | 12 | 39.8764 | 0
2024-12-31 22:00 | 20.3 | 82 | 1.74 | 0 | 26 | 30 | 12 | 68.289 | 0
2024-12-31 23:00 | 19.2 | 82 | 2.92 | 0 | 26 | 30 | 12 | 99.3297 | 0