Pressurization Systems

Closed-circuit expansion, pressurization & makeup design

| Project Information |  |
| --- | --- |
| Project Name | Marina Commercial Tower |
| Project No. | MCT-2026-MEP-001 |
| Revision | P2 |
| Client | — |
| Prepared by | Hussein Ragab |
| Checked by | — |
| Date | 2026-10-20 |

Values in this report are displayed in SI (metric) units.

# 1.  Methodology

Integrated pressurization scheme: vessel/station sizing, make-up provisions and safety-valve selection assembled from the governing methods listed in the references.

# 2.  Inputs

| Parameter | Value |
| --- | --- |
| Pressure maintenance | vessel |
| Vessel sizing method | en12828 |
| Vessel: System water content | 40000.0 L |
| Vessel: Maximum operating temperature | 46.0 °C |
| Vessel: Lowest system temperature | 6.0 °C |
| Vessel: Static height | 8.0 m |
| Vessel: Antifreeze content | 0 |
| Vessel: Site altitude (km) | 0 |
| Vessel: Fill temperature | 25.0 °C |
| Vessel: Safety valve set pressure | 3.00 bar |
| Vessel: Safety valve class | DGH |
| Vessel: Expansion coefficient basis | EN 12828 Formula (D.1) water-density ratio |
| Makeup: System water content | 40000.0 L |
| Makeup: Minimum operating pressure | 0.99 bar |
| Makeup: Make-up supply pressure | 3.00 bar |
| Makeup: Pini | 1.37 bar |
| Application | Chilled water |

# 3.  Assumptions

Internal calculations are performed in SI (bar gauge, litres, degC); IP values are display conversions only.

Standards-native quantities (DN sizes, valve classes) are never unit-converted.

Printed clause values govern; where a standard's own worked examples use different margins (BS 7074 Ps 0.3 vs 0.35 bar; SV margin 0.3 vs 0.5 bar) the margin is an editable input and the value used is recorded in the steps below.

Tool scope is capped at 120 degC flow (no HTHW gas-cushion sizing).

# 4.  Step-by-Step Calculation

Step 1: Expansion coefficient

Formula: e = 1 - rho(tmax)/rho(tmin)

Substitution: tmin = 6 degC; tmax = 46 degC

Result: e = 0.01010

Note: Source: EN 12828 Formula (D.1) with printed steam-table densities

Step 2: Expansion volume

Formula: Vex = VSystem x e

Substitution: VSystem = 40000 L; e = 0.01010

Result: Vex = 403.8 L

Note: Source: EN 12828 Annex D (D.2 lead-in)

Step 3: Minimum operating pressure (= vessel pre-charge)

Formula: p0 = pst + pv + 0.2

Substitution: pst = 0.784 bar; pv = 0.000 bar

Result: p0 = 0.984 bar

Note: Source: EN 12828 D.1 e): p0 >= pst + pv, +0.2 bar recommended; suction-side pressurisation, safety valve at the vessel level assumed (EN 12828 D.1 b), e), h))

Step 4: Final pressure

Formula: pfin = psv - max(0.5 bar, 10 % x psv)

Substitution: psv = 3 bar; closing difference 0.50 bar (Annex E minimum 0.30 bar, E.5.6)

Result: pfin = 2.500 bar

Note: Source: pfin = psv - max(0.5 bar, 10 % psv): Reflex closing-pressure rule (Reflex Solutions Guide p. 95; Reflex Product Guide p. 10); EN 12828 D.1 g), Annex E minimum 0.30 bar (E.5.6)

Step 5: Minimum nominal volume (diaphragm vessel)

Formula: VN,min = (Vex + Vwr,min) x (pfin + 1)/(pfin - p0)

Substitution: Vex = 403.8 L; Vwr = 200.0 L; pfin = 2.500 bar; p0 = 0.984 bar

Result: VN,min = 1394.4 L

Note: Source: EN 12828 Formula (D.2)

Step 6: Nominal volume bound from the initial-pressure condition

Formula: VN >= Vex (pfin+1)(p0+1.3) / [(p0+1)(pfin-p0-0.3)]

Substitution: Vex = 403.8 L; pfin = 2.500; p0 = 0.984

Result: VN >= 1338.5 L

Note: Source: EN 12828 Formulae (D.6)/(D.7), solved for VN

Step 7: Water reserve for the selected vessel

Formula: Vwr >= 20 % VN (VN <= 15 L) ¦ >= 0.5 % VSystem, min 3 L (VN > 15 L)

Substitution: VN = 1500 L; VSystem = 40000 L

Result: Vwr = 200.0 L

Note: Source: EN 12828 Annex D (D.2 water-reserve rules)

Step 8: Initial pressure for the selected vessel

Formula: pini = (pfin+1) / (1 + (Vex/VN)(pfin+1)/(p0+1)) - 1

Substitution: Vex = 403.8 L; VN = 1500 L

Result: pini = 1.373 bar

Note: Source: EN 12828 Formula (D.6)

Step 9: Filling pressure

Formula: pfil = VN(p0+1) / (VN - VSystem(1 - rho_fil/rho_min) - Vwr) - 1

Substitution: VN = 1500 L; fill at 25 degC, tmin 6 degC

Result: pfil = 1.517 bar

Note: Source: EN 12828 Formula (D.8) — density of water as printed

Step 10: Make-up loss allowance

Formula: V_loss = 0.5 % x VSystem

Substitution: VSystem = 40000 L

Result: V_loss = 200.0 L

Note: Source: Reflex Solutions Guide p. 131 (7.5.2)

Step 11: Fill connection size

Formula: minimum fill pipe by system volume

Substitution: VSystem = 40000 L

Result: fill pipe >= 50 mm

Note: Source: CIBSE B1 Table 1.A1.6 (basis: 1.3 bar at the top of the system)

Step 12: Make-up switching (static vessel)

Formula: cut-out = pini (vessel initial pressure); cut-in = cut-out - 0.2

Substitution: pini = 1.37 bar; p0 = 0.98 bar

Result: ON = 1.17 bar; OFF = 1.37 bar

Note: Source: Vessel initial pressure (EN 12828 D.6) and Reflex Fig. 90 gap

Step 13: Make-up arrangement

Formula: pump-less requires supply >= p0 + 1.3 bar at the device

Substitution: p0 = 0.98 bar

Result: direct (pump-less) make-up from the supply

Note: Source: Reflex p. 141

# 5.  Results

| Parameter | Value |
| --- | --- |
| Vessel: Expansion coefficient | 0.010096 |
| Vessel: Expansion volume | 403.8 L |
| Vessel: Water reserve | 200.0 L |
| Vessel: Required nominal volume Vn | 1394.4 L |
| Vessel: Vn selected | 1500.0 L |
| Vessel: Minimum operating pressure | 0.99 bar |
| Vessel: Vessel precharge | 0.99 bar |
| Vessel: Pini | 1.37 bar |
| Vessel: Pfil | 1.52 bar |
| Vessel: Pfin | 2.50 bar |
| Vessel: Safety valve set pressure | 3.00 bar |
| Vessel: Connection dn | 32 |
| Makeup: Loss allowance | 200.0 L |
| Makeup: Fill connection mm | 50 |
| Make-up ON (refill) pressure | 1.17 bar |
| Make-up OFF pressure | 1.37 bar |
| Makeup: Pumpless min supply | 2.29 bar |
| Makeup: Arrangement | direct (pump-less) make-up from the supply |

⚠ Advisory

• [vessel] Assumed: the vessel connects on the SUCTION side of the circulation pump and the safety valve sits at the vessel level (EN 12828 D.1 b), e), h)). For a connection on the pump discharge side, D.1 e) requires the pump pressure increase to be added to p0; for a safety valve above or below the vessel, D.1 h) requires the height difference to be taken into account in pfin. Neither is modelled here - check them if the layout differs.

• [vessel] Selected VN 1500 L is the smallest size on the tool's TRADE ladder (a convenience list, NOT standards data) at or above the required 1394.4 L — confirm against the vendor catalogue (suggestions below) or enter the chosen vessel as Selected VN.

• [vessel] Minimum vessel water connection DN 32 (EN 13831 Table 2); actual vessel volume may be as little as 95 % of nominal (EN 13831 6.1.7).

• [makeup] Connect make-up to potable water only through the required system separation/backflow prevention (EN 1717 / EN 806-2; EN 12828 4.7.5). Fit a water meter in the fill/make-up line for systems > 50 kW and monitor make-up quantity against corrosion/scaling (Reflex p. 146; ASHRAE Ch. 13 p. 13.21).

• [makeup] Water quality: VDI 2035 sheet 1 (not held - not verified) hardness limits apply per generator capacity and specific volume, as reprinted in the Reflex Solutions Guide Fig. 104 (p. 146); that reprint shows a suspected misprint (Group 2 middle column) — verify against the printed VDI 2035 before specifying softening (see METHODOLOGY_PROPOSAL.md #3).

# R.  Reference Standards

BS EN 12828:2012+A1:2014 — Heating systems in buildings — design for water-based heating systems (Annex D, Annex E)

BS 7074:1989 Parts 1-3 — Expansion vessels and ancillary equipment for sealed water systems

BS EN 13831:2007 — Closed expansion vessels with built-in diaphragm

ASHRAE Handbook 2020, Ch. 13 — HVAC Systems and Equipment (SI) — Hydronic Heating and Cooling (cross-check method)

CIBSE Guide B1:2016 — Heating — system pressurisation guidance

Reflex Solutions Guide — Pressure maintenance planning (vendor methodology, cited as guidance; incl. its reprint of the DIN 1988 T5 booster-vessel forms - DIN 1988 T5 itself not held - not verified)

BS EN 806-2:2005 — Specifications for installations conveying water for human consumption — clause 15.3 pressure boosters (booster-tank mode frame)

BS EN 806-3:2006 — Pipe sizing, simplified method — peak-flow basis for the booster-tank maximum flow input