## Equipment Schedule
Pressurization Systems — Equipment Schedule
Project: Marina Commercial Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: - ¦ By: Hussein Ragab ¦ Chkd: - ¦ Rev: P2 ¦ Date: 2026-10-20
Unit system: SI ¦ Vendor nameplate data (volume, PS, pre-charge) is catalogue-native and is never unit-converted
Tag | Equipment | Description | Nominal volume | Pre-charge p0 (computed) | Key pressures & duty | Vendor selection (catalogue nameplate) | Sizing basis
EV-01 | Expansion vessel | Closed diaphragm expansion vessel to BS EN 13831, water connection DN 32 | 1500.0 L selected (1394.4 L required) | 0.99 | p_ini 1.37 bar; p_fil 1.52 bar; p_fin 2.50 bar; p_SV 3.00 bar; expansion 403.8 L + reserve 200.0 L | Reflex G 1500 — 1500 L nominal, PS 6 bar, pre-charge 3.5 bar, conn DN 65/PN 6 — catalogue nameplate | BS EN 12828:2012+A1:2014 Annex D
MU-01 | Make-up set | direct (pump-less) make-up from the supply | loss allowance 200.0 L | — | fill connection DN 50; supply 3.00 bar; cut-in 1.17 bar; cut-out 1.37 bar; pump-less threshold 2.29 bar | system separation / backflow prevention to EN 1717 — select with the water authority | Reflex Solutions Guide pp. 131/141; CIBSE Guide B1:2016 Table 1.A1.6
Advisories — check before issue
⚠ [vessel] Assumed: the vessel connects on the SUCTION side of the circulation pump and the safety valve sits at the vessel level (EN 12828 D.1 b), e), h)). For a connection on the pump discharge side, D.1 e) requires the pump pressure increase to be added to p0; for a safety valve above or below the vessel, D.1 h) requires the height difference to be taken into account in pfin. Neither is modelled here - check them if the layout differs.
⚠ [vessel] Selected VN 1500 L is the smallest size on the tool's TRADE ladder (a convenience list, NOT standards data) at or above the required 1394.4 L — confirm against the vendor catalogue (suggestions below) or enter the chosen vessel as Selected VN.
⚠ [vessel] Minimum vessel water connection DN 32 (EN 13831 Table 2); actual vessel volume may be as little as 95 % of nominal (EN 13831 6.1.7).
⚠ [makeup] Connect make-up to potable water only through the required system separation/backflow prevention (EN 1717 / EN 806-2; EN 12828 4.7.5). Fit a water meter in the fill/make-up line for systems > 50 kW and monitor make-up quantity against corrosion/scaling (Reflex p. 146; ASHRAE Ch. 13 p. 13.21).
⚠ [makeup] Water quality: VDI 2035 sheet 1 (not held - not verified) hardness limits apply per generator capacity and specific volume, as reprinted in the Reflex Solutions Guide Fig. 104 (p. 146); that reprint shows a suspected misprint (Group 2 middle column) — verify against the printed VDI 2035 before specifying softening (see METHODOLOGY_PROPOSAL.md #3).
Reference |  | Application
BS EN 12828:2012+A1:2014 |  | Heating systems in buildings — design for water-based heating systems (Annex D, Annex E)
BS 7074:1989 Parts 1-3 |  | Expansion vessels and ancillary equipment for sealed water systems
BS EN 13831:2007 |  | Closed expansion vessels with built-in diaphragm
ASHRAE Handbook 2020, Ch. 13 |  | HVAC Systems and Equipment (SI) — Hydronic Heating and Cooling (cross-check method)
CIBSE Guide B1:2016 |  | Heating — system pressurisation guidance
Reflex Solutions Guide |  | Pressure maintenance planning (vendor methodology, cited as guidance; incl. its reprint of the DIN 1988 T5 booster-vessel forms - DIN 1988 T5 itself not held - not verified)
BS EN 806-2:2005 |  | Specifications for installations conveying water for human consumption — clause 15.3 pressure boosters (booster-tank mode frame)
BS EN 806-3:2006 |  | Pipe sizing, simplified method — peak-flow basis for the booster-tank maximum flow input