Stairwell Pressurization Design Report

Stairwell Pressurization System ¦ NFPA 92 / IBC 909

Smoke Control ¦ Location: Dubai, United Arab Emirates

| Project Information |  |
| --- | --- |
| Project Name | Test Tower |
| Project No. | MCT-2026-MEP-001 |
| Revision | P2 |
| Client | Test Dev |
| Prepared by | Hussein Ragab |
| Checked by | Principal MEP Review |
| Date | 2026-09-02 |

Values in this report are displayed in SI (metric) units.

# 1.  Methodology & Standards

| Reference | Application |
| --- | --- |
| NFPA 92 (2024) — Smoke Control Systems | Table 4.4.2.1.1 minimum design ΔP: 12.5 Pa (0.05 in. w.g.) for sprinklered (AS) buildings any ceiling height; 25 Pa (0.10 in. w.g.) non-sprinklered at 2.7 m ceiling. Evaluates stack, wind and HVAC interaction. |
| IBC # 909.6 / # 909.20.5 — Smokeproof Enclosures | Requires rational analysis by a licensed professional. # 909.20.5 stairway pressurization alternative: shaft held at 25–87 Pa (0.10–0.35 in. w.g.) with all doors closed. |
| NFPA 101 # 7.2.1.4.5 — Door Operating Force | Maximum force to set a door in motion: 133 N (30 lbf). Typical closer bias: 67 N. |
| EN 12101-13:2022 — Pressure Differential Systems (design) | Current European design standard (EN 12101-6 was reissued in 2022 as a kits/product specification). Table 1: door force ≤ 100 N; ΔP ≥ 30 Pa; air velocity ≥ 1 m/s (Class 1) or ≥ 2 m/s (Class 2). |
| BS EN 12101-6:2005 # 4.2 — Pressure-Differential Systems (superseded) | Legacy Class A basis (means of escape, all doors closed): ΔP ≥ 50 Pa; door force ≤ 100 N (governs max ΔP); flow at open door ≥ 0.75 m/s. Retained for projects designed to the 2005 edition. |
| ASHRAE Handbook — Fundamentals (Ch. 14 & 16) | ASHRAE 1%/99% percentile methodology for design outdoor temperatures; stack-effect theory. |
| Klote & Milke — Principles of Smoke Management (SFPE) | K_s = 3460 Pa·K (SI form of 7.64 in.wg·°R/ft), C_d = 0.839 SI leakage discharge coefficient, 1.15 open-door turbulence factor, and the NFPA 92 linear pressure-profile model used throughout this report. |
| Manual design temperatures (user-specified) | Winter / summer design temperatures entered by the engineer (1 % / 99 % annual-percentile convention, ASHRAE Ch. 14); no weather-archive fetch was used for this calculation. |
| Local code adoption | Confirm the locally adopted editions and amendments of the standards above with the Authority Having Jurisdiction (AHJ). |
| Selected design basis for this report | NFPA 92 / IBC 909 (NFPA 92 # 4.4.2.1 + IBC # 909.20.5 + NFPA 101 # 7.2.1.4) — min ΔP = 25 Pa, max ΔP = 87 Pa, max door force = 133 N. |

# 2.  Design Inputs

| Parameter | Value |
| --- | --- |
| Location | Dubai, United Arab Emirates |
| Design basis | NFPA 92 / IBC 909 |
| Stairwell conditioning | Air Conditioned |
| Internal setpoint | 24.0 °C |
| Design temperature source | Manual design temperatures (user-specified) |
| Winter design temperature (1 %) | 12.0 °C |
| Summer design temperature (99 %) | 46.0 °C |
| Number of floors | 41 |
| Stairwell length | 5.4 m |
| Stairwell width | 2.6 m |
| Total stairwell height | 129.3 m |
| Wall leakage tightness | Tight (ratio = 1.40e-05 m²/m²) |
| Floor/Ceiling leakage tightness | Average (ratio = 5.20e-05 m²/m²) |
| Effective minimum ΔP | 25.0 Pa |
| Max open-door velocity | 1.00 m/s |
| Door closer opening force (F_closer) | 45 N |
| Safety margin | 10 % |
| Door Type 1 | Qty 41, 0.9 m × 2.1 m, crack 2.0 mm, open in fire: 3 |
| Door Type 2 | Qty 4, 0.9 m × 2.1 m, crack 2.0 mm, open in fire: 0 |

# 3.  Design Assumptions

Manual design temperatures (user-specified); the winter / summer values represent the 1 % / 99 % annual design conditions (ASHRAE Ch. 14 convention).

Leakage discharge coefficient C_d = 0.839 (NFPA 92 SI form; equivalent to C_d approx. 0.65 with ρ_air = 1.2 kg/m³).

Open-door turbulence factor = 1.15 — a conservative tool allowance on the open-door airflow term; NFPA 92 methodology does not print this factor (standards echo: BS EN 12101-6:2005 # 11.2.2.2 adds a 15 % allowance for ductwork losses).

Door-closer opening force  (F_closer)  = 45 N.  This is the force required at the latch edge to overcome the door closer alone (with ΔP = 0).  Typical values — EN 1154 size 2 approx. 25 N,  size 3 approx. 35 N,  size 4 approx. 45 N.  A heavy US commercial closer (NFPA 101 default) is taken as 67 N.  EN 1154 requires power size ≥ 3 on fire/smoke door assemblies.

Stack effect evaluated in both seasons; the case yielding the larger ΔP governs the design (NFPA 92 Annex).

Wind effect is NOT modelled — the calculation adds the worst-season STACK effect only. IBC # 909.20.5 requires the pressurization band to hold under maximum anticipated conditions of stack effect AND wind effect, and NFPA 92 # 4.4.2.1.4 names wind explicitly — verify wind pressures separately for exposed stairwells (advisory note; changes no computed value).

Linear pressure-profile model with the neutral plane assumed at mid-height of the stairwell (NFPA 92 / Klote & Milke Chapter 5).

Horizontal leakage = floor-plan area × 2 slabs × N_floors × ratio.

Door-crack leakage = (door perimeter × crack gap) / 2 per door (one-sided flow convention).

Injection strategy: Multi-point injection (9 points). Building height > 30.0 m — use multiple injection points (recommended every 10–15 m). 9 points suggested for this height (129.3 m). Spacing and exact locations must be confirmed with the AHJ and shall follow the rational-analysis requirements of IBC # 909.6.

# 4.  Step-by-Step Calculation

4.1  Design Temperatures

Step 1: Winter Design Temperature

Formula: T_winter = user-specified winter design temperature

Substitution: Manual design temperatures (user-specified)

Result: T_winter = 12.0 °C

Note: Taken as the 1 % annual cold-season percentile by convention (ASHRAE Ch. 14).

Step 2: Summer Design Temperature

Formula: T_summer = user-specified summer design temperature

Substitution: Manual design temperatures (user-specified)

Result: T_summer = 46.0 °C

4.2  Internal Stairwell Temperature

Step 3: Ti — Air-Conditioned Stairwell

Formula: Ti = user setpoint

Substitution: Ti_winter = Ti_summer = 24.0 °C

Result: Ti = 24.0 °C

4.3  Stack-Effect Pressure Difference

Step 4: ΔP_stack — Winter

Formula: ΔP_w = K_s × max(0, 1/T_out − 1/T_in) × (H/2)

Substitution: 3460 × max(0, 1/285.150 − 1/297.150) × (129.30/2)

Result: ΔP_stack_w = 31.7 Pa

Note: Winter: cold outside ⇒ positive stack drives air up.

Step 5: ΔP_stack — Summer

Formula: ΔP_s = K_s × max(0, 1/T_in − 1/T_out) × (H/2)

Substitution: 3460 × max(0, 1/297.150 − 1/319.150) × (129.30/2)

Result: ΔP_stack_s = 51.9 Pa

Note: Summer: cooler inside ⇒ reverse stack.

Step 6: Governing Stack Effect

Formula: ΔP_stack = max(ΔP_w, ΔP_s)

Substitution: max(31.7 Pa, 51.9 Pa)

Result: ΔP_stack = 51.9 Pa (Summer governing)

4.4  Design Pressure Differential

Step 7: Design ΔP

Formula: ΔP_design = ΔP_min + ΔP_stack (capped at basis maximum if applicable)

Substitution: 25.0 Pa + 51.9 Pa

Result: ΔP_design = 76.9 Pa

4.5  Leakage Areas (NFPA 92 Table A.4.4.4.3)

Step 8: Wall Leakage Area

Formula: A_wall = 2(L+W) × H_total × ratio

Substitution: 2(5.4 m+2.6 m) × 129.3 m × 1.40e-05

Result: A_leak_wall = 0.0290 m²

Step 9: Floor / Ceiling Leakage Area

Formula: A_horiz = L × W × 2 slabs × N_floors × ratio

Substitution: 5.4 m × 2.6 m × 2 × 41 × 5.20e-05

Result: A_leak_horiz = 0.0599 m²

Step 10: Door-Crack Leakage Area

Formula: A_doors = Σ [N × (2W + 2H) × crack / 2]

Substitution: Sum over all door types with qty > 0

Result: A_leak_doors = 0.2700 m²

Note: Crack divided by 2 — one-sided flow convention.

Step 11: Total Leakage Area

Formula: A_total = A_wall + A_horiz + A_doors

Substitution: 0.0290 m² + 0.0599 m² + 0.2700 m²

Result: A_leak_total = 0.3588 m²

4.6  Leakage Flow Rate

Step 12: Q_leak (NFPA 92 SI)

Formula: Q_leak = C_d × A_total × √ΔP_design

Substitution: 0.839 × 0.3588 m² × √76.89

Result: Q_leak = 2.640 m³/s = 2,640 L/s

Note: C_d = 0.839 = 0.65·√(2/1.2), the SI orifice coefficient (Klote/SFPE; NFPA 92 methodology) — the substitution is in SI (ΔP in Pa).

4.7  Open-Door Flow Rate

Step 13: Q_open — Open-Door Airflow

Formula: Q_open = 1.15 × V_max × A_door × N_open

Substitution: 1.15 × 1.00 m/s × ΣA_door × N_open (total 3 doors)

Result: Q_open = 6.520 m³/s = 6,520 L/s

Note: 1.15 is the tool's conservative open-door allowance (turbulence / vena contracta at doorways); NFPA 92 methodology does not print this factor.

4.8  Total Fan Flow with Safety Margin

Step 14: Sub-Total Flow

Formula: Q_total = Q_leak + Q_open

Substitution: 2.640 m³/s + 6.520 m³/s

Result: Q_total = 9.160 m³/s = 9,160 L/s

Step 15: Final Fan Flow

Formula: Q_final = Q_total × (1 + margin/100)

Substitution: 9.160 m³/s × (1 + 10 %/100)

Result: Q_final = 10.076 m³/s = 10,076 L/s

4.9  Door Opening Forces

Step 16: Door Type 1 Opening Force

Formula: F = F_closer + (W × A × ΔP) / (2 × (W − d)) [NFPA 92 A.4.4.2.2 / BS EN 12101-6:2005 Clause 15 + Annex A]

Substitution: F = 45 N + (0.9 m × 0.9 m × 2.1 m × 76.9 Pa) / (2 × (0.9 m − 70 mm))

Result: F_closer = 45 N + F_pressure = 79 N = F = 124 N [OK]

Note: Max allowable per NFPA 92 / IBC 909: 133 N. d = handle set-back from latch edge = 70 mm.

Step 17: Door Type 2 Opening Force

Formula: F = F_closer + (W × A × ΔP) / (2 × (W − d)) [NFPA 92 A.4.4.2.2 / BS EN 12101-6:2005 Clause 15 + Annex A]

Substitution: F = 45 N + (0.9 m × 0.9 m × 2.1 m × 76.9 Pa) / (2 × (0.9 m − 70 mm))

Result: F_closer = 45 N + F_pressure = 79 N = F = 124 N [OK]

Note: Max allowable per NFPA 92 / IBC 909: 133 N. d = handle set-back from latch edge = 70 mm.

4.10  Max Allowable ΔP & Relief Vent

Step 18: Max Allowable ΔP

Formula: ΔP_max = 2 × (W − d) × (F_max − F_closer) / (W × A)

Substitution: Solved against the governing door (lowest allowable ΔP): Door Type 1 (0.9 m × 2.1 m); F_max = 133 N, F_closer = 45 N

Result: ΔP_max = 85.9 Pa

Step 19: Relief Vent Area

Formula: A_relief = max(0, Q_total / (C_d × √ΔP_max) − A_total)

Substitution: Q_total = 9.160 m³/s, ΔP_max = 85.9 Pa

Result: A_relief = 0.8193 m²

Note: Required when fan output at ΔP_max exceeds what the leakage area alone can pass.

# 5.  Results

| Parameter | Value |
| --- | --- |
| Design temperature source | Manual (user-specified) |
| Winter design T (1%) | 12.0 °C |
| Summer design T (99%) | 46.0 °C |
| Internal T — winter | 24.0 °C |
| Internal T — summer | 24.0 °C |
| Governing season | Summer |
| ΔP_stack (governing) | 51.9 Pa |
| ΔP_design | 76.9 Pa |
| ─── LEAKAGE ─── |  |
| Wall leakage area | 0.0290 m² |
| Floor/ceiling leakage area | 0.0599 m² |
| Door-crack leakage area | 0.2700 m² |
| Total leakage area | 0.3588 m² |
| ─── FLOWS ─── |  |
| Leakage flow | 2,640 L/s |
| Open-door flow | 6,520 L/s |
| Sub-total flow | 9,160 L/s |
| Final fan flow (+10 %) | 10,076 L/s |
| ─── DOOR FORCE / RELIEF ─── |  |
| Max allowable ΔP (door force) | 85.9 Pa |
| Relief vent area | 0.8193 m² |
| Injection strategy | Multi-point injection (9 points) |

Design Checks

| Check | Status | Detail |
| --- | --- | --- |
| Min ΔP ≥ 25 Pa (NFPA 92 / IBC 909) | PASS | Effective min ΔP = 25.0 Pa, basis minimum = 25 Pa. |
| Design ΔP ≤ 87 Pa cap | PASS | Raw design ΔP = 76.9 Pa ≤ 87 Pa — no relief required on pressure grounds. |
| Safety margin applied | PASS | 10% additional margin on Q_final. |
| Door Type 1 force ≤ 133 N | PASS | Total 124 N (closer 45 N + pressure 79 N) ≤ 133 N per NFPA 92 # 4.4.2.1 + IBC # 909.20.5 + NFPA 101 # 7.2.1.4. |
| Door Type 2 force ≤ 133 N | PASS | Total 124 N (closer 45 N + pressure 79 N) ≤ 133 N per NFPA 92 # 4.4.2.1 + IBC # 909.20.5 + NFPA 101 # 7.2.1.4. |
| Relief vent required | INFO | A_relief = 0.8193 m² |
| Injection strategy | INFO | Building height > 30.0 m — use multiple injection points (recommended every 10–15 m). 9 points suggested for this height (129.3 m). Spacing and exact locations must be confirmed with the AHJ and shall follow the rational-analysis requirements of IBC # 909.6. |

# 6.  System Schematic & Pressure Profile

The schematic below shows a single-zone stairwell section with pressurization fan(s) and (if required) relief vent. The pressure-profile chart shows ΔP across each floor door, with code-minimum and door-force-limited bounds shaded for reference.

6.1  Pressure Profile (per NFPA 92 linear model)

# 7.  Pressurization Fan & Motor Schedule

| Parameter | Pressurization Fan | Unit |
| --- | --- | --- |
| Service | Stairwell pressurization | — |
| Tag | SF-1 … SF-2 | — |
| Quantity | 2 | nos. |
| Injection points | 9 (multi-point injection (9 points)) | — |
| Flow per fan | 5,038 | L/s |
| Design ΔP | 76.9 | Pa |
| Duct system losses | 0.0 | Pa |
| Total fan static | 76.9 | Pa |
| Fan efficiency | 65 | % |
| Absorbed shaft power | 0.60 | kW |
| Motor efficiency | 91 | % |
| Motor input power | 0.65 | kW |
| Selected motor (× 1.15 SF) | 0.75 | kW |

Notes

1.  Fans are constant-speed (non-VFD).  Pressurization runs on receipt of fire-alarm signal; fan speed and motor selection assume steady-state operation at the design ΔP.

2.  All fan motors shall be connected to the EMERGENCY power source (generator or equivalent) in accordance with NFPA 92, IBC # 909.6, and the local fire code.  Normal-to-emergency transfer time shall not exceed the activation requirements of the smoke-control system.

3.  Motor selection applies a safety factor of 1.15 to the absorbed shaft power; the nearest IEC preferred motor rating at or above that value is selected (0.37 – 400 kW series).

4.  Air-injection arrangement — Spacing and exact locations must be confirmed with the AHJ and shall follow the rational-analysis requirements of IBC # 909.6.

5.  Fan and motor efficiencies are user-specified inputs.  Fan operating point (flow, static) must be confirmed against the manufacturer's published curves before procurement.

# R.  Reference Standards

NFPA 92 (2024) — Smoke Control Systems — Pressurization-system methodology; minimum design ΔP and stack/wind/HVAC interaction (Chapter 4, Table 4.4.2.1.1).

IBC # 909.6 — Smokeproof Enclosures — Pressurization method by rational analysis; demonstrated by calculation.

NFPA 101 # 7.2.1.4.5 — Door Operating Force — Maximum force to set a door in motion.

BS EN 12101-6:2005 # 4.2 — Pressure-Differential Systems — Class A (means of escape) criteria (ΔP, door force, open-door velocity).

BS EN 1154 — Controlled Door Closing Devices — Closer power sizes — source of the EN closer opening-force presets (size 2 approx. 25 N, 3 approx. 35 N, 4 approx. 45 N, 5 approx. 55 N); minimum power size 3 on fire/smoke door assemblies.

ASHRAE Handbook — Fundamentals (Ch. 14 & 16) — Design outdoor temperatures (1%/99% percentile) and stack-effect theory.

Klote & Milke — Principles of Smoke Management (SFPE) — K_s stack constant, leakage discharge coefficient, open-door turbulence factor and the NFPA 92 linear pressure-profile model.

Engineer of record: Hussein Ragab

Generated by Stairwell Pressurization Calculator — NFPA 92 / BS EN 12101-6 stairwell smoke control.