## Fan Schedule
Stairwell Pressurization — Fan & Motor Schedule
Fan equipment schedule — all values in SI (metric) units
Project: Test Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: Test Dev ¦ By: Hussein Ragab ¦ Chkd: Principal MEP Review ¦ Rev: P2 ¦ Date: 2026-09-02
Design Basis & Governing Values
Design basis | NFPA 92 / IBC 909
Basis reference | NFPA 92 # 4.4.2.1 + IBC # 909.20.5 + NFPA 101 # 7.2.1.4
Governing season | Summer
Design ΔP | 76.9 Pa
Stack-effect ΔP | 51.9 Pa
Max allowable ΔP (door force) | 85.9 Pa
Total design flow (fan duty) | 10,076 L/s
Safety margin | 10 %
Injection strategy | Multi-point injection (9 points)
Relief vent area | 0.8193 m²
Floors served | 41
Outdoor winter design T (1 %) | 12.0 °C
Outdoor summer design T (99 %) | 46.0 °C
Design temperature source | Manual design temperatures (user-specified)
Fan & Motor Schedule
Parameter | Pressurization Fan | Unit
Service | Stairwell pressurization | —
Tag | SF-1 … SF-2 | —
Quantity | 2 | nos.
Injection points | 9 (multi-point injection (9 points)) | —
Flow per fan | 5038 | L/s
Design ΔP | 76.9 | Pa
Duct system losses | 0 | Pa
Total fan static | 76.9 | Pa
Fan efficiency | 65 | %
Absorbed shaft power | 0.6 | kW
Motor efficiency | 91 | %
Motor input power | 0.65 | kW
Selected motor (× 1.15 SF) | 0.75 | kW
Reference Standards
Reference | Application
NFPA 92 (2024) — Smoke Control Systems | Pressurization-system methodology; minimum design ΔP and stack/wind/HVAC interaction (Chapter 4, Table 4.4.2.1.1).
IBC # 909.6 — Smokeproof Enclosures | Pressurization method by rational analysis; demonstrated by calculation.
NFPA 101 # 7.2.1.4.5 — Door Operating Force | Maximum force to set a door in motion.
BS EN 12101-6:2005 # 4.2 — Pressure-Differential Systems | Class A (means of escape) criteria (ΔP, door force, open-door velocity).
ASHRAE Handbook — Fundamentals (Ch. 14 & 16) | Design outdoor temperatures (1%/99% percentile) and stack-effect theory.
Klote & Milke — Principles of Smoke Management (SFPE) | K_s stack constant, leakage discharge coefficient, open-door turbulence factor and the NFPA 92 linear pressure-profile model.
Open-Meteo Archive API | Hourly historical 2 m temperature; 1st / 99th percentiles used as winter / summer design temperatures.