Static Regain Duct Sizing Report

SMACNA HVAC Systems Duct Design / ASHRAE F-21

Branched supply-air network sized by the static-regain method

| Project Information |  |
| --- | --- |
| Project Name | Marina Commercial Tower |
| Project No. | MCT-2026-MEP-001 |
| Revision | P2 |
| Client | — |
| Prepared by | Hussein Ragab |
| Checked by | — |
| Date | 2026-10-20 |

Values in this report are displayed in SI (metric) units.

# 1.  Methodology & Standards

Each duct section is sized so that the static-pressure regain from velocity reduction equals the friction and fitting losses across the section. The result is a roughly balanced static across all branches — minimising the use of balancing dampers and lowering the fan static-pressure requirement.

| Reference | Application |
| --- | --- |
| ASHRAE Handbook – Fundamentals (2021), Chapter 21 | Eq. (41) static-regain balance ps = (pv1 - pv2) - pt, printed p. 21.20 (the regain coefficient R de-rates a recovery only; an acceleration is charged in full); the printed selection step (p. 21.19, Example 8 p. 21.23: the size whose Eq. (41) result is closest to zero, never above the upstream duct except one catalogue step at a shape change, capped at the upstream De plus one step - the round equivalent of the upstream size, Eq. (25) p. 21.9); Eq. (8) velocity pressure, (18) Darcy friction loss, (19) Colebrook–White, (20) Reynolds, (25) equivalent diameter; Table 1 roughness; Table 12 recommended maximum velocities; fitting losses referred to the ASHRAE Duct Fitting Database. |
| SMACNA HVAC Systems – Duct Design (4th ed., 2006) | Vp-to-SP conversion (Ch. 5 Duct Design Fundamentals, Sec. 5.6.3); regainable fraction of velocity pressure (Sec. 7.2 (g), 75 to 90 percent - the printed basis of a fractional R); duct-sizing procedures (Ch. 7). |
| Colebrook, C. F. (1938-1939), Journal of the Institution of Civil Engineers 11:133 | Implicit friction-factor formula for turbulent flow in rough pipes. |
| Darcy–Weisbach equation | Pipe / duct head loss per unit length, applied at every section. |

# 2.  Design Inputs

| Parameter | Value |
| --- | --- |
| Design velocity | 8.00 m/s |
| Air density ρ | 1.204 kg/m³ |
| Dynamic viscosity μ | 1.810e-05 Pa·s |
| Roughness material | Galvanised steel, longitudinal seam, 4 ft joints |
| Roughness ε (mm, both unit systems) | 0.090 mm |
| Minimum velocity floor (solver bound; advisory when sizing) | 1.02 m/s |
| Maximum velocity cap V_max (binding; upsizes snapped sizes) | 10.00 m/s |
| Fan inlet SP | 0.0 Pa |
| Catalogue system | SI |
| Snap to standard sizes (then bounded by V_max) | Yes |
| Sections in network | 19 |
| Terminal (leaf) count | 10 |

# 3.  Design Assumptions

Single-phase, incompressible, isothermal air flow.

Air properties unless overridden: density 1.204 kg/m³, the standard air of the ASHRAE F-21 friction chart (Fundamentals 2021 SI, printed p. 21.6); dynamic viscosity 1.81 × 10⁻⁵ Pa·s, dry air at 20 °C and 101.325 kPa (Fundamentals 2021 SI Ch. 3, printed p. 3.1: 18.1 µN·s/m²).

Roughness ε per ASHRAE F-21 Ch. 21 Table 1 (galvanised, longitudinal seam approx. 0.09 mm); user-editable through the in-app library.

Duct absolute roughness ε is stated in mm in BOTH unit systems — the pinned ASHRAE Fundamentals edition is the SI printing and gives no IP roughness table, so there is no printed IP value to convert to.

Static-regain coefficients R are engineering defaults (0.85 conical, 0.75 tee straight, 0.50 tee branch / abrupt) applied to the static-regain method of SMACNA Ch. 5 Sec. 5.6.3; that clause defines the Vp-to-SP conversion and prints no R table. SMACNA Sec. 7.2 (g) states that in well-designed ductwork at least 75 to 90 percent of the original velocity pressure can be regained — 0.75 and 0.85 sit inside that band; 0.50 is the tool's conservative value for branch tap-offs and abrupt reducers with no printed support. Set R per the fitting manufacturer's data where it matters.

Fitting K-coefficients: RE-GROUNDED 2026-09-01 on the ASHRAE Duct Fitting Database v5.00.10. Of the 44 bundled rows, 35 are read from a printed Database sheet (33 directly, 2 from the gored elbow sheet CD3-12 and named as gored) and 9 are curated typicals with no Database counterpart — every one of those 9 is marked in the K-builder and carries the wording 'curated typical - no DFDB v5.00.10 counterpart (verified 2026-09-01)'. Most Database coefficients are printed against a geometric parameter (duct diameter, aspect ratio, area ratio, flow ratio), so a row is read at the section's own solved geometry where that is known and at a stated library default where it is not. Co is referenced to the section's own velocity pressure per ASHRAE F-2021 SI Ch. 21, printed p. 21.9 Eq. (30) and p. 21.11 Eq. (34). Per-section ΣK is the sum of the named fittings or the user's manual override. Since 2026-09-23 (ruling R2-06) every named fitting of a section committed in Local losses is re-read at the section's solved size inside the solve's fixed-point loop, as ASHRAE Example 8 re-reads each coefficient at every trial size (Table 15, printed pp. 21.27-21.28); a typed direct K and a Library-edited row never move, and a section from a file saved earlier keeps its saved ΣK until it is re-opened.

Round-equivalent diameter for rectangular ducts: De = 1.30·(a·b)^0.625 / (a+b)^0.25  (ASHRAE F-21 Eq. (25)); friction is evaluated on De at the equivalent-round velocity V_e = Q/(π·De²/4).

Friction factor: Colebrook–White, iterated to 1×10⁻¹⁰; laminar regime (Re < 2300) uses f = 64/Re.

Standard market sizes: SI 100–2000 mm in 50-mm steps, or IP SMACNA round / rectangular catalogues.

The first section is sized at the design velocity and snapped up to the catalogue. Each downstream section starts at the upstream duct size and steps down the catalogue; the size whose Eq. (41) result is nearest zero (either sign) is selected, never larger than the upstream duct (ASHRAE F-21 p. 21.19, Example 8 Table 16). The selected size is then upsized where needed so that V ≤ V_max; V_min is advisory — a duct is never reduced to raise its velocity; the section is flagged instead, on every sizing path (round or rectangular, free or locked). V_max is a user input: ASHRAE F-21 Ch. 21 Table 12 gives recommended maxima by duct location and NC/RC rating.

Fan SP requirement on each path = fan inlet SP + Σ duct losses to the leaf − Σ regain credits (together: the leaf's cumulative SP)  +  the leaf's terminal SP requirement. A leaf with no flow carries no terminal requirement and never governs (ruling D63, 2026-09-22).

# 4.  Step-by-Step Calculation

Each section below shows the inputs, the named fitting breakdown, and a numbered set of step-boxes for the regain balance, geometry, friction factor, friction loss, fitting losses, regain credit, and cumulative SP. Sections appear in breadth-first order from the fan. Linked-bundle instances share one master block; subsequent instances are listed by name with a back-reference.

★ Section  FAHU-01 discharge    (governing path)

Inputs

| Input | Value |
| --- | --- |
| Parent | (root – fan inlet) |
| Length L | 6.00 m |
| Flow Q (through) | 6,220 L/s |
| Shape | Rectangular |
| Aspect ratio (derived) | 1.92:1 |
| Regain coefficient R | 0.75 |
| Σ K (fittings) | 0.600 |

Fittings on this section

1 × (Direct input of K value)    (K = 0.600)    →    0.600

─── Σ K  =  0.600  ───

Equipment (constant ΔP):

1 × Sound attenuator, 1200 mm length    (ΔP = 50.0 Pa)    →    50.0 Pa

─── Σ ΔP_eq  =  50.0 Pa  ───

Step 1: Sizing velocity (root / dead-leg)

Formula: V = V_design

Substitution: V = 8.00 m/s

Result: V = 7.66 m/s

Note: Root trunk is sized at the user's design velocity. Downstream sections follow the static-regain balance.

Step 2: Cross-section sizing (snap to standard catalogue)

Formula: Rect: a, b chosen so that De = 1.30 (a · b)^0.625 / (a + b)^0.25 [ASHRAE F-21 Eq. (25)]

Substitution: A = Q / V = 6.2200 m³/s / 7.655 m/s = 0.8125 m² = selected 1,250 mm × 650 mm (AR = 1.92:1); De = 973 mm (selected); continuous regain solution De_calc = 950 mm (bisection; catalogue step selected the sides above)

Result: Final size = Rect 1250 × 650 mm

Note: Catalogue: SI 100–2000 mm in 50-mm steps

Step 3: Reynolds number and Darcy friction factor

Formula: Re = ρ · V_e · De / μ [ASHRAE F-21 Eq. (20)]; 1/√f = −2 · log₁₀(ε / (3.7 De) + 2.51 / (Re · √f)) [Colebrook–White, Eq. (19)]

Substitution: ρ = 1.204 kg/m³, μ = 1.810e-05 Pa·s, De = 973 mm, V_e = 8.37 m/s, ε = 0.090 mm → Re = 541,694, ε/De = 0.00009

Result: f = 0.01421

Note: Friction uses the equivalent-round velocity V_e = Q/(π·De²/4) = 8.37 m/s; the rectangular face velocity V = 7.66 m/s drives Vp and the regain credit (Steps 1, 5, 6).

Step 4: Friction loss along the section

Formula: ΔPf = f · (L / De) · ½ · ρ · V_e² [Darcy–Weisbach, ASHRAE F-21 Eq. (18)]

Substitution: f = 0.01421, L = 6.00 m, De = 973 mm, ½ρV_e² = 42.2 Pa

Result: ΔPf = 3.7 Pa

Step 5: Fitting losses

Formula: ΔPfit = Σ K · Vp, Vp = ½ · ρ · V²

Substitution: Σ K = 0.600, Vp = 35.3 Pa → ΔPfit = 0.600 × 35.3 Pa

Result: ΔPfit = 21.2 Pa

Step 7: Cumulative duct losses to end of section

Formula: Σ SP_n = Σ SP_(n−1) + ΔPf + ΔPfit + ΔP_eq − ΔPs

Substitution: Σ SP_prev = 0.0 Pa + ΔPf 3.7 Pa + ΔPfit 21.2 Pa + ΔP_eq 50.0 Pa − ΔPs 0.0 Pa

Result: Σ SP_end = 74.9 Pa

Section  L10 floor branch

Inputs

| Input | Value |
| --- | --- |
| Parent | FAHU-01 discharge |
| Length L | 4.00 m |
| Flow Q (through) | 622 L/s |
| Shape | Rectangular |
| Aspect ratio (derived) | 2.00:1 |
| Regain coefficient R | 0.50 |
| Σ K (fittings) | 0.350 |
| Terminal SP | 125.0 Pa |

Fittings on this section

1 × (Direct input of K value)    (K = 0.350)    →    0.350

─── Σ K  =  0.350  ───

Step 1: Static-regain balance for V_down

Formula: R · (Vp_up − Vp_down) = ΔPf + Σ K · Vp_down [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g); Vp-to-SP conversion SMACNA Sec. 5.6.3]

Substitution: R = 0.50, Vp_up = ½ · ρ · V_up² = 35.3 Pa, Vp_down = ½ · ρ · V_down² = 14.9 Pa, regain credit = 10.2 Pa approx. ΔPf + Σ K · Vp_down = 3.4 Pa + 5.2 Pa

Result: V_down = 4.98 m/s

Note: Solver: bisection on V ∈ [V_min, V_up] until the regain credit equals the sum of friction and fitting losses.

Step 2: Cross-section sizing (snap to standard catalogue)

Formula: Rect: a, b chosen so that De = 1.30 (a · b)^0.625 / (a + b)^0.25 [ASHRAE F-21 Eq. (25)]

Substitution: A = Q / V = 0.6220 m³/s / 4.976 m/s = 0.1250 m² = selected 500 mm × 250 mm (AR = 2.00:1); De = 381 mm (selected); continuous regain solution De_calc = 373 mm (bisection; catalogue step selected the sides above)

Result: Final size = Rect 500 × 250 mm

Note: Catalogue: SI 100–2000 mm in 50-mm steps

Step 3: Reynolds number and Darcy friction factor

Formula: Re = ρ · V_e · De / μ [ASHRAE F-21 Eq. (20)]; 1/√f = −2 · log₁₀(ε / (3.7 De) + 2.51 / (Re · √f)) [Colebrook–White, Eq. (19)]

Substitution: ρ = 1.204 kg/m³, μ = 1.810e-05 Pa·s, De = 381 mm, V_e = 5.46 m/s, ε = 0.090 mm → Re = 138,325, ε/De = 0.00024

Result: f = 0.01823

Note: Friction uses the equivalent-round velocity V_e = Q/(π·De²/4) = 5.46 m/s; the rectangular face velocity V = 4.98 m/s drives Vp and the regain credit (Steps 1, 5, 6).

Step 4: Friction loss along the section

Formula: ΔPf = f · (L / De) · ½ · ρ · V_e² [Darcy–Weisbach, ASHRAE F-21 Eq. (18)]

Substitution: f = 0.01823, L = 4.00 m, De = 381 mm, ½ρV_e² = 17.9 Pa

Result: ΔPf = 3.4 Pa

Step 5: Fitting losses

Formula: ΔPfit = Σ K · Vp, Vp = ½ · ρ · V²

Substitution: Σ K = 0.350, Vp = 14.9 Pa → ΔPfit = 0.350 × 14.9 Pa

Result: ΔPfit = 5.2 Pa

Step 6: Static-regain credit

Formula: ΔPs = R · (Vp_up − Vp_down) [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g)]

Substitution: R = 0.50, Vp_up = 35.3 Pa, Vp_down = 14.9 Pa

Result: ΔPs = 10.2 Pa

Step 7: Cumulative duct losses to end of section

Formula: Σ SP_n = Σ SP_(n−1) + ΔPf + ΔPfit − ΔPs

Substitution: Σ SP_prev = 74.9 Pa + ΔPf 3.4 Pa + ΔPfit 5.2 Pa − ΔPs 10.2 Pa

Result: Σ SP_end = 73.3 Pa

Note: Add the leaf's terminal-SP requirement to obtain the fan SP needed on this path.

★ Section  Riser L10-L09    (governing path)

Inputs

| Input | Value |
| --- | --- |
| Parent | FAHU-01 discharge |
| Length L | 3.60 m |
| Flow Q (through) | 5,598 L/s |
| Shape | Rectangular |
| Aspect ratio (derived) | 1.92:1 |
| Regain coefficient R | 0.75 |
| Σ K (fittings) | 0.050 |

Fittings on this section

1 × (Direct input of K value)    (K = 0.050)    →    0.050

─── Σ K  =  0.050  ───

Step 1: Static-regain balance for V_down

Formula: R · (Vp_up − Vp_down) = ΔPf + Σ K · Vp_down [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g); Vp-to-SP conversion SMACNA Sec. 5.6.3]

Substitution: R = 0.75, Vp_up = ½ · ρ · V_up² = 35.3 Pa, Vp_down = ½ · ρ · V_down² = 28.6 Pa, regain credit = 5.0 Pa approx. ΔPf + Σ K · Vp_down = 1.8 Pa + 1.4 Pa

Result: V_down = 6.89 m/s

Note: Solver: bisection on V ∈ [V_min, V_up] until the regain credit equals the sum of friction and fitting losses.

Step 2: Cross-section sizing (snap to standard catalogue)

Formula: Rect: a, b chosen so that De = 1.30 (a · b)^0.625 / (a + b)^0.25 [ASHRAE F-21 Eq. (25)]

Substitution: A = Q / V = 5.5980 m³/s / 6.890 m/s = 0.8125 m² = selected 1,250 mm × 650 mm (AR = 1.92:1); De = 973 mm (selected); continuous regain solution De_calc = 955 mm (bisection; catalogue step selected the sides above)

Result: Final size = Rect 1250 × 650 mm

Note: Catalogue: SI 100–2000 mm in 50-mm steps

Step 3: Reynolds number and Darcy friction factor

Formula: Re = ρ · V_e · De / μ [ASHRAE F-21 Eq. (20)]; 1/√f = −2 · log₁₀(ε / (3.7 De) + 2.51 / (Re · √f)) [Colebrook–White, Eq. (19)]

Substitution: ρ = 1.204 kg/m³, μ = 1.810e-05 Pa·s, De = 973 mm, V_e = 7.54 m/s, ε = 0.090 mm → Re = 487,524, ε/De = 0.00009

Result: f = 0.01439

Note: Friction uses the equivalent-round velocity V_e = Q/(π·De²/4) = 7.54 m/s; the rectangular face velocity V = 6.89 m/s drives Vp and the regain credit (Steps 1, 5, 6).

Step 4: Friction loss along the section

Formula: ΔPf = f · (L / De) · ½ · ρ · V_e² [Darcy–Weisbach, ASHRAE F-21 Eq. (18)]

Substitution: f = 0.01439, L = 3.60 m, De = 973 mm, ½ρV_e² = 34.2 Pa

Result: ΔPf = 1.8 Pa

Step 5: Fitting losses

Formula: ΔPfit = Σ K · Vp, Vp = ½ · ρ · V²

Substitution: Σ K = 0.050, Vp = 28.6 Pa → ΔPfit = 0.050 × 28.6 Pa

Result: ΔPfit = 1.4 Pa

Step 6: Static-regain credit

Formula: ΔPs = R · (Vp_up − Vp_down) [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g)]

Substitution: R = 0.75, Vp_up = 35.3 Pa, Vp_down = 28.6 Pa

Result: ΔPs = 5.0 Pa

Step 7: Cumulative duct losses to end of section

Formula: Σ SP_n = Σ SP_(n−1) + ΔPf + ΔPfit − ΔPs

Substitution: Σ SP_prev = 74.9 Pa + ΔPf 1.8 Pa + ΔPfit 1.4 Pa − ΔPs 5.0 Pa

Result: Σ SP_end = 73.1 Pa

★ Section  L09 floor branch    (governing path)

Inputs

| Input | Value |
| --- | --- |
| Parent | Riser L10-L09 |
| Length L | 4.00 m |
| Flow Q (through) | 622 L/s |
| Shape | Rectangular |
| Aspect ratio (derived) | 2.00:1 |
| Regain coefficient R | 0.50 |
| Σ K (fittings) | 0.350 |
| Terminal SP | 125.0 Pa |

Fittings on this section

1 × (Direct input of K value)    (K = 0.350)    →    0.350

─── Σ K  =  0.350  ───

Step 1: Static-regain balance for V_down

Formula: R · (Vp_up − Vp_down) = ΔPf + Σ K · Vp_down [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g); Vp-to-SP conversion SMACNA Sec. 5.6.3]

Substitution: R = 0.50, Vp_up = ½ · ρ · V_up² = 28.6 Pa, Vp_down = ½ · ρ · V_down² = 14.9 Pa, regain credit = 6.8 Pa approx. ΔPf + Σ K · Vp_down = 3.4 Pa + 5.2 Pa

Result: V_down = 4.98 m/s

Note: Solver: bisection on V ∈ [V_min, V_up] until the regain credit equals the sum of friction and fitting losses.

Step 2: Cross-section sizing (snap to standard catalogue)

Formula: Rect: a, b chosen so that De = 1.30 (a · b)^0.625 / (a + b)^0.25 [ASHRAE F-21 Eq. (25)]

Substitution: A = Q / V = 0.6220 m³/s / 4.976 m/s = 0.1250 m² = selected 500 mm × 250 mm (AR = 2.00:1); De = 381 mm (selected); continuous regain solution De_calc = 392 mm (bisection; catalogue step selected the sides above)

Result: Final size = Rect 500 × 250 mm

Note: Catalogue: SI 100–2000 mm in 50-mm steps

Step 3: Reynolds number and Darcy friction factor

Formula: Re = ρ · V_e · De / μ [ASHRAE F-21 Eq. (20)]; 1/√f = −2 · log₁₀(ε / (3.7 De) + 2.51 / (Re · √f)) [Colebrook–White, Eq. (19)]

Substitution: ρ = 1.204 kg/m³, μ = 1.810e-05 Pa·s, De = 381 mm, V_e = 5.46 m/s, ε = 0.090 mm → Re = 138,325, ε/De = 0.00024

Result: f = 0.01823

Note: Friction uses the equivalent-round velocity V_e = Q/(π·De²/4) = 5.46 m/s; the rectangular face velocity V = 4.98 m/s drives Vp and the regain credit (Steps 1, 5, 6).

Step 4: Friction loss along the section

Formula: ΔPf = f · (L / De) · ½ · ρ · V_e² [Darcy–Weisbach, ASHRAE F-21 Eq. (18)]

Substitution: f = 0.01823, L = 4.00 m, De = 381 mm, ½ρV_e² = 17.9 Pa

Result: ΔPf = 3.4 Pa

Step 5: Fitting losses

Formula: ΔPfit = Σ K · Vp, Vp = ½ · ρ · V²

Substitution: Σ K = 0.350, Vp = 14.9 Pa → ΔPfit = 0.350 × 14.9 Pa

Result: ΔPfit = 5.2 Pa

Step 6: Static-regain credit

Formula: ΔPs = R · (Vp_up − Vp_down) [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g)]

Substitution: R = 0.50, Vp_up = 28.6 Pa, Vp_down = 14.9 Pa

Result: ΔPs = 6.8 Pa

Step 7: Cumulative duct losses to end of section

Formula: Σ SP_n = Σ SP_(n−1) + ΔPf + ΔPfit − ΔPs

Substitution: Σ SP_prev = 73.1 Pa + ΔPf 3.4 Pa + ΔPfit 5.2 Pa − ΔPs 6.8 Pa

Result: Σ SP_end = 74.9 Pa

Note: Add the leaf's terminal-SP requirement to obtain the fan SP needed on this path.

Section  Riser L09-L08

Inputs

| Input | Value |
| --- | --- |
| Parent | Riser L10-L09 |
| Length L | 3.60 m |
| Flow Q (through) | 4,976 L/s |
| Shape | Rectangular |
| Aspect ratio (derived) | 1.92:1 |
| Regain coefficient R | 0.75 |
| Σ K (fittings) | 0.050 |

Fittings on this section

1 × (Direct input of K value)    (K = 0.050)    →    0.050

─── Σ K  =  0.050  ───

Step 1: Static-regain balance for V_down

Formula: R · (Vp_up − Vp_down) = ΔPf + Σ K · Vp_down [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g); Vp-to-SP conversion SMACNA Sec. 5.6.3]

Substitution: R = 0.75, Vp_up = ½ · ρ · V_up² = 28.6 Pa, Vp_down = ½ · ρ · V_down² = 22.6 Pa, regain credit = 4.5 Pa approx. ΔPf + Σ K · Vp_down = 1.5 Pa + 1.1 Pa

Result: V_down = 6.12 m/s

Note: Solver: bisection on V ∈ [V_min, V_up] until the regain credit equals the sum of friction and fitting losses.

Step 2: Cross-section sizing (snap to standard catalogue)

Formula: Rect: a, b chosen so that De = 1.30 (a · b)^0.625 / (a + b)^0.25 [ASHRAE F-21 Eq. (25)]

Substitution: A = Q / V = 4.9760 m³/s / 6.124 m/s = 0.8125 m² = selected 1,250 mm × 650 mm (AR = 1.92:1); De = 973 mm (selected); continuous regain solution De_calc = 949 mm (bisection; catalogue step selected the sides above)

Result: Final size = Rect 1250 × 650 mm

Note: Catalogue: SI 100–2000 mm in 50-mm steps

Step 3: Reynolds number and Darcy friction factor

Formula: Re = ρ · V_e · De / μ [ASHRAE F-21 Eq. (20)]; 1/√f = −2 · log₁₀(ε / (3.7 De) + 2.51 / (Re · √f)) [Colebrook–White, Eq. (19)]

Substitution: ρ = 1.204 kg/m³, μ = 1.810e-05 Pa·s, De = 973 mm, V_e = 6.70 m/s, ε = 0.090 mm → Re = 433,355, ε/De = 0.00009

Result: f = 0.01461

Note: Friction uses the equivalent-round velocity V_e = Q/(π·De²/4) = 6.70 m/s; the rectangular face velocity V = 6.12 m/s drives Vp and the regain credit (Steps 1, 5, 6).

Step 4: Friction loss along the section

Formula: ΔPf = f · (L / De) · ½ · ρ · V_e² [Darcy–Weisbach, ASHRAE F-21 Eq. (18)]

Substitution: f = 0.01461, L = 3.60 m, De = 973 mm, ½ρV_e² = 27.0 Pa

Result: ΔPf = 1.5 Pa

Step 5: Fitting losses

Formula: ΔPfit = Σ K · Vp, Vp = ½ · ρ · V²

Substitution: Σ K = 0.050, Vp = 22.6 Pa → ΔPfit = 0.050 × 22.6 Pa

Result: ΔPfit = 1.1 Pa

Step 6: Static-regain credit

Formula: ΔPs = R · (Vp_up − Vp_down) [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g)]

Substitution: R = 0.75, Vp_up = 28.6 Pa, Vp_down = 22.6 Pa

Result: ΔPs = 4.5 Pa

Step 7: Cumulative duct losses to end of section

Formula: Σ SP_n = Σ SP_(n−1) + ΔPf + ΔPfit − ΔPs

Substitution: Σ SP_prev = 73.1 Pa + ΔPf 1.5 Pa + ΔPfit 1.1 Pa − ΔPs 4.5 Pa

Result: Σ SP_end = 71.2 Pa

Section  L08 floor branch

Inputs

| Input | Value |
| --- | --- |
| Parent | Riser L09-L08 |
| Length L | 4.00 m |
| Flow Q (through) | 622 L/s |
| Shape | Rectangular |
| Aspect ratio (derived) | 1.83:1 |
| Regain coefficient R | 0.50 |
| Σ K (fittings) | 0.350 |
| Terminal SP | 125.0 Pa |

Fittings on this section

1 × (Direct input of K value)    (K = 0.350)    →    0.350

─── Σ K  =  0.350  ───

Step 1: Static-regain balance for V_down

Formula: R · (Vp_up − Vp_down) = ΔPf + Σ K · Vp_down [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g); Vp-to-SP conversion SMACNA Sec. 5.6.3]

Substitution: R = 0.50, Vp_up = ½ · ρ · V_up² = 22.6 Pa, Vp_down = ½ · ρ · V_down² = 8.6 Pa, regain credit = 7.0 Pa approx. ΔPf + Σ K · Vp_down = 1.7 Pa + 3.0 Pa

Result: V_down = 3.77 m/s

Note: Solver: bisection on V ∈ [V_min, V_up] until the regain credit equals the sum of friction and fitting losses.

Step 2: Cross-section sizing (snap to standard catalogue)

Formula: Rect: a, b chosen so that De = 1.30 (a · b)^0.625 / (a + b)^0.25 [ASHRAE F-21 Eq. (25)]

Substitution: A = Q / V = 0.6220 m³/s / 3.770 m/s = 0.1650 m² = selected 550 mm × 300 mm (AR = 1.83:1); De = 439 mm (selected); continuous regain solution De_calc = 415 mm (bisection; catalogue step selected the sides above)

Result: Final size = Rect 550 × 300 mm

Note: Catalogue: SI 100–2000 mm in 50-mm steps

Step 3: Reynolds number and Darcy friction factor

Formula: Re = ρ · V_e · De / μ [ASHRAE F-21 Eq. (20)]; 1/√f = −2 · log₁₀(ε / (3.7 De) + 2.51 / (Re · √f)) [Colebrook–White, Eq. (19)]

Substitution: ρ = 1.204 kg/m³, μ = 1.810e-05 Pa·s, De = 439 mm, V_e = 4.11 m/s, ε = 0.090 mm → Re = 119,986, ε/De = 0.00020

Result: f = 0.01847

Note: Friction uses the equivalent-round velocity V_e = Q/(π·De²/4) = 4.11 m/s; the rectangular face velocity V = 3.77 m/s drives Vp and the regain credit (Steps 1, 5, 6).

Step 4: Friction loss along the section

Formula: ΔPf = f · (L / De) · ½ · ρ · V_e² [Darcy–Weisbach, ASHRAE F-21 Eq. (18)]

Substitution: f = 0.01847, L = 4.00 m, De = 439 mm, ½ρV_e² = 10.2 Pa

Result: ΔPf = 1.7 Pa

Step 5: Fitting losses

Formula: ΔPfit = Σ K · Vp, Vp = ½ · ρ · V²

Substitution: Σ K = 0.350, Vp = 8.6 Pa → ΔPfit = 0.350 × 8.6 Pa

Result: ΔPfit = 3.0 Pa

Step 6: Static-regain credit

Formula: ΔPs = R · (Vp_up − Vp_down) [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g)]

Substitution: R = 0.50, Vp_up = 22.6 Pa, Vp_down = 8.6 Pa

Result: ΔPs = 7.0 Pa

Step 7: Cumulative duct losses to end of section

Formula: Σ SP_n = Σ SP_(n−1) + ΔPf + ΔPfit − ΔPs

Substitution: Σ SP_prev = 71.2 Pa + ΔPf 1.7 Pa + ΔPfit 3.0 Pa − ΔPs 7.0 Pa

Result: Σ SP_end = 68.9 Pa

Note: Add the leaf's terminal-SP requirement to obtain the fan SP needed on this path.

Section  Riser L08-L07

Inputs

| Input | Value |
| --- | --- |
| Parent | Riser L09-L08 |
| Length L | 3.60 m |
| Flow Q (through) | 4,354 L/s |
| Shape | Rectangular |
| Aspect ratio (derived) | 1.92:1 |
| Regain coefficient R | 0.75 |
| Σ K (fittings) | 0.050 |

Fittings on this section

1 × (Direct input of K value)    (K = 0.050)    →    0.050

─── Σ K  =  0.050  ───

Step 1: Static-regain balance for V_down

Formula: R · (Vp_up − Vp_down) = ΔPf + Σ K · Vp_down [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g); Vp-to-SP conversion SMACNA Sec. 5.6.3]

Substitution: R = 0.75, Vp_up = ½ · ρ · V_up² = 22.6 Pa, Vp_down = ½ · ρ · V_down² = 17.3 Pa, regain credit = 4.0 Pa approx. ΔPf + Σ K · Vp_down = 1.1 Pa + 0.9 Pa

Result: V_down = 5.36 m/s

Note: Solver: bisection on V ∈ [V_min, V_up] until the regain credit equals the sum of friction and fitting losses.

Step 2: Cross-section sizing (snap to standard catalogue)

Formula: Rect: a, b chosen so that De = 1.30 (a · b)^0.625 / (a + b)^0.25 [ASHRAE F-21 Eq. (25)]

Substitution: A = Q / V = 4.3540 m³/s / 5.359 m/s = 0.8125 m² = selected 1,250 mm × 650 mm (AR = 1.92:1); De = 973 mm (selected); continuous regain solution De_calc = 942 mm (bisection; catalogue step selected the sides above)

Result: Final size = Rect 1250 × 650 mm

Note: Catalogue: SI 100–2000 mm in 50-mm steps

Step 3: Reynolds number and Darcy friction factor

Formula: Re = ρ · V_e · De / μ [ASHRAE F-21 Eq. (20)]; 1/√f = −2 · log₁₀(ε / (3.7 De) + 2.51 / (Re · √f)) [Colebrook–White, Eq. (19)]

Substitution: ρ = 1.204 kg/m³, μ = 1.810e-05 Pa·s, De = 973 mm, V_e = 5.86 m/s, ε = 0.090 mm → Re = 379,186, ε/De = 0.00009

Result: f = 0.01487

Note: Friction uses the equivalent-round velocity V_e = Q/(π·De²/4) = 5.86 m/s; the rectangular face velocity V = 5.36 m/s drives Vp and the regain credit (Steps 1, 5, 6).

Step 4: Friction loss along the section

Formula: ΔPf = f · (L / De) · ½ · ρ · V_e² [Darcy–Weisbach, ASHRAE F-21 Eq. (18)]

Substitution: f = 0.01487, L = 3.60 m, De = 973 mm, ½ρV_e² = 20.7 Pa

Result: ΔPf = 1.1 Pa

Step 5: Fitting losses

Formula: ΔPfit = Σ K · Vp, Vp = ½ · ρ · V²

Substitution: Σ K = 0.050, Vp = 17.3 Pa → ΔPfit = 0.050 × 17.3 Pa

Result: ΔPfit = 0.9 Pa

Step 6: Static-regain credit

Formula: ΔPs = R · (Vp_up − Vp_down) [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g)]

Substitution: R = 0.75, Vp_up = 22.6 Pa, Vp_down = 17.3 Pa

Result: ΔPs = 4.0 Pa

Step 7: Cumulative duct losses to end of section

Formula: Σ SP_n = Σ SP_(n−1) + ΔPf + ΔPfit − ΔPs

Substitution: Σ SP_prev = 71.2 Pa + ΔPf 1.1 Pa + ΔPfit 0.9 Pa − ΔPs 4.0 Pa

Result: Σ SP_end = 69.2 Pa

Section  L07 floor branch

Inputs

| Input | Value |
| --- | --- |
| Parent | Riser L08-L07 |
| Length L | 4.00 m |
| Flow Q (through) | 622 L/s |
| Shape | Rectangular |
| Aspect ratio (derived) | 1.83:1 |
| Regain coefficient R | 0.50 |
| Σ K (fittings) | 0.350 |
| Terminal SP | 125.0 Pa |

Fittings on this section

1 × (Direct input of K value)    (K = 0.350)    →    0.350

─── Σ K  =  0.350  ───

Step 1: Static-regain balance for V_down

Formula: R · (Vp_up − Vp_down) = ΔPf + Σ K · Vp_down [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g); Vp-to-SP conversion SMACNA Sec. 5.6.3]

Substitution: R = 0.50, Vp_up = ½ · ρ · V_up² = 17.3 Pa, Vp_down = ½ · ρ · V_down² = 8.6 Pa, regain credit = 4.4 Pa approx. ΔPf + Σ K · Vp_down = 1.7 Pa + 3.0 Pa

Result: V_down = 3.77 m/s

Note: Solver: bisection on V ∈ [V_min, V_up] until the regain credit equals the sum of friction and fitting losses.

Step 2: Cross-section sizing (snap to standard catalogue)

Formula: Rect: a, b chosen so that De = 1.30 (a · b)^0.625 / (a + b)^0.25 [ASHRAE F-21 Eq. (25)]

Substitution: A = Q / V = 0.6220 m³/s / 3.770 m/s = 0.1650 m² = selected 550 mm × 300 mm (AR = 1.83:1); De = 439 mm (selected); continuous regain solution De_calc = 442 mm (bisection; catalogue step selected the sides above)

Result: Final size = Rect 550 × 300 mm

Note: Catalogue: SI 100–2000 mm in 50-mm steps

Step 3: Reynolds number and Darcy friction factor

Formula: Re = ρ · V_e · De / μ [ASHRAE F-21 Eq. (20)]; 1/√f = −2 · log₁₀(ε / (3.7 De) + 2.51 / (Re · √f)) [Colebrook–White, Eq. (19)]

Substitution: ρ = 1.204 kg/m³, μ = 1.810e-05 Pa·s, De = 439 mm, V_e = 4.11 m/s, ε = 0.090 mm → Re = 119,986, ε/De = 0.00020

Result: f = 0.01847

Note: Friction uses the equivalent-round velocity V_e = Q/(π·De²/4) = 4.11 m/s; the rectangular face velocity V = 3.77 m/s drives Vp and the regain credit (Steps 1, 5, 6).

Step 4: Friction loss along the section

Formula: ΔPf = f · (L / De) · ½ · ρ · V_e² [Darcy–Weisbach, ASHRAE F-21 Eq. (18)]

Substitution: f = 0.01847, L = 4.00 m, De = 439 mm, ½ρV_e² = 10.2 Pa

Result: ΔPf = 1.7 Pa

Step 5: Fitting losses

Formula: ΔPfit = Σ K · Vp, Vp = ½ · ρ · V²

Substitution: Σ K = 0.350, Vp = 8.6 Pa → ΔPfit = 0.350 × 8.6 Pa

Result: ΔPfit = 3.0 Pa

Step 6: Static-regain credit

Formula: ΔPs = R · (Vp_up − Vp_down) [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g)]

Substitution: R = 0.50, Vp_up = 17.3 Pa, Vp_down = 8.6 Pa

Result: ΔPs = 4.4 Pa

Step 7: Cumulative duct losses to end of section

Formula: Σ SP_n = Σ SP_(n−1) + ΔPf + ΔPfit − ΔPs

Substitution: Σ SP_prev = 69.2 Pa + ΔPf 1.7 Pa + ΔPfit 3.0 Pa − ΔPs 4.4 Pa

Result: Σ SP_end = 69.6 Pa

Note: Add the leaf's terminal-SP requirement to obtain the fan SP needed on this path.

Section  Riser L07-L06

Inputs

| Input | Value |
| --- | --- |
| Parent | Riser L08-L07 |
| Length L | 3.60 m |
| Flow Q (through) | 3,732 L/s |
| Shape | Rectangular |
| Aspect ratio (derived) | 2.00:1 |
| Regain coefficient R | 0.75 |
| Σ K (fittings) | 0.050 |

Fittings on this section

1 × (Direct input of K value)    (K = 0.050)    →    0.050

─── Σ K  =  0.050  ───

Step 1: Static-regain balance for V_down

Formula: R · (Vp_up − Vp_down) = ΔPf + Σ K · Vp_down [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g); Vp-to-SP conversion SMACNA Sec. 5.6.3]

Substitution: R = 0.75, Vp_up = ½ · ρ · V_up² = 17.3 Pa, Vp_down = ½ · ρ · V_down² = 16.2 Pa, regain credit = 0.8 Pa approx. ΔPf + Σ K · Vp_down = 1.2 Pa + 0.8 Pa

Result: V_down = 5.18 m/s

Note: Solver: bisection on V ∈ [V_min, V_up] until the regain credit equals the sum of friction and fitting losses.

Step 2: Cross-section sizing (snap to standard catalogue)

Formula: Rect: a, b chosen so that De = 1.30 (a · b)^0.625 / (a + b)^0.25 [ASHRAE F-21 Eq. (25)]

Substitution: A = Q / V = 3.7320 m³/s / 5.183 m/s = 0.7200 m² = selected 1,200 mm × 600 mm (AR = 2.00:1); De = 914 mm (selected); continuous regain solution De_calc = 933 mm (bisection; catalogue step selected the sides above)

Result: Final size = Rect 1200 × 600 mm

Note: Catalogue: SI 100–2000 mm in 50-mm steps

Step 3: Reynolds number and Darcy friction factor

Formula: Re = ρ · V_e · De / μ [ASHRAE F-21 Eq. (20)]; 1/√f = −2 · log₁₀(ε / (3.7 De) + 2.51 / (Re · √f)) [Colebrook–White, Eq. (19)]

Substitution: ρ = 1.204 kg/m³, μ = 1.810e-05 Pa·s, De = 914 mm, V_e = 5.69 m/s, ε = 0.090 mm → Re = 345,813, ε/De = 0.00010

Result: f = 0.01511

Note: Friction uses the equivalent-round velocity V_e = Q/(π·De²/4) = 5.69 m/s; the rectangular face velocity V = 5.18 m/s drives Vp and the regain credit (Steps 1, 5, 6).

Step 4: Friction loss along the section

Formula: ΔPf = f · (L / De) · ½ · ρ · V_e² [Darcy–Weisbach, ASHRAE F-21 Eq. (18)]

Substitution: f = 0.01511, L = 3.60 m, De = 914 mm, ½ρV_e² = 19.5 Pa

Result: ΔPf = 1.2 Pa

Step 5: Fitting losses

Formula: ΔPfit = Σ K · Vp, Vp = ½ · ρ · V²

Substitution: Σ K = 0.050, Vp = 16.2 Pa → ΔPfit = 0.050 × 16.2 Pa

Result: ΔPfit = 0.8 Pa

Step 6: Static-regain credit

Formula: ΔPs = R · (Vp_up − Vp_down) [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g)]

Substitution: R = 0.75, Vp_up = 17.3 Pa, Vp_down = 16.2 Pa

Result: ΔPs = 0.8 Pa

Step 7: Cumulative duct losses to end of section

Formula: Σ SP_n = Σ SP_(n−1) + ΔPf + ΔPfit − ΔPs

Substitution: Σ SP_prev = 69.2 Pa + ΔPf 1.2 Pa + ΔPfit 0.8 Pa − ΔPs 0.8 Pa

Result: Σ SP_end = 70.3 Pa

Section  L06 floor branch

Inputs

| Input | Value |
| --- | --- |
| Parent | Riser L07-L06 |
| Length L | 4.00 m |
| Flow Q (through) | 622 L/s |
| Shape | Rectangular |
| Aspect ratio (derived) | 2.00:1 |
| Regain coefficient R | 0.50 |
| Σ K (fittings) | 0.350 |
| Terminal SP | 125.0 Pa |

Fittings on this section

1 × (Direct input of K value)    (K = 0.350)    →    0.350

─── Σ K  =  0.350  ───

Step 1: Static-regain balance for V_down

Formula: R · (Vp_up − Vp_down) = ΔPf + Σ K · Vp_down [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g); Vp-to-SP conversion SMACNA Sec. 5.6.3]

Substitution: R = 0.50, Vp_up = ½ · ρ · V_up² = 16.2 Pa, Vp_down = ½ · ρ · V_down² = 7.2 Pa, regain credit = 4.5 Pa approx. ΔPf + Σ K · Vp_down = 1.4 Pa + 2.5 Pa

Result: V_down = 3.46 m/s

Note: Solver: bisection on V ∈ [V_min, V_up] until the regain credit equals the sum of friction and fitting losses.

Step 2: Cross-section sizing (snap to standard catalogue)

Formula: Rect: a, b chosen so that De = 1.30 (a · b)^0.625 / (a + b)^0.25 [ASHRAE F-21 Eq. (25)]

Substitution: A = Q / V = 0.6220 m³/s / 3.456 m/s = 0.1800 m² = selected 600 mm × 300 mm (AR = 2.00:1); De = 457 mm (selected); continuous regain solution De_calc = 449 mm (bisection; catalogue step selected the sides above)

Result: Final size = Rect 600 × 300 mm

Note: Catalogue: SI 100–2000 mm in 50-mm steps

Step 3: Reynolds number and Darcy friction factor

Formula: Re = ρ · V_e · De / μ [ASHRAE F-21 Eq. (20)]; 1/√f = −2 · log₁₀(ε / (3.7 De) + 2.51 / (Re · √f)) [Colebrook–White, Eq. (19)]

Substitution: ρ = 1.204 kg/m³, μ = 1.810e-05 Pa·s, De = 457 mm, V_e = 3.79 m/s, ε = 0.090 mm → Re = 115,271, ε/De = 0.00020

Result: f = 0.01855

Note: Friction uses the equivalent-round velocity V_e = Q/(π·De²/4) = 3.79 m/s; the rectangular face velocity V = 3.46 m/s drives Vp and the regain credit (Steps 1, 5, 6).

Step 4: Friction loss along the section

Formula: ΔPf = f · (L / De) · ½ · ρ · V_e² [Darcy–Weisbach, ASHRAE F-21 Eq. (18)]

Substitution: f = 0.01855, L = 4.00 m, De = 457 mm, ½ρV_e² = 8.7 Pa

Result: ΔPf = 1.4 Pa

Step 5: Fitting losses

Formula: ΔPfit = Σ K · Vp, Vp = ½ · ρ · V²

Substitution: Σ K = 0.350, Vp = 7.2 Pa → ΔPfit = 0.350 × 7.2 Pa

Result: ΔPfit = 2.5 Pa

Step 6: Static-regain credit

Formula: ΔPs = R · (Vp_up − Vp_down) [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g)]

Substitution: R = 0.50, Vp_up = 16.2 Pa, Vp_down = 7.2 Pa

Result: ΔPs = 4.5 Pa

Step 7: Cumulative duct losses to end of section

Formula: Σ SP_n = Σ SP_(n−1) + ΔPf + ΔPfit − ΔPs

Substitution: Σ SP_prev = 70.3 Pa + ΔPf 1.4 Pa + ΔPfit 2.5 Pa − ΔPs 4.5 Pa

Result: Σ SP_end = 69.8 Pa

Note: Add the leaf's terminal-SP requirement to obtain the fan SP needed on this path.

Section  Riser L06-L05

Inputs

| Input | Value |
| --- | --- |
| Parent | Riser L07-L06 |
| Length L | 3.60 m |
| Flow Q (through) | 3,110 L/s |
| Shape | Rectangular |
| Aspect ratio (derived) | 1.92:1 |
| Regain coefficient R | 0.75 |
| Σ K (fittings) | 0.050 |

Fittings on this section

1 × (Direct input of K value)    (K = 0.050)    →    0.050

─── Σ K  =  0.050  ───

Step 1: Static-regain balance for V_down

Formula: R · (Vp_up − Vp_down) = ΔPf + Σ K · Vp_down [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g); Vp-to-SP conversion SMACNA Sec. 5.6.3]

Substitution: R = 0.75, Vp_up = ½ · ρ · V_up² = 16.2 Pa, Vp_down = ½ · ρ · V_down² = 12.2 Pa, regain credit = 3.0 Pa approx. ΔPf + Σ K · Vp_down = 0.9 Pa + 0.6 Pa

Result: V_down = 4.51 m/s

Note: Solver: bisection on V ∈ [V_min, V_up] until the regain credit equals the sum of friction and fitting losses.

Step 2: Cross-section sizing (snap to standard catalogue)

Formula: Rect: a, b chosen so that De = 1.30 (a · b)^0.625 / (a + b)^0.25 [ASHRAE F-21 Eq. (25)]

Substitution: A = Q / V = 3.1100 m³/s / 4.507 m/s = 0.6900 m² = selected 1,150 mm × 600 mm (AR = 1.92:1); De = 896 mm (selected); continuous regain solution De_calc = 868 mm (bisection; catalogue step selected the sides above)

Result: Final size = Rect 1150 × 600 mm

Note: Catalogue: SI 100–2000 mm in 50-mm steps

Step 3: Reynolds number and Darcy friction factor

Formula: Re = ρ · V_e · De / μ [ASHRAE F-21 Eq. (20)]; 1/√f = −2 · log₁₀(ε / (3.7 De) + 2.51 / (Re · √f)) [Colebrook–White, Eq. (19)]

Substitution: ρ = 1.204 kg/m³, μ = 1.810e-05 Pa·s, De = 896 mm, V_e = 4.93 m/s, ε = 0.090 mm → Re = 293,869, ε/De = 0.00010

Result: f = 0.01548

Note: Friction uses the equivalent-round velocity V_e = Q/(π·De²/4) = 4.93 m/s; the rectangular face velocity V = 4.51 m/s drives Vp and the regain credit (Steps 1, 5, 6).

Step 4: Friction loss along the section

Formula: ΔPf = f · (L / De) · ½ · ρ · V_e² [Darcy–Weisbach, ASHRAE F-21 Eq. (18)]

Substitution: f = 0.01548, L = 3.60 m, De = 896 mm, ½ρV_e² = 14.6 Pa

Result: ΔPf = 0.9 Pa

Step 5: Fitting losses

Formula: ΔPfit = Σ K · Vp, Vp = ½ · ρ · V²

Substitution: Σ K = 0.050, Vp = 12.2 Pa → ΔPfit = 0.050 × 12.2 Pa

Result: ΔPfit = 0.6 Pa

Step 6: Static-regain credit

Formula: ΔPs = R · (Vp_up − Vp_down) [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g)]

Substitution: R = 0.75, Vp_up = 16.2 Pa, Vp_down = 12.2 Pa

Result: ΔPs = 3.0 Pa

Step 7: Cumulative duct losses to end of section

Formula: Σ SP_n = Σ SP_(n−1) + ΔPf + ΔPfit − ΔPs

Substitution: Σ SP_prev = 70.3 Pa + ΔPf 0.9 Pa + ΔPfit 0.6 Pa − ΔPs 3.0 Pa

Result: Σ SP_end = 68.9 Pa

Section  L05 floor branch

Inputs

| Input | Value |
| --- | --- |
| Parent | Riser L06-L05 |
| Length L | 4.00 m |
| Flow Q (through) | 622 L/s |
| Shape | Rectangular |
| Aspect ratio (derived) | 2.00:1 |
| Regain coefficient R | 0.50 |
| Σ K (fittings) | 0.350 |
| Terminal SP | 125.0 Pa |

Fittings on this section

1 × (Direct input of K value)    (K = 0.350)    →    0.350

─── Σ K  =  0.350  ───

Step 1: Static-regain balance for V_down

Formula: R · (Vp_up − Vp_down) = ΔPf + Σ K · Vp_down [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g); Vp-to-SP conversion SMACNA Sec. 5.6.3]

Substitution: R = 0.50, Vp_up = ½ · ρ · V_up² = 12.2 Pa, Vp_down = ½ · ρ · V_down² = 7.2 Pa, regain credit = 2.5 Pa approx. ΔPf + Σ K · Vp_down = 1.4 Pa + 2.5 Pa

Result: V_down = 3.46 m/s

Note: Solver: bisection on V ∈ [V_min, V_up] until the regain credit equals the sum of friction and fitting losses.

Step 2: Cross-section sizing (snap to standard catalogue)

Formula: Rect: a, b chosen so that De = 1.30 (a · b)^0.625 / (a + b)^0.25 [ASHRAE F-21 Eq. (25)]

Substitution: A = Q / V = 0.6220 m³/s / 3.456 m/s = 0.1800 m² = selected 600 mm × 300 mm (AR = 2.00:1); De = 457 mm (selected); continuous regain solution De_calc = 480 mm (bisection; catalogue step selected the sides above)

Result: Final size = Rect 600 × 300 mm

Note: Catalogue: SI 100–2000 mm in 50-mm steps

Step 3: Reynolds number and Darcy friction factor

Formula: Re = ρ · V_e · De / μ [ASHRAE F-21 Eq. (20)]; 1/√f = −2 · log₁₀(ε / (3.7 De) + 2.51 / (Re · √f)) [Colebrook–White, Eq. (19)]

Substitution: ρ = 1.204 kg/m³, μ = 1.810e-05 Pa·s, De = 457 mm, V_e = 3.79 m/s, ε = 0.090 mm → Re = 115,271, ε/De = 0.00020

Result: f = 0.01855

Note: Friction uses the equivalent-round velocity V_e = Q/(π·De²/4) = 3.79 m/s; the rectangular face velocity V = 3.46 m/s drives Vp and the regain credit (Steps 1, 5, 6).

Step 4: Friction loss along the section

Formula: ΔPf = f · (L / De) · ½ · ρ · V_e² [Darcy–Weisbach, ASHRAE F-21 Eq. (18)]

Substitution: f = 0.01855, L = 4.00 m, De = 457 mm, ½ρV_e² = 8.7 Pa

Result: ΔPf = 1.4 Pa

Step 5: Fitting losses

Formula: ΔPfit = Σ K · Vp, Vp = ½ · ρ · V²

Substitution: Σ K = 0.350, Vp = 7.2 Pa → ΔPfit = 0.350 × 7.2 Pa

Result: ΔPfit = 2.5 Pa

Step 6: Static-regain credit

Formula: ΔPs = R · (Vp_up − Vp_down) [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g)]

Substitution: R = 0.50, Vp_up = 12.2 Pa, Vp_down = 7.2 Pa

Result: ΔPs = 2.5 Pa

Step 7: Cumulative duct losses to end of section

Formula: Σ SP_n = Σ SP_(n−1) + ΔPf + ΔPfit − ΔPs

Substitution: Σ SP_prev = 68.9 Pa + ΔPf 1.4 Pa + ΔPfit 2.5 Pa − ΔPs 2.5 Pa

Result: Σ SP_end = 70.3 Pa

Note: Add the leaf's terminal-SP requirement to obtain the fan SP needed on this path.

Section  Riser L05-L04

Inputs

| Input | Value |
| --- | --- |
| Parent | Riser L06-L05 |
| Length L | 3.60 m |
| Flow Q (through) | 2,488 L/s |
| Shape | Rectangular |
| Aspect ratio (derived) | 2.00:1 |
| Regain coefficient R | 0.75 |
| Σ K (fittings) | 0.050 |

Fittings on this section

1 × (Direct input of K value)    (K = 0.050)    →    0.050

─── Σ K  =  0.050  ───

Step 1: Static-regain balance for V_down

Formula: R · (Vp_up − Vp_down) = ΔPf + Σ K · Vp_down [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g); Vp-to-SP conversion SMACNA Sec. 5.6.3]

Substitution: R = 0.75, Vp_up = ½ · ρ · V_up² = 12.2 Pa, Vp_down = ½ · ρ · V_down² = 10.2 Pa, regain credit = 1.5 Pa approx. ΔPf + Σ K · Vp_down = 0.8 Pa + 0.5 Pa

Result: V_down = 4.11 m/s

Note: Solver: bisection on V ∈ [V_min, V_up] until the regain credit equals the sum of friction and fitting losses.

Step 2: Cross-section sizing (snap to standard catalogue)

Formula: Rect: a, b chosen so that De = 1.30 (a · b)^0.625 / (a + b)^0.25 [ASHRAE F-21 Eq. (25)]

Substitution: A = Q / V = 2.4880 m³/s / 4.112 m/s = 0.6050 m² = selected 1,100 mm × 550 mm (AR = 2.00:1); De = 838 mm (selected); continuous regain solution De_calc = 834 mm (bisection; catalogue step selected the sides above)

Result: Final size = Rect 1100 × 550 mm

Note: Catalogue: SI 100–2000 mm in 50-mm steps

Step 3: Reynolds number and Darcy friction factor

Formula: Re = ρ · V_e · De / μ [ASHRAE F-21 Eq. (20)]; 1/√f = −2 · log₁₀(ε / (3.7 De) + 2.51 / (Re · √f)) [Colebrook–White, Eq. (19)]

Substitution: ρ = 1.204 kg/m³, μ = 1.810e-05 Pa·s, De = 838 mm, V_e = 4.51 m/s, ε = 0.090 mm → Re = 251,501, ε/De = 0.00011

Result: f = 0.01590

Note: Friction uses the equivalent-round velocity V_e = Q/(π·De²/4) = 4.51 m/s; the rectangular face velocity V = 4.11 m/s drives Vp and the regain credit (Steps 1, 5, 6).

Step 4: Friction loss along the section

Formula: ΔPf = f · (L / De) · ½ · ρ · V_e² [Darcy–Weisbach, ASHRAE F-21 Eq. (18)]

Substitution: f = 0.01590, L = 3.60 m, De = 838 mm, ½ρV_e² = 12.3 Pa

Result: ΔPf = 0.8 Pa

Step 5: Fitting losses

Formula: ΔPfit = Σ K · Vp, Vp = ½ · ρ · V²

Substitution: Σ K = 0.050, Vp = 10.2 Pa → ΔPfit = 0.050 × 10.2 Pa

Result: ΔPfit = 0.5 Pa

Step 6: Static-regain credit

Formula: ΔPs = R · (Vp_up − Vp_down) [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g)]

Substitution: R = 0.75, Vp_up = 12.2 Pa, Vp_down = 10.2 Pa

Result: ΔPs = 1.5 Pa

Step 7: Cumulative duct losses to end of section

Formula: Σ SP_n = Σ SP_(n−1) + ΔPf + ΔPfit − ΔPs

Substitution: Σ SP_prev = 68.9 Pa + ΔPf 0.8 Pa + ΔPfit 0.5 Pa − ΔPs 1.5 Pa

Result: Σ SP_end = 68.7 Pa

Section  L04 floor branch

Inputs

| Input | Value |
| --- | --- |
| Parent | Riser L05-L04 |
| Length L | 4.00 m |
| Flow Q (through) | 622 L/s |
| Shape | Rectangular |
| Aspect ratio (derived) | 1.86:1 |
| Regain coefficient R | 0.50 |
| Σ K (fittings) | 0.350 |
| Terminal SP | 125.0 Pa |

Fittings on this section

1 × (Direct input of K value)    (K = 0.350)    →    0.350

─── Σ K  =  0.350  ───

Step 1: Static-regain balance for V_down

Formula: R · (Vp_up − Vp_down) = ΔPf + Σ K · Vp_down [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g); Vp-to-SP conversion SMACNA Sec. 5.6.3]

Substitution: R = 0.50, Vp_up = ½ · ρ · V_up² = 10.2 Pa, Vp_down = ½ · ρ · V_down² = 4.5 Pa, regain credit = 2.8 Pa approx. ΔPf + Σ K · Vp_down = 0.8 Pa + 1.6 Pa

Result: V_down = 2.73 m/s

Note: Solver: bisection on V ∈ [V_min, V_up] until the regain credit equals the sum of friction and fitting losses.

Step 2: Cross-section sizing (snap to standard catalogue)

Formula: Rect: a, b chosen so that De = 1.30 (a · b)^0.625 / (a + b)^0.25 [ASHRAE F-21 Eq. (25)]

Substitution: A = Q / V = 0.6220 m³/s / 2.734 m/s = 0.2275 m² = selected 650 mm × 350 mm (AR = 1.86:1); De = 515 mm (selected); continuous regain solution De_calc = 502 mm (bisection; catalogue step selected the sides above)

Result: Final size = Rect 650 × 350 mm

Note: Catalogue: SI 100–2000 mm in 50-mm steps

Step 3: Reynolds number and Darcy friction factor

Formula: Re = ρ · V_e · De / μ [ASHRAE F-21 Eq. (20)]; 1/√f = −2 · log₁₀(ε / (3.7 De) + 2.51 / (Re · √f)) [Colebrook–White, Eq. (19)]

Substitution: ρ = 1.204 kg/m³, μ = 1.810e-05 Pa·s, De = 515 mm, V_e = 2.98 m/s, ε = 0.090 mm → Re = 102,233, ε/De = 0.00017

Result: f = 0.01881

Note: Friction uses the equivalent-round velocity V_e = Q/(π·De²/4) = 2.98 m/s; the rectangular face velocity V = 2.73 m/s drives Vp and the regain credit (Steps 1, 5, 6).

Step 4: Friction loss along the section

Formula: ΔPf = f · (L / De) · ½ · ρ · V_e² [Darcy–Weisbach, ASHRAE F-21 Eq. (18)]

Substitution: f = 0.01881, L = 4.00 m, De = 515 mm, ½ρV_e² = 5.4 Pa

Result: ΔPf = 0.8 Pa

Step 5: Fitting losses

Formula: ΔPfit = Σ K · Vp, Vp = ½ · ρ · V²

Substitution: Σ K = 0.350, Vp = 4.5 Pa → ΔPfit = 0.350 × 4.5 Pa

Result: ΔPfit = 1.6 Pa

Step 6: Static-regain credit

Formula: ΔPs = R · (Vp_up − Vp_down) [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g)]

Substitution: R = 0.50, Vp_up = 10.2 Pa, Vp_down = 4.5 Pa

Result: ΔPs = 2.8 Pa

Step 7: Cumulative duct losses to end of section

Formula: Σ SP_n = Σ SP_(n−1) + ΔPf + ΔPfit − ΔPs

Substitution: Σ SP_prev = 68.7 Pa + ΔPf 0.8 Pa + ΔPfit 1.6 Pa − ΔPs 2.8 Pa

Result: Σ SP_end = 68.2 Pa

Note: Add the leaf's terminal-SP requirement to obtain the fan SP needed on this path.

Section  Riser L04-L03

Inputs

| Input | Value |
| --- | --- |
| Parent | Riser L05-L04 |
| Length L | 3.60 m |
| Flow Q (through) | 1,866 L/s |
| Shape | Rectangular |
| Aspect ratio (derived) | 2.00:1 |
| Regain coefficient R | 0.75 |
| Σ K (fittings) | 0.050 |

Fittings on this section

1 × (Direct input of K value)    (K = 0.050)    →    0.050

─── Σ K  =  0.050  ───

Step 1: Static-regain balance for V_down

Formula: R · (Vp_up − Vp_down) = ΔPf + Σ K · Vp_down [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g); Vp-to-SP conversion SMACNA Sec. 5.6.3]

Substitution: R = 0.75, Vp_up = ½ · ρ · V_up² = 10.2 Pa, Vp_down = ½ · ρ · V_down² = 8.4 Pa, regain credit = 1.3 Pa approx. ΔPf + Σ K · Vp_down = 0.8 Pa + 0.4 Pa

Result: V_down = 3.73 m/s

Note: Solver: bisection on V ∈ [V_min, V_up] until the regain credit equals the sum of friction and fitting losses.

Step 2: Cross-section sizing (snap to standard catalogue)

Formula: Rect: a, b chosen so that De = 1.30 (a · b)^0.625 / (a + b)^0.25 [ASHRAE F-21 Eq. (25)]

Substitution: A = Q / V = 1.8660 m³/s / 3.732 m/s = 0.5000 m² = selected 1,000 mm × 500 mm (AR = 2.00:1); De = 762 mm (selected); continuous regain solution De_calc = 758 mm (bisection; catalogue step selected the sides above)

Result: Final size = Rect 1000 × 500 mm

Note: Catalogue: SI 100–2000 mm in 50-mm steps

Step 3: Reynolds number and Darcy friction factor

Formula: Re = ρ · V_e · De / μ [ASHRAE F-21 Eq. (20)]; 1/√f = −2 · log₁₀(ε / (3.7 De) + 2.51 / (Re · √f)) [Colebrook–White, Eq. (19)]

Substitution: ρ = 1.204 kg/m³, μ = 1.810e-05 Pa·s, De = 762 mm, V_e = 4.10 m/s, ε = 0.090 mm → Re = 207,488, ε/De = 0.00012

Result: f = 0.01645

Note: Friction uses the equivalent-round velocity V_e = Q/(π·De²/4) = 4.10 m/s; the rectangular face velocity V = 3.73 m/s drives Vp and the regain credit (Steps 1, 5, 6).

Step 4: Friction loss along the section

Formula: ΔPf = f · (L / De) · ½ · ρ · V_e² [Darcy–Weisbach, ASHRAE F-21 Eq. (18)]

Substitution: f = 0.01645, L = 3.60 m, De = 762 mm, ½ρV_e² = 10.1 Pa

Result: ΔPf = 0.8 Pa

Step 5: Fitting losses

Formula: ΔPfit = Σ K · Vp, Vp = ½ · ρ · V²

Substitution: Σ K = 0.050, Vp = 8.4 Pa → ΔPfit = 0.050 × 8.4 Pa

Result: ΔPfit = 0.4 Pa

Step 6: Static-regain credit

Formula: ΔPs = R · (Vp_up − Vp_down) [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g)]

Substitution: R = 0.75, Vp_up = 10.2 Pa, Vp_down = 8.4 Pa

Result: ΔPs = 1.3 Pa

Step 7: Cumulative duct losses to end of section

Formula: Σ SP_n = Σ SP_(n−1) + ΔPf + ΔPfit − ΔPs

Substitution: Σ SP_prev = 68.7 Pa + ΔPf 0.8 Pa + ΔPfit 0.4 Pa − ΔPs 1.3 Pa

Result: Σ SP_end = 68.6 Pa

Section  L03 floor branch

Inputs

| Input | Value |
| --- | --- |
| Parent | Riser L04-L03 |
| Length L | 4.00 m |
| Flow Q (through) | 622 L/s |
| Shape | Rectangular |
| Aspect ratio (derived) | 2.00:1 |
| Regain coefficient R | 0.50 |
| Σ K (fittings) | 0.350 |
| Terminal SP | 125.0 Pa |

Fittings on this section

1 × (Direct input of K value)    (K = 0.350)    →    0.350

─── Σ K  =  0.350  ───

Step 1: Static-regain balance for V_down

Formula: R · (Vp_up − Vp_down) = ΔPf + Σ K · Vp_down [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g); Vp-to-SP conversion SMACNA Sec. 5.6.3]

Substitution: R = 0.50, Vp_up = ½ · ρ · V_up² = 8.4 Pa, Vp_down = ½ · ρ · V_down² = 3.9 Pa, regain credit = 2.3 Pa approx. ΔPf + Σ K · Vp_down = 0.7 Pa + 1.4 Pa

Result: V_down = 2.54 m/s

Note: Solver: bisection on V ∈ [V_min, V_up] until the regain credit equals the sum of friction and fitting losses.

Step 2: Cross-section sizing (snap to standard catalogue)

Formula: Rect: a, b chosen so that De = 1.30 (a · b)^0.625 / (a + b)^0.25 [ASHRAE F-21 Eq. (25)]

Substitution: A = Q / V = 0.6220 m³/s / 2.539 m/s = 0.2450 m² = selected 700 mm × 350 mm (AR = 2.00:1); De = 533 mm (selected); continuous regain solution De_calc = 526 mm (bisection; catalogue step selected the sides above)

Result: Final size = Rect 700 × 350 mm

Note: Catalogue: SI 100–2000 mm in 50-mm steps

Step 3: Reynolds number and Darcy friction factor

Formula: Re = ρ · V_e · De / μ [ASHRAE F-21 Eq. (20)]; 1/√f = −2 · log₁₀(ε / (3.7 De) + 2.51 / (Re · √f)) [Colebrook–White, Eq. (19)]

Substitution: ρ = 1.204 kg/m³, μ = 1.810e-05 Pa·s, De = 533 mm, V_e = 2.79 m/s, ε = 0.090 mm → Re = 98,804, ε/De = 0.00017

Result: f = 0.01889

Note: Friction uses the equivalent-round velocity V_e = Q/(π·De²/4) = 2.79 m/s; the rectangular face velocity V = 2.54 m/s drives Vp and the regain credit (Steps 1, 5, 6).

Step 4: Friction loss along the section

Formula: ΔPf = f · (L / De) · ½ · ρ · V_e² [Darcy–Weisbach, ASHRAE F-21 Eq. (18)]

Substitution: f = 0.01889, L = 4.00 m, De = 533 mm, ½ρV_e² = 4.7 Pa

Result: ΔPf = 0.7 Pa

Step 5: Fitting losses

Formula: ΔPfit = Σ K · Vp, Vp = ½ · ρ · V²

Substitution: Σ K = 0.350, Vp = 3.9 Pa → ΔPfit = 0.350 × 3.9 Pa

Result: ΔPfit = 1.4 Pa

Step 6: Static-regain credit

Formula: ΔPs = R · (Vp_up − Vp_down) [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g)]

Substitution: R = 0.50, Vp_up = 8.4 Pa, Vp_down = 3.9 Pa

Result: ΔPs = 2.3 Pa

Step 7: Cumulative duct losses to end of section

Formula: Σ SP_n = Σ SP_(n−1) + ΔPf + ΔPfit − ΔPs

Substitution: Σ SP_prev = 68.6 Pa + ΔPf 0.7 Pa + ΔPfit 1.4 Pa − ΔPs 2.3 Pa

Result: Σ SP_end = 68.3 Pa

Note: Add the leaf's terminal-SP requirement to obtain the fan SP needed on this path.

Section  Riser L03-L02

Inputs

| Input | Value |
| --- | --- |
| Parent | Riser L04-L03 |
| Length L | 3.60 m |
| Flow Q (through) | 1,244 L/s |
| Shape | Rectangular |
| Aspect ratio (derived) | 1.89:1 |
| Regain coefficient R | 0.75 |
| Σ K (fittings) | 0.050 |

Fittings on this section

1 × (Direct input of K value)    (K = 0.050)    →    0.050

─── Σ K  =  0.050  ───

Step 1: Static-regain balance for V_down

Formula: R · (Vp_up − Vp_down) = ΔPf + Σ K · Vp_down [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g); Vp-to-SP conversion SMACNA Sec. 5.6.3]

Substitution: R = 0.75, Vp_up = ½ · ρ · V_up² = 8.4 Pa, Vp_down = ½ · ρ · V_down² = 6.4 Pa, regain credit = 1.5 Pa approx. ΔPf + Σ K · Vp_down = 0.7 Pa + 0.3 Pa

Result: V_down = 3.25 m/s

Note: Solver: bisection on V ∈ [V_min, V_up] until the regain credit equals the sum of friction and fitting losses.

Step 2: Cross-section sizing (snap to standard catalogue)

Formula: Rect: a, b chosen so that De = 1.30 (a · b)^0.625 / (a + b)^0.25 [ASHRAE F-21 Eq. (25)]

Substitution: A = Q / V = 1.2440 m³/s / 3.252 m/s = 0.3825 m² = selected 850 mm × 450 mm (AR = 1.89:1); De = 668 mm (selected); continuous regain solution De_calc = 653 mm (bisection; catalogue step selected the sides above)

Result: Final size = Rect 850 × 450 mm

Note: Catalogue: SI 100–2000 mm in 50-mm steps

Step 3: Reynolds number and Darcy friction factor

Formula: Re = ρ · V_e · De / μ [ASHRAE F-21 Eq. (20)]; 1/√f = −2 · log₁₀(ε / (3.7 De) + 2.51 / (Re · √f)) [Colebrook–White, Eq. (19)]

Substitution: ρ = 1.204 kg/m³, μ = 1.810e-05 Pa·s, De = 668 mm, V_e = 3.55 m/s, ε = 0.090 mm → Re = 157,789, ε/De = 0.00013

Result: f = 0.01729

Note: Friction uses the equivalent-round velocity V_e = Q/(π·De²/4) = 3.55 m/s; the rectangular face velocity V = 3.25 m/s drives Vp and the regain credit (Steps 1, 5, 6).

Step 4: Friction loss along the section

Formula: ΔPf = f · (L / De) · ½ · ρ · V_e² [Darcy–Weisbach, ASHRAE F-21 Eq. (18)]

Substitution: f = 0.01729, L = 3.60 m, De = 668 mm, ½ρV_e² = 7.6 Pa

Result: ΔPf = 0.7 Pa

Step 5: Fitting losses

Formula: ΔPfit = Σ K · Vp, Vp = ½ · ρ · V²

Substitution: Σ K = 0.050, Vp = 6.4 Pa → ΔPfit = 0.050 × 6.4 Pa

Result: ΔPfit = 0.3 Pa

Step 6: Static-regain credit

Formula: ΔPs = R · (Vp_up − Vp_down) [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g)]

Substitution: R = 0.75, Vp_up = 8.4 Pa, Vp_down = 6.4 Pa

Result: ΔPs = 1.5 Pa

Step 7: Cumulative duct losses to end of section

Formula: Σ SP_n = Σ SP_(n−1) + ΔPf + ΔPfit − ΔPs

Substitution: Σ SP_prev = 68.6 Pa + ΔPf 0.7 Pa + ΔPfit 0.3 Pa − ΔPs 1.5 Pa

Result: Σ SP_end = 68.1 Pa

Section  L02 floor branch

Inputs

| Input | Value |
| --- | --- |
| Parent | Riser L03-L02 |
| Length L | 4.00 m |
| Flow Q (through) | 622 L/s |
| Shape | Rectangular |
| Aspect ratio (derived) | 1.88:1 |
| Regain coefficient R | 0.50 |
| Σ K (fittings) | 0.350 |
| Terminal SP | 125.0 Pa |

Fittings on this section

1 × (Direct input of K value)    (K = 0.350)    →    0.350

─── Σ K  =  0.350  ───

Step 1: Static-regain balance for V_down

Formula: R · (Vp_up − Vp_down) = ΔPf + Σ K · Vp_down [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g); Vp-to-SP conversion SMACNA Sec. 5.6.3]

Substitution: R = 0.50, Vp_up = ½ · ρ · V_up² = 6.4 Pa, Vp_down = ½ · ρ · V_down² = 2.6 Pa, regain credit = 1.9 Pa approx. ΔPf + Σ K · Vp_down = 0.4 Pa + 0.9 Pa

Result: V_down = 2.07 m/s

Note: Solver: bisection on V ∈ [V_min, V_up] until the regain credit equals the sum of friction and fitting losses.

Step 2: Cross-section sizing (snap to standard catalogue)

Formula: Rect: a, b chosen so that De = 1.30 (a · b)^0.625 / (a + b)^0.25 [ASHRAE F-21 Eq. (25)]

Substitution: A = Q / V = 0.6220 m³/s / 2.073 m/s = 0.3000 m² = selected 750 mm × 400 mm (AR = 1.88:1); De = 592 mm (selected); continuous regain solution De_calc = 562 mm (bisection; catalogue step selected the sides above)

Result: Final size = Rect 750 × 400 mm

Note: Catalogue: SI 100–2000 mm in 50-mm steps

Step 3: Reynolds number and Darcy friction factor

Formula: Re = ρ · V_e · De / μ [ASHRAE F-21 Eq. (20)]; 1/√f = −2 · log₁₀(ε / (3.7 De) + 2.51 / (Re · √f)) [Colebrook–White, Eq. (19)]

Substitution: ρ = 1.204 kg/m³, μ = 1.810e-05 Pa·s, De = 592 mm, V_e = 2.26 m/s, ε = 0.090 mm → Re = 89,059, ε/De = 0.00015

Result: f = 0.01917

Note: Friction uses the equivalent-round velocity V_e = Q/(π·De²/4) = 2.26 m/s; the rectangular face velocity V = 2.07 m/s drives Vp and the regain credit (Steps 1, 5, 6).

Step 4: Friction loss along the section

Formula: ΔPf = f · (L / De) · ½ · ρ · V_e² [Darcy–Weisbach, ASHRAE F-21 Eq. (18)]

Substitution: f = 0.01917, L = 4.00 m, De = 592 mm, ½ρV_e² = 3.1 Pa

Result: ΔPf = 0.4 Pa

Step 5: Fitting losses

Formula: ΔPfit = Σ K · Vp, Vp = ½ · ρ · V²

Substitution: Σ K = 0.350, Vp = 2.6 Pa → ΔPfit = 0.350 × 2.6 Pa

Result: ΔPfit = 0.9 Pa

Step 6: Static-regain credit

Formula: ΔPs = R · (Vp_up − Vp_down) [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g)]

Substitution: R = 0.50, Vp_up = 6.4 Pa, Vp_down = 2.6 Pa

Result: ΔPs = 1.9 Pa

Step 7: Cumulative duct losses to end of section

Formula: Σ SP_n = Σ SP_(n−1) + ΔPf + ΔPfit − ΔPs

Substitution: Σ SP_prev = 68.1 Pa + ΔPf 0.4 Pa + ΔPfit 0.9 Pa − ΔPs 1.9 Pa

Result: Σ SP_end = 67.5 Pa

Note: Add the leaf's terminal-SP requirement to obtain the fan SP needed on this path.

Section  Riser end run to L01

Inputs

| Input | Value |
| --- | --- |
| Parent | Riser L03-L02 |
| Length L | 7.60 m |
| Flow Q (through) | 622 L/s |
| Shape | Rectangular |
| Aspect ratio (derived) | 2.00:1 |
| Regain coefficient R | 0.75 |
| Σ K (fittings) | 0.300 |
| Terminal SP | 125.0 Pa |

Fittings on this section

1 × (Direct input of K value)    (K = 0.300)    →    0.300

─── Σ K  =  0.300  ───

Step 1: Static-regain balance for V_down

Formula: R · (Vp_up − Vp_down) = ΔPf + Σ K · Vp_down [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g); Vp-to-SP conversion SMACNA Sec. 5.6.3]

Substitution: R = 0.75, Vp_up = ½ · ρ · V_up² = 6.4 Pa, Vp_down = ½ · ρ · V_down² = 3.9 Pa, regain credit = 1.9 Pa approx. ΔPf + Σ K · Vp_down = 1.3 Pa + 1.2 Pa

Result: V_down = 2.54 m/s

Note: Solver: bisection on V ∈ [V_min, V_up] until the regain credit equals the sum of friction and fitting losses.

Step 2: Cross-section sizing (snap to standard catalogue)

Formula: Rect: a, b chosen so that De = 1.30 (a · b)^0.625 / (a + b)^0.25 [ASHRAE F-21 Eq. (25)]

Substitution: A = Q / V = 0.6220 m³/s / 2.539 m/s = 0.2450 m² = selected 700 mm × 350 mm (AR = 2.00:1); De = 533 mm (selected); continuous regain solution De_calc = 547 mm (bisection; catalogue step selected the sides above)

Result: Final size = Rect 700 × 350 mm

Note: Catalogue: SI 100–2000 mm in 50-mm steps

Step 3: Reynolds number and Darcy friction factor

Formula: Re = ρ · V_e · De / μ [ASHRAE F-21 Eq. (20)]; 1/√f = −2 · log₁₀(ε / (3.7 De) + 2.51 / (Re · √f)) [Colebrook–White, Eq. (19)]

Substitution: ρ = 1.204 kg/m³, μ = 1.810e-05 Pa·s, De = 533 mm, V_e = 2.79 m/s, ε = 0.090 mm → Re = 98,804, ε/De = 0.00017

Result: f = 0.01889

Note: Friction uses the equivalent-round velocity V_e = Q/(π·De²/4) = 2.79 m/s; the rectangular face velocity V = 2.54 m/s drives Vp and the regain credit (Steps 1, 5, 6).

Step 4: Friction loss along the section

Formula: ΔPf = f · (L / De) · ½ · ρ · V_e² [Darcy–Weisbach, ASHRAE F-21 Eq. (18)]

Substitution: f = 0.01889, L = 7.60 m, De = 533 mm, ½ρV_e² = 4.7 Pa

Result: ΔPf = 1.3 Pa

Step 5: Fitting losses

Formula: ΔPfit = Σ K · Vp, Vp = ½ · ρ · V²

Substitution: Σ K = 0.300, Vp = 3.9 Pa → ΔPfit = 0.300 × 3.9 Pa

Result: ΔPfit = 1.2 Pa

Step 6: Static-regain credit

Formula: ΔPs = R · (Vp_up − Vp_down) [ASHRAE F-21 Eq. (41); R per SMACNA Sec. 7.2 (g)]

Substitution: R = 0.75, Vp_up = 6.4 Pa, Vp_down = 3.9 Pa

Result: ΔPs = 1.9 Pa

Step 7: Cumulative duct losses to end of section

Formula: Σ SP_n = Σ SP_(n−1) + ΔPf + ΔPfit − ΔPs

Substitution: Σ SP_prev = 68.1 Pa + ΔPf 1.3 Pa + ΔPfit 1.2 Pa − ΔPs 1.9 Pa

Result: Σ SP_end = 68.6 Pa

Note: Add the leaf's terminal-SP requirement to obtain the fan SP needed on this path.

ℹ Informational notes

• [L10 floor branch] Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).

• [Riser L10-L09] Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).

• [Riser L09-L08] Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).

• [L08 floor branch] Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).

• [Riser L08-L07] Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).

• [L06 floor branch] Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).

• [Riser L06-L05] Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).

• [Riser L05-L04] Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).

• [L04 floor branch] Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).

• [Riser L04-L03] Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).

• [L03 floor branch] Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).

• [Riser L03-L02] Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).

• [L02 floor branch] Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).

# 5.  Results — All Sections

| Section | Q | L | V | Shape | Size | ΔPf | ΔPfit | ΔP_eq | Regain | Σ SP |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | L/s | m | m/s |  |  | Pa | Pa | Pa | Pa | Pa |
| ★ FAHU-01 discharge | 6,220.0 | 6.00 | 7.66 | Rect | Rect 1250 × 650 mm | 3.7 | 21.2 | 50.0 | 0.0 | 74.9 |
| L10 floor branch | 622.0 | 4.00 | 4.98 | Rect | Rect 500 × 250 mm | 3.4 | 5.2 | 0.0 | 10.2 | 73.3 |
| ★ Riser L10-L09 | 5,598.0 | 3.60 | 6.89 | Rect | Rect 1250 × 650 mm | 1.8 | 1.4 | 0.0 | 5.0 | 73.1 |
| ★ L09 floor branch | 622.0 | 4.00 | 4.98 | Rect | Rect 500 × 250 mm | 3.4 | 5.2 | 0.0 | 6.8 | 74.9 |
| Riser L09-L08 | 4,976.0 | 3.60 | 6.12 | Rect | Rect 1250 × 650 mm | 1.5 | 1.1 | 0.0 | 4.5 | 71.2 |
| L08 floor branch | 622.0 | 4.00 | 3.77 | Rect | Rect 550 × 300 mm | 1.7 | 3.0 | 0.0 | 7.0 | 68.9 |
| Riser L08-L07 | 4,354.0 | 3.60 | 5.36 | Rect | Rect 1250 × 650 mm | 1.1 | 0.9 | 0.0 | 4.0 | 69.2 |
| L07 floor branch | 622.0 | 4.00 | 3.77 | Rect | Rect 550 × 300 mm | 1.7 | 3.0 | 0.0 | 4.4 | 69.6 |
| Riser L07-L06 | 3,732.0 | 3.60 | 5.18 | Rect | Rect 1200 × 600 mm | 1.2 | 0.8 | 0.0 | 0.8 | 70.3 |
| L06 floor branch | 622.0 | 4.00 | 3.46 | Rect | Rect 600 × 300 mm | 1.4 | 2.5 | 0.0 | 4.5 | 69.8 |
| Riser L06-L05 | 3,110.0 | 3.60 | 4.51 | Rect | Rect 1150 × 600 mm | 0.9 | 0.6 | 0.0 | 3.0 | 68.9 |
| L05 floor branch | 622.0 | 4.00 | 3.46 | Rect | Rect 600 × 300 mm | 1.4 | 2.5 | 0.0 | 2.5 | 70.3 |
| Riser L05-L04 | 2,488.0 | 3.60 | 4.11 | Rect | Rect 1100 × 550 mm | 0.8 | 0.5 | 0.0 | 1.5 | 68.7 |
| L04 floor branch | 622.0 | 4.00 | 2.73 | Rect | Rect 650 × 350 mm | 0.8 | 1.6 | 0.0 | 2.8 | 68.2 |
| Riser L04-L03 | 1,866.0 | 3.60 | 3.73 | Rect | Rect 1000 × 500 mm | 0.8 | 0.4 | 0.0 | 1.3 | 68.6 |
| L03 floor branch | 622.0 | 4.00 | 2.54 | Rect | Rect 700 × 350 mm | 0.7 | 1.4 | 0.0 | 2.3 | 68.3 |
| Riser L03-L02 | 1,244.0 | 3.60 | 3.25 | Rect | Rect 850 × 450 mm | 0.7 | 0.3 | 0.0 | 1.5 | 68.1 |
| L02 floor branch | 622.0 | 4.00 | 2.07 | Rect | Rect 750 × 400 mm | 0.4 | 0.9 | 0.0 | 1.9 | 67.5 |
| Riser end run to L01 | 622.0 | 7.60 | 2.54 | Rect | Rect 700 × 350 mm | 1.3 | 1.2 | 0.0 | 1.9 | 68.6 |

Summary

| Result | Value |
| --- | --- |
| Governing path | FAHU-01 discharge → Riser L10-L09 → L09 floor branch |
| Fan SP requirement (fan inlet + duct + terminal) | 199.9 Pa |
| Duct losses on governing path, net of regain (Σ SP at the governing terminal) | 74.9 Pa |
| Terminal SP at governing leaf | 125.0 Pa |

# R.  Reference Standards

SMACNA HVAC Systems – Duct Design 4th ed. (2006) — Ch. 5 Sec. 5.6.3 static-regain method; Sec. 7.2 (g) regainable fraction; Ch. 7 sizing procedures.

ASHRAE Handbook – Fundamentals 2021 Ch. 21 — Duct-design equations (8, 18–25), roughness Table 1, velocity Table 12, fitting losses (Duct Fitting Database).

Colebrook–White (1938-1939) — Friction factor for turbulent flow.

Darcy–Weisbach equation — Section friction loss.

Engineer of record: Hussein Ragab

Static Regain Duct Sizer — engineering aid; verify all results against project standards and stamped design.