## Project
Static Regain Duct Sizer — Project Summary
Project: Marina Commercial Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: - ¦ By: Hussein Ragab ¦ Chkd: - ¦ Rev: P2 ¦ Date: 2026-10-20
Project: | Marina Commercial Tower
Project No.: | MCT-2026-MEP-001
Client: | -
Date: | 2026-10-20
Prepared by: | Hussein Ragab
Checked by: | -
Revision: | P2
Unit system | SI
Design Assumptions
Design velocity (V_design) | 8 | m/s
Velocity floor (V_min) | 1.016 | m/s
Velocity cap (V_max) | 10 | m/s
Air density (ρ) | 1.204 | kg/m³
Material | Galvanised steel, longitudinal seam, 4 ft joints
Roughness ε (mm, both unit systems) | 0.09 | mm
Snap to standard sizes | yes
Catalogue system | SI
Sizing Result
Fan SP required (fan inlet + duct + terminal) | 199.9099 | Pa

## Sizing Inputs
Section | Parent | L (m) | Q terminal, input (L/s) | Q through (L/s) | Shape | AR (input default) | R | Σ K | Σ ΔP_eq (Pa) | Term SP (Pa) | Branch direction | Bundle | Note
FAHU-01 discharge | — | 6 | — | 6220 | Rect | 2 | 0.75 | 0.6 | 50 | — | south
L10 floor branch | FAHU-01 discharge | 4 | 622 | 622 | Rect | 2 | 0.5 | 0.35 | 0 | 125 | east
Riser L10-L09 | FAHU-01 discharge | 3.6 | — | 5598 | Rect | 2 | 0.75 | 0.05 | 0 | — | south
L09 floor branch | Riser L10-L09 | 4 | 622 | 622 | Rect | 2 | 0.5 | 0.35 | 0 | 125 | east
Riser L09-L08 | Riser L10-L09 | 3.6 | — | 4976 | Rect | 2 | 0.75 | 0.05 | 0 | — | south
L08 floor branch | Riser L09-L08 | 4 | 622 | 622 | Rect | 2 | 0.5 | 0.35 | 0 | 125 | east
Riser L08-L07 | Riser L09-L08 | 3.6 | — | 4354 | Rect | 2 | 0.75 | 0.05 | 0 | — | south
L07 floor branch | Riser L08-L07 | 4 | 622 | 622 | Rect | 2 | 0.5 | 0.35 | 0 | 125 | east
Riser L07-L06 | Riser L08-L07 | 3.6 | — | 3732 | Rect | 2 | 0.75 | 0.05 | 0 | — | south
L06 floor branch | Riser L07-L06 | 4 | 622 | 622 | Rect | 2 | 0.5 | 0.35 | 0 | 125 | east
Riser L06-L05 | Riser L07-L06 | 3.6 | — | 3110 | Rect | 2 | 0.75 | 0.05 | 0 | — | south
L05 floor branch | Riser L06-L05 | 4 | 622 | 622 | Rect | 2 | 0.5 | 0.35 | 0 | 125 | east
Riser L05-L04 | Riser L06-L05 | 3.6 | — | 2488 | Rect | 2 | 0.75 | 0.05 | 0 | — | south
L04 floor branch | Riser L05-L04 | 4 | 622 | 622 | Rect | 2 | 0.5 | 0.35 | 0 | 125 | east
Riser L04-L03 | Riser L05-L04 | 3.6 | — | 1866 | Rect | 2 | 0.75 | 0.05 | 0 | — | south
L03 floor branch | Riser L04-L03 | 4 | 622 | 622 | Rect | 2 | 0.5 | 0.35 | 0 | 125 | east
Riser L03-L02 | Riser L04-L03 | 3.6 | — | 1244 | Rect | 2 | 0.75 | 0.05 | 0 | — | south
L02 floor branch | Riser L03-L02 | 4 | 622 | 622 | Rect | 2 | 0.5 | 0.35 | 0 | 125 | east
Riser end run to L01 | Riser L03-L02 | 7.6 | 622 | 622 | Rect | 2 | 0.75 | 0.3 | 0 | 125 | south

## Sizing Results
Section | Parent | V (m/s) | Shape | Width (mm) | Height (mm) | AR (snapped) | Vp (Pa) | ΔPf (Pa) | ΔPfit (Pa) | Σ ΔP_eq (Pa) | Regain (Pa) | Σ SP (Pa) | Warnings
FAHU-01 discharge | — | 7.6554 | Rect | 1250 | 650 | 1.92 | 35.2802 | 3.7003 | 21.1681 | 50 | 0 | 74.8684
L10 floor branch | FAHU-01 discharge | 4.976 | Rect | 500 | 250 | 2 | 14.9059 | 3.4372 | 5.2171 | 0 | 10.1871 | 73.3355 | Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).
Riser L10-L09 | FAHU-01 discharge | 6.8898 | Rect | 1250 | 650 | 1.92 | 28.5769 | 1.8214 | 1.4288 | 0 | 5.0274 | 73.0912 | Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).
L09 floor branch | Riser L10-L09 | 4.976 | Rect | 500 | 250 | 2 | 14.9059 | 3.4372 | 5.2171 | 0 | 6.8355 | 74.9099
Riser L09-L08 | Riser L10-L09 | 6.1243 | Rect | 1250 | 650 | 1.92 | 22.5793 | 1.4607 | 1.129 | 0 | 4.4982 | 71.1827 | Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).
L08 floor branch | Riser L09-L08 | 3.7697 | Rect | 550 | 300 | 1.83 | 8.5548 | 1.7097 | 2.9942 | 0 | 7.0123 | 68.8743 | Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).
Riser L08-L07 | Riser L09-L08 | 5.3588 | Rect | 1250 | 650 | 1.92 | 17.2873 | 1.1383 | 0.86436 | 0 | 3.969 | 69.2163 | Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).
L07 floor branch | Riser L08-L07 | 3.7697 | Rect | 550 | 300 | 1.83 | 8.5548 | 1.7097 | 2.9942 | 0 | 4.3662 | 69.5539
Riser L07-L06 | Riser L08-L07 | 5.1833 | Rect | 1200 | 600 | 2 | 16.1739 | 1.1592 | 0.8087 | 0 | 0.83503 | 70.3491
L06 floor branch | Riser L07-L06 | 3.4556 | Rect | 600 | 300 | 2 | 7.1884 | 1.4051 | 2.5159 | 0 | 4.4928 | 69.7774 | Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).
Riser L06-L05 | Riser L07-L06 | 4.5072 | Rect | 1150 | 600 | 1.92 | 12.2298 | 0.90926 | 0.61149 | 0 | 2.9581 | 68.9118 | Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).
L05 floor branch | Riser L06-L05 | 3.4556 | Rect | 600 | 300 | 2 | 7.1884 | 1.4051 | 2.5159 | 0 | 2.5207 | 70.3121
Riser L05-L04 | Riser L06-L05 | 4.1124 | Rect | 1100 | 550 | 2 | 10.1809 | 0.83724 | 0.50905 | 0 | 1.5367 | 68.7214 | Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).
L04 floor branch | Riser L05-L04 | 2.7341 | Rect | 650 | 350 | 1.86 | 4.5 | 0.78199 | 1.575 | 0 | 2.8404 | 68.2379 | Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).
Riser L04-L03 | Riser L05-L04 | 3.732 | Rect | 1000 | 500 | 2 | 8.3846 | 0.78479 | 0.41923 | 0 | 1.3473 | 68.5781 | Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).
L03 floor branch | Riser L04-L03 | 2.5388 | Rect | 700 | 350 | 2 | 3.8801 | 0.66226 | 1.358 | 0 | 2.2522 | 68.3462 | Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).
Riser L03-L02 | Riser L04-L03 | 3.2523 | Rect | 850 | 450 | 1.89 | 6.3676 | 0.70803 | 0.31838 | 0 | 1.5127 | 68.0918 | Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).
L02 floor branch | Riser L03-L02 | 2.0733 | Rect | 750 | 400 | 1.88 | 2.5878 | 0.39976 | 0.90574 | 0 | 1.8899 | 67.5074 | Over-recovery: regain credit exceeds friction + fitting + equipment losses (section pressure drop is negative — the expected, intended behaviour of the static-regain method).
Riser end run to L01 | Riser L03-L02 | 2.5388 | Rect | 700 | 350 | 2 | 3.8801 | 1.2583 | 1.164 | 0 | 1.8656 | 68.6485

## Equipment & Fittings
Section | Type | Item | Count | Unit value | Total | Unit
FAHU-01 discharge | K | (Direct input of K value) | 1 | 0.6 | 0.6 | —
FAHU-01 discharge | ΔP | Sound attenuator, 1200 mm length | 1 | 50 | 50 | Pa
L10 floor branch | K | (Direct input of K value) | 1 | 0.35 | 0.35 | —
Riser L10-L09 | K | (Direct input of K value) | 1 | 0.05 | 0.05 | —
L09 floor branch | K | (Direct input of K value) | 1 | 0.35 | 0.35 | —
Riser L09-L08 | K | (Direct input of K value) | 1 | 0.05 | 0.05 | —
L08 floor branch | K | (Direct input of K value) | 1 | 0.35 | 0.35 | —
Riser L08-L07 | K | (Direct input of K value) | 1 | 0.05 | 0.05 | —
L07 floor branch | K | (Direct input of K value) | 1 | 0.35 | 0.35 | —
Riser L07-L06 | K | (Direct input of K value) | 1 | 0.05 | 0.05 | —
L06 floor branch | K | (Direct input of K value) | 1 | 0.35 | 0.35 | —
Riser L06-L05 | K | (Direct input of K value) | 1 | 0.05 | 0.05 | —
L05 floor branch | K | (Direct input of K value) | 1 | 0.35 | 0.35 | —
Riser L05-L04 | K | (Direct input of K value) | 1 | 0.05 | 0.05 | —
L04 floor branch | K | (Direct input of K value) | 1 | 0.35 | 0.35 | —
Riser L04-L03 | K | (Direct input of K value) | 1 | 0.05 | 0.05 | —
L03 floor branch | K | (Direct input of K value) | 1 | 0.35 | 0.35 | —
Riser L03-L02 | K | (Direct input of K value) | 1 | 0.05 | 0.05 | —
L02 floor branch | K | (Direct input of K value) | 1 | 0.35 | 0.35 | —
Riser end run to L01 | K | (Direct input of K value) | 1 | 0.3 | 0.3 | —

## Reference
Reference | Application
ASHRAE Handbook — Fundamentals 2021, Ch. 21 (Duct Design) | Eq. (41) static-regain balance ps = (pv1 - pv2) - pt (p. 21.20; R de-rates a recovery only, an acceleration is charged in full); the printed size-selection step (p. 21.19 / Example 8 p. 21.23: residual nearest zero, never above the upstream duct except one catalogue step at a shape change, capped at the upstream De plus one step - the round equivalent, Eq. (25) p. 21.9); Eq. (8) velocity pressure, (18) Darcy friction loss, (19) Colebrook–White, (20) Reynolds, (25) equivalent diameter; Table 12 recommended maximum velocities by duct location and NC/RC.
SMACNA HVAC Systems — Duct Design 4th ed. (2006) | Vp-to-SP conversion — Ch. 5 (Duct Design Fundamentals) Sec. 5.6.3; regainable fraction Sec. 7.2 (g) (75 to 90 percent, the printed basis of a fractional R); duct-sizing procedures Ch. 7.
Colebrook (1938-1939) | Original transcendental friction-factor formula; iterated to 1×10⁻¹⁰ in this engine.
ASHRAE F-21 Ch. 21, Table 1 | Absolute roughness ε for typical duct materials (galvanised, longitudinal seam approx. 0.09 mm).
ASHRAE Duct Fitting Database v5.00.10 | The bundled fitting-K library was re-grounded on it 2026-09-01: 35 of the 44 rows are read from a printed Database sheet, most at the section's own solved geometry (Co varies with duct diameter, aspect ratio, area ratio and flow ratio). The remaining 9 rows have no Database counterpart and are marked as curated typicals.