Substation Ventilation Compliance

Transformer room heat balance (AHJ defaults)

Basement — forced mechanical ventilation

| Project Information |  |
| --- | --- |
| Project Name | Marina Commercial Tower |
| Project No. | MCT-2026-MEP-001 |
| Revision | P2 |
| Client | — |
| Prepared by | Hussein Ragab |
| Checked by | — |
| Date | 2026-10-20 |

Values in this report are displayed in SI (metric) units.

# 1.  Methodology & Standards

This report sizes the ventilation of an electrical substation transformer room. For a basement transformer room with no exterior walls, independent mechanical supply and exhaust ventilation is sized to hold the interior air at the maximum interior temperature for the design outside air temperature (AHJ defaults, listed under Design Assumptions), with louvers on two sides as a natural back-up. For a ground-floor room with two exterior walls, natural ventilation through louvered doors and fixed louvers is verified against the same heat balance; the same design point and grill-area floor are applied on that path as the tool's conservative design basis. Every jurisdiction-dependent value is an editable default - verify each against the local AHJ requirement.

Transformer heat is taken either as the authority preset loss (1.29 % of rated kVA) or as the datasheet loss P_loss = P0 + Pk x LF^2 at the load factor LF (this tool evaluates full load, LF = 1, so P_loss = P0 + Pk) per IEC 60076-8:1997. The required airflow follows Figure G.52 forced-ventilation nomogram, as measured from the figure: the figure's rays were measured from its own vector geometry by two independent routes, giving a volumetric heat capacity of 1125 J/(m3.K) at sea level, i.e. V = P_loss / ((rho.cp) x dT). The figure's drawn 4 x 1,000 kVA example (51.14 kW on the 7 K ray) reads 23,238 m3/h and this method reproduces it to within 1 %. The physics value used before 2026-09-07 — standard air, rho = 1.225 kg/m3 at ISA 15 degC times cp = 1005 J/(kg.K) = 1231 J/(m3.K) at sea level — is printed in the calculation trace as a comparison; it asks for 8.6 % LESS air than the governing figure and is no longer the basis. The louver/grill total free area is taken as the larger of (a) the prescriptive minimum (AHJ defaults) — 14.9 m2 for a 1000 kVA transformer and 18.6 m2 for a 1500 kVA transformer, applied per transformer and summed over the transformer rows (a rating between or outside the two anchors is interpolated or extrapolated per unit and flagged for AHJ confirmation) — and (b) a supplementary natural-convection free area (CIBSE AM10 stack effect). The forced system uses a duty + standby fan arrangement on both supply (make-up) and extract, with fire-rated GI ductwork, non-return dampers and motorised smoke/fire dampers (advisory - confirm with the AHJ).

| Standard / Clause | Application |
| --- | --- |
| Figure G.52 forced-ventilation nomogram (Dubai Building Code 2021, Part G, page G 96) | AIRFLOW METHOD SOURCE only - measured from the figure's own vector geometry (rho.cp = 1125 J/(m3.K) at sea level). Limits and preset values used with it are AHJ defaults (see Design Assumptions) |
| IEC 60076-8:1997 | Datasheet loss method P_loss = P0 + Pk x LF^2 (cl. 10.3: the load loss varies with the square of the current), evaluated at each transformer row's load factor, full load by default; transformer application guide |
| BS EN 60034-30-1:2014 (= IEC 60034-30-1:2014) | Motor efficiency for an IE class: the nominal efficiency limit printed for the SELECTED motor rating, 50 Hz, 4-pole (Tables 3 / 5 / 7 / 9); a Custom efficiency is the engineer's own value |
| IEC 60072 (all parts) | Dimensions and output series for rotating electrical machines — preferred kW series the motor rung is selected from (rating basis: BS EN 60034-1:2010) |
| CIBSE AM10 (2005), Natural ventilation, Eq 4.12 (p. 45; PDF p. 51 of the ref copy) | Stack-effect free-area back-up check (internal temperature T_I in the buoyancy term) & the 0.6 sharp-opening Cd the louver value is derated from |
| ICAO Doc 7488 / US Std Atmosphere 1976 | ISA pressure ratio — altitude correction of the Fig G.52 basis, and the standard air density of the comparison line |

# 2.  Design Inputs

| Parameter | Value |
| --- | --- |
| Ventilation path | Basement — forced mechanical ventilation |
| Supply air temperature | 48.0 °C |
| Max interior temperature | 55.0 °C |
| Design temperature rise dT | 7.0 K |
| Site altitude | 0.00 m |
| Room height (bounds the outlet centre height) | 4.50 m |
| Inlet / outlet centre height | 0.60 m / 3.90 m |
| Stack height H | 3.30 m |
| Room total rating | 3000 kVA |
| Heat-loss basis | Authority preset (1.29 % kVA) |
| Intake/exhaust separation | 12.00 m |

| Transformer | Rating & heat loss |
| --- | --- |
| SS01-TX1 | 1500 kVA ¦ x1 ¦ authority preset heat 19.35 kW |
| SS01-TX2 | 1500 kVA ¦ x1 ¦ authority preset heat 19.35 kW |

# 3.  Design Assumptions

Heat-loss basis: authority preset loss = 1.29 % of rated kVA (AHJ default - verify against the local AHJ requirement).

Airflow basis: Figure G.52 forced-ventilation nomogram, as measured from the figure, rho.cp = 1125 J/(m3.K) at sea level, altitude-corrected on the ISA pressure ratio. The figure is a nomogram, so it fixes the PRODUCT of density and specific heat directly. Comparison only: the standard-air physics value (standard air rho = 1.225 kg/m3 at ISA 15 degC x cp = 1005 J/(kg.K) = 1231 J/(m3.K) at sea level) asks for 8.6 % less air and is not used; at the 48 degC intake the room-air density is about 1.10 kg/m3, so selecting the fans on the hot-intake volume remains the conservative option.

Prescriptive grill area is the TOTAL free area (sum of inlet + outlet openings). The defaults are two discrete points, each for ONE transformer (14.9 m2 for a 1000 kVA transformer, 18.6 m2 for a 1500 kVA transformer; AHJ defaults); the engine applies them per transformer and sums over the transformer rows. A rating other than the two anchors is interpolated or extrapolated PER UNIT by the tool and carries an AHJ-confirmation flag.

Natural-convection back-up uses an effective louver discharge coefficient Cd = 0.35 (an engineering derate of the CIBSE AM10 p. 45 (PDF p. 51) sharp-opening 0.6; AM10 prints no louver Cd) and an outlet/inlet area ratio of 1.10 (engineering practice, no cited document); the buoyancy term divides by the internal temperature T_I = T_max as AM10 Eq 4.12 prints it.

The natural-convection free area is a supplementary engineering check, not a mandated method; taking the governing area as the larger of it and the prescriptive minimum can only increase the required area (conservative).

AHJ basis: Authority preset transformer heat loss 1.29 % of kVA (default)

AHJ basis: Design outside (supply) air temperature 48 degC (default)

AHJ basis: Maximum interior air temperature 55 degC (default)

AHJ basis: Prescriptive grill area - lower anchor rating 1000 kVA (default)

AHJ basis: Prescriptive total grill area at the lower anchor 14.9 m2 (default)

AHJ basis: Prescriptive grill area - upper anchor rating 1500 kVA (default)

AHJ basis: Prescriptive total grill area at the upper anchor 18.6 m2 (default)

AHJ basis: Minimum intake / exhaust louvre separation 10 m (default)

# 4.  Step-by-Step Calculation

Step 1: Total heat to dissipate (authority preset loss)

Formula: P_loss = Σ (1.29% · kVA)·n

Substitution: 1.29% · ΣkVA(3000) = 38.70 kW

Result: 38.70 kW

Step 2: Airflow basis — Figure G.52 forced-ventilation nomogram, as measured from the figure

Formula: (ρ·cp)_G.52 = 1125 J/(m³·K) at sea level · (1−2.2558e-5·z)^5.25588

Substitution: z = 0 m → (ρ·cp) = 1125.0 J/(m³·K)

Result: 1125.0 J/(m³·K)

Note: V = 3200·Q/ΔT with Q in kW. Comparison only, not the basis: the standard-air physics value ρ = 1.2250 kg/m³ · cp = 1005 J/(kg·K) = 1231 J/(m³·K) asks for 8.6 % LESS air; the hot room air is about 1.099 kg/m³ at 48 °C, so sizing the fans on the hot-intake volume stays the conservative option.

Step 3: Required ventilation airflow (Fig G.52 nomogram, dϑ_L = ΔT ray)

Formula: V = P_loss / ((ρ·cp)_G.52·ΔT), ΔT = T_max − T_supply

Substitution: 38700 / (1125.0·7.0) = 4.9143 m³/s = 17691 m³/h

Result: 17691 m³/h

Step 4: Prescriptive total grill free area (AHJ default anchors per transformer)

Formula: A_presc = Σ n·A(kVA), A(kVA) = 14.9 + (18.6−14.9)/(1500−1000)·(kVA − 1000)

Substitution: 1·A(1500) = 1·18.60 + 1·A(1500) = 1·18.60 → A_presc = 37.20 m²

Result: 37.20 m²

Step 5: Natural-convection back-up free area (CIBSE AM10 Eq 4.12 stack effect)

Formula: A_eff = V / (Cd·√(2g·H·ΔT/T_I)), T_I = T_max [K]; A_in,A_out series; A = A_in+A_out

Substitution: Cd=0.35, H=3.30 m, ΔT=7.0 K, T_I=328.15 K → A_in=16.15, A_out=17.76, A_buoy=33.91 m²

Result: 33.91 m²

Step 6: Governing louver/grill total free area

Formula: A_required = max(A_presc, A_buoy)

Substitution: max(37.20, 33.91) = 37.20 m²

Result: 37.20 m²

Note: Prescriptive (AHJ default) governs.

Step 7: Fan selection (per service: duty + standby)

Formula: P_shaft = (V/n_duty)·ESP/(η_fan·1000); motor = next IEC 60072 rung ≥ P_shaft · sizing margin

Substitution: supply 2 duty +1 standby @ 8846 m³/h (2 x 8846 = 17692 >= 17691 m³/h) → 1.024 kW shaft, 1.5 kW motor; exhaust 2+1 standby (2 x 8846 = 17692 >= 17691 m³/h)

Result: 17691 m³/h)

Note: Motor efficiency: supply IE2 82.8 % at 1.5 kW - BS EN 60034-30-1:2014 Table 5 (50 Hz, 4-pole); exhaust IE2 82.8 % at 1.5 kW - BS EN 60034-30-1:2014 Table 5 (50 Hz, 4-pole).

# 5.  Results

| Parameter | Value |
| --- | --- |
| Total heat to dissipate (full load) | 38.70 kW |
| Required ventilation airflow | 17,691 m³/h |
| Prescriptive grill area (AHJ-default anchors per transformer) | 37.20 m² |
| Natural-convection free area (CIBSE AM10) | 33.91 m² |
| ... inlet / outlet split | 16.15 m² / 17.76 m² |
| GOVERNING louver free area | 37.20 m² (prescriptive (AHJ default) governs) |

Fan Equipment Schedule (duty + standby)

| Parameter | Supply (Make-up) | Extract | Unit |
| --- | --- | --- | --- |
| Tag | SF-1..SF-3 | EF-1..EF-3 |  |
| Arrangement | 2 duty + 1 standby | 2 duty + 1 standby | auto changeover |
| Flow per fan | 8,846 m³/h | 8,846 m³/h |  |
| External static pressure | 250 | 250 | Pa |
| Fan efficiency | 60 | 60 | % |
| Absorbed shaft power | 1.024 | 1.024 | kW |
| Motor efficiency | 82.8 | 82.8 | % |
| Motor efficiency basis | IE2 - BS EN 60034-30-1 Table 5, 4-pole | IE2 - BS EN 60034-30-1 Table 5, 4-pole |  |
| Motor electrical input | 1.236 | 1.236 | kW |
| SELECTED MOTOR (x sizing margin 1.15) | 1.5 | 1.5 | kW |
| Ductwork & dampers | Fire-rated GI duct, NRD, MSFD | Fire-rated GI duct, NRD, MSFD |  |

Fire-Safety Provisions (advisory - confirm with the AHJ)

| Provision | Status / requirement |
| --- | --- |
| Enclosure fire rating | Provided. Transformer / RMU room 2 h fire rated. |
| Exit door | Provided. At least one exit door, door swing in the direction of egress. If in a 2 h fire rated wall the door shall be 90 min fire rated. |
| Room location (AHJ) | Provided. Confirm the transformer room location with the AHJ. Requirements differ: some place a transformer / HV room above grade level on the exterior perimeter of the building; others provide mechanical ventilation for transformer rooms with no exterior walls (e.g. in a basement). |
| Louver back-up | Provided. Louvers provided on two sides of the room as a back-up to the mechanical ventilation. |
| Louver fire protection | Provided. Louvers protected by automatic 2 h fire rated shutters or 2 h fire rated curtains on the landlord side. |
| Detection | Provided. Two combined fire and smoke detectors on the landlord side, on the slab soffit within the vicinity of the louver (door release service). |
| Automatic shutdown | Provided. On activation of both detectors: fire rated shutters/curtains automatically close AND mechanical ventilation automatically stops. |
| Override switch | Provided. Fire rated shutters/curtains have an automatic override switch on the landlord side. |
| Fire rated exit door | Provided. At least one fire rated (90 min) exit door, with door swing in the direction of egress. |
| Alternative exit | Provided. Equipment access doors may include louvers but are blocked by the closing fire curtains/shutters; an alternative exit shall be provided and equipment doors shall NOT be marked as an exit. |
| Duty + standby fans | Provided. Duty + standby fan arrangement mandatory on BOTH the supply (make-up) and the extract systems, with automatic changeover. |
| Fire-rated GI ductwork | Provided. All supply and extract ductwork shall be fire-rated galvanised-iron (GI). |
| Non-return dampers (NRD) | Provided. Non-return dampers on the supply and extract branches to prevent reverse airflow. |
| Motorised smoke/fire dampers (MSFD) | Provided. Motorised smoke/fire dampers on the supply and extract branches for smoke containment and fire isolation. |
| Sand-trap louvers | Provided. Sand-trap louvers on ALL fresh-air intake openings to minimise dust/sand ingress. |
| Intake/exhaust separation | Provided. Minimum 10 m separation between intake and exhaust louvers; supply grilles at low level, exhaust grilles at high level, to prevent hot-air short-circuiting. |
| BMS controls & alarms | Provided. All fans connected to BMS with automatic duty/standby changeover, high-temperature alarm, and fan-failure detection/alert. |
| No equipment inside the room | Provided. No fan units, projecting ductwork or temperature sensors inside the transformer room; grilles shall be flush with the walls. |

# R.  Reference Standards

Figure G.52 forced-ventilation nomogram (Dubai Building Code 2021, Part G, page G 96) — AIRFLOW METHOD SOURCE only - measured from the figure's own vector geometry (rho.cp = 1125 J/(m3.K) at sea level). Limits and preset values used with it are AHJ defaults (see Design Assumptions)

IEC 60076-8:1997 — Datasheet loss method P_loss = P0 + Pk x LF^2 (cl. 10.3: the load loss varies with the square of the current), evaluated at each transformer row's load factor, full load by default; transformer application guide

BS EN 60034-30-1:2014 (= IEC 60034-30-1:2014) — Motor efficiency for an IE class: the nominal efficiency limit printed for the SELECTED motor rating, 50 Hz, 4-pole (Tables 3 / 5 / 7 / 9); a Custom efficiency is the engineer's own value

IEC 60072 (all parts) — Dimensions and output series for rotating electrical machines — preferred kW series the motor rung is selected from (rating basis: BS EN 60034-1:2010)

CIBSE AM10 (2005), Natural ventilation, Eq 4.12 (p. 45; PDF p. 51 of the ref copy) — Stack-effect free-area back-up check (internal temperature T_I in the buoyancy term) & the 0.6 sharp-opening Cd the louver value is derated from

ICAO Doc 7488 / US Std Atmosphere 1976 — ISA pressure ratio — altitude correction of the Fig G.52 basis, and the standard air density of the comparison line

Generated by the MEP Suite — Substation Ventilation tool.