## Fan Schedule
Substation Ventilation — Fan / Motor Equipment Schedule
Transformer room ventilation - heat balance, AHJ defaults
Project: Marina Commercial Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: - ¦ By: Hussein Ragab ¦ Chkd: - ¦ Rev: P2 ¦ Date: 2026-10-20
Compliance basis: Transformer room ventilation - heat balance, AHJ defaults ¦ Unit system: SI ¦ Heat-loss basis: authority preset loss (1.29% x kVA) ¦ Airflow per Figure G.52 forced-ventilation nomogram, as measured from the figure, rho.cp = 1125 J/(m3.K).
Room rating 3000 kVA ¦ Total heat 38.70 kW ¦ Design dT 7.0 K ¦ Total required airflow 17,691 m³/h ¦ Governing louver free area 37.2 m² — basis: prescriptive (AHJ default)
Fan / motor schedule (duty + standby)
Tag | Service | Duty status | Qty (No. off) | Airflow per fan (m³/h) | External static pressure (Pa) | Fan efficiency (%) | Absorbed shaft power per fan (kW) | Motor efficiency (%) | Motor electrical input per fan (kW) | Design margin (x) | Selected motor — IEC 60072 (kW) | Margin over required (%) | Remarks
SF-1..SF-2 | Supply (make-up) | Duty | 2 | 8846 | 250 | 60 | 1.024 | 82.8 | 1.236 | 1.15 | 1.5 | 27.4 | Fire-rated GI duct, NRD, MSFD; automatic changeover to the standby fan on duty-fan failure (advisory — confirm with the AHJ).
SF-3 | Supply (make-up) | Standby | 1 | 8846 | 250 | 60 | 1.024 | 82.8 | 1.236 | 1.15 | 1.5 | 27.4 | Identical to the duty fan — 100% standby on automatic changeover (advisory — confirm with the AHJ).
EF-1..EF-2 | Extract | Duty | 2 | 8846 | 250 | 60 | 1.024 | 82.8 | 1.236 | 1.15 | 1.5 | 27.4 | Fire-rated GI duct, NRD, MSFD; automatic changeover to the standby fan on duty-fan failure (advisory — confirm with the AHJ).
EF-3 | Extract | Standby | 1 | 8846 | 250 | 60 | 1.024 | 82.8 | 1.236 | 1.15 | 1.5 | 27.4 | Identical to the duty fan — 100% standby on automatic changeover (advisory — confirm with the AHJ).
Selection basis: P_shaft = (V/n_duty)·ESP/(η_fan·1000); motor = next IEC 60072 rung ≥ P_shaft · sizing margin [Fan selection (per service: duty + standby)]
AHJ defaults used
AHJ basis: Authority preset transformer heat loss 1.29 % of kVA (default)
AHJ basis: Design outside (supply) air temperature 48 degC (default)
AHJ basis: Maximum interior air temperature 55 degC (default)
AHJ basis: Prescriptive grill area - lower anchor rating 1000 kVA (default)
AHJ basis: Prescriptive total grill area at the lower anchor 14.9 m2 (default)
AHJ basis: Prescriptive grill area - upper anchor rating 1500 kVA (default)
AHJ basis: Prescriptive total grill area at the upper anchor 18.6 m2 (default)
AHJ basis: Minimum intake / exhaust louvre separation 10 m (default)
Reference |  |  | Application
Figure G.52 forced-ventilation nomogram (Dubai Building Code 2021, Part G, page G 96) |  |  | AIRFLOW METHOD SOURCE only - measured from the figure's own vector geometry (rho.cp = 1125 J/(m3.K) at sea level). Limits and preset values used with it are AHJ defaults (see Design Assumptions)
IEC 60076-8:1997 |  |  | Datasheet loss method P_loss = P0 + Pk x LF^2 (cl. 10.3: the load loss varies with the square of the current), evaluated at each transformer row's load factor, full load by default; transformer application guide
BS EN 60034-30-1:2014 (= IEC 60034-30-1:2014) |  |  | Motor efficiency for an IE class: the nominal efficiency limit printed for the SELECTED motor rating, 50 Hz, 4-pole (Tables 3 / 5 / 7 / 9); a Custom efficiency is the engineer's own value
IEC 60072 (all parts) |  |  | Dimensions and output series for rotating electrical machines — preferred kW series the motor rung is selected from (rating basis: BS EN 60034-1:2010)
CIBSE AM10 (2005), Natural ventilation, Eq 4.12 (p. 45; PDF p. 51 of the ref copy) |  |  | Stack-effect free-area back-up check (internal temperature T_I in the buoyancy term) & the 0.6 sharp-opening Cd the louver value is derated from
ICAO Doc 7488 / US Std Atmosphere 1976 |  |  | ISA pressure ratio — altitude correction of the Fig G.52 basis, and the standard air density of the comparison line