Sump Pit Sizing Calculation

Based on Motor Start-Frequency Limits (short-cycling)

BS EN 12056-2 ¦ IEC 60072 / EN 50347 ¦ IEC 60034-30-1 ¦ NEMA MG-10 basis

| Project Information |  |
| --- | --- |
| Project Name | Test Tower |
| Project No. | MCT-2026-MEP-001 |
| Revision | P2 |
| Client | Test Dev |
| Prepared by | Hussein Ragab |
| Checked by | Principal MEP Review |
| Date | 2026-09-02 |

Values in this report are displayed in SI (metric) units.

# 1.  Methodology & Standards

| Reference | Application |
| --- | --- |
| BS EN 12056-2 | Gravity drainage systems inside buildings — design and calculation of the wastewater flow feeding the sump pit. |
| Motor starts-per-hour banding | Maximum allowable starts per hour by motor size — industry-practice banding (per-hour schedules are published in NEMA MG-10; NEMA MG-1 # 12.54 itself grants 2 successive starts from cold / 1 hot). Sets the minimum cycle time used to size the active sump volume so the windings do not overheat. |
| Active-Volume Formula (short-cycling) | V_active = Q_pump (m3/min) x T_cycle (min) / 4 — the classic pump short-cycling result: the divisor 4 is the worst-case inflow = Q_pump/2 that maximises cycling frequency. |
| Shaft-Power Formula | P_shaft = rho*g x Q x H / eta_pump with rho*g = 9810 N/m3 (brake power at the coupling). The electrical input P_elec = P_shaft / eta_motor sizes the cable / breaker only. |
| IEC 60072 / EN 50347 | Standard motor frame kW ratings — rated by SHAFT OUTPUT. The selected frame is the next rating at or above P_shaft x service factor (1.15). |
| IEC 60034-30-1 | Motor efficiency classes (IE1-IE4). The selected IE class sets the indicative motor efficiency used for the electrical-input figure. |
| NPSH (submersible) | NPSH_avail = H_atm - H_vapor + H_submergence - H_suction_friction, checked against the pump-curve NPSH_required to flag cavitation risk. |

# 2.  Design Inputs

Inflow & Pump Configuration

| Parameter | Value |
| --- | --- |
| Maximum inflow Q_max | 12.000 l/s (190.2 GPM) |
| Duty pump sizing (%) | 60% of Q_max |
| No. of Duty pumps | 2 |
| Q per pump | 3.600 l/s (57.1 GPM) |
| Assist pumps included | Yes |
| No. of Assist pumps | 1 |
| Total pumps installed | 3 |
| Total head H | 18.00 m (59.06 ft) (static 14.5 + friction 3.5 m) |
| Pump efficiency eta_p | 0.65 (65%) |
| Motor class / eta_m | IE3 (premium) (91%) |

Stage Depths

| Parameter | Value |
| --- | --- |
| Stage 1 - Dead zone buffer | 250 mm (9.8 in) |
| Stage 2 - Duty pump ON | 300 mm (11.8 in) |
| Stage 3 - Assist ON | 250 mm (9.8 in) |
| Stage 4 - High alarm | 200 mm (7.9 in) |
| Clearance (alarm -> inlet) | 150 mm (5.9 in) |
| Above inlet to pit cover | 300 mm (11.8 in) |

# 3.  Design Assumptions

Active sump volume is sized to the short-cycling worst case: inflow equal to half the per-pump flow, which maximises the pump cycling frequency.

All pumps (duty and assist) are sized identically — same flow, head and motor rating per pump.

Duty pumps run under the normal inflow profile; assist pumps start at the Stage 3 level to handle inflow surges beyond duty capacity.

The operating storage range is the sum of Stage 2, Stage 3 and Stage 4 depths; the dead zone (Stage 1) keeps the pump submerged and lets silt settle but is not active storage.

Submergence for the NPSH check is taken as the Stage 1 dead-band depth at the switch-on level (conservative).

The motor efficiency taken from the IE class is a nominal mid-band ENGINEERING ESTIMATE, not a printed code value: IEC 60034-30-1 tabulates the efficiency limit by rated power and pole count, so no single figure per class exists. It is used ONLY to derive the electrical input P_elec (cable / breaker sizing) — the motor frame is selected on shaft power x service factor and is unaffected. At small ratings the class figure is optimistic (an IE3 motor at 0.75 kW has a printed band near 82.5 %, not 91 %), which UNDERSTATES P_elec; enter the selected motor's rated efficiency for a real selection.

# 4.  Step-by-Step Calculation

Step 1: Pump Flow Rate per Pump

Formula: Q_pump = Q_max x (Duty% / 100) / N_duty

Substitution: Q_pump = 12.000 x (60 / 100) / 2

Result: Q_pump = 3.600 l/s

Step 2: Shaft Power (per pump)

Formula: P_shaft = rho*g x Q x H / eta_pump [rho*g = 9810 N/m3]

Substitution: P_shaft = 9810 x 0.003600 x 18.0 / 0.65

Result: P_shaft = 978.0 W = 0.978 kW

Note: Electrical input P_elec = P_shaft / eta_motor = 1.075 kW (cable / breaker sizing).

Step 3: Motor Frame Selection (IEC 60072 / EN 50347)

Formula: Frame = next standard kW >= P_shaft x service_factor

Substitution: Required = 0.978 x 1.15 = 1.125 kW

Result: Selected motor = 1.5 kW

Step 4: Active Volume (short-cycling)

Formula: V_active = Q_pump (m3/min) x T_cycle (min) / 4

Substitution: V = 0.21600 x 10.0 / 4

Result: V_active = 0.5400 m3

Note: Minimum storage between the pump start and stop levels; the divisor 4 is the worst-case inflow = Q_pump/2.

Step 5: Required Plan Area

Formula: A_required = V_active / Operating_range

Substitution: A = 0.5400 / 0.750 [Op. range = Stage2+3+4 = 750 mm]

Result: A_required = 0.7200 m2

# 5.  Results

Motor Power & Selection

| Parameter | Value |
| --- | --- |
| Shaft (brake) power P_shaft | 0.978 kW (978.0 W) |
| Electrical input P_elec | 1.075 kW |
| Service factor on shaft | x 1.15 |
| Required (shaft x SF) | 1.125 kW |
| Selected IEC motor frame | 1.50 kW |

Motor Start Frequency

Starts per hour of AC induction motors are limited to prevent winding overheating; the active volume is sized so this limit is never exceeded.  The banding below is industry practice (per-hour schedules are published in NEMA MG-10; NEMA MG-1 # 12.54 itself grants 2 successive starts from cold / 1 hot).

| Parameter | Value |
| --- | --- |
| Selected motor (kW) | 1.50 kW |
| Max starts / hour (band) | 6 starts/hr |
| Max starts applied | 6 starts/hr |
| Minimum cycle time T_cycle | 10.0 min/cycle |

| Motor size band | Max starts/hr (practice; MG-10 basis) |
| --- | --- |
| <= 0.75 kW | 20 starts/hr |
| > 0.75 to 7.5 kW | 6 starts/hr |
| > 7.5 to 37 kW | 4 starts/hr |
| > 37 kW | 2 starts/hr |

Active Sump Volume

| Parameter | Value |
| --- | --- |
| Q per duty pump | 3.600 l/s (57.1 GPM) |
| Q per duty pump (m3/min) | 0.21600 |
| Cycle time T (min) | 10.0 |
| V_active required | 0.5400 m3 (19.070 ft3) |

Pit Dimension Sizing

| Parameter | Value |
| --- | --- |
| Operating range | 750 mm (29.5 in) |
| Required plan area | 0.720 m2 (7.75 ft2) |
| Selected Width W | 1.20 m (3.94 ft) |
| Selected Length L | 1.50 m (4.92 ft) |
| Actual pit area | 1.800 m2 (19.38 ft2) |
| Area check | PASS |
| Total pit depth | 1.45 m (4.76 ft) |
| Selected pit dimensions | 1.20 m x 1.50 m x 1.45 m (W x L x D) (3.94 x 4.92 x 4.76 ft) |

# 6.  Sump Pit Cross-Section

# 7.  Equipment Schedule

Sump Pit Level Schedule

| Level | Elevation from pit bottom | Depth (mm) | Description |
| --- | --- | --- | --- |
| Pit bottom | 0 mm | — | Base slab |
| Stage 1 top | 250 mm (9.8 in) | 250 | LOW LEVEL — pump STOP |
| Stage 2 top | 550 mm (21.7 in) | 300 | DUTY PUMP START |
| Stage 3 top | 800 mm (31.5 in) | 250 | ASSIST PUMP START |
| Stage 4 top | 1000 mm (39.4 in) | 200 | HIGH ALARM |
| Clearance top | 1150 mm (45.3 in) | 150 | INLET PIPE INVERT |
| Pit cover | 1450 mm (57.1 in) | 300 | Cover level / grade |

Sump Pump Schedule

All pumps are sized identically. Duty pumps run under the normal inflow profile; assist pumps start at Stage 3 to handle surges the duty pumps alone cannot match.

| Pump Tag | Duty | Flow (l/s) | Head (m) | Shaft kW | Motor kW | Starts/hr | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- |
| P-D01 | Duty | 3.600 | 18.0 | 0.978 | 1.50 | 6 | Runs under normal inflow — the starts/hr cycling limit governs pit volume |
| P-D02 | Duty | 3.600 | 18.0 | 0.978 | 1.50 | 6 | Runs under normal inflow — the starts/hr cycling limit governs pit volume |
| P-A01 | Assist | 3.600 | 18.0 | 0.978 | 1.50 | 6 | Starts at Stage 3 level — handles inflow surges beyond duty capacity |

Pump Schedule Summary

| Parameter | Value |
| --- | --- |
| Total pumps installed | 3 |
| Duty pumps | 2 |
| Assist pumps | 1 |
| Flow per pump (l/s) | 3.600 |
| Motor rating per pump | 1.50 kW |
| Total installed motor power | 4.50 kW (3 x 1.50 kW) |
| Starts/hour limit | 6 starts/hr |

# R.  Reference Standards

BS EN 12056-2 — Gravity drainage systems inside buildings — design and calculation of the wastewater flow feeding the sump pit.

Motor starts-per-hour banding — Maximum allowable starts per hour by motor size — industry-practice banding (per-hour schedules are published in NEMA MG-10; NEMA MG-1 # 12.54 itself grants 2 successive starts from cold / 1 hot). Sets the minimum cycle time used to size the active sump volume so the windings do not overheat.

Active-Volume Formula (short-cycling) — V_active = Q_pump (m3/min) x T_cycle (min) / 4 — the classic pump short-cycling result: the divisor 4 is the worst-case inflow = Q_pump/2 that maximises cycling frequency.

Shaft-Power Formula — P_shaft = rho*g x Q x H / eta_pump with rho*g = 9810 N/m3 (brake power at the coupling). The electrical input P_elec = P_shaft / eta_motor sizes the cable / breaker only.

IEC 60072 / EN 50347 — Standard motor frame kW ratings — rated by SHAFT OUTPUT. The selected frame is the next rating at or above P_shaft x service factor (1.15).

IEC 60034-30-1 — Motor efficiency classes (IE1-IE4). The selected IE class sets the indicative motor efficiency used for the electrical-input figure.

NPSH (submersible) — NPSH_avail = H_atm - H_vapor + H_submergence - H_suction_friction, checked against the pump-curve NPSH_required to flag cavitation risk.

Engineer of record: Hussein Ragab

Generated by Sump Pit Calculator — short-cycling / BS EN 12056-2 active-volume sizing.