## Pump Schedule
Sump Pit — Pump Duty Schedule
Result: SP-B3-01
Project: Test Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: Test Dev ¦ By: Hussein Ragab ¦ Chkd: Principal MEP Review ¦ Rev: P2 ¦ Date: 2026-09-02
BS EN 12056-2 ¦ IEC 60072 / EN 50347 ¦ IEC 60034-30-1 ¦ NEMA MG-10 basis
Unit system: SI (metric) · 3 pump(s) installed · Generated 02 Sep 2026
Pump Tag | Duty | Flow (l/s) | Head (m) | Shaft kW | Motor kW | Starts/hr | Remarks
P-D01 | Duty | 3.6 | 18 | 0.978 | 1.5 | 6 | Runs under normal inflow — the starts/hr cycling limit governs pit volume
P-D02 | Duty | 3.6 | 18 | 0.978 | 1.5 | 6 | Runs under normal inflow — the starts/hr cycling limit governs pit volume
P-A01 | Assist | 3.6 | 18 | 0.978 | 1.5 | 6 | Starts at Stage 3 level — handles inflow surges beyond duty capacity
Methodology & Standards
Reference |  | Application
BS EN 12056-2 |  | Gravity drainage systems inside buildings — design and calculation of the wastewater flow feeding the sump pit.
Motor starts-per-hour banding |  | Maximum allowable starts per hour by motor size — industry-practice banding (per-hour schedules are published in NEMA MG-10; NEMA MG-1 # 12.54 itself grants 2 successive starts from cold / 1 hot). Sets the minimum cycle time used to size the active sump volume so the windings do not overheat.
Active-Volume Formula (short-cycling) |  | V_active = Q_pump (m3/min) x T_cycle (min) / 4 — the classic pump short-cycling result: the divisor 4 is the worst-case inflow = Q_pump/2 that maximises cycling frequency.
Shaft-Power Formula |  | P_shaft = rho*g x Q x H / eta_pump with rho*g = 9810 N/m3 (brake power at the coupling). The electrical input P_elec = P_shaft / eta_motor sizes the cable / breaker only.
IEC 60072 / EN 50347 |  | Standard motor frame kW ratings — rated by SHAFT OUTPUT. The selected frame is the next rating at or above P_shaft x service factor (1.15).
IEC 60034-30-1 |  | Motor efficiency classes (IE1-IE4). The selected IE class sets the indicative motor efficiency used for the electrical-input figure.
NPSH (submersible) |  | NPSH_avail = H_atm - H_vapor + H_submergence - H_suction_friction, checked against the pump-curve NPSH_required to flag cavitation risk.

## Sizing Basis
Sump Pit — Sizing Basis
Result: SP-B3-01
Project: Test Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: Test Dev ¦ By: Hussein Ragab ¦ Chkd: Principal MEP Review ¦ Rev: P2 ¦ Date: 2026-09-02
BS EN 12056-2 ¦ IEC 60072 / EN 50347 ¦ IEC 60034-30-1 ¦ NEMA MG-10 basis
Unit system: SI (metric) · Generated 02 Sep 2026
Parameter | Value | Basis
Maximum inflow Q_max | 12 | Total peak inflow arriving at the pit
Duty share per pump | 60 | User input
No. of duty pumps | 2 | User input
Q per duty pump | 3.6 | Q_pump = Q_max x (Duty% / 100) / N_duty
Assist pumps | 1 | Start at the Stage 3 level (inflow surges)
Total pumps installed | 3 | All pumps sized identically
Total head H | 18 | static 14.50 m + friction 3.50 m
Pump efficiency eta_p | 0.65 (65 %) | Pump curve at the duty point
Motor class / eta_m | IE3 (premium) (91 %) | IEC 60034-30-1 class — the class figure is a nominal mid-band ENGINEERING ESTIMATE (the standard tabulates by kW and poles; optimistic at small ratings); drives P_elec only
Shaft (brake) power P_shaft | 0.978 | P_shaft = rho*g x Q x H / eta_pump [rho*g = 9810 N/m3]
Electrical input P_elec | 1.075 | P_elec = P_shaft / eta_motor — cable / breaker sizing only
Service factor on shaft | x 1.15 | Frame = next standard kW >= P_shaft x service factor
Required (shaft x SF) | 1.125 | IEC 60072 / EN 50347
Selected IEC motor frame | 1.5 | IEC 60072 / EN 50347 standard kW ladder (rated by SHAFT output)
Max starts / hour (band) | 6 | Industry-practice banding; per-hour schedules NEMA MG-10
Max starts applied | 6 | Auto band, or the engineer's override
Minimum cycle time T_cycle | 10 | Motor start-frequency limit
Q per duty pump (m3/min) | 0.216 | Q_pump x 60 / 1000
Active volume V_active | 0.5400 m3 (540 L) | V_active = Q_pump (m3/min) x T_cycle (min) / 4
Operating range (Stage 2+3+4) | 750 | Storage between the pump start and stop levels
Required plan area | 0.72 | A_required = V_active / Operating_range
Selected pit W x L | 1.20 m x 1.50 m | User input
Actual pit area | 1.8 | W x L
Area check | PASS | Actual >= required
Total pit depth | 1.45 | Stages 1-4 + clearance + above-inlet headroom
NPSH available | 10.34 | H_atm - H_vapor + H_submergence - H_suction_friction
NPSH required (curve) | 3.5 | From the pump curve (0 skips the check)
NPSH margin | 6.84 | Safety margin 0.60 m — OK
✓ PIT AREA ADEQUATE — actual area meets the short-cycling requirement

## Level Schedule
Sump Pit — Level Schedule
Result: SP-B3-01
Project: Test Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: Test Dev ¦ By: Hussein Ragab ¦ Chkd: Principal MEP Review ¦ Rev: P2 ¦ Date: 2026-09-02
Unit system: SI (metric) · Generated 02 Sep 2026
Level | Elevation from pit floor | Band depth (mm) | Description
Pit bottom | 0 | — | Base slab
Stage 1 top | 250 | 250 | LOW LEVEL — pump STOP
Stage 2 top | 550 | 300 | DUTY PUMP START
Stage 3 top | 800 | 250 | ASSIST PUMP START
Stage 4 top | 1000 | 200 | HIGH ALARM
Clearance top | 1150 | 150 | INLET PIPE INVERT
Pit cover | 1450 | 300 | Cover level / grade