Ventilation Energy Consumption

FAHU-01 Office Floors - Dubai

FAHU with double heat recovery wheels ¦ Dubai, United Arab Emirates ¦ 2025-01-01 to 2025-12-31 (365 days)

| Project Information |  |
| --- | --- |
| Project Name | Marina Commercial Tower |
| Project No. | MCT-2026-MEP-001 |
| Revision | P2 |
| Client | — |
| Prepared by | Hussein Ragab |
| Checked by | — |
| Date | 2026-10-20 |

Values in this report are displayed in SI (metric) units.  Energy (kWh, TRh), power (kW, TR), plant efficiency and money read the same in both systems; only airflow and temperatures change.

Weather data: Open-Meteo archive — live fetch, site timezone Asia/Dubai, data written 2026-10-20 10:08

# 1.  Methodology & Standards

Hour by hour over the simulation period: the outdoor state from the weather archive, the on-coil state (after the wheel on the recovery types), the coil load to the off-coil state, the fan and cooling-source electricity, then monthly sums put on one year and priced at the tariff.

| Reference | Application |
| --- | --- |
| Weather data | Open-Meteo archive — live fetch, site timezone Asia/Dubai, data written 2026-10-20 10:08. Weather data by Open-Meteo.com (https://open-meteo.com/), licensed CC BY 4.0 (https://creativecommons.org/licenses/by/4.0/). Generated using Copernicus Climate Change Service information 2022. Values derived from the hourly data (percentiles, simulation frames) were computed by this tool. |
| ASHRAE Fundamentals 2021 SI Ch.1 Eq (43) p.1.12, Eq (30), Eq (32) | Hourly cooling coil load from the moist-air enthalpy change across the coil, less the enthalpy of the condensate leaving at the off-coil temperature. |
| psychrolib (ASHRAE Fundamentals 2021 Ch. 1 equations) | Moist-air properties of every simulated hour. |
| ASHRAE Fundamentals 2021 SI Ch.40 Table 1 p.40.1 | Ton of refrigeration: 1 TR = 3.517 kW. |
| ANSI/ASHRAE 84-1991 6.3.1 Eq 7 | Wheel effectiveness applied on dry-air mass flows to give the on-coil state after the wheel. |
| ASHRAE SE 2020 Ch.26 Table 3 (p.26.24) | Catalogue effectiveness bands behind the Library pre-fills (see # 3). |
| ASHRAE S&E 2020 SI Ch.21 #18 p.21.14-21.15 (Ho, eta_t = Ho/Hi, eta_s = eta_t Psf/Ptf) | Fan electrical input from airflow, static pressure, fan static efficiency and motor efficiency. |

# 2.  Design Inputs

| Parameter | Value |
| --- | --- |
| System type | FAHU with double heat recovery wheels |
| Location | Dubai, United Arab Emirates |
| Simulation period | 2025-01-01 to 2025-12-31 (365 days) |
| Fresh air flow | 3,000 L/s |
| Extract air flow | 2,400 L/s |
| Off-coil dry bulb | 13.0 °C |
| Off-coil relative humidity | 90 % |
| Room dry bulb | 24.0 °C |
| Room wet bulb | 17.0 °C |
| Enthalpy wheel sensible effectiveness (0-1) | 0.72 |
| Enthalpy wheel latent effectiveness (0-1) | 0.68 |
| Sensible wheel effectiveness (0-1) | 0.6 |
| Operating schedule | Office: Mon-Fri 06:00-22:00 ¦ Sat 06:00-18:00 ¦ Sun closed |
| Fan power method | From static pressure (TSP) |
| Supply fan static pressure | 750 Pa |
| Extract fan static pressure | 500 Pa |
| Fan static efficiency (0-1) | 0.65 |
| Motor efficiency (0-1) | 0.92 |
| Wheel drive input per wheel | 0.75 kW |
| Cooling source | District cooling |
| Currency | AED |
| Electricity price | 0.38 AED/kWh |
| DC consumption charge | 0.55 AED/TRh |
| DC fuel surcharge | - |
| DC capacity charge | - |

# 3.  Design Assumptions

Annual figures: 2025 (1 full year). Whole calendar years are averaged; any other period is scaled to one year by the ratio of the days in a year to the days in the run, and labelled.

The coil load of each open hour is the engine's hourly figure; an hour at or below the off-coil dry bulb needs no cooling and is counted at zero load.

The fans run at the design electrical input in every open hour (schedule above zero) and are off in a closed hour.

Operating schedule: Office: Mon-Fri 06:00-22:00  |  Sat 06:00-18:00  |  Sun closed.

Schedule template basis: ASHRAE Standard 90.1 User's Manual (based on ANSI/ASHRAE/IES 90.1-2016), Appendix G Table G-H Office, printed p.455 - HVAC-system operating hours (from Std 90.1-1989).

Wheel effectiveness: the values in # 2 are this run's inputs. The Library pre-fills behind them are engineering picks inside the printed ASHRAE SE 2020 Ch.26 Table 3 (p.26.24) catalogue bands - an engineering default, NOT a printed cell - use the AHRI-1060 tested values for the selected unit instead.

Room design condition: the DB and WB in # 2 are this run's inputs. The Library pre-fills are typical cooling-season values (ASHRAE Standard 55-2010 summer comfort zone; ASHRAE Handbook - HVAC Applications (2019) Ch. 1 / 2 / 9 / 20; ASHRAE TC 9.9 (2011) Class A1) - an engineering default, NOT a printed cell for this specific space - confirm the setpoint against the project specification. ASHRAE 55-2010 and TC 9.9 are held with the tool; the HVAC Applications handbook is cited as a design reference and is NOT bundled, so these pairs are engineering estimates, not transcribed handbook cells.

District cooling: no plant electricity is counted; the cooling energy is billed per TRh at the tariff in # 2. A capacity charge is an annual figure and is split to months by days.

Every tariff in # 2 is the engineer's project input, not a code value. A blank rate the cost needs withholds the cost and is named; the energy results still stand.

# 4.  Step-by-Step Calculation

At the peak coil-load hour of the run - the trace the Results tab shows. Values are the engine's SI figures.

Step 1: Peak coil-load hour

Formula: The hour of maximum coil load q

Substitution: Values (SI): 2025-09-08 19:00, outdoor 33.0 °C / 81.0 %, P = 99600 Pa

Result: 33.0 °C

Step 2: Outdoor humidity ratio W_o

Formula: W = 0.621945 p_w / (p - p_w), p_w = RH x p_ws [Fundamentals 2021 SI Ch.1 Eq (20)]

Substitution: Values (SI): T = 33.0 °C, RH = 81.0 %, P = 99600 Pa

Result: 0.02655 kg/kg

Step 3: Outdoor air density

Formula: rho = (1 + W) / v, moist-air specific volume [Fundamentals 2021 SI Ch.1 Eq (11)]

Substitution: Values (SI): T = 33.0 °C, W = 0.02655

Result: 1.1158 kg/m³

Step 4: Dry-air mass flow m_da

Formula: m_da = rho x V / (1 + W_o)

Substitution: Values (SI): V = 3.0000 m³/s (effective fresh air this hour)

Result: 3.2610 kg/s

Step 5: On-coil state (after the wheel)

Formula: From the engine's wheel step (ANSI/ASHRAE 84-1991 6.3.1 Eq 7), W_on from the on-coil DB and RH

Substitution: Values (SI): T_on = 23.49 °C, RH_on = 89.9 %, W_on = 0.01670

Result: 23.5 °C

Step 6: Leaving humidity ratio W_2

Formula: W_2 = min(W_on, W_off); W_off from the off-coil DB and condition

Substitution: Values (SI): W_on = 0.01670, W_off = 0.00853

Result: 0.00853 kg/kg

Step 7: On-coil enthalpy h_1

Formula: h = 1.006 t + W (2501 + 1.86 t) [ASHRAE Fundamentals 2021 SI Ch.1 Eq (30)]

Substitution: Values (SI): t = 23.49 °C, W = 0.01670

Result: 66.116 kJ/kg

Step 8: Off-coil enthalpy h_2

Formula: h = 1.006 t + W (2501 + 1.86 t) [ASHRAE Fundamentals 2021 SI Ch.1 Eq (30)]

Substitution: Values (SI): t = 13.00 °C, W = 0.00853

Result: 34.626 kJ/kg

Step 9: Condensate term

Formula: (W_1 - W_2) h_w2, h_w2 = 4.186 t_2 [Ch.1 Eq (32) form, at the off-coil DB]

Substitution: Values (SI): h_w2 = 54.418 kJ/kg, W_1 - W_2 = 0.00816

Result: 0.444 kJ/kg

Step 10: Coil load q

Formula: q = m_da [(h_1 - h_2) - (W_1 - W_2) h_w2] [ASHRAE Fundamentals 2021 SI Ch.1 Eq (43) p.1.12]

Substitution: Values (SI): m_da = 3.2610 kg/s, h_1 - h_2 = 31.490 kJ/kg, term = 0.4442 kJ/kg

Result: 101.2 kW

Step 11: Coil load in TR

Formula: TR = q / 3.517 [ASHRAE Fundamentals 2021 SI Ch.40 Table 1 p.40.1]

Substitution: Values (SI): q = 101.241 kW

Result: 28.8 TR

Step 12: Fan electrical input (design)

Formula: P = Q x TSP / (eta_fan x eta_motor) per fan, plus the wheel drives [ASHRAE S&E 2020 SI Ch.21 #18 p.21.14-21.15]

Substitution: Values (SI): supply 3000 L/s at 750.0 Pa, extract 2400 L/s at 500.0 Pa, eta_fan = 0.65, eta_motor = 0.92, wheels 2 x 0.75 kW; supply 3.763 kW, extract 2.007 kW

Result: 7.3 kW

Step 13: Cooling-source electricity at the peak hour

Formula: District cooling: no plant electricity (the TRh is billed)

Substitution: -

Result: 0.0 kW

Step 14: Annual cooling energy

Formula: Sum of q x 1 h over the run, put on one year (2025 (1 full year)); TRh = kWh / 3.517

Substitution: Values (SI): 70,216 TRh

Result: 246,950 kWh

Step 15: Annual electricity

Formula: Plant kWh + fan kWh (fans run at the design input in every open hour)

Substitution: Values (SI): plant 0 kWh + fans 34,892 kWh

Result: 34,892 kWh

Step 16: Annual cost

Formula: Electricity = (plant + fan) kWh x price per kWh; DC = TRh x consumption rate + TRh x fuel surcharge + contracted TR x capacity rate x d_m / d_y per month

Substitution: Values (SI): price 0.38 AED/kWh; electricity 13,259, consumption 38,619, fuel 0, capacity 0

Result: 51,878 AED

# 5.  Results

| Parameter | Value |
| --- | --- |
| Annual figures | 2025 (1 full year) |
| Annual cooling energy | 246,950 kWh |
| Annual cooling energy | 70,216 TRh |
| Peak coil load | 101.2 kW |
| Peak coil load | 28.8 TR |
| Peak hour | 2025-09-08 19:00 |
| Annual plant electricity | 0 kWh |
| Annual fan electricity | 34,892 kWh |
| Annual electricity (plant + fans) | 34,892 kWh |
| Design fan input (while open) | 7.27 kW |
| Annual electricity cost | 13,259 AED |
| Annual DC consumption cost | 38,619 AED |
| Annual DC fuel surcharge | 0 AED |
| Annual DC capacity cost | 0 AED |
| Annual total cost | 51,878 AED |
| Cooling hours in the run | 4,800 h |
| Open hours with no cooling | 0 h |
| Closed hours | 3,960 h |
| Open hours with condensate but no coil load | 0 h |

Monthly energy

| Month | Cooling (kWh) | Cooling (TRh) | Plant (kWh) | Fans (kWh) | Electricity cost (AED) | DC consumption (AED) | DC fuel surcharge (AED) | DC capacity (AED) | Total cost (AED) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Jan 2025 | 10,277 | 2,922 | 0 | 3,024 | 1,149 | 1,607 | 0 | 0 | 2,756 |
| Feb 2025 | 11,389 | 3,238 | 0 | 2,675 | 1,017 | 1,781 | 0 | 0 | 2,798 |
| Mar 2025 | 13,952 | 3,967 | 0 | 2,879 | 1,094 | 2,182 | 0 | 0 | 3,276 |
| Apr 2025 | 18,175 | 5,168 | 0 | 2,908 | 1,105 | 2,842 | 0 | 0 | 3,947 |
| May 2025 | 23,921 | 6,802 | 0 | 2,995 | 1,138 | 3,741 | 0 | 0 | 4,879 |
| Jun 2025 | 26,231 | 7,458 | 0 | 2,791 | 1,061 | 4,102 | 0 | 0 | 5,163 |
| Jul 2025 | 29,825 | 8,480 | 0 | 3,024 | 1,149 | 4,664 | 0 | 0 | 5,813 |
| Aug 2025 | 27,826 | 7,912 | 0 | 2,879 | 1,094 | 4,352 | 0 | 0 | 5,445 |
| Sep 2025 | 29,975 | 8,523 | 0 | 2,908 | 1,105 | 4,688 | 0 | 0 | 5,793 |
| Oct 2025 | 25,932 | 7,373 | 0 | 3,024 | 1,149 | 4,055 | 0 | 0 | 5,204 |
| Nov 2025 | 15,568 | 4,426 | 0 | 2,762 | 1,050 | 2,435 | 0 | 0 | 3,484 |
| Dec 2025 | 13,881 | 3,947 | 0 | 3,024 | 1,149 | 2,171 | 0 | 0 | 3,320 |

# 6.  Charts

# R.  Reference Standards

Weather data — Open-Meteo archive — live fetch, site timezone Asia/Dubai, data written 2026-10-20 10:08. Weather data by Open-Meteo.com (https://open-meteo.com/), licensed CC BY 4.0 (https://creativecommons.org/licenses/by/4.0/). Generated using Copernicus Climate Change Service information 2022. Values derived from the hourly data (percentiles, simulation frames) were computed by this tool.

ASHRAE Fundamentals 2021 SI Ch.1 Eq (43) p.1.12, Eq (30), Eq (32) — Hourly cooling coil load from the moist-air enthalpy change across the coil, less the enthalpy of the condensate leaving at the off-coil temperature.

psychrolib (ASHRAE Fundamentals 2021 Ch. 1 equations) — Moist-air properties of every simulated hour.

ASHRAE Fundamentals 2021 SI Ch.40 Table 1 p.40.1 — Ton of refrigeration: 1 TR = 3.517 kW.

ANSI/ASHRAE 84-1991 6.3.1 Eq 7 — Wheel effectiveness applied on dry-air mass flows to give the on-coil state after the wheel.

ASHRAE SE 2020 Ch.26 Table 3 (p.26.24) — Catalogue effectiveness bands behind the Library pre-fills (see # 3).

ASHRAE S&E 2020 SI Ch.21 #18 p.21.14-21.15 (Ho, eta_t = Ho/Hi, eta_s = eta_t Psf/Ptf) — Fan electrical input from airflow, static pressure, fan static efficiency and motor efficiency.

Engineer of record: Hussein Ragab

Generated by Ventilation Energy Consumption 1.0.0 - hourly coil load, fan and cooling-source energy and cost.