## Summary
Ventilation Energy Consumption - Workbook
FAHU-01 Office Floors - Dubai ¦ FAHU with double heat recovery wheels ¦ working units: SI
Project: Marina Commercial Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: - ¦ By: Hussein Ragab ¦ Chkd: - ¦ Rev: P2 ¦ Date: 2026-10-20
Location: Dubai, United Arab Emirates ¦ Period: 2025-01-01 to 2025-12-31 (365 days)
Weather data: Open-Meteo archive — live fetch, site timezone Asia/Dubai, data written 2026-10-20 10:08
Design Inputs
Quantity | Value | Unit
System type | FAHU with double heat recovery wheels
Location | Dubai, United Arab Emirates
Simulation period | 2025-01-01 to 2025-12-31 (365 days)
Fresh air flow | 3000 | L/s
Extract air flow | 2400 | L/s
Off-coil dry bulb | 13 | °C
Off-coil relative humidity | 90 | %
Room dry bulb | 24 | °C
Room wet bulb | 17 | °C
Enthalpy wheel sensible effectiveness (0-1) | 0.72
Enthalpy wheel latent effectiveness (0-1) | 0.68
Sensible wheel effectiveness (0-1) | 0.6
Operating schedule | Office: Mon-Fri 06:00-22:00 ¦ Sat 06:00-18:00 ¦ Sun closed
Fan power method | From static pressure (TSP)
Supply fan static pressure | 750 | Pa
Extract fan static pressure | 500 | Pa
Fan static efficiency (0-1) | 0.65
Motor efficiency (0-1) | 0.92
Wheel drive input per wheel | 0.75 | kW
Cooling source | District cooling
Currency | AED
Electricity price | 0.38 | AED/kWh
DC consumption charge | 0.55 | AED/TRh
DC fuel surcharge | - | AED/TRh
DC capacity charge | - | AED/TR/year
Annual Results
Quantity | Value | Unit
Annual figures | 2025 (1 full year)
Annual cooling energy | 246950.249 | kWh
Annual cooling energy | 70216.1641 | TRh
Peak coil load | 101.2408 | kW
Peak coil load | 28.7861 | TR
Peak hour | 2025-09-08 19:00
Annual plant electricity | 0 | kWh
Annual fan electricity | 34892.3077 | kWh
Annual electricity (plant + fans) | 34892.3077 | kWh
Design fan input (while open) | 7.2692 | kW
Annual electricity cost | 13259.0769 | AED
Annual DC consumption cost | 38618.8902 | AED
Annual DC fuel surcharge | 0 | AED
Annual DC capacity cost | 0 | AED
Annual total cost | 51877.9672 | AED
Cooling hours in the run | 4800 | h
Open hours with no cooling | 0 | h
Closed hours | 3960 | h
Open hours with condensate but no coil load | 0 | h
References
Reference | Application
Weather data | Open-Meteo archive — live fetch, site timezone Asia/Dubai, data written 2026-10-20 10:08. Weather data by Open-Meteo.com (https://open-meteo.com/), licensed CC BY 4.0 (https://creativecommons.org/licenses/by/4.0/). Generated using Copernicus Climate Change Service information 2022. Values derived from the hourly data (percentiles, simulation frames) were computed by this tool.
ASHRAE Fundamentals 2021 SI Ch.1 Eq (43) p.1.12, Eq (30), Eq (32) | Hourly cooling coil load from the moist-air enthalpy change across the coil, less the enthalpy of the condensate leaving at the off-coil temperature.
psychrolib (ASHRAE Fundamentals 2021 Ch. 1 equations) | Moist-air properties of every simulated hour.
ASHRAE Fundamentals 2021 SI Ch.40 Table 1 p.40.1 | Ton of refrigeration: 1 TR = 3.517 kW.
ANSI/ASHRAE 84-1991 6.3.1 Eq 7 | Wheel effectiveness applied on dry-air mass flows to give the on-coil state after the wheel.
ASHRAE SE 2020 Ch.26 Table 3 (p.26.24) | Catalogue effectiveness bands behind the Library pre-fills (see # 3).
ASHRAE S&E 2020 SI Ch.21 #18 p.21.14-21.15 (Ho, eta_t = Ho/Hi, eta_s = eta_t Psf/Ptf) | Fan electrical input from airflow, static pressure, fan static efficiency and motor efficiency.
Generated by Ventilation Energy Consumption. Internal calculation is SI; only airflow and temperatures follow the unit system.

## Monthly
Ventilation Energy Consumption - Monthly
FAHU-01 Office Floors - Dubai ¦ FAHU with double heat recovery wheels ¦ working units: SI
Project: Marina Commercial Tower ¦ No.: MCT-2026-MEP-001 ¦ Client: - ¦ By: Hussein Ragab ¦ Chkd: - ¦ Rev: P2 ¦ Date: 2026-10-20
Location: Dubai, United Arab Emirates ¦ Period: 2025-01-01 to 2025-12-31 (365 days)
Weather data: Open-Meteo archive — live fetch, site timezone Asia/Dubai, data written 2026-10-20 10:08
Annual figures: 2025 (1 full year)
Every month of the run
Month | Cooling (kWh) | Cooling (TRh) | Plant (kWh) | Fans (kWh) | Electricity (kWh) | Electricity cost (AED) | DC consumption (AED) | DC fuel surcharge (AED) | DC capacity (AED) | Total cost (AED)
Jan 2025 | 10276.8294 | 2922.0442 | 0 | 3024 | 3024 | 1149.12 | 1607.1243 | 0 | 0 | 2756.2443
Feb 2025 | 11388.6575 | 3238.1739 | 0 | 2675.0769 | 2675.0769 | 1016.5292 | 1780.9956 | 0 | 0 | 2797.5249
Mar 2025 | 13951.5666 | 3966.8941 | 0 | 2878.6154 | 2878.6154 | 1093.8738 | 2181.7918 | 0 | 0 | 3275.6656
Apr 2025 | 18174.8947 | 5167.7267 | 0 | 2907.6923 | 2907.6923 | 1104.9231 | 2842.2497 | 0 | 0 | 3947.1727
May 2025 | 23921.0242 | 6801.5423 | 0 | 2994.9231 | 2994.9231 | 1138.0708 | 3740.8483 | 0 | 0 | 4878.919
Jun 2025 | 26230.6017 | 7458.2319 | 0 | 2791.3846 | 2791.3846 | 1060.7262 | 4102.0276 | 0 | 0 | 5162.7537
Jul 2025 | 29824.7542 | 8480.1689 | 0 | 3024 | 3024 | 1149.12 | 4664.0929 | 0 | 0 | 5813.2129
Aug 2025 | 27825.9939 | 7911.855 | 0 | 2878.6154 | 2878.6154 | 1093.8738 | 4351.5202 | 0 | 0 | 5445.3941
Sep 2025 | 29975.3414 | 8522.9859 | 0 | 2907.6923 | 2907.6923 | 1104.9231 | 4687.6422 | 0 | 0 | 5792.5653
Oct 2025 | 25932.2418 | 7373.3983 | 0 | 3024 | 3024 | 1149.12 | 4055.3691 | 0 | 0 | 5204.4891
Nov 2025 | 15567.7036 | 4426.4156 | 0 | 2762.3077 | 2762.3077 | 1049.6769 | 2434.5286 | 0 | 0 | 3484.2055
Dec 2025 | 13880.6399 | 3946.7273 | 0 | 3024 | 3024 | 1149.12 | 2170.7 | 0 | 0 | 3319.82

## Hourly
Ventilation Energy Consumption - Hourly
FAHU-01 Office Floors - Dubai ¦ per-hour simulation frame ¦ working units: SI
Time | Outdoor DB (°C) | Outdoor RH (%) | Pressure (Pa) | Schedule (%) | Fresh air (L/s) | On-coil DB (°C) | On-coil RH (%) | Coil load (kW) | Plant (kW) | Fans (kW) | Open, no cooling | Condensate, no coil load
2025-01-01 | 18.15 | 82 | 101320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-01 01:00 | 17.7 | 81.5 | 101290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-01 02:00 | 17.2 | 79 | 101255 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-01 03:00 | 16.95 | 72 | 101215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-01 04:00 | 17.35 | 68 | 101205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-01 05:00 | 17.7 | 67 | 101215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-01 06:00 | 17.55 | 64 | 101250 | 100 | 3000 | 17.4656 | 69.5603 | 18.6647 | 0 | 7.2692 | FALSE | FALSE
2025-01-01 07:00 | 17.8 | 61 | 101320 | 100 | 3000 | 17.5749 | 68.1278 | 17.991 | 0 | 7.2692 | FALSE | FALSE
2025-01-01 08:00 | 19.1 | 55.5 | 101400 | 100 | 3000 | 18.1394 | 65.4066 | 19.5945 | 0 | 7.2692 | FALSE | FALSE
2025-01-01 09:00 | 21.15 | 49.5 | 101450 | 100 | 3000 | 19.0158 | 62.274 | 23.0923 | 0 | 7.2692 | FALSE | FALSE
2025-01-01 10:00 | 23.3 | 44 | 101450 | 100 | 3000 | 19.917 | 59.2428 | 26.642 | 0 | 7.2692 | FALSE | FALSE
2025-01-01 11:00 | 24.85 | 40.5 | 101405 | 100 | 3000 | 20.5554 | 57.2226 | 29.1432 | 0 | 7.2692 | FALSE | FALSE
2025-01-01 12:00 | 25.25 | 48 | 101315 | 100 | 3000 | 20.7065 | 61.7628 | 36.3371 | 0 | 7.2692 | FALSE | FALSE
2025-01-01 13:00 | 24.8 | 57.5 | 101220 | 100 | 3000 | 20.5123 | 67.3384 | 41.9875 | 0 | 7.2692 | FALSE | FALSE
2025-01-01 14:00 | 24.05 | 62 | 101170 | 100 | 3000 | 20.2045 | 69.7217 | 42.3778 | 0 | 7.2692 | FALSE | FALSE
2025-01-01 15:00 | 23.3 | 66 | 101170 | 100 | 3000 | 19.8957 | 71.7263 | 42.2083 | 0 | 7.2692 | FALSE | FALSE
2025-01-01 16:00 | 22.8 | 68 | 101205 | 100 | 3000 | 19.6894 | 72.6474 | 41.5437 | 0 | 7.2692 | FALSE | FALSE
2025-01-01 17:00 | 22.2 | 68.5 | 101255 | 100 | 3000 | 19.4422 | 72.6902 | 39.4148 | 0 | 7.2692 | FALSE | FALSE
2025-01-01 18:00 | 21.55 | 65.5 | 101330 | 100 | 3000 | 19.1744 | 70.8554 | 34.832 | 0 | 7.2692 | FALSE | FALSE
2025-01-01 19:00 | 21 | 64 | 101420 | 100 | 3000 | 18.945 | 69.9159 | 31.7248 | 0 | 7.2692 | FALSE | FALSE
2025-01-01 20:00 | 20.5 | 66 | 101470 | 100 | 3000 | 18.7334 | 70.8449 | 31.0174 | 0 | 7.2692 | FALSE | FALSE
2025-01-01 21:00 | 20.1 | 66.5 | 101495 | 100 | 3000 | 18.5639 | 71.0155 | 29.7565 | 0 | 7.2692 | FALSE | FALSE
2025-01-01 22:00 | 19.6 | 67 | 101515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-01 23:00 | 19.2 | 67 | 101510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-02 | 19.05 | 63.5 | 101485 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-02 01:00 | 18.95 | 61.5 | 101460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-02 02:00 | 18.95 | 61 | 101445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-02 03:00 | 19.05 | 58.5 | 101440 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-02 04:00 | 18.9 | 56 | 101470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-02 05:00 | 18.65 | 55.5 | 101530 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-02 06:00 | 18.6 | 56 | 101575 | 100 | 3000 | 17.9232 | 65.6545 | 18.1258 | 0 | 7.2692 | FALSE | FALSE
2025-01-02 07:00 | 19 | 54 | 101615 | 100 | 3000 | 18.0965 | 64.643 | 18.704 | 0 | 7.2692 | FALSE | FALSE
2025-01-02 08:00 | 20.15 | 49 | 101665 | 100 | 3000 | 18.5915 | 62.0359 | 20.4531 | 0 | 7.2692 | FALSE | FALSE
2025-01-02 09:00 | 21.25 | 44.5 | 101705 | 100 | 3000 | 19.0607 | 59.5844 | 22.0984 | 0 | 7.2692 | FALSE | FALSE
2025-01-02 10:00 | 21.9 | 42 | 101710 | 100 | 3000 | 19.3359 | 58.1754 | 23.0545 | 0 | 7.2692 | FALSE | FALSE
2025-01-02 11:00 | 22.1 | 42.5 | 101665 | 100 | 3000 | 19.4194 | 58.4342 | 23.3294 | 0 | 7.2692 | FALSE | FALSE
2025-01-02 12:00 | 22.15 | 43.5 | 101590 | 100 | 3000 | 19.4396 | 58.9859 | 23.3785 | 0 | 7.2692 | FALSE | FALSE
2025-01-02 13:00 | 22.35 | 42 | 101520 | 100 | 3000 | 19.5244 | 58.1547 | 23.6568 | 0 | 7.2692 | FALSE | FALSE
2025-01-02 14:00 | 22.35 | 40 | 101475 | 100 | 3000 | 19.5259 | 57.0568 | 23.6579 | 0 | 7.2692 | FALSE | FALSE
2025-01-02 15:00 | 22.05 | 38.5 | 101460 | 100 | 3000 | 19.4013 | 56.2755 | 23.2328 | 0 | 7.2692 | FALSE | FALSE
2025-01-02 16:00 | 21.6 | 39 | 101475 | 100 | 3000 | 19.2116 | 56.6183 | 22.5836 | 0 | 7.2692 | FALSE | FALSE
2025-01-02 17:00 | 20.85 | 42.5 | 101515 | 100 | 3000 | 18.8923 | 58.5957 | 21.4815 | 0 | 7.2692 | FALSE | FALSE
2025-01-02 18:00 | 20.1 | 46.5 | 101565 | 100 | 3000 | 18.5711 | 60.7688 | 20.3678 | 0 | 7.2692 | FALSE | FALSE
2025-01-02 19:00 | 19.75 | 48.5 | 101610 | 100 | 3000 | 18.4206 | 61.8241 | 19.8477 | 0 | 7.2692 | FALSE | FALSE
2025-01-02 20:00 | 19.5 | 49 | 101635 | 100 | 3000 | 18.3131 | 62.1016 | 19.476 | 0 | 7.2692 | FALSE | FALSE
2025-01-02 21:00 | 19.2 | 49.5 | 101645 | 100 | 3000 | 18.1838 | 62.3862 | 19.0242 | 0 | 7.2692 | FALSE | FALSE
2025-01-02 22:00 | 18.9 | 50 | 101650 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-02 23:00 | 18.6 | 50.5 | 101630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-03 | 18.25 | 51 | 101605 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-03 01:00 | 17.95 | 51.5 | 101595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-03 02:00 | 17.65 | 52.5 | 101585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-03 03:00 | 17.3 | 53.5 | 101585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-03 04:00 | 17.25 | 51.5 | 101605 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-03 05:00 | 17.2 | 49 | 101635 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-03 06:00 | 17.05 | 49 | 101685 | 100 | 3000 | 17.2459 | 62.5407 | 15.7141 | 0 | 7.2692 | FALSE | FALSE
2025-01-03 07:00 | 17.75 | 47 | 101750 | 100 | 3000 | 17.5537 | 61.4187 | 16.8233 | 0 | 7.2692 | FALSE | FALSE
2025-01-03 08:00 | 19.05 | 43 | 101810 | 100 | 3000 | 18.1203 | 59.1586 | 18.8446 | 0 | 7.2692 | FALSE | FALSE
2025-01-03 09:00 | 19.7 | 42.5 | 101880 | 100 | 3000 | 18.4009 | 58.7573 | 19.8441 | 0 | 7.2692 | FALSE | FALSE
2025-01-03 10:00 | 20.05 | 42.5 | 101895 | 100 | 3000 | 18.5511 | 58.6868 | 20.3726 | 0 | 7.2692 | FALSE | FALSE
2025-01-03 11:00 | 20.65 | 40.5 | 101835 | 100 | 3000 | 18.8081 | 57.5448 | 21.2613 | 0 | 7.2692 | FALSE | FALSE
2025-01-03 12:00 | 21 | 40 | 101760 | 100 | 3000 | 18.9572 | 57.2254 | 21.7642 | 0 | 7.2692 | FALSE | FALSE
2025-01-03 13:00 | 21.15 | 40 | 101690 | 100 | 3000 | 19.0208 | 57.2066 | 21.9695 | 0 | 7.2692 | FALSE | FALSE
2025-01-03 14:00 | 21.05 | 39.5 | 101650 | 100 | 3000 | 18.9787 | 56.9639 | 21.8165 | 0 | 7.2692 | FALSE | FALSE
2025-01-03 15:00 | 20.7 | 40 | 101650 | 100 | 3000 | 18.8297 | 57.2943 | 21.299 | 0 | 7.2692 | FALSE | FALSE
2025-01-03 16:00 | 20.5 | 40.5 | 101680 | 100 | 3000 | 18.7442 | 57.5913 | 21.0072 | 0 | 7.2692 | FALSE | FALSE
2025-01-03 17:00 | 19.9 | 42 | 101715 | 100 | 3000 | 18.4869 | 58.4809 | 20.1142 | 0 | 7.2692 | FALSE | FALSE
2025-01-03 18:00 | 18.95 | 45 | 101760 | 100 | 3000 | 18.0767 | 60.1783 | 18.6779 | 0 | 7.2692 | FALSE | FALSE
2025-01-03 19:00 | 18.1 | 48 | 101810 | 100 | 3000 | 17.7067 | 61.8122 | 17.3747 | 0 | 7.2692 | FALSE | FALSE
2025-01-03 20:00 | 17.2 | 51.5 | 101850 | 100 | 3000 | 17.312 | 63.6529 | 15.9723 | 0 | 7.2692 | FALSE | FALSE
2025-01-03 21:00 | 16.25 | 54 | 101875 | 100 | 3000 | 16.8921 | 65.0044 | 14.4682 | 0 | 7.2692 | FALSE | FALSE
2025-01-03 22:00 | 15.2 | 55.5 | 101875 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-03 23:00 | 14.15 | 55 | 101850 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-04 | 13.2 | 53 | 101825 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-04 01:00 | 12.55 | 51.5 | 101815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-04 02:00 | 11.95 | 52 | 101795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-04 03:00 | 11.4 | 53.5 | 101780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-04 04:00 | 11.65 | 49.5 | 101795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-04 05:00 | 12.25 | 44 | 101830 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-04 06:00 | 12 | 44 | 101890 | 100 | 3000 | 14.9594 | 62.5588 | 7.4057 | 0 | 7.2692 | FALSE | FALSE
2025-01-04 07:00 | 12.15 | 43 | 101955 | 100 | 3000 | 15.0285 | 62.059 | 7.668 | 0 | 7.2692 | FALSE | FALSE
2025-01-04 08:00 | 14.2 | 37 | 101995 | 100 | 3000 | 15.967 | 58.3452 | 11.1405 | 0 | 7.2692 | FALSE | FALSE
2025-01-04 09:00 | 17.15 | 30.5 | 102030 | 100 | 3000 | 17.2895 | 53.8128 | 15.9489 | 0 | 7.2692 | FALSE | FALSE
2025-01-04 10:00 | 19.6 | 28.5 | 102005 | 100 | 3000 | 18.3617 | 51.6736 | 19.7603 | 0 | 7.2692 | FALSE | FALSE
2025-01-04 11:00 | 21.05 | 30 | 101905 | 100 | 3000 | 18.9835 | 51.899 | 21.9123 | 0 | 7.2692 | FALSE | FALSE
2025-01-04 12:00 | 21.9 | 30.5 | 101800 | 100 | 3000 | 19.3435 | 51.9063 | 23.135 | 0 | 7.2692 | FALSE | FALSE
2025-01-04 13:00 | 22.55 | 30 | 101710 | 100 | 3000 | 19.6173 | 51.4532 | 24.0574 | 0 | 7.2692 | FALSE | FALSE
2025-01-04 14:00 | 22.65 | 31 | 101650 | 100 | 3000 | 19.6584 | 51.9899 | 24.1809 | 0 | 7.2692 | FALSE | FALSE
2025-01-04 15:00 | 22.2 | 33 | 101625 | 100 | 3000 | 19.4682 | 53.2126 | 23.5166 | 0 | 7.2692 | FALSE | FALSE
2025-01-04 16:00 | 21.55 | 34.5 | 101645 | 100 | 3000 | 19.1932 | 54.1857 | 22.5703 | 0 | 7.2692 | FALSE | FALSE
2025-01-04 17:00 | 20.6 | 38 | 101690 | 100 | 3000 | 18.7879 | 56.2652 | 21.1673 | 0 | 7.2692 | FALSE | FALSE
2025-01-04 18:00 | 19.55 | 41 | 101740 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-04 19:00 | 18.55 | 43 | 101795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-04 20:00 | 17.7 | 46.5 | 101825 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-04 21:00 | 17.25 | 49.5 | 101825 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-04 22:00 | 16.85 | 52.5 | 101805 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-04 23:00 | 16.45 | 55 | 101770 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 | 16.25 | 57.5 | 101730 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 01:00 | 16.2 | 59.5 | 101705 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 02:00 | 16.35 | 60.5 | 101700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 03:00 | 16.05 | 63 | 101690 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 04:00 | 15.7 | 64.5 | 101695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 05:00 | 15.8 | 64.5 | 101730 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 06:00 | 15.55 | 66.5 | 101760 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 07:00 | 15.5 | 68 | 101800 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 08:00 | 17.2 | 62 | 101865 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 09:00 | 19.7 | 52 | 101915 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 10:00 | 21.4 | 44.5 | 101910 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 11:00 | 22.35 | 40 | 101840 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 12:00 | 22.65 | 39.5 | 101750 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 13:00 | 22.65 | 40 | 101680 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 14:00 | 22.5 | 40.5 | 101645 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 15:00 | 22.25 | 42 | 101635 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 16:00 | 21.6 | 45 | 101650 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 17:00 | 20.5 | 49.5 | 101685 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 18:00 | 19.4 | 54 | 101730 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 19:00 | 18.6 | 58 | 101785 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 20:00 | 18.05 | 62 | 101815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 21:00 | 17.65 | 65.5 | 101820 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 22:00 | 17.2 | 68.5 | 101815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-05 23:00 | 16.3 | 72 | 101780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-06 | 15 | 76 | 101735 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-06 01:00 | 13.75 | 79.5 | 101710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-06 02:00 | 12.95 | 81.5 | 101700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-06 03:00 | 12.4 | 82.5 | 101690 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-06 04:00 | 11.8 | 82 | 101685 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-06 05:00 | 11.2 | 82 | 101710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-06 06:00 | 10.75 | 83 | 101745 | 100 | 3000 | 14.3948 | 78.184 | 5.2768 | 0 | 7.2692 | FALSE | FALSE
2025-01-06 07:00 | 11.25 | 79 | 101795 | 100 | 3000 | 14.6262 | 76.5417 | 6.1447 | 0 | 7.2692 | FALSE | FALSE
2025-01-06 08:00 | 13.65 | 67.5 | 101865 | 100 | 3000 | 15.726 | 71.4194 | 10.2216 | 0 | 7.2692 | FALSE | FALSE
2025-01-06 09:00 | 17.1 | 55 | 101910 | 100 | 3000 | 17.2681 | 65.2971 | 15.8198 | 0 | 7.2692 | FALSE | FALSE
2025-01-06 10:00 | 20.1 | 45 | 101895 | 100 | 3000 | 18.5716 | 59.9612 | 20.4386 | 0 | 7.2692 | FALSE | FALSE
2025-01-06 11:00 | 22.2 | 36 | 101815 | 100 | 3000 | 19.4659 | 54.8411 | 23.5433 | 0 | 7.2692 | FALSE | FALSE
2025-01-06 12:00 | 23.6 | 31 | 101700 | 100 | 3000 | 20.0539 | 51.7601 | 25.542 | 0 | 7.2692 | FALSE | FALSE
2025-01-06 13:00 | 24.7 | 29.5 | 101590 | 100 | 3000 | 20.5087 | 50.6679 | 27.0579 | 0 | 7.2692 | FALSE | FALSE
2025-01-06 14:00 | 25.55 | 28 | 101505 | 100 | 3000 | 20.8575 | 49.6079 | 28.211 | 0 | 7.2692 | FALSE | FALSE
2025-01-06 15:00 | 25.65 | 27.5 | 101455 | 100 | 3000 | 20.8989 | 49.2877 | 28.3377 | 0 | 7.2692 | FALSE | FALSE
2025-01-06 16:00 | 24.35 | 34.5 | 101430 | 100 | 3000 | 20.3592 | 53.6959 | 26.4918 | 0 | 7.2692 | FALSE | FALSE
2025-01-06 17:00 | 22.45 | 45 | 101430 | 100 | 3000 | 19.5638 | 59.815 | 24.5089 | 0 | 7.2692 | FALSE | FALSE
2025-01-06 18:00 | 21.05 | 51 | 101465 | 100 | 3000 | 18.9728 | 63.0666 | 23.7034 | 0 | 7.2692 | FALSE | FALSE
2025-01-06 19:00 | 20.1 | 49 | 101525 | 100 | 3000 | 18.5702 | 62.0559 | 20.351 | 0 | 7.2692 | FALSE | FALSE
2025-01-06 20:00 | 19.3 | 47 | 101580 | 100 | 3000 | 18.2275 | 61.1313 | 19.1702 | 0 | 7.2692 | FALSE | FALSE
2025-01-06 21:00 | 18.45 | 53.5 | 101605 | 100 | 3000 | 17.8585 | 64.4444 | 17.8665 | 0 | 7.2692 | FALSE | FALSE
2025-01-06 22:00 | 17.7 | 59 | 101605 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-06 23:00 | 17.05 | 60 | 101585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-07 | 16.2 | 61 | 101570 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-07 01:00 | 15.2 | 63 | 101560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-07 02:00 | 14.35 | 64.5 | 101570 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-07 03:00 | 13.75 | 65 | 101595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-07 04:00 | 13.35 | 65 | 101640 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-07 05:00 | 12.95 | 63.5 | 101705 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-07 06:00 | 12.55 | 61 | 101765 | 100 | 3000 | 15.2202 | 69.0891 | 8.3551 | 0 | 7.2692 | FALSE | FALSE
2025-01-07 07:00 | 13 | 58.5 | 101820 | 100 | 3000 | 15.426 | 67.9039 | 9.1206 | 0 | 7.2692 | FALSE | FALSE
2025-01-07 08:00 | 15.15 | 51.5 | 101875 | 100 | 3000 | 16.4001 | 64.1931 | 12.6936 | 0 | 7.2692 | FALSE | FALSE
2025-01-07 09:00 | 18.45 | 41.5 | 101905 | 100 | 3000 | 17.86 | 58.5646 | 17.9452 | 0 | 7.2692 | FALSE | FALSE
2025-01-07 10:00 | 21.75 | 33 | 101870 | 100 | 3000 | 19.2786 | 53.2997 | 22.9192 | 0 | 7.2692 | FALSE | FALSE
2025-01-07 11:00 | 24.1 | 27 | 101780 | 100 | 3000 | 20.265 | 49.3139 | 26.294 | 0 | 7.2692 | FALSE | FALSE
2025-01-07 12:00 | 25.35 | 23.5 | 101660 | 100 | 3000 | 20.7827 | 46.8981 | 28.0242 | 0 | 7.2692 | FALSE | FALSE
2025-01-07 13:00 | 26 | 22 | 101545 | 100 | 3000 | 21.0496 | 45.8037 | 28.8928 | 0 | 7.2692 | FALSE | FALSE
2025-01-07 14:00 | 25.85 | 25.5 | 101470 | 100 | 3000 | 20.9831 | 48.0144 | 28.6326 | 0 | 7.2692 | FALSE | FALSE
2025-01-07 15:00 | 24.65 | 33.5 | 101440 | 100 | 3000 | 20.4832 | 53.0674 | 26.9154 | 0 | 7.2692 | FALSE | FALSE
2025-01-07 16:00 | 23.2 | 40.5 | 101455 | 100 | 3000 | 19.8791 | 57.2613 | 24.8537 | 0 | 7.2692 | FALSE | FALSE
2025-01-07 17:00 | 22 | 48.5 | 101485 | 100 | 3000 | 19.3734 | 61.7314 | 25.3569 | 0 | 7.2692 | FALSE | FALSE
2025-01-07 18:00 | 20.9 | 57 | 101505 | 100 | 3000 | 18.9064 | 66.2139 | 26.9584 | 0 | 7.2692 | FALSE | FALSE
2025-01-07 19:00 | 19.8 | 64 | 101540 | 100 | 3000 | 18.4371 | 69.6878 | 27.1128 | 0 | 7.2692 | FALSE | FALSE
2025-01-07 20:00 | 18.95 | 68 | 101570 | 100 | 3000 | 18.0723 | 71.5561 | 26.1519 | 0 | 7.2692 | FALSE | FALSE
2025-01-07 21:00 | 18.4 | 68 | 101585 | 100 | 3000 | 17.8351 | 71.4804 | 24.0253 | 0 | 7.2692 | FALSE | FALSE
2025-01-07 22:00 | 17.55 | 67 | 101565 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-07 23:00 | 16.75 | 66.5 | 101520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-08 | 16.15 | 69 | 101485 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-08 01:00 | 15.25 | 72.5 | 101465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-08 02:00 | 14.25 | 75 | 101445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-08 03:00 | 13.55 | 75 | 101420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-08 04:00 | 12.8 | 72.5 | 101420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-08 05:00 | 11.9 | 71.5 | 101445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-08 06:00 | 11.25 | 71 | 101495 | 100 | 3000 | 14.6225 | 73.5112 | 6.1157 | 0 | 7.2692 | FALSE | FALSE
2025-01-08 07:00 | 11.55 | 66 | 101575 | 100 | 3000 | 14.7598 | 71.461 | 6.633 | 0 | 7.2692 | FALSE | FALSE
2025-01-08 08:00 | 13.6 | 57 | 101655 | 100 | 3000 | 15.6998 | 67.093 | 10.1119 | 0 | 7.2692 | FALSE | FALSE
2025-01-08 09:00 | 16.3 | 48.5 | 101720 | 100 | 3000 | 16.9136 | 62.5133 | 14.5304 | 0 | 7.2692 | FALSE | FALSE
2025-01-08 10:00 | 18.7 | 42.5 | 101695 | 100 | 3000 | 17.9687 | 59.0109 | 18.2903 | 0 | 7.2692 | FALSE | FALSE
2025-01-08 11:00 | 20.4 | 39.5 | 101575 | 100 | 3000 | 18.702 | 57.1044 | 20.8412 | 0 | 7.2692 | FALSE | FALSE
2025-01-08 12:00 | 21.65 | 37 | 101460 | 100 | 3000 | 19.234 | 55.5318 | 22.6628 | 0 | 7.2692 | FALSE | FALSE
2025-01-08 13:00 | 23 | 33.5 | 101360 | 100 | 3000 | 19.8025 | 53.3429 | 24.595 | 0 | 7.2692 | FALSE | FALSE
2025-01-08 14:00 | 23.85 | 33 | 101295 | 100 | 3000 | 20.1553 | 52.9075 | 25.7763 | 0 | 7.2692 | FALSE | FALSE
2025-01-08 15:00 | 24 | 36.5 | 101285 | 100 | 3000 | 20.2132 | 54.9183 | 25.9554 | 0 | 7.2692 | FALSE | FALSE
2025-01-08 16:00 | 23.35 | 42.5 | 101290 | 100 | 3000 | 19.9392 | 58.407 | 25.7166 | 0 | 7.2692 | FALSE | FALSE
2025-01-08 17:00 | 21.75 | 53 | 101305 | 100 | 3000 | 19.2658 | 64.1793 | 27.4453 | 0 | 7.2692 | FALSE | FALSE
2025-01-08 18:00 | 20.65 | 66 | 101340 | 100 | 3000 | 18.7967 | 70.893 | 31.597 | 0 | 7.2692 | FALSE | FALSE
2025-01-08 19:00 | 20.05 | 76.5 | 101375 | 100 | 3000 | 18.5391 | 76.112 | 35.5148 | 0 | 7.2692 | FALSE | FALSE
2025-01-08 20:00 | 19.35 | 81 | 101400 | 100 | 3000 | 18.2406 | 78.1133 | 35.1668 | 0 | 7.2692 | FALSE | FALSE
2025-01-08 21:00 | 18.95 | 82.5 | 101400 | 100 | 3000 | 18.0695 | 78.7026 | 34.298 | 0 | 7.2692 | FALSE | FALSE
2025-01-08 22:00 | 18.4 | 85.5 | 101385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-08 23:00 | 17.95 | 87 | 101355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-09 | 17.55 | 87.5 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-09 01:00 | 16.95 | 88.5 | 101280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-09 02:00 | 16.3 | 89.5 | 101270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-09 03:00 | 15.85 | 90 | 101260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-09 04:00 | 15.75 | 91.5 | 101250 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-09 05:00 | 15.7 | 92.5 | 101275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-09 06:00 | 15.6 | 90.5 | 101325 | 100 | 3000 | 16.6087 | 81.3762 | 24.0564 | 0 | 7.2692 | FALSE | FALSE
2025-01-09 07:00 | 16.05 | 87 | 101365 | 100 | 3000 | 16.8076 | 79.9269 | 24.2999 | 0 | 7.2692 | FALSE | FALSE
2025-01-09 08:00 | 17.75 | 79.5 | 101410 | 100 | 3000 | 17.5524 | 76.8832 | 27.6101 | 0 | 7.2692 | FALSE | FALSE
2025-01-09 09:00 | 20.05 | 66.5 | 101455 | 100 | 3000 | 18.5427 | 71.0102 | 29.5587 | 0 | 7.2692 | FALSE | FALSE
2025-01-09 10:00 | 21.65 | 55 | 101440 | 100 | 3000 | 19.2227 | 65.2328 | 28.4063 | 0 | 7.2692 | FALSE | FALSE
2025-01-09 11:00 | 22.4 | 50.5 | 101350 | 100 | 3000 | 19.5387 | 62.8575 | 28.0807 | 0 | 7.2692 | FALSE | FALSE
2025-01-09 12:00 | 22.65 | 49.5 | 101235 | 100 | 3000 | 19.6433 | 62.333 | 28.2612 | 0 | 7.2692 | FALSE | FALSE
2025-01-09 13:00 | 22.7 | 49 | 101150 | 100 | 3000 | 19.6645 | 62.0673 | 28.0821 | 0 | 7.2692 | FALSE | FALSE
2025-01-09 14:00 | 22.55 | 50 | 101105 | 100 | 3000 | 19.6014 | 62.6179 | 28.2425 | 0 | 7.2692 | FALSE | FALSE
2025-01-09 15:00 | 22.2 | 51.5 | 101110 | 100 | 3000 | 19.4548 | 63.4188 | 28.0296 | 0 | 7.2692 | FALSE | FALSE
2025-01-09 16:00 | 21.8 | 53.5 | 101145 | 100 | 3000 | 19.2865 | 64.471 | 27.9393 | 0 | 7.2692 | FALSE | FALSE
2025-01-09 17:00 | 21.1 | 58 | 101180 | 100 | 3000 | 18.9902 | 66.7985 | 28.3004 | 0 | 7.2692 | FALSE | FALSE
2025-01-09 18:00 | 20.05 | 65 | 101235 | 100 | 3000 | 18.5432 | 70.2706 | 28.6486 | 0 | 7.2692 | FALSE | FALSE
2025-01-09 19:00 | 19.1 | 71 | 101300 | 100 | 3000 | 18.1361 | 73.095 | 28.428 | 0 | 7.2692 | FALSE | FALSE
2025-01-09 20:00 | 18.35 | 75 | 101350 | 100 | 3000 | 17.8127 | 74.8818 | 27.6476 | 0 | 7.2692 | FALSE | FALSE
2025-01-09 21:00 | 17.6 | 78.5 | 101365 | 100 | 3000 | 17.4872 | 76.382 | 26.4672 | 0 | 7.2692 | FALSE | FALSE
2025-01-09 22:00 | 16.75 | 82 | 101355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-09 23:00 | 15.85 | 86 | 101345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-10 | 15.1 | 89 | 101325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-10 01:00 | 14.5 | 91 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-10 02:00 | 14 | 92 | 101320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-10 03:00 | 13.8 | 92 | 101345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-10 04:00 | 13.75 | 92.5 | 101375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-10 05:00 | 13.45 | 94 | 101405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-10 06:00 | 12.9 | 95.5 | 101455 | 100 | 3000 | 15.3937 | 82.9815 | 14.8374 | 0 | 7.2692 | FALSE | FALSE
2025-01-10 07:00 | 12.95 | 94.5 | 101525 | 100 | 3000 | 15.4162 | 82.5731 | 14.6379 | 0 | 7.2692 | FALSE | FALSE
2025-01-10 08:00 | 15.15 | 85.5 | 101600 | 100 | 3000 | 16.4073 | 79.0638 | 19.8543 | 0 | 7.2692 | FALSE | FALSE
2025-01-10 09:00 | 18.65 | 71 | 101660 | 100 | 3000 | 17.9426 | 72.9652 | 26.6587 | 0 | 7.2692 | FALSE | FALSE
2025-01-10 10:00 | 21.35 | 59 | 101665 | 100 | 3000 | 19.0946 | 67.3086 | 29.9056 | 0 | 7.2692 | FALSE | FALSE
2025-01-10 11:00 | 23.15 | 48.5 | 101600 | 100 | 3000 | 19.8509 | 61.768 | 29.3441 | 0 | 7.2692 | FALSE | FALSE
2025-01-10 12:00 | 24.4 | 39 | 101495 | 100 | 3000 | 20.3741 | 56.3306 | 26.5554 | 0 | 7.2692 | FALSE | FALSE
2025-01-10 13:00 | 25.15 | 33.5 | 101410 | 100 | 3000 | 20.687 | 53.0131 | 27.5898 | 0 | 7.2692 | FALSE | FALSE
2025-01-10 14:00 | 25.2 | 34.5 | 101375 | 100 | 3000 | 20.7058 | 53.615 | 27.6389 | 0 | 7.2692 | FALSE | FALSE
2025-01-10 15:00 | 24.45 | 41.5 | 101375 | 100 | 3000 | 20.3915 | 57.8131 | 28.5963 | 0 | 7.2692 | FALSE | FALSE
2025-01-10 16:00 | 23.1 | 51.5 | 101385 | 100 | 3000 | 19.8275 | 63.4771 | 31.2607 | 0 | 7.2692 | FALSE | FALSE
2025-01-10 17:00 | 21.55 | 63 | 101410 | 100 | 3000 | 19.1759 | 69.5096 | 33.224 | 0 | 7.2692 | FALSE | FALSE
2025-01-10 18:00 | 20.4 | 72 | 101470 | 100 | 3000 | 18.6887 | 73.9148 | 34.2718 | 0 | 7.2692 | FALSE | FALSE
2025-01-10 19:00 | 19.5 | 76.5 | 101545 | 100 | 3000 | 18.3057 | 75.9058 | 33.2205 | 0 | 7.2692 | FALSE | FALSE
2025-01-10 20:00 | 18.75 | 77 | 101600 | 100 | 3000 | 17.9847 | 75.9218 | 30.3933 | 0 | 7.2692 | FALSE | FALSE
2025-01-10 21:00 | 17.95 | 77 | 101635 | 100 | 3000 | 17.6393 | 75.7169 | 27.1109 | 0 | 7.2692 | FALSE | FALSE
2025-01-10 22:00 | 16.9 | 79 | 101650 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-10 23:00 | 15.85 | 81 | 101640 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-11 | 14.9 | 81 | 101615 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-11 01:00 | 14.1 | 78.5 | 101585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-11 02:00 | 13.4 | 76.5 | 101570 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-11 03:00 | 12.7 | 77 | 101575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-11 04:00 | 12.2 | 78.5 | 101580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-11 05:00 | 11.9 | 78 | 101600 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-11 06:00 | 11.6 | 75 | 101640 | 100 | 3000 | 14.7869 | 74.9341 | 6.7346 | 0 | 7.2692 | FALSE | FALSE
2025-01-11 07:00 | 12.15 | 67.5 | 101690 | 100 | 3000 | 15.0384 | 71.8288 | 7.6735 | 0 | 7.2692 | FALSE | FALSE
2025-01-11 08:00 | 14.7 | 53.5 | 101755 | 100 | 3000 | 16.1978 | 65.2251 | 11.9428 | 0 | 7.2692 | FALSE | FALSE
2025-01-11 09:00 | 18.45 | 39.5 | 101805 | 100 | 3000 | 17.8603 | 57.6009 | 17.9321 | 0 | 7.2692 | FALSE | FALSE
2025-01-11 10:00 | 21.8 | 30.5 | 101800 | 100 | 3000 | 19.3013 | 51.9363 | 22.9893 | 0 | 7.2692 | FALSE | FALSE
2025-01-11 11:00 | 24.3 | 24.5 | 101720 | 100 | 3000 | 20.3505 | 47.7977 | 26.5783 | 0 | 7.2692 | FALSE | FALSE
2025-01-11 12:00 | 25.8 | 21.5 | 101600 | 100 | 3000 | 20.9692 | 45.5482 | 28.6419 | 0 | 7.2692 | FALSE | FALSE
2025-01-11 13:00 | 26.6 | 20.5 | 101485 | 100 | 3000 | 21.295 | 44.6962 | 29.7005 | 0 | 7.2692 | FALSE | FALSE
2025-01-11 14:00 | 26.85 | 20.5 | 101400 | 100 | 3000 | 21.3958 | 44.6319 | 30.01 | 0 | 7.2692 | FALSE | FALSE
2025-01-11 15:00 | 26 | 28.5 | 101380 | 100 | 3000 | 21.0389 | 49.8483 | 28.7783 | 0 | 7.2692 | FALSE | FALSE
2025-01-11 16:00 | 24.2 | 43.5 | 101390 | 100 | 3000 | 20.287 | 58.9779 | 29.2743 | 0 | 7.2692 | FALSE | FALSE
2025-01-11 17:00 | 22.5 | 55 | 101415 | 100 | 3000 | 19.5766 | 65.3434 | 31.5088 | 0 | 7.2692 | FALSE | FALSE
2025-01-11 18:00 | 21.5 | 61.5 | 101465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-11 19:00 | 20.85 | 65 | 101520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-11 20:00 | 19.9 | 68.5 | 101565 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-11 21:00 | 18.55 | 70 | 101580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-11 22:00 | 17.15 | 64.5 | 101560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-11 23:00 | 15.95 | 58.5 | 101530 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 | 15.1 | 57 | 101510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 01:00 | 14.75 | 56 | 101500 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 02:00 | 14.65 | 53.5 | 101480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 03:00 | 14.4 | 53.5 | 101455 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 04:00 | 13.9 | 57.5 | 101455 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 05:00 | 13.3 | 63 | 101485 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 06:00 | 12.4 | 68.5 | 101540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 07:00 | 11.9 | 67 | 101610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 08:00 | 13.35 | 54.5 | 101680 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 09:00 | 16.35 | 40.5 | 101725 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 10:00 | 19.65 | 31.5 | 101710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 11:00 | 22.45 | 28 | 101625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 12:00 | 24.25 | 28 | 101525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 13:00 | 25.2 | 27 | 101450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 14:00 | 25.4 | 26.5 | 101395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 15:00 | 24.75 | 29.5 | 101380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 16:00 | 23.2 | 40 | 101405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 17:00 | 21.25 | 56.5 | 101435 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 18:00 | 19.85 | 68 | 101475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 19:00 | 19.15 | 71 | 101515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 20:00 | 18.8 | 70.5 | 101550 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 21:00 | 18.75 | 70 | 101585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 22:00 | 18.5 | 70.5 | 101595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-12 23:00 | 17.9 | 71.5 | 101580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-13 | 17.2 | 73 | 101555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-13 01:00 | 16.3 | 75.5 | 101530 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-13 02:00 | 15.85 | 77.5 | 101510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-13 03:00 | 16 | 78 | 101495 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-13 04:00 | 16.35 | 77.5 | 101500 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-13 05:00 | 16 | 82 | 101510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-13 06:00 | 15.75 | 86 | 101525 | 100 | 3000 | 16.6746 | 79.3966 | 22.5679 | 0 | 7.2692 | FALSE | FALSE
2025-01-13 07:00 | 16.4 | 83.5 | 101570 | 100 | 3000 | 16.9617 | 78.4044 | 24.0624 | 0 | 7.2692 | FALSE | FALSE
2025-01-13 08:00 | 17.7 | 77.5 | 101630 | 100 | 3000 | 17.5307 | 75.8999 | 26.3569 | 0 | 7.2692 | FALSE | FALSE
2025-01-13 09:00 | 20.15 | 67 | 101685 | 100 | 3000 | 18.5849 | 71.2595 | 30.2639 | 0 | 7.2692 | FALSE | FALSE
2025-01-13 10:00 | 22.1 | 59 | 101700 | 100 | 3000 | 19.4076 | 67.4363 | 32.7359 | 0 | 7.2692 | FALSE | FALSE
2025-01-13 11:00 | 22.95 | 54.5 | 101650 | 100 | 3000 | 19.7629 | 65.1115 | 32.8432 | 0 | 7.2692 | FALSE | FALSE
2025-01-13 12:00 | 23.15 | 53.5 | 101570 | 100 | 3000 | 19.8462 | 64.5911 | 32.8689 | 0 | 7.2692 | FALSE | FALSE
2025-01-13 13:00 | 23.1 | 54.5 | 101495 | 100 | 3000 | 19.8247 | 65.1538 | 33.3806 | 0 | 7.2692 | FALSE | FALSE
2025-01-13 14:00 | 23.1 | 54.5 | 101455 | 100 | 3000 | 19.8247 | 65.1581 | 33.3765 | 0 | 7.2692 | FALSE | FALSE
2025-01-13 15:00 | 22.7 | 57 | 101460 | 100 | 3000 | 19.6577 | 66.4806 | 33.6245 | 0 | 7.2692 | FALSE | FALSE
2025-01-13 16:00 | 22.25 | 60.5 | 101480 | 100 | 3000 | 19.4688 | 68.3114 | 34.2914 | 0 | 7.2692 | FALSE | FALSE
2025-01-13 17:00 | 21.6 | 63 | 101510 | 100 | 3000 | 19.1968 | 69.5101 | 33.4266 | 0 | 7.2692 | FALSE | FALSE
2025-01-13 18:00 | 20.9 | 65 | 101560 | 100 | 3000 | 18.9025 | 70.4028 | 31.9715 | 0 | 7.2692 | FALSE | FALSE
2025-01-13 19:00 | 20.55 | 67 | 101610 | 100 | 3000 | 18.7541 | 71.3579 | 31.8359 | 0 | 7.2692 | FALSE | FALSE
2025-01-13 20:00 | 20.15 | 69.5 | 101635 | 100 | 3000 | 18.584 | 72.5434 | 31.7613 | 0 | 7.2692 | FALSE | FALSE
2025-01-13 21:00 | 19.6 | 72 | 101645 | 100 | 3000 | 18.3495 | 73.6686 | 31.0255 | 0 | 7.2692 | FALSE | FALSE
2025-01-13 22:00 | 19.05 | 73.5 | 101635 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-13 23:00 | 18.7 | 74.5 | 101605 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-14 | 18.35 | 76 | 101575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-14 01:00 | 17.85 | 78 | 101560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-14 02:00 | 17.45 | 79.5 | 101545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-14 03:00 | 17.1 | 80.5 | 101530 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-14 04:00 | 17.2 | 78 | 101545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-14 05:00 | 17.25 | 76 | 101580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-14 06:00 | 16.55 | 79.5 | 101620 | 100 | 3000 | 17.0274 | 76.611 | 22.7066 | 0 | 7.2692 | FALSE | FALSE
2025-01-14 07:00 | 16.4 | 79 | 101670 | 100 | 3000 | 16.9612 | 76.3545 | 21.8546 | 0 | 7.2692 | FALSE | FALSE
2025-01-14 08:00 | 17.9 | 69 | 101725 | 100 | 3000 | 17.6181 | 71.8893 | 22.6452 | 0 | 7.2692 | FALSE | FALSE
2025-01-14 09:00 | 20.2 | 58 | 101770 | 100 | 3000 | 18.6095 | 66.6453 | 25.0328 | 0 | 7.2692 | FALSE | FALSE
2025-01-14 10:00 | 22 | 51 | 101760 | 100 | 3000 | 19.3716 | 63.0619 | 27.0476 | 0 | 7.2692 | FALSE | FALSE
2025-01-14 11:00 | 23.1 | 45.5 | 101675 | 100 | 3000 | 19.833 | 60.0655 | 27.0606 | 0 | 7.2692 | FALSE | FALSE
2025-01-14 12:00 | 23.65 | 42.5 | 101570 | 100 | 3000 | 20.0627 | 58.3726 | 26.7322 | 0 | 7.2692 | FALSE | FALSE
2025-01-14 13:00 | 23.8 | 42 | 101510 | 100 | 3000 | 20.1249 | 58.0899 | 26.8528 | 0 | 7.2692 | FALSE | FALSE
2025-01-14 14:00 | 23.45 | 44 | 101495 | 100 | 3000 | 19.9789 | 59.2387 | 27.1467 | 0 | 7.2692 | FALSE | FALSE
2025-01-14 15:00 | 22.65 | 49 | 101500 | 100 | 3000 | 19.6437 | 62.0267 | 27.9425 | 0 | 7.2692 | FALSE | FALSE
2025-01-14 16:00 | 22.1 | 50.5 | 101510 | 100 | 3000 | 19.4137 | 62.8222 | 27.0426 | 0 | 7.2692 | FALSE | FALSE
2025-01-14 17:00 | 21.55 | 48.5 | 101520 | 100 | 3000 | 19.1848 | 61.7273 | 23.8203 | 0 | 7.2692 | FALSE | FALSE
2025-01-14 18:00 | 20.6 | 50 | 101560 | 100 | 3000 | 18.7827 | 62.5391 | 21.5322 | 0 | 7.2692 | FALSE | FALSE
2025-01-14 19:00 | 19.65 | 54 | 101625 | 100 | 3000 | 18.3761 | 64.613 | 20.6663 | 0 | 7.2692 | FALSE | FALSE
2025-01-14 20:00 | 18.8 | 59.5 | 101680 | 100 | 3000 | 18.0092 | 67.3515 | 20.8043 | 0 | 7.2692 | FALSE | FALSE
2025-01-14 21:00 | 18.15 | 65 | 101710 | 100 | 3000 | 17.727 | 69.9974 | 21.4431 | 0 | 7.2692 | FALSE | FALSE
2025-01-14 22:00 | 17.65 | 69 | 101730 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-14 23:00 | 17.05 | 73 | 101725 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-15 | 16.3 | 76 | 101705 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-15 01:00 | 15.5 | 77.5 | 101705 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-15 02:00 | 14.65 | 79.5 | 101700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-15 03:00 | 13.65 | 84 | 101695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-15 04:00 | 13.25 | 84 | 101715 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-15 05:00 | 13.3 | 81.5 | 101755 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-15 06:00 | 13 | 83 | 101815 | 100 | 3000 | 15.4349 | 77.876 | 10.1502 | 0 | 7.2692 | FALSE | FALSE
2025-01-15 07:00 | 13.4 | 81 | 101890 | 100 | 3000 | 15.6167 | 77.0308 | 10.8825 | 0 | 7.2692 | FALSE | FALSE
2025-01-15 08:00 | 15.55 | 71 | 101970 | 100 | 3000 | 16.583 | 72.6872 | 14.6916 | 0 | 7.2692 | FALSE | FALSE
2025-01-15 09:00 | 18.7 | 58 | 102035 | 100 | 3000 | 17.9662 | 66.5742 | 19.6168 | 0 | 7.2692 | FALSE | FALSE
2025-01-15 10:00 | 21.3 | 47.5 | 102045 | 100 | 3000 | 19.08 | 61.1408 | 22.3663 | 0 | 7.2692 | FALSE | FALSE
2025-01-15 11:00 | 23 | 41.5 | 101980 | 100 | 3000 | 19.7952 | 57.7822 | 24.6918 | 0 | 7.2692 | FALSE | FALSE
2025-01-15 12:00 | 24.15 | 39 | 101865 | 100 | 3000 | 20.2717 | 56.3027 | 26.2909 | 0 | 7.2692 | FALSE | FALSE
2025-01-15 13:00 | 24.85 | 37.5 | 101755 | 100 | 3000 | 20.5594 | 55.3981 | 27.2371 | 0 | 7.2692 | FALSE | FALSE
2025-01-15 14:00 | 24.95 | 39.5 | 101680 | 100 | 3000 | 20.5973 | 56.598 | 28.7275 | 0 | 7.2692 | FALSE | FALSE
2025-01-15 15:00 | 24.2 | 47 | 101640 | 100 | 3000 | 20.2828 | 60.9941 | 31.916 | 0 | 7.2692 | FALSE | FALSE
2025-01-15 16:00 | 23 | 55.5 | 101645 | 100 | 3000 | 19.7826 | 65.6812 | 33.7254 | 0 | 7.2692 | FALSE | FALSE
2025-01-15 17:00 | 22 | 62 | 101685 | 100 | 3000 | 19.364 | 69.047 | 34.3419 | 0 | 7.2692 | FALSE | FALSE
2025-01-15 18:00 | 21.3 | 67 | 101735 | 100 | 3000 | 19.0691 | 71.539 | 34.829 | 0 | 7.2692 | FALSE | FALSE
2025-01-15 19:00 | 20.65 | 69.5 | 101795 | 100 | 3000 | 18.7951 | 72.6592 | 33.7832 | 0 | 7.2692 | FALSE | FALSE
2025-01-15 20:00 | 19.8 | 70.5 | 101835 | 100 | 3000 | 18.4351 | 72.9412 | 30.9635 | 0 | 7.2692 | FALSE | FALSE
2025-01-15 21:00 | 19.1 | 71 | 101865 | 100 | 3000 | 18.1361 | 73.0283 | 28.4537 | 0 | 7.2692 | FALSE | FALSE
2025-01-15 22:00 | 18.6 | 71.5 | 101900 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-15 23:00 | 17.8 | 73 | 101895 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-16 | 16.85 | 75 | 101840 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-16 01:00 | 16.1 | 77 | 101800 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-16 02:00 | 15.75 | 77.5 | 101785 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-16 03:00 | 15.6 | 77 | 101750 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-16 04:00 | 15.5 | 76 | 101730 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-16 05:00 | 15.1 | 76 | 101735 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-16 06:00 | 14.3 | 78 | 101760 | 100 | 3000 | 16.0238 | 75.7692 | 13.097 | 0 | 7.2692 | FALSE | FALSE
2025-01-16 07:00 | 14.3 | 77.5 | 101805 | 100 | 3000 | 16.0236 | 75.5513 | 12.8763 | 0 | 7.2692 | FALSE | FALSE
2025-01-16 08:00 | 16.35 | 69.5 | 101855 | 100 | 3000 | 16.9381 | 72.0229 | 16.9909 | 0 | 7.2692 | FALSE | FALSE
2025-01-16 09:00 | 19.65 | 56.5 | 101915 | 100 | 3000 | 18.3753 | 65.8416 | 22.155 | 0 | 7.2692 | FALSE | FALSE
2025-01-16 10:00 | 22.2 | 48.5 | 101930 | 100 | 3000 | 19.4568 | 61.6864 | 26.0846 | 0 | 7.2692 | FALSE | FALSE
2025-01-16 11:00 | 23.7 | 45 | 101860 | 100 | 3000 | 20.0806 | 59.7785 | 28.7513 | 0 | 7.2692 | FALSE | FALSE
2025-01-16 12:00 | 24.65 | 42 | 101750 | 100 | 3000 | 20.4721 | 58.074 | 29.683 | 0 | 7.2692 | FALSE | FALSE
2025-01-16 13:00 | 24.9 | 44 | 101660 | 100 | 3000 | 20.5709 | 59.2857 | 32.0489 | 0 | 7.2692 | FALSE | FALSE
2025-01-16 14:00 | 24.35 | 49 | 101630 | 100 | 3000 | 20.3415 | 62.1824 | 33.938 | 0 | 7.2692 | FALSE | FALSE
2025-01-16 15:00 | 23.65 | 52 | 101635 | 100 | 3000 | 20.0527 | 63.8124 | 33.6289 | 0 | 7.2692 | FALSE | FALSE
2025-01-16 16:00 | 23.25 | 54 | 101635 | 100 | 3000 | 19.8868 | 64.8831 | 33.5958 | 0 | 7.2692 | FALSE | FALSE
2025-01-16 17:00 | 22.45 | 57.5 | 101640 | 100 | 3000 | 19.5539 | 66.6891 | 33.0437 | 0 | 7.2692 | FALSE | FALSE
2025-01-16 18:00 | 21.45 | 63 | 101685 | 100 | 3000 | 19.1341 | 69.456 | 32.8575 | 0 | 7.2692 | FALSE | FALSE
2025-01-16 19:00 | 20.5 | 69.5 | 101710 | 100 | 3000 | 18.7319 | 72.627 | 33.1723 | 0 | 7.2692 | FALSE | FALSE
2025-01-16 20:00 | 19.5 | 76 | 101705 | 100 | 3000 | 18.3058 | 75.6371 | 32.9396 | 0 | 7.2692 | FALSE | FALSE
2025-01-16 21:00 | 18.75 | 82 | 101720 | 100 | 3000 | 17.9839 | 78.3469 | 33.1747 | 0 | 7.2692 | FALSE | FALSE
2025-01-16 22:00 | 18.15 | 86 | 101710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-16 23:00 | 17.65 | 86.5 | 101670 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-17 | 17.1 | 86 | 101615 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-17 01:00 | 16.35 | 87 | 101570 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-17 02:00 | 15.55 | 88 | 101535 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-17 03:00 | 14.95 | 89 | 101515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-17 04:00 | 14.75 | 89.5 | 101515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-17 05:00 | 14.75 | 89 | 101515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-17 06:00 | 14.6 | 89.5 | 101550 | 100 | 3000 | 16.1619 | 80.7082 | 19.3852 | 0 | 7.2692 | FALSE | FALSE
2025-01-17 07:00 | 14.9 | 89 | 101600 | 100 | 3000 | 16.2963 | 80.5378 | 20.4112 | 0 | 7.2692 | FALSE | FALSE
2025-01-17 08:00 | 16.5 | 82.5 | 101635 | 100 | 3000 | 17.0057 | 77.9636 | 23.9846 | 0 | 7.2692 | FALSE | FALSE
2025-01-17 09:00 | 18.9 | 73 | 101655 | 100 | 3000 | 18.0498 | 73.9948 | 28.7725 | 0 | 7.2692 | FALSE | FALSE
2025-01-17 10:00 | 20.8 | 65 | 101625 | 100 | 3000 | 18.8604 | 70.3732 | 31.5851 | 0 | 7.2692 | FALSE | FALSE
2025-01-17 11:00 | 21.9 | 57.5 | 101540 | 100 | 3000 | 19.3255 | 66.6035 | 30.9755 | 0 | 7.2692 | FALSE | FALSE
2025-01-17 12:00 | 22.55 | 53 | 101435 | 100 | 3000 | 19.599 | 64.2426 | 30.3277 | 0 | 7.2692 | FALSE | FALSE
2025-01-17 13:00 | 22.6 | 54 | 101355 | 100 | 3000 | 19.6189 | 64.8113 | 31.1859 | 0 | 7.2692 | FALSE | FALSE
2025-01-17 14:00 | 22.25 | 56 | 101285 | 100 | 3000 | 19.4722 | 65.8694 | 31.2525 | 0 | 7.2692 | FALSE | FALSE
2025-01-17 15:00 | 21.85 | 57 | 101235 | 100 | 3000 | 19.305 | 66.3589 | 30.4339 | 0 | 7.2692 | FALSE | FALSE
2025-01-17 16:00 | 21.45 | 59 | 101230 | 100 | 3000 | 19.1366 | 67.3728 | 30.2461 | 0 | 7.2692 | FALSE | FALSE
2025-01-17 17:00 | 20.7 | 62 | 101220 | 100 | 3000 | 18.8197 | 68.8351 | 29.31 | 0 | 7.2692 | FALSE | FALSE
2025-01-17 18:00 | 19.6 | 67 | 101240 | 100 | 3000 | 18.351 | 71.2041 | 28.0882 | 0 | 7.2692 | FALSE | FALSE
2025-01-17 19:00 | 18.7 | 72.5 | 101275 | 100 | 3000 | 17.9639 | 73.7522 | 27.6753 | 0 | 7.2692 | FALSE | FALSE
2025-01-17 20:00 | 17.9 | 76 | 101280 | 100 | 3000 | 17.6177 | 75.2737 | 26.3651 | 0 | 7.2692 | FALSE | FALSE
2025-01-17 21:00 | 17.1 | 77.5 | 101255 | 100 | 3000 | 17.2688 | 75.8304 | 23.9187 | 0 | 7.2692 | FALSE | FALSE
2025-01-17 22:00 | 16.45 | 78 | 101235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-17 23:00 | 16.05 | 75.5 | 101225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-18 | 15.75 | 71 | 101190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-18 01:00 | 15.5 | 68.5 | 101160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-18 02:00 | 15.4 | 68.5 | 101130 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-18 03:00 | 15.4 | 70.5 | 101100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-18 04:00 | 15.5 | 70.5 | 101105 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-18 05:00 | 15.5 | 73 | 101135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-18 06:00 | 15.45 | 78.5 | 101170 | 100 | 3000 | 16.5398 | 76.0927 | 17.8288 | 0 | 7.2692 | FALSE | FALSE
2025-01-18 07:00 | 15.65 | 80 | 101210 | 100 | 3000 | 16.6291 | 76.7664 | 19.3269 | 0 | 7.2692 | FALSE | FALSE
2025-01-18 08:00 | 16.9 | 76.5 | 101245 | 100 | 3000 | 17.1811 | 75.3383 | 22.6094 | 0 | 7.2692 | FALSE | FALSE
2025-01-18 09:00 | 19.45 | 68.5 | 101270 | 100 | 3000 | 18.2865 | 71.9252 | 28.3759 | 0 | 7.2692 | FALSE | FALSE
2025-01-18 10:00 | 21.65 | 58.5 | 101260 | 100 | 3000 | 19.2205 | 67.1337 | 30.6736 | 0 | 7.2692 | FALSE | FALSE
2025-01-18 11:00 | 22.45 | 53 | 101200 | 100 | 3000 | 19.5575 | 64.2565 | 29.9449 | 0 | 7.2692 | FALSE | FALSE
2025-01-18 12:00 | 22.7 | 50 | 101115 | 100 | 3000 | 19.6636 | 62.6274 | 28.7694 | 0 | 7.2692 | FALSE | FALSE
2025-01-18 13:00 | 22.35 | 50 | 101030 | 100 | 3000 | 19.5183 | 62.6139 | 27.5361 | 0 | 7.2692 | FALSE | FALSE
2025-01-18 14:00 | 21.6 | 53.5 | 100970 | 100 | 3000 | 19.2028 | 64.4744 | 27.209 | 0 | 7.2692 | FALSE | FALSE
2025-01-18 15:00 | 21.45 | 54 | 100955 | 100 | 3000 | 19.1396 | 64.7328 | 26.9959 | 0 | 7.2692 | FALSE | FALSE
2025-01-18 16:00 | 21.45 | 52.5 | 100975 | 100 | 3000 | 19.1404 | 63.9288 | 26.0271 | 0 | 7.2692 | FALSE | FALSE
2025-01-18 17:00 | 20.9 | 50.5 | 101005 | 100 | 3000 | 18.9097 | 62.8556 | 22.8346 | 0 | 7.2692 | FALSE | FALSE
2025-01-18 18:00 | 20.15 | 53.5 | 101055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-18 19:00 | 19.75 | 56.5 | 101115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-18 20:00 | 19.4 | 57 | 101160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-18 21:00 | 19.1 | 58 | 101175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-18 22:00 | 18.85 | 57.5 | 101175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-18 23:00 | 18.65 | 57 | 101165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 | 18.4 | 57.5 | 101140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 01:00 | 18.15 | 57.5 | 101140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 02:00 | 18.05 | 57 | 101140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 03:00 | 17.9 | 57.5 | 101135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 04:00 | 17.9 | 56.5 | 101160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 05:00 | 17.8 | 55.5 | 101190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 06:00 | 17.45 | 56.5 | 101230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 07:00 | 17.7 | 56 | 101295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 08:00 | 19.1 | 51.5 | 101360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 09:00 | 20.9 | 44.5 | 101410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 10:00 | 21.95 | 40 | 101420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 11:00 | 22.4 | 37.5 | 101375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 12:00 | 22.7 | 36 | 101305 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 13:00 | 22.75 | 35.5 | 101235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 14:00 | 22.45 | 36 | 101190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 15:00 | 22.05 | 38 | 101175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 16:00 | 21.8 | 40 | 101185 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 17:00 | 21.25 | 43.5 | 101205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 18:00 | 20.4 | 47.5 | 101235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 19:00 | 19.7 | 50.5 | 101295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 20:00 | 19.1 | 53.5 | 101335 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 21:00 | 18.5 | 56.5 | 101355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 22:00 | 17.95 | 59.5 | 101355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-19 23:00 | 17.55 | 63.5 | 101340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-20 | 17.25 | 67 | 101330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-20 01:00 | 16.8 | 70 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-20 02:00 | 16.3 | 72.5 | 101295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-20 03:00 | 15.9 | 73 | 101295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-20 04:00 | 15.3 | 76 | 101315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-20 05:00 | 14.9 | 79.5 | 101350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-20 06:00 | 14.75 | 80.5 | 101405 | 100 | 3000 | 16.227 | 76.8897 | 15.9764 | 0 | 7.2692 | FALSE | FALSE
2025-01-20 07:00 | 15.25 | 78 | 101480 | 100 | 3000 | 16.4504 | 75.8215 | 16.8062 | 0 | 7.2692 | FALSE | FALSE
2025-01-20 08:00 | 17.25 | 69 | 101550 | 100 | 3000 | 17.3343 | 71.8595 | 20.1505 | 0 | 7.2692 | FALSE | FALSE
2025-01-20 09:00 | 19.55 | 57.5 | 101600 | 100 | 3000 | 18.3322 | 66.3801 | 22.3655 | 0 | 7.2692 | FALSE | FALSE
2025-01-20 10:00 | 20.85 | 50.5 | 101610 | 100 | 3000 | 18.8884 | 62.7883 | 22.7065 | 0 | 7.2692 | FALSE | FALSE
2025-01-20 11:00 | 21.45 | 48 | 101560 | 100 | 3000 | 19.143 | 61.4567 | 23.1582 | 0 | 7.2692 | FALSE | FALSE
2025-01-20 12:00 | 21.8 | 46.5 | 101475 | 100 | 3000 | 19.291 | 60.6488 | 23.3492 | 0 | 7.2692 | FALSE | FALSE
2025-01-20 13:00 | 21.85 | 46 | 101390 | 100 | 3000 | 19.3123 | 60.3855 | 23.1781 | 0 | 7.2692 | FALSE | FALSE
2025-01-20 14:00 | 21.65 | 46 | 101335 | 100 | 3000 | 19.2284 | 60.4002 | 22.5902 | 0 | 7.2692 | FALSE | FALSE
2025-01-20 15:00 | 21.25 | 47 | 101320 | 100 | 3000 | 19.0593 | 60.9576 | 22.0041 | 0 | 7.2692 | FALSE | FALSE
2025-01-20 16:00 | 20.85 | 49 | 101325 | 100 | 3000 | 18.8892 | 62.0328 | 21.7428 | 0 | 7.2692 | FALSE | FALSE
2025-01-20 17:00 | 20.2 | 52.5 | 101340 | 100 | 3000 | 18.6116 | 63.8691 | 21.6722 | 0 | 7.2692 | FALSE | FALSE
2025-01-20 18:00 | 19.3 | 57.5 | 101385 | 100 | 3000 | 18.225 | 66.4011 | 21.4551 | 0 | 7.2692 | FALSE | FALSE
2025-01-20 19:00 | 18.6 | 61.5 | 101450 | 100 | 3000 | 17.9225 | 68.3535 | 21.1831 | 0 | 7.2692 | FALSE | FALSE
2025-01-20 20:00 | 18.05 | 64.5 | 101495 | 100 | 3000 | 17.6836 | 69.7787 | 20.7917 | 0 | 7.2692 | FALSE | FALSE
2025-01-20 21:00 | 17.6 | 67.5 | 101515 | 100 | 3000 | 17.4874 | 71.1802 | 20.6984 | 0 | 7.2692 | FALSE | FALSE
2025-01-20 22:00 | 17.1 | 69.5 | 101505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-20 23:00 | 16.6 | 71 | 101470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-21 | 16.25 | 73.5 | 101430 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-21 01:00 | 16 | 76 | 101410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-21 02:00 | 15.95 | 76.5 | 101400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-21 03:00 | 16.2 | 74 | 101385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-21 04:00 | 16.2 | 71 | 101375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-21 05:00 | 16.4 | 65.5 | 101390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-21 06:00 | 16.9 | 61 | 101435 | 100 | 3000 | 17.1803 | 68.1638 | 15.4259 | 0 | 7.2692 | FALSE | FALSE
2025-01-21 07:00 | 17.45 | 60.5 | 101490 | 100 | 3000 | 17.4219 | 67.8854 | 16.4706 | 0 | 7.2692 | FALSE | FALSE
2025-01-21 08:00 | 19.2 | 54.5 | 101545 | 100 | 3000 | 18.1827 | 64.8887 | 19.3782 | 0 | 7.2692 | FALSE | FALSE
2025-01-21 09:00 | 20.95 | 47.5 | 101590 | 100 | 3000 | 18.9322 | 61.209 | 21.6225 | 0 | 7.2692 | FALSE | FALSE
2025-01-21 10:00 | 21.8 | 43 | 101610 | 100 | 3000 | 19.2933 | 58.7387 | 22.8827 | 0 | 7.2692 | FALSE | FALSE
2025-01-21 11:00 | 22.3 | 39.5 | 101565 | 100 | 3000 | 19.5053 | 56.7775 | 23.61 | 0 | 7.2692 | FALSE | FALSE
2025-01-21 12:00 | 22.45 | 39.5 | 101465 | 100 | 3000 | 19.5681 | 56.7699 | 23.8012 | 0 | 7.2692 | FALSE | FALSE
2025-01-21 13:00 | 22.45 | 40.5 | 101380 | 100 | 3000 | 19.5673 | 57.3323 | 23.7757 | 0 | 7.2692 | FALSE | FALSE
2025-01-21 14:00 | 22.3 | 40.5 | 101330 | 100 | 3000 | 19.5046 | 57.3536 | 23.5503 | 0 | 7.2692 | FALSE | FALSE
2025-01-21 15:00 | 21.85 | 40.5 | 101310 | 100 | 3000 | 19.316 | 57.4101 | 22.9007 | 0 | 7.2692 | FALSE | FALSE
2025-01-21 16:00 | 21.3 | 42.5 | 101325 | 100 | 3000 | 19.083 | 58.5554 | 22.0986 | 0 | 7.2692 | FALSE | FALSE
2025-01-21 17:00 | 20.7 | 46 | 101350 | 100 | 3000 | 18.827 | 60.4683 | 21.2124 | 0 | 7.2692 | FALSE | FALSE
2025-01-21 18:00 | 20.15 | 49 | 101380 | 100 | 3000 | 18.5916 | 62.0685 | 20.3963 | 0 | 7.2692 | FALSE | FALSE
2025-01-21 19:00 | 19.9 | 50 | 101415 | 100 | 3000 | 18.4844 | 62.5954 | 20.0286 | 0 | 7.2692 | FALSE | FALSE
2025-01-21 20:00 | 19.75 | 49.5 | 101450 | 100 | 3000 | 18.4203 | 62.3498 | 19.8135 | 0 | 7.2692 | FALSE | FALSE
2025-01-21 21:00 | 19.7 | 49 | 101485 | 100 | 3000 | 18.399 | 62.0973 | 19.7472 | 0 | 7.2692 | FALSE | FALSE
2025-01-21 22:00 | 19.65 | 50 | 101500 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-21 23:00 | 19.5 | 50.5 | 101490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-22 | 19.3 | 51 | 101470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-22 01:00 | 19.05 | 53 | 101460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-22 02:00 | 18.6 | 54.5 | 101460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-22 03:00 | 17.8 | 55.5 | 101455 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-22 04:00 | 17.2 | 54.5 | 101465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-22 05:00 | 16.55 | 54 | 101520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-22 06:00 | 15.4 | 57.5 | 101600 | 100 | 3000 | 16.5134 | 66.7961 | 13.0633 | 0 | 7.2692 | FALSE | FALSE
2025-01-22 07:00 | 14.85 | 61 | 101690 | 100 | 3000 | 16.2672 | 68.4347 | 12.1806 | 0 | 7.2692 | FALSE | FALSE
2025-01-22 08:00 | 16.25 | 58 | 101775 | 100 | 3000 | 16.8925 | 66.8299 | 14.451 | 0 | 7.2692 | FALSE | FALSE
2025-01-22 09:00 | 19 | 47 | 101840 | 100 | 3000 | 18.0979 | 61.1502 | 18.7634 | 0 | 7.2692 | FALSE | FALSE
2025-01-22 10:00 | 21.45 | 35.5 | 101860 | 100 | 3000 | 19.1503 | 54.7239 | 22.4664 | 0 | 7.2692 | FALSE | FALSE
2025-01-22 11:00 | 23.2 | 26.5 | 101800 | 100 | 3000 | 19.8921 | 49.2842 | 25.0312 | 0 | 7.2692 | FALSE | FALSE
2025-01-22 12:00 | 24.15 | 21.5 | 101690 | 100 | 3000 | 20.292 | 46.09 | 26.3843 | 0 | 7.2692 | FALSE | FALSE
2025-01-22 13:00 | 24.45 | 20.5 | 101595 | 100 | 3000 | 20.4173 | 45.4006 | 26.7882 | 0 | 7.2692 | FALSE | FALSE
2025-01-22 14:00 | 24.65 | 20.5 | 101560 | 100 | 3000 | 20.4998 | 45.3306 | 27.0579 | 0 | 7.2692 | FALSE | FALSE
2025-01-22 15:00 | 24.4 | 23 | 101560 | 100 | 3000 | 20.3936 | 46.8986 | 26.6888 | 0 | 7.2692 | FALSE | FALSE
2025-01-22 16:00 | 23.45 | 29 | 101575 | 100 | 3000 | 19.9938 | 50.6618 | 25.3139 | 0 | 7.2692 | FALSE | FALSE
2025-01-22 17:00 | 22.1 | 34.5 | 101625 | 100 | 3000 | 19.4251 | 54.0592 | 23.364 | 0 | 7.2692 | FALSE | FALSE
2025-01-22 18:00 | 20.9 | 37 | 101695 | 100 | 3000 | 18.9162 | 55.6693 | 21.6161 | 0 | 7.2692 | FALSE | FALSE
2025-01-22 19:00 | 20.05 | 40 | 101780 | 100 | 3000 | 18.5519 | 57.4174 | 20.3585 | 0 | 7.2692 | FALSE | FALSE
2025-01-22 20:00 | 18.95 | 42.5 | 101860 | 100 | 3000 | 18.0771 | 58.9286 | 18.7025 | 0 | 7.2692 | FALSE | FALSE
2025-01-22 21:00 | 17.6 | 43 | 101905 | 100 | 3000 | 17.488 | 59.5393 | 16.6209 | 0 | 7.2692 | FALSE | FALSE
2025-01-22 22:00 | 16.25 | 44 | 101910 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-22 23:00 | 15.1 | 47 | 101890 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-23 | 14.25 | 49.5 | 101870 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-23 01:00 | 13.45 | 51 | 101850 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-23 02:00 | 12.6 | 53 | 101825 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-23 03:00 | 12.2 | 51.5 | 101815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-23 04:00 | 12.6 | 47 | 101805 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-23 05:00 | 13.1 | 48.5 | 101815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-23 06:00 | 13.2 | 55 | 101860 | 100 | 3000 | 15.5164 | 66.3881 | 9.4593 | 0 | 7.2692 | FALSE | FALSE
2025-01-23 07:00 | 13.7 | 56 | 101925 | 100 | 3000 | 15.7451 | 66.6045 | 10.3056 | 0 | 7.2692 | FALSE | FALSE
2025-01-23 08:00 | 15.8 | 50 | 102015 | 100 | 3000 | 16.691 | 63.305 | 13.7671 | 0 | 7.2692 | FALSE | FALSE
2025-01-23 09:00 | 19 | 42 | 102080 | 100 | 3000 | 18.0989 | 58.6426 | 18.8203 | 0 | 7.2692 | FALSE | FALSE
2025-01-23 10:00 | 21.7 | 33 | 102080 | 100 | 3000 | 19.2574 | 53.29 | 22.8928 | 0 | 7.2692 | FALSE | FALSE
2025-01-23 11:00 | 23.4 | 24.5 | 102000 | 100 | 3000 | 19.9772 | 48.0582 | 25.3786 | 0 | 7.2692 | FALSE | FALSE
2025-01-23 12:00 | 24.3 | 20 | 101870 | 100 | 3000 | 20.3557 | 45.1346 | 26.6531 | 0 | 7.2692 | FALSE | FALSE
2025-01-23 13:00 | 24.75 | 18.5 | 101755 | 100 | 3000 | 20.5435 | 44.0807 | 27.2656 | 0 | 7.2692 | FALSE | FALSE
2025-01-23 14:00 | 24.95 | 17.5 | 101690 | 100 | 3000 | 20.6272 | 43.4075 | 27.5355 | 0 | 7.2692 | FALSE | FALSE
2025-01-23 15:00 | 24.8 | 17 | 101655 | 100 | 3000 | 20.5661 | 43.1736 | 27.3219 | 0 | 7.2692 | FALSE | FALSE
2025-01-23 16:00 | 24.2 | 19 | 101620 | 100 | 3000 | 20.3156 | 44.6118 | 26.4563 | 0 | 7.2692 | FALSE | FALSE
2025-01-23 17:00 | 22.65 | 22 | 101610 | 100 | 3000 | 19.6658 | 46.9679 | 24.2258 | 0 | 7.2692 | FALSE | FALSE
2025-01-23 18:00 | 20.7 | 25.5 | 101640 | 100 | 3000 | 18.8362 | 49.688 | 21.3556 | 0 | 7.2692 | FALSE | FALSE
2025-01-23 19:00 | 19.3 | 30.5 | 101695 | 100 | 3000 | 18.2314 | 52.8464 | 19.2386 | 0 | 7.2692 | FALSE | FALSE
2025-01-23 20:00 | 18.1 | 33 | 101745 | 100 | 3000 | 17.7079 | 54.5836 | 17.3927 | 0 | 7.2692 | FALSE | FALSE
2025-01-23 21:00 | 16.9 | 34.5 | 101760 | 100 | 3000 | 17.1789 | 55.8383 | 15.5055 | 0 | 7.2692 | FALSE | FALSE
2025-01-23 22:00 | 15.7 | 39 | 101740 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-23 23:00 | 14.5 | 44.5 | 101700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-24 | 13.4 | 49 | 101650 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-24 01:00 | 12.5 | 52.5 | 101620 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-24 02:00 | 11.85 | 53.5 | 101590 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-24 03:00 | 11.6 | 50.5 | 101550 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-24 04:00 | 11.8 | 49.5 | 101535 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-24 05:00 | 11.7 | 53.5 | 101550 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-24 06:00 | 11.2 | 59 | 101585 | 100 | 3000 | 14.5938 | 68.9022 | 6.0184 | 0 | 7.2692 | FALSE | FALSE
2025-01-24 07:00 | 11.5 | 62 | 101635 | 100 | 3000 | 14.7349 | 69.9182 | 6.5456 | 0 | 7.2692 | FALSE | FALSE
2025-01-24 08:00 | 13.6 | 57 | 101690 | 100 | 3000 | 15.6998 | 67.0883 | 10.1154 | 0 | 7.2692 | FALSE | FALSE
2025-01-24 09:00 | 17.1 | 46 | 101720 | 100 | 3000 | 17.2678 | 61.1241 | 15.802 | 0 | 7.2692 | FALSE | FALSE
2025-01-24 10:00 | 20.5 | 36.5 | 101710 | 100 | 3000 | 18.7459 | 55.5053 | 21.0288 | 0 | 7.2692 | FALSE | FALSE
2025-01-24 11:00 | 23.1 | 28 | 101625 | 100 | 3000 | 19.849 | 50.1834 | 24.8365 | 0 | 7.2692 | FALSE | FALSE
2025-01-24 12:00 | 24.7 | 20.5 | 101500 | 100 | 3000 | 20.5204 | 45.3184 | 27.1117 | 0 | 7.2692 | FALSE | FALSE
2025-01-24 13:00 | 25.5 | 17.5 | 101385 | 100 | 3000 | 20.8531 | 43.2179 | 28.2126 | 0 | 7.2692 | FALSE | FALSE
2025-01-24 14:00 | 25.75 | 16.5 | 101305 | 100 | 3000 | 20.9569 | 42.5131 | 28.5426 | 0 | 7.2692 | FALSE | FALSE
2025-01-24 15:00 | 25.05 | 21.5 | 101275 | 100 | 3000 | 20.663 | 45.8186 | 27.5271 | 0 | 7.2692 | FALSE | FALSE
2025-01-24 16:00 | 23.35 | 32.5 | 101295 | 100 | 3000 | 19.9489 | 52.713 | 25.08 | 0 | 7.2692 | FALSE | FALSE
2025-01-24 17:00 | 21.65 | 41 | 101340 | 100 | 3000 | 19.2315 | 57.7039 | 22.6163 | 0 | 7.2692 | FALSE | FALSE
2025-01-24 18:00 | 20.5 | 46.5 | 101395 | 100 | 3000 | 18.7417 | 60.7437 | 20.9256 | 0 | 7.2692 | FALSE | FALSE
2025-01-24 19:00 | 19.6 | 50.5 | 101460 | 100 | 3000 | 18.3556 | 62.8679 | 19.5881 | 0 | 7.2692 | FALSE | FALSE
2025-01-24 20:00 | 18.6 | 55.5 | 101500 | 100 | 3000 | 17.9233 | 65.4192 | 18.0724 | 0 | 7.2692 | FALSE | FALSE
2025-01-24 21:00 | 17.35 | 57.5 | 101515 | 100 | 3000 | 17.3781 | 66.4811 | 16.146 | 0 | 7.2692 | FALSE | FALSE
2025-01-24 22:00 | 16.2 | 55 | 101510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-24 23:00 | 15.1 | 55.5 | 101480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-25 | 14 | 59.5 | 101455 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-25 01:00 | 13 | 63.5 | 101445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-25 02:00 | 12.1 | 66.5 | 101425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-25 03:00 | 11.4 | 70 | 101410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-25 04:00 | 11.3 | 69.5 | 101410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-25 05:00 | 11.25 | 69 | 101430 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-25 06:00 | 10.75 | 70 | 101475 | 100 | 3000 | 14.3887 | 73.3107 | 5.2435 | 0 | 7.2692 | FALSE | FALSE
2025-01-25 07:00 | 10.95 | 65.5 | 101540 | 100 | 3000 | 14.4801 | 71.5118 | 5.5896 | 0 | 7.2692 | FALSE | FALSE
2025-01-25 08:00 | 13.05 | 56 | 101620 | 100 | 3000 | 15.448 | 66.8909 | 9.1851 | 0 | 7.2692 | FALSE | FALSE
2025-01-25 09:00 | 16.5 | 45 | 101680 | 100 | 3000 | 17.0021 | 60.8568 | 14.8466 | 0 | 7.2692 | FALSE | FALSE
2025-01-25 10:00 | 19.4 | 40 | 101680 | 100 | 3000 | 18.2723 | 57.588 | 19.3604 | 0 | 7.2692 | FALSE | FALSE
2025-01-25 11:00 | 21.4 | 36.5 | 101605 | 100 | 3000 | 19.1286 | 55.2995 | 22.333 | 0 | 7.2692 | FALSE | FALSE
2025-01-25 12:00 | 22.95 | 30.5 | 101480 | 100 | 3000 | 19.7843 | 51.6511 | 24.572 | 0 | 7.2692 | FALSE | FALSE
2025-01-25 13:00 | 23.85 | 28 | 101365 | 100 | 3000 | 20.1607 | 50.0042 | 25.8314 | 0 | 7.2692 | FALSE | FALSE
2025-01-25 14:00 | 24.05 | 29 | 101295 | 100 | 3000 | 20.2423 | 50.5434 | 26.0853 | 0 | 7.2692 | FALSE | FALSE
2025-01-25 15:00 | 23.6 | 30.5 | 101275 | 100 | 3000 | 20.0546 | 51.517 | 25.4403 | 0 | 7.2692 | FALSE | FALSE
2025-01-25 16:00 | 22.6 | 36 | 101280 | 100 | 3000 | 19.6335 | 54.8258 | 23.9926 | 0 | 7.2692 | FALSE | FALSE
2025-01-25 17:00 | 21.3 | 49 | 101305 | 100 | 3000 | 19.0793 | 62.0221 | 23.2735 | 0 | 7.2692 | FALSE | FALSE
2025-01-25 18:00 | 20.1 | 61.5 | 101360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-25 19:00 | 19.2 | 67 | 101430 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-25 20:00 | 18.5 | 68 | 101480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-25 21:00 | 17.8 | 66.5 | 101485 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-25 22:00 | 16.95 | 65 | 101485 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-25 23:00 | 16.15 | 66 | 101480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 | 15.65 | 68.5 | 101450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 01:00 | 15.3 | 72 | 101425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 02:00 | 14.65 | 76.5 | 101395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 03:00 | 13.75 | 81 | 101360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 04:00 | 13 | 84.5 | 101365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 05:00 | 12.5 | 86 | 101405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 06:00 | 12.15 | 85.5 | 101465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 07:00 | 12.55 | 80.5 | 101535 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 08:00 | 14.9 | 68 | 101600 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 09:00 | 18.45 | 54.5 | 101630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 10:00 | 21.25 | 47 | 101610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 11:00 | 23.1 | 40.5 | 101530 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 12:00 | 24.45 | 34 | 101405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 13:00 | 24.95 | 34.5 | 101290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 14:00 | 24.5 | 38.5 | 101215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 15:00 | 23.75 | 39.5 | 101180 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 16:00 | 22.95 | 45.5 | 101170 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 17:00 | 21.75 | 57 | 101185 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 18:00 | 20.45 | 65 | 101225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 19:00 | 19.4 | 71.5 | 101285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 20:00 | 18.65 | 76 | 101345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 21:00 | 17.95 | 77.5 | 101365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 22:00 | 17 | 78.5 | 101365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-26 23:00 | 16.15 | 80 | 101350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-27 | 15.5 | 82 | 101315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-27 01:00 | 14.9 | 84 | 101285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-27 02:00 | 14.3 | 86 | 101255 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-27 03:00 | 13.7 | 88 | 101230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-27 04:00 | 13.25 | 89 | 101220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-27 05:00 | 13 | 89 | 101240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-27 06:00 | 12.8 | 89.5 | 101275 | 100 | 3000 | 15.3457 | 80.5812 | 12.0157 | 0 | 7.2692 | FALSE | FALSE
2025-01-27 07:00 | 13.4 | 88 | 101320 | 100 | 3000 | 15.619 | 79.9858 | 13.8234 | 0 | 7.2692 | FALSE | FALSE
2025-01-27 08:00 | 15.65 | 80 | 101380 | 100 | 3000 | 16.6291 | 76.7445 | 19.3259 | 0 | 7.2692 | FALSE | FALSE
2025-01-27 09:00 | 18.75 | 70.5 | 101410 | 100 | 3000 | 17.9858 | 72.7688 | 26.7653 | 0 | 7.2692 | FALSE | FALSE
2025-01-27 10:00 | 21.35 | 65.5 | 101385 | 100 | 3000 | 19.0909 | 70.7958 | 34.0443 | 0 | 7.2692 | FALSE | FALSE
2025-01-27 11:00 | 23.3 | 58 | 101315 | 100 | 3000 | 19.9035 | 67.1899 | 36.58 | 0 | 7.2692 | FALSE | FALSE
2025-01-27 12:00 | 24.8 | 46.5 | 101215 | 100 | 3000 | 20.5272 | 60.8099 | 33.5747 | 0 | 7.2692 | FALSE | FALSE
2025-01-27 13:00 | 24.75 | 47 | 101120 | 100 | 3000 | 20.5063 | 61.1105 | 33.7717 | 0 | 7.2692 | FALSE | FALSE
2025-01-27 14:00 | 23.45 | 57 | 101060 | 100 | 3000 | 19.9659 | 66.6865 | 36.4137 | 0 | 7.2692 | FALSE | FALSE
2025-01-27 15:00 | 23.05 | 59.5 | 101035 | 100 | 3000 | 19.7996 | 68.0017 | 36.6455 | 0 | 7.2692 | FALSE | FALSE
2025-01-27 16:00 | 23.2 | 58 | 101030 | 100 | 3000 | 19.8625 | 67.196 | 36.1685 | 0 | 7.2692 | FALSE | FALSE
2025-01-27 17:00 | 22.3 | 64 | 101040 | 100 | 3000 | 19.4869 | 70.2882 | 36.7933 | 0 | 7.2692 | FALSE | FALSE
2025-01-27 18:00 | 21.05 | 75 | 101070 | 100 | 3000 | 18.9603 | 75.7496 | 38.7988 | 0 | 7.2692 | FALSE | FALSE
2025-01-27 19:00 | 20.3 | 83.5 | 101115 | 100 | 3000 | 18.6419 | 79.8186 | 40.7583 | 0 | 7.2692 | FALSE | FALSE
2025-01-27 20:00 | 20.1 | 87 | 101155 | 100 | 3000 | 18.5564 | 81.4973 | 41.951 | 0 | 7.2692 | FALSE | FALSE
2025-01-27 21:00 | 20.3 | 86 | 101165 | 100 | 3000 | 18.6409 | 81.0917 | 42.2593 | 0 | 7.2692 | FALSE | FALSE
2025-01-27 22:00 | 20.35 | 84 | 101155 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-27 23:00 | 19.85 | 86 | 101140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-28 | 19.1 | 90.5 | 101105 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-28 01:00 | 18.6 | 92.5 | 101090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-28 02:00 | 18.2 | 93 | 101095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-28 03:00 | 18 | 93 | 101085 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-28 04:00 | 18.05 | 91.5 | 101095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-28 05:00 | 18.35 | 89.5 | 101145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-28 06:00 | 18.75 | 88.5 | 101200 | 100 | 3000 | 17.9828 | 81.5756 | 36.7532 | 0 | 7.2692 | FALSE | FALSE
2025-01-28 07:00 | 19.2 | 87 | 101240 | 100 | 3000 | 18.1753 | 81.0416 | 37.9188 | 0 | 7.2692 | FALSE | FALSE
2025-01-28 08:00 | 20.4 | 81.5 | 101285 | 100 | 3000 | 18.6848 | 78.821 | 40.007 | 0 | 7.2692 | FALSE | FALSE
2025-01-28 09:00 | 22 | 72.5 | 101330 | 100 | 3000 | 19.3566 | 74.7763 | 41.2327 | 0 | 7.2692 | FALSE | FALSE
2025-01-28 10:00 | 23.1 | 64 | 101345 | 100 | 3000 | 19.8159 | 70.5086 | 40.014 | 0 | 7.2692 | FALSE | FALSE
2025-01-28 11:00 | 23.75 | 58 | 101310 | 100 | 3000 | 20.0872 | 67.3075 | 38.3052 | 0 | 7.2692 | FALSE | FALSE
2025-01-28 12:00 | 24.1 | 54.5 | 101235 | 100 | 3000 | 20.2334 | 65.3838 | 37.0687 | 0 | 7.2692 | FALSE | FALSE
2025-01-28 13:00 | 24.05 | 54 | 101160 | 100 | 3000 | 20.2137 | 65.0905 | 36.505 | 0 | 7.2692 | FALSE | FALSE
2025-01-28 14:00 | 23.8 | 55 | 101110 | 100 | 3000 | 20.1108 | 65.6182 | 36.2979 | 0 | 7.2692 | FALSE | FALSE
2025-01-28 15:00 | 23.4 | 55.5 | 101080 | 100 | 3000 | 19.9469 | 65.821 | 35.1585 | 0 | 7.2692 | FALSE | FALSE
2025-01-28 16:00 | 22.75 | 59 | 101095 | 100 | 3000 | 19.6767 | 67.6421 | 35.1536 | 0 | 7.2692 | FALSE | FALSE
2025-01-28 17:00 | 21.85 | 64 | 101140 | 100 | 3000 | 19.3003 | 70.1515 | 35.0257 | 0 | 7.2692 | FALSE | FALSE
2025-01-28 18:00 | 21.05 | 66.5 | 101190 | 100 | 3000 | 18.9647 | 71.2684 | 33.4756 | 0 | 7.2692 | FALSE | FALSE
2025-01-28 19:00 | 20.6 | 67 | 101260 | 100 | 3000 | 18.7752 | 71.4097 | 32.0101 | 0 | 7.2692 | FALSE | FALSE
2025-01-28 20:00 | 20.2 | 68 | 101320 | 100 | 3000 | 18.6057 | 71.8243 | 31.04 | 0 | 7.2692 | FALSE | FALSE
2025-01-28 21:00 | 19.75 | 70 | 101350 | 100 | 3000 | 18.414 | 72.7331 | 30.4424 | 0 | 7.2692 | FALSE | FALSE
2025-01-28 22:00 | 19.25 | 72.5 | 101375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-28 23:00 | 18.8 | 76 | 101385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-29 | 18.45 | 79 | 101365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-29 01:00 | 18.25 | 81 | 101355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-29 02:00 | 18.15 | 82 | 101345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-29 03:00 | 18 | 82 | 101335 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-29 04:00 | 17.85 | 81 | 101350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-29 05:00 | 17.6 | 80.5 | 101370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-29 06:00 | 17.15 | 81 | 101415 | 100 | 3000 | 17.2908 | 77.4427 | 25.9115 | 0 | 7.2692 | FALSE | FALSE
2025-01-29 07:00 | 17.45 | 79.5 | 101485 | 100 | 3000 | 17.4218 | 76.8031 | 26.3761 | 0 | 7.2692 | FALSE | FALSE
2025-01-29 08:00 | 19.2 | 72 | 101560 | 100 | 3000 | 18.1787 | 73.5812 | 29.409 | 0 | 7.2692 | FALSE | FALSE
2025-01-29 09:00 | 21.15 | 61 | 101625 | 100 | 3000 | 19.0096 | 68.3408 | 30.423 | 0 | 7.2692 | FALSE | FALSE
2025-01-29 10:00 | 22.25 | 54.5 | 101640 | 100 | 3000 | 19.4733 | 65.0089 | 30.2759 | 0 | 7.2692 | FALSE | FALSE
2025-01-29 11:00 | 22.75 | 52.5 | 101605 | 100 | 3000 | 19.6821 | 63.9707 | 30.7219 | 0 | 7.2692 | FALSE | FALSE
2025-01-29 12:00 | 23 | 51 | 101535 | 100 | 3000 | 19.7867 | 63.1684 | 30.5676 | 0 | 7.2692 | FALSE | FALSE
2025-01-29 13:00 | 23.05 | 50 | 101465 | 100 | 3000 | 19.8083 | 62.6191 | 30.0364 | 0 | 7.2692 | FALSE | FALSE
2025-01-29 14:00 | 22.85 | 51 | 101425 | 100 | 3000 | 19.7248 | 63.1646 | 30.0226 | 0 | 7.2692 | FALSE | FALSE
2025-01-29 15:00 | 22.5 | 53 | 101405 | 100 | 3000 | 19.5782 | 64.2399 | 30.1445 | 0 | 7.2692 | FALSE | FALSE
2025-01-29 16:00 | 22 | 54.5 | 101415 | 100 | 3000 | 19.3692 | 65.0033 | 29.3458 | 0 | 7.2692 | FALSE | FALSE
2025-01-29 17:00 | 21.2 | 56.5 | 101425 | 100 | 3000 | 19.033 | 65.9887 | 27.7332 | 0 | 7.2692 | FALSE | FALSE
2025-01-29 18:00 | 20.25 | 60.5 | 101445 | 100 | 3000 | 18.6298 | 67.9711 | 26.711 | 0 | 7.2692 | FALSE | FALSE
2025-01-29 19:00 | 19.3 | 65.5 | 101500 | 100 | 3000 | 18.223 | 70.3765 | 26.074 | 0 | 7.2692 | FALSE | FALSE
2025-01-29 20:00 | 18.4 | 70 | 101555 | 100 | 3000 | 17.8348 | 72.4515 | 25.1207 | 0 | 7.2692 | FALSE | FALSE
2025-01-29 21:00 | 17.7 | 75.5 | 101580 | 100 | 3000 | 17.5308 | 74.9614 | 25.3023 | 0 | 7.2692 | FALSE | FALSE
2025-01-29 22:00 | 17.15 | 81 | 101585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-29 23:00 | 16.8 | 82.5 | 101575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-30 | 16.6 | 81.5 | 101535 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-30 01:00 | 16 | 83 | 101500 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-30 02:00 | 14.95 | 87 | 101460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-30 03:00 | 13.75 | 91.5 | 101425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-30 04:00 | 13.1 | 92.5 | 101445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-30 05:00 | 13 | 91.5 | 101490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-30 06:00 | 12.7 | 92.5 | 101550 | 100 | 3000 | 15.3011 | 81.7453 | 12.7985 | 0 | 7.2692 | FALSE | FALSE
2025-01-30 07:00 | 12.9 | 91 | 101625 | 100 | 3000 | 15.3921 | 81.1413 | 13.0096 | 0 | 7.2692 | FALSE | FALSE
2025-01-30 08:00 | 15.25 | 80 | 101700 | 100 | 3000 | 16.4508 | 76.6663 | 17.7274 | 0 | 7.2692 | FALSE | FALSE
2025-01-30 09:00 | 18.75 | 65.5 | 101750 | 100 | 3000 | 17.9866 | 70.2821 | 23.9864 | 0 | 7.2692 | FALSE | FALSE
2025-01-30 10:00 | 21.25 | 57.5 | 101735 | 100 | 3000 | 19.0535 | 66.49 | 28.5789 | 0 | 7.2692 | FALSE | FALSE
2025-01-30 11:00 | 22.85 | 52 | 101665 | 100 | 3000 | 19.7239 | 63.6974 | 30.7414 | 0 | 7.2692 | FALSE | FALSE
2025-01-30 12:00 | 23.6 | 48 | 101570 | 100 | 3000 | 20.0365 | 61.5231 | 30.5521 | 0 | 7.2692 | FALSE | FALSE
2025-01-30 13:00 | 23.75 | 45.5 | 101465 | 100 | 3000 | 20.1006 | 60.1098 | 29.2412 | 0 | 7.2692 | FALSE | FALSE
2025-01-30 14:00 | 23.65 | 45 | 101385 | 100 | 3000 | 20.0601 | 59.8267 | 28.5291 | 0 | 7.2692 | FALSE | FALSE
2025-01-30 15:00 | 23.1 | 48.5 | 101360 | 100 | 3000 | 19.8303 | 61.7901 | 29.1451 | 0 | 7.2692 | FALSE | FALSE
2025-01-30 16:00 | 22.6 | 50.5 | 101355 | 100 | 3000 | 19.6217 | 62.8715 | 28.7852 | 0 | 7.2692 | FALSE | FALSE
2025-01-30 17:00 | 22 | 54 | 101355 | 100 | 3000 | 19.3696 | 64.738 | 29.0082 | 0 | 7.2692 | FALSE | FALSE
2025-01-30 18:00 | 21.25 | 59.5 | 101380 | 100 | 3000 | 19.0524 | 67.5907 | 29.8281 | 0 | 7.2692 | FALSE | FALSE
2025-01-30 19:00 | 20.85 | 60.5 | 101430 | 100 | 3000 | 18.8836 | 68.0513 | 28.9591 | 0 | 7.2692 | FALSE | FALSE
2025-01-30 20:00 | 20.45 | 59.5 | 101470 | 100 | 3000 | 18.715 | 67.4749 | 26.8478 | 0 | 7.2692 | FALSE | FALSE
2025-01-30 21:00 | 20.05 | 60 | 101485 | 100 | 3000 | 18.545 | 67.6898 | 25.6682 | 0 | 7.2692 | FALSE | FALSE
2025-01-30 22:00 | 19.8 | 60 | 101480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-30 23:00 | 19.5 | 58.5 | 101450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-31 | 19.1 | 59.5 | 101400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-31 01:00 | 18.7 | 61.5 | 101360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-31 02:00 | 18.4 | 63 | 101340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-31 03:00 | 18.2 | 63 | 101330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-31 04:00 | 18.1 | 60.5 | 101335 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-31 05:00 | 17.8 | 57 | 101355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-31 06:00 | 17.15 | 56 | 101405 | 100 | 3000 | 17.2901 | 65.8179 | 15.8188 | 0 | 7.2692 | FALSE | FALSE
2025-01-31 07:00 | 17.3 | 56 | 101475 | 100 | 3000 | 17.3561 | 65.7886 | 16.0639 | 0 | 7.2692 | FALSE | FALSE
2025-01-31 08:00 | 18.95 | 51 | 101520 | 100 | 3000 | 18.0755 | 63.1748 | 18.6187 | 0 | 7.2692 | FALSE | FALSE
2025-01-31 09:00 | 21 | 42 | 101545 | 100 | 3000 | 18.9562 | 58.3066 | 21.71 | 0 | 7.2692 | FALSE | FALSE
2025-01-31 10:00 | 22.25 | 35.5 | 101540 | 100 | 3000 | 19.4874 | 54.5861 | 23.5552 | 0 | 7.2692 | FALSE | FALSE
2025-01-31 11:00 | 22.85 | 33.5 | 101460 | 100 | 3000 | 19.7399 | 53.3625 | 24.406 | 0 | 7.2692 | FALSE | FALSE
2025-01-31 12:00 | 22.95 | 35.5 | 101360 | 100 | 3000 | 19.7799 | 54.4782 | 24.5113 | 0 | 7.2692 | FALSE | FALSE
2025-01-31 13:00 | 22.9 | 37.5 | 101305 | 100 | 3000 | 19.7573 | 55.6155 | 24.4147 | 0 | 7.2692 | FALSE | FALSE
2025-01-31 14:00 | 22.65 | 39.5 | 101270 | 100 | 3000 | 19.6516 | 56.7679 | 24.0401 | 0 | 7.2692 | FALSE | FALSE
2025-01-31 15:00 | 22.15 | 42.5 | 101245 | 100 | 3000 | 19.4404 | 58.4757 | 23.3054 | 0 | 7.2692 | FALSE | FALSE
2025-01-31 16:00 | 21.8 | 44.5 | 101245 | 100 | 3000 | 19.2923 | 59.5912 | 22.7935 | 0 | 7.2692 | FALSE | FALSE
2025-01-31 17:00 | 21.1 | 47.5 | 101255 | 100 | 3000 | 18.9957 | 61.2381 | 21.7701 | 0 | 7.2692 | FALSE | FALSE
2025-01-31 18:00 | 20.1 | 51.5 | 101295 | 100 | 3000 | 18.5693 | 63.364 | 20.7177 | 0 | 7.2692 | FALSE | FALSE
2025-01-31 19:00 | 19.25 | 56 | 101355 | 100 | 3000 | 18.2038 | 65.6567 | 20.4093 | 0 | 7.2692 | FALSE | FALSE
2025-01-31 20:00 | 18.7 | 58.5 | 101395 | 100 | 3000 | 17.9662 | 66.895 | 19.8704 | 0 | 7.2692 | FALSE | FALSE
2025-01-31 21:00 | 18.25 | 60 | 101415 | 100 | 3000 | 17.7709 | 67.6276 | 19.0803 | 0 | 7.2692 | FALSE | FALSE
2025-01-31 22:00 | 17.6 | 62 | 101415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-01-31 23:00 | 16.75 | 64.5 | 101390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-01 | 15.7 | 68.5 | 101355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-01 01:00 | 14.55 | 74 | 101335 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-01 02:00 | 13.3 | 81 | 101320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-01 03:00 | 12.1 | 87.5 | 101315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-01 04:00 | 12.1 | 85.5 | 101330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-01 05:00 | 12.45 | 81 | 101365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-01 06:00 | 11.95 | 82.5 | 101425 | 100 | 3000 | 14.9521 | 77.8255 | 7.3284 | 0 | 7.2692 | FALSE | FALSE
2025-02-01 07:00 | 12 | 81.5 | 101480 | 100 | 3000 | 14.9748 | 77.418 | 7.4166 | 0 | 7.2692 | FALSE | FALSE
2025-02-01 08:00 | 14.2 | 72 | 101535 | 100 | 3000 | 15.9769 | 73.2655 | 11.0994 | 0 | 7.2692 | FALSE | FALSE
2025-02-01 09:00 | 17.75 | 57 | 101595 | 100 | 3000 | 17.5533 | 66.1957 | 16.7808 | 0 | 7.2692 | FALSE | FALSE
2025-02-01 10:00 | 20.65 | 43 | 101615 | 100 | 3000 | 18.807 | 58.8763 | 21.2058 | 0 | 7.2692 | FALSE | FALSE
2025-02-01 11:00 | 22.6 | 31.5 | 101565 | 100 | 3000 | 19.6371 | 52.2903 | 24.0863 | 0 | 7.2692 | FALSE | FALSE
2025-02-01 12:00 | 23.9 | 23.5 | 101475 | 100 | 3000 | 20.1863 | 47.3667 | 25.963 | 0 | 7.2692 | FALSE | FALSE
2025-02-01 13:00 | 24.6 | 20.5 | 101375 | 100 | 3000 | 20.4793 | 45.3675 | 26.9399 | 0 | 7.2692 | FALSE | FALSE
2025-02-01 14:00 | 24.65 | 22.5 | 101280 | 100 | 3000 | 20.4974 | 46.5487 | 26.9675 | 0 | 7.2692 | FALSE | FALSE
2025-02-01 15:00 | 23.85 | 27.5 | 101235 | 100 | 3000 | 20.1613 | 49.7279 | 25.8025 | 0 | 7.2692 | FALSE | FALSE
2025-02-01 16:00 | 22.65 | 36 | 101220 | 100 | 3000 | 19.6544 | 54.8236 | 24.0496 | 0 | 7.2692 | FALSE | FALSE
2025-02-01 17:00 | 21.6 | 43.5 | 101225 | 100 | 3000 | 19.2089 | 59.0695 | 22.5063 | 0 | 7.2692 | FALSE | FALSE
2025-02-01 18:00 | 20.65 | 48 | 101270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-01 19:00 | 19.75 | 54.5 | 101345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-01 20:00 | 18.9 | 61 | 101415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-01 21:00 | 18.1 | 64 | 101435 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-01 22:00 | 17.25 | 65.5 | 101410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-01 23:00 | 16.3 | 69 | 101360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 | 15.25 | 73 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 01:00 | 14.3 | 75 | 101280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 02:00 | 13.75 | 73.5 | 101255 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 03:00 | 13.45 | 70 | 101240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 04:00 | 13.5 | 67 | 101240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 05:00 | 13.6 | 63.5 | 101270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 06:00 | 13.35 | 60.5 | 101330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 07:00 | 13.35 | 58.5 | 101390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 08:00 | 15.35 | 52 | 101460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 09:00 | 18.7 | 45.5 | 101515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 10:00 | 21.05 | 42.5 | 101525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 11:00 | 22.35 | 38.5 | 101470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 12:00 | 21.75 | 43.5 | 101395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 13:00 | 20.4 | 54 | 101350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 14:00 | 20.25 | 54 | 101315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 15:00 | 20.45 | 49.5 | 101300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 16:00 | 20.55 | 44 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 17:00 | 20.05 | 41.5 | 101340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 18:00 | 19.15 | 44.5 | 101390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 19:00 | 18.6 | 48 | 101455 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 20:00 | 18.45 | 49.5 | 101505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 21:00 | 18.4 | 50 | 101515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 22:00 | 18.15 | 52 | 101510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-02 23:00 | 17.85 | 53.5 | 101495 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-03 | 17.5 | 55 | 101445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-03 01:00 | 17.15 | 57 | 101400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-03 02:00 | 16.85 | 58.5 | 101375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-03 03:00 | 16.7 | 59 | 101355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-03 04:00 | 16.65 | 57 | 101365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-03 05:00 | 16.75 | 55 | 101420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-03 06:00 | 17 | 55.5 | 101480 | 100 | 3000 | 17.2241 | 65.5985 | 15.5961 | 0 | 7.2692 | FALSE | FALSE
2025-02-03 07:00 | 17.25 | 56.5 | 101520 | 100 | 3000 | 17.3341 | 66.0238 | 15.9923 | 0 | 7.2692 | FALSE | FALSE
2025-02-03 08:00 | 18.7 | 52 | 101560 | 100 | 3000 | 17.9672 | 63.6905 | 18.2436 | 0 | 7.2692 | FALSE | FALSE
2025-02-03 09:00 | 20.8 | 43.5 | 101600 | 100 | 3000 | 18.8706 | 59.1186 | 21.4216 | 0 | 7.2692 | FALSE | FALSE
2025-02-03 10:00 | 21.8 | 40 | 101610 | 100 | 3000 | 19.2952 | 57.1129 | 22.8981 | 0 | 7.2692 | FALSE | FALSE
2025-02-03 11:00 | 22.15 | 40 | 101550 | 100 | 3000 | 19.4422 | 57.0727 | 23.3888 | 0 | 7.2692 | FALSE | FALSE
2025-02-03 12:00 | 22.7 | 38 | 101450 | 100 | 3000 | 19.6736 | 55.9065 | 24.1625 | 0 | 7.2692 | FALSE | FALSE
2025-02-03 13:00 | 22.9 | 36.5 | 101350 | 100 | 3000 | 19.7582 | 55.0493 | 24.4318 | 0 | 7.2692 | FALSE | FALSE
2025-02-03 14:00 | 22.65 | 37.5 | 101280 | 100 | 3000 | 19.6532 | 55.653 | 24.0546 | 0 | 7.2692 | FALSE | FALSE
2025-02-03 15:00 | 22.45 | 38.5 | 101265 | 100 | 3000 | 19.5689 | 56.238 | 23.7607 | 0 | 7.2692 | FALSE | FALSE
2025-02-03 16:00 | 22.15 | 39.5 | 101275 | 100 | 3000 | 19.4426 | 56.8285 | 23.3289 | 0 | 7.2692 | FALSE | FALSE
2025-02-03 17:00 | 21.45 | 42 | 101295 | 100 | 3000 | 19.1466 | 58.2725 | 22.3121 | 0 | 7.2692 | FALSE | FALSE
2025-02-03 18:00 | 20.2 | 47 | 101340 | 100 | 3000 | 18.6137 | 61.0399 | 20.4695 | 0 | 7.2692 | FALSE | FALSE
2025-02-03 19:00 | 19.05 | 52.5 | 101415 | 100 | 3000 | 18.1184 | 63.9199 | 18.747 | 0 | 7.2692 | FALSE | FALSE
2025-02-03 20:00 | 18.35 | 58 | 101485 | 100 | 3000 | 17.8146 | 66.6497 | 18.3453 | 0 | 7.2692 | FALSE | FALSE
2025-02-03 21:00 | 17.8 | 64.5 | 101515 | 100 | 3000 | 17.5748 | 69.768 | 19.8613 | 0 | 7.2692 | FALSE | FALSE
2025-02-03 22:00 | 17.35 | 69.5 | 101530 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-03 23:00 | 17.1 | 69 | 101540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-04 | 17 | 63.5 | 101535 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-04 01:00 | 16.8 | 61.5 | 101520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-04 02:00 | 16.35 | 65 | 101510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-04 03:00 | 15.85 | 69.5 | 101510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-04 04:00 | 15.5 | 70 | 101520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-04 05:00 | 15.25 | 69 | 101550 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-04 06:00 | 14.5 | 72.5 | 101600 | 100 | 3000 | 16.1125 | 73.4416 | 11.5987 | 0 | 7.2692 | FALSE | FALSE
2025-02-04 07:00 | 13.75 | 74 | 101660 | 100 | 3000 | 15.7735 | 74.1372 | 10.3703 | 0 | 7.2692 | FALSE | FALSE
2025-02-04 08:00 | 15.15 | 66.5 | 101720 | 100 | 3000 | 16.4032 | 70.7722 | 12.6716 | 0 | 7.2692 | FALSE | FALSE
2025-02-04 09:00 | 18.25 | 55 | 101775 | 100 | 3000 | 17.7714 | 65.1704 | 17.586 | 0 | 7.2692 | FALSE | FALSE
2025-02-04 10:00 | 20.7 | 47.5 | 101790 | 100 | 3000 | 18.8262 | 61.2031 | 21.2975 | 0 | 7.2692 | FALSE | FALSE
2025-02-04 11:00 | 22 | 43.5 | 101740 | 100 | 3000 | 19.3768 | 58.9798 | 23.1973 | 0 | 7.2692 | FALSE | FALSE
2025-02-04 12:00 | 22.65 | 41 | 101650 | 100 | 3000 | 19.6502 | 57.5622 | 24.1202 | 0 | 7.2692 | FALSE | FALSE
2025-02-04 13:00 | 22.95 | 40 | 101555 | 100 | 3000 | 19.7758 | 56.9876 | 24.529 | 0 | 7.2692 | FALSE | FALSE
2025-02-04 14:00 | 22.7 | 41.5 | 101485 | 100 | 3000 | 19.6707 | 57.8545 | 24.1493 | 0 | 7.2692 | FALSE | FALSE
2025-02-04 15:00 | 22.05 | 44.5 | 101460 | 100 | 3000 | 19.3971 | 59.5527 | 23.2003 | 0 | 7.2692 | FALSE | FALSE
2025-02-04 16:00 | 21.5 | 47.5 | 101480 | 100 | 3000 | 19.1644 | 61.1964 | 22.9959 | 0 | 7.2692 | FALSE | FALSE
2025-02-04 17:00 | 20.75 | 51 | 101510 | 100 | 3000 | 18.8459 | 63.063 | 22.6673 | 0 | 7.2692 | FALSE | FALSE
2025-02-04 18:00 | 19.75 | 55.5 | 101545 | 100 | 3000 | 18.4184 | 65.3798 | 21.9009 | 0 | 7.2692 | FALSE | FALSE
2025-02-04 19:00 | 18.9 | 60 | 101600 | 100 | 3000 | 18.0523 | 67.6086 | 21.4465 | 0 | 7.2692 | FALSE | FALSE
2025-02-04 20:00 | 18.1 | 64 | 101640 | 100 | 3000 | 17.7054 | 69.5235 | 20.7124 | 0 | 7.2692 | FALSE | FALSE
2025-02-04 21:00 | 17.2 | 68.5 | 101645 | 100 | 3000 | 17.3124 | 71.6121 | 19.7043 | 0 | 7.2692 | FALSE | FALSE
2025-02-04 22:00 | 16.45 | 74 | 101630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-04 23:00 | 15.95 | 78.5 | 101600 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-05 | 15.4 | 81.5 | 101560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-05 01:00 | 14.8 | 83.5 | 101530 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-05 02:00 | 14.15 | 85 | 101490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-05 03:00 | 13.35 | 87 | 101450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-05 04:00 | 12.55 | 85.5 | 101425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-05 05:00 | 11.4 | 87 | 101430 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-05 06:00 | 10.45 | 91.5 | 101475 | 100 | 3000 | 14.2584 | 81.4674 | 4.7514 | 0 | 7.2692 | FALSE | FALSE
2025-02-05 07:00 | 11 | 88.5 | 101530 | 100 | 3000 | 14.514 | 80.2542 | 5.7083 | 0 | 7.2692 | FALSE | FALSE
2025-02-05 08:00 | 13.45 | 79.5 | 101590 | 100 | 3000 | 15.6389 | 76.4514 | 10.4613 | 0 | 7.2692 | FALSE | FALSE
2025-02-05 09:00 | 16.75 | 67.5 | 101625 | 100 | 3000 | 17.1146 | 71.141 | 17.4987 | 0 | 7.2692 | FALSE | FALSE
2025-02-05 10:00 | 19.15 | 58.5 | 101595 | 100 | 3000 | 18.1602 | 66.8725 | 21.5004 | 0 | 7.2692 | FALSE | FALSE
2025-02-05 11:00 | 20.6 | 53 | 101510 | 100 | 3000 | 18.7814 | 64.1068 | 23.3888 | 0 | 7.2692 | FALSE | FALSE
2025-02-05 12:00 | 21.75 | 47.5 | 101390 | 100 | 3000 | 19.2694 | 61.2002 | 23.8335 | 0 | 7.2692 | FALSE | FALSE
2025-02-05 13:00 | 22.75 | 42.5 | 101280 | 100 | 3000 | 19.6907 | 58.4311 | 24.1655 | 0 | 7.2692 | FALSE | FALSE
2025-02-05 14:00 | 23.35 | 40 | 101215 | 100 | 3000 | 19.9416 | 56.9928 | 25.0087 | 0 | 7.2692 | FALSE | FALSE
2025-02-05 15:00 | 22.85 | 46 | 101185 | 100 | 3000 | 19.7292 | 60.395 | 26.5171 | 0 | 7.2692 | FALSE | FALSE
2025-02-05 16:00 | 21.75 | 53 | 101170 | 100 | 3000 | 19.2659 | 64.1942 | 27.4339 | 0 | 7.2692 | FALSE | FALSE
2025-02-05 17:00 | 20.55 | 60.5 | 101175 | 100 | 3000 | 18.757 | 68.0384 | 27.8149 | 0 | 7.2692 | FALSE | FALSE
2025-02-05 18:00 | 19.1 | 72 | 101225 | 100 | 3000 | 18.1359 | 73.5981 | 28.9923 | 0 | 7.2692 | FALSE | FALSE
2025-02-05 19:00 | 18.1 | 78 | 101270 | 100 | 3000 | 17.7042 | 76.2736 | 28.2496 | 0 | 7.2692 | FALSE | FALSE
2025-02-05 20:00 | 17.55 | 79.5 | 101305 | 100 | 3000 | 17.4654 | 76.8481 | 26.7834 | 0 | 7.2692 | FALSE | FALSE
2025-02-05 21:00 | 17 | 80.5 | 101350 | 100 | 3000 | 17.2252 | 77.1868 | 25.0389 | 0 | 7.2692 | FALSE | FALSE
2025-02-05 22:00 | 16.3 | 82.5 | 101360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-05 23:00 | 15.45 | 85.5 | 101325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-06 | 14.55 | 88.5 | 101270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-06 01:00 | 13.75 | 91 | 101240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-06 02:00 | 13.25 | 93 | 101220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-06 03:00 | 13.25 | 93.5 | 101185 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-06 04:00 | 13.4 | 91.5 | 101190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-06 05:00 | 13.25 | 90.5 | 101210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-06 06:00 | 13.05 | 89.5 | 101220 | 100 | 3000 | 15.46 | 80.5965 | 13.0295 | 0 | 7.2692 | FALSE | FALSE
2025-02-06 07:00 | 13.75 | 87.5 | 101220 | 100 | 3000 | 15.7778 | 79.8131 | 15.034 | 0 | 7.2692 | FALSE | FALSE
2025-02-06 08:00 | 15.8 | 80 | 101215 | 100 | 3000 | 16.6958 | 76.7824 | 19.9272 | 0 | 7.2692 | FALSE | FALSE
2025-02-06 09:00 | 18.9 | 64.5 | 101230 | 100 | 3000 | 18.0514 | 69.8676 | 23.971 | 0 | 7.2692 | FALSE | FALSE
2025-02-06 10:00 | 22.35 | 47.5 | 101235 | 100 | 3000 | 19.5202 | 61.2156 | 25.8579 | 0 | 7.2692 | FALSE | FALSE
2025-02-06 11:00 | 24.85 | 32 | 101200 | 100 | 3000 | 20.5669 | 52.1718 | 27.1389 | 0 | 7.2692 | FALSE | FALSE
2025-02-06 12:00 | 26.05 | 24 | 101115 | 100 | 3000 | 21.0668 | 47.0735 | 28.8187 | 0 | 7.2692 | FALSE | FALSE
2025-02-06 13:00 | 26.65 | 23.5 | 101015 | 100 | 3000 | 21.3099 | 46.6251 | 29.5973 | 0 | 7.2692 | FALSE | FALSE
2025-02-06 14:00 | 27.05 | 24 | 100940 | 100 | 3000 | 21.4695 | 46.8614 | 30.0982 | 0 | 7.2692 | FALSE | FALSE
2025-02-06 15:00 | 27.1 | 24.5 | 100895 | 100 | 3000 | 21.4885 | 47.1758 | 30.1445 | 0 | 7.2692 | FALSE | FALSE
2025-02-06 16:00 | 26.85 | 28 | 100885 | 100 | 3000 | 21.3816 | 49.4542 | 29.771 | 0 | 7.2692 | FALSE | FALSE
2025-02-06 17:00 | 25.5 | 37 | 100920 | 100 | 3000 | 20.8237 | 55.1598 | 28.4063 | 0 | 7.2692 | FALSE | FALSE
2025-02-06 18:00 | 23.65 | 44 | 100975 | 100 | 3000 | 20.0613 | 59.2961 | 27.7568 | 0 | 7.2692 | FALSE | FALSE
2025-02-06 19:00 | 21.9 | 49.5 | 101025 | 100 | 3000 | 19.331 | 62.3236 | 25.6375 | 0 | 7.2692 | FALSE | FALSE
2025-02-06 20:00 | 20.25 | 65 | 101060 | 100 | 3000 | 18.6281 | 70.3264 | 29.4101 | 0 | 7.2692 | FALSE | FALSE
2025-02-06 21:00 | 19.25 | 80.5 | 101075 | 100 | 3000 | 18.1981 | 77.8662 | 34.4383 | 0 | 7.2692 | FALSE | FALSE
2025-02-06 22:00 | 18.65 | 85 | 101080 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-06 23:00 | 18.3 | 82.5 | 101065 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-07 | 17.85 | 80 | 101040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-07 01:00 | 17.3 | 82 | 101030 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-07 02:00 | 16.9 | 83 | 101015 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-07 03:00 | 16.7 | 80 | 100995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-07 04:00 | 17.15 | 75 | 101005 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-07 05:00 | 17.95 | 69 | 101040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-07 06:00 | 18.05 | 67.5 | 101105 | 100 | 3000 | 17.6834 | 71.2622 | 22.3969 | 0 | 7.2692 | FALSE | FALSE
2025-02-07 07:00 | 18.1 | 69 | 101195 | 100 | 3000 | 17.705 | 71.9746 | 23.4002 | 0 | 7.2692 | FALSE | FALSE
2025-02-07 08:00 | 19 | 67.5 | 101275 | 100 | 3000 | 18.0939 | 71.3521 | 26.0501 | 0 | 7.2692 | FALSE | FALSE
2025-02-07 09:00 | 20.6 | 63.5 | 101350 | 100 | 3000 | 18.7768 | 69.5832 | 29.8631 | 0 | 7.2692 | FALSE | FALSE
2025-02-07 10:00 | 22.15 | 58 | 101370 | 100 | 3000 | 19.4292 | 66.9368 | 32.2281 | 0 | 7.2692 | FALSE | FALSE
2025-02-07 11:00 | 23.3 | 53 | 101305 | 100 | 3000 | 19.9084 | 64.3609 | 33.0356 | 0 | 7.2692 | FALSE | FALSE
2025-02-07 12:00 | 24.4 | 49.5 | 101195 | 100 | 3000 | 20.3612 | 62.5283 | 34.4394 | 0 | 7.2692 | FALSE | FALSE
2025-02-07 13:00 | 25.5 | 45.5 | 101075 | 100 | 3000 | 20.8106 | 60.3132 | 35.2108 | 0 | 7.2692 | FALSE | FALSE
2025-02-07 14:00 | 26.45 | 40.5 | 100965 | 100 | 3000 | 21.1986 | 57.3458 | 34.3462 | 0 | 7.2692 | FALSE | FALSE
2025-02-07 15:00 | 27.1 | 36 | 100895 | 100 | 3000 | 21.4653 | 54.5413 | 32.6112 | 0 | 7.2692 | FALSE | FALSE
2025-02-07 16:00 | 27.1 | 37 | 100880 | 100 | 3000 | 21.4633 | 55.1823 | 33.4748 | 0 | 7.2692 | FALSE | FALSE
2025-02-07 17:00 | 26.35 | 43 | 100885 | 100 | 3000 | 21.1543 | 58.906 | 36.0811 | 0 | 7.2692 | FALSE | FALSE
2025-02-07 18:00 | 24.3 | 53 | 100915 | 100 | 3000 | 20.3164 | 64.5881 | 36.6624 | 0 | 7.2692 | FALSE | FALSE
2025-02-07 19:00 | 22.3 | 66.5 | 100955 | 100 | 3000 | 19.485 | 71.6658 | 38.4606 | 0 | 7.2692 | FALSE | FALSE
2025-02-07 20:00 | 21.45 | 74.5 | 100970 | 100 | 3000 | 19.1273 | 75.6596 | 40.1698 | 0 | 7.2692 | FALSE | FALSE
2025-02-07 21:00 | 20.8 | 76.5 | 100955 | 100 | 3000 | 18.8549 | 76.4464 | 38.6619 | 0 | 7.2692 | FALSE | FALSE
2025-02-07 22:00 | 20.2 | 78.5 | 100935 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-07 23:00 | 19.8 | 78.5 | 100915 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-08 | 19.45 | 77.5 | 100880 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-08 01:00 | 19.1 | 76.5 | 100850 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-08 02:00 | 18.95 | 71 | 100820 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-08 03:00 | 18.95 | 66 | 100805 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-08 04:00 | 19.15 | 65 | 100825 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-08 05:00 | 19.55 | 65 | 100870 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-08 06:00 | 19.8 | 66.5 | 100940 | 100 | 3000 | 18.4364 | 71.0226 | 28.5555 | 0 | 7.2692 | FALSE | FALSE
2025-02-08 07:00 | 20 | 68.5 | 101035 | 100 | 3000 | 18.5208 | 72.0668 | 30.5307 | 0 | 7.2692 | FALSE | FALSE
2025-02-08 08:00 | 20.85 | 67.5 | 101120 | 100 | 3000 | 18.8802 | 71.7487 | 33.3014 | 0 | 7.2692 | FALSE | FALSE
2025-02-08 09:00 | 22.25 | 64 | 101160 | 100 | 3000 | 19.4662 | 70.2605 | 36.6061 | 0 | 7.2692 | FALSE | FALSE
2025-02-08 10:00 | 23.8 | 59.5 | 101155 | 100 | 3000 | 20.1059 | 68.1993 | 39.5674 | 0 | 7.2692 | FALSE | FALSE
2025-02-08 11:00 | 25.2 | 54.5 | 101085 | 100 | 3000 | 20.6769 | 65.6848 | 41.2002 | 0 | 7.2692 | FALSE | FALSE
2025-02-08 12:00 | 26.25 | 50.5 | 100985 | 100 | 3000 | 21.1013 | 63.5453 | 41.9328 | 0 | 7.2692 | FALSE | FALSE
2025-02-08 13:00 | 27.4 | 46 | 100890 | 100 | 3000 | 21.5625 | 61.001 | 42.3082 | 0 | 7.2692 | FALSE | FALSE
2025-02-08 14:00 | 26.8 | 52.5 | 100830 | 100 | 3000 | 21.3142 | 64.9797 | 45.6414 | 0 | 7.2692 | FALSE | FALSE
2025-02-08 15:00 | 24.55 | 66.5 | 100830 | 100 | 3000 | 20.4002 | 72.588 | 47.7162 | 0 | 7.2692 | FALSE | FALSE
2025-02-08 16:00 | 23.2 | 73.5 | 100865 | 100 | 3000 | 19.8477 | 75.9377 | 47.0039 | 0 | 7.2692 | FALSE | FALSE
2025-02-08 17:00 | 22.1 | 80.5 | 100910 | 100 | 3000 | 19.3921 | 79.2039 | 46.8867 | 0 | 7.2692 | FALSE | FALSE
2025-02-08 18:00 | 21.1 | 87 | 100960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-08 19:00 | 20.55 | 90 | 101025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-08 20:00 | 20.05 | 91.5 | 101090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-08 21:00 | 19.45 | 92 | 101125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-08 22:00 | 18.8 | 92 | 101125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-08 23:00 | 18.25 | 92 | 101115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 | 17.8 | 92 | 101090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 01:00 | 17.45 | 91.5 | 101065 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 02:00 | 17.3 | 90.5 | 101045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 03:00 | 17.3 | 89 | 101025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 04:00 | 18.15 | 85 | 101015 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 05:00 | 18.8 | 81.5 | 101030 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 06:00 | 18.15 | 81.5 | 101075 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 07:00 | 18.4 | 79 | 101135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 08:00 | 19.55 | 72.5 | 101220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 09:00 | 20.4 | 67 | 101295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 10:00 | 21.15 | 63 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 11:00 | 21.6 | 59.5 | 101270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 12:00 | 21.9 | 56.5 | 101210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 13:00 | 22.25 | 51.5 | 101150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 14:00 | 22.35 | 46 | 101095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 15:00 | 22 | 45 | 101080 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 16:00 | 21.45 | 45 | 101095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 17:00 | 20.55 | 48.5 | 101115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 18:00 | 19.5 | 54 | 101160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 19:00 | 18.9 | 56.5 | 101210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 20:00 | 18.45 | 60 | 101240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 21:00 | 18.05 | 63.5 | 101250 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 22:00 | 17.7 | 67 | 101245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-09 23:00 | 17.3 | 70.5 | 101230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-10 | 16.85 | 73.5 | 101210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-10 01:00 | 16.4 | 76.5 | 101205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-10 02:00 | 16.05 | 79.5 | 101195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-10 03:00 | 15.8 | 81.5 | 101190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-10 04:00 | 15.9 | 81.5 | 101215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-10 05:00 | 16.1 | 81 | 101260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-10 06:00 | 16.05 | 81.5 | 101320 | 100 | 3000 | 16.8068 | 77.4719 | 21.6537 | 0 | 7.2692 | FALSE | FALSE
2025-02-10 07:00 | 16.6 | 79.5 | 101400 | 100 | 3000 | 17.0494 | 76.6469 | 22.9074 | 0 | 7.2692 | FALSE | FALSE
2025-02-10 08:00 | 18.25 | 71 | 101490 | 100 | 3000 | 17.7698 | 72.9193 | 25.0765 | 0 | 7.2692 | FALSE | FALSE
2025-02-10 09:00 | 19.65 | 63.5 | 101550 | 100 | 3000 | 18.3733 | 69.4141 | 26.2485 | 0 | 7.2692 | FALSE | FALSE
2025-02-10 10:00 | 20.3 | 60.5 | 101555 | 100 | 3000 | 18.651 | 67.9643 | 26.9047 | 0 | 7.2692 | FALSE | FALSE
2025-02-10 11:00 | 20.8 | 57.5 | 101520 | 100 | 3000 | 18.864 | 66.4647 | 26.9062 | 0 | 7.2692 | FALSE | FALSE
2025-02-10 12:00 | 21.1 | 55 | 101465 | 100 | 3000 | 18.9918 | 65.1817 | 26.4191 | 0 | 7.2692 | FALSE | FALSE
2025-02-10 13:00 | 21.2 | 53 | 101395 | 100 | 3000 | 19.035 | 64.1366 | 25.4975 | 0 | 7.2692 | FALSE | FALSE
2025-02-10 14:00 | 21.1 | 52.5 | 101340 | 100 | 3000 | 18.9931 | 63.8742 | 24.8215 | 0 | 7.2692 | FALSE | FALSE
2025-02-10 15:00 | 20.75 | 54.5 | 101315 | 100 | 3000 | 18.8443 | 64.9155 | 24.8388 | 0 | 7.2692 | FALSE | FALSE
2025-02-10 16:00 | 20.15 | 58 | 101325 | 100 | 3000 | 18.5883 | 66.6929 | 24.8226 | 0 | 7.2692 | FALSE | FALSE
2025-02-10 17:00 | 19.3 | 63 | 101350 | 100 | 3000 | 18.2237 | 69.1484 | 24.627 | 0 | 7.2692 | FALSE | FALSE
2025-02-10 18:00 | 18.35 | 69.5 | 101375 | 100 | 3000 | 17.8133 | 72.2244 | 24.6458 | 0 | 7.2692 | FALSE | FALSE
2025-02-10 19:00 | 17.7 | 73.5 | 101420 | 100 | 3000 | 17.5308 | 74.0358 | 24.244 | 0 | 7.2692 | FALSE | FALSE
2025-02-10 20:00 | 17.2 | 75 | 101475 | 100 | 3000 | 17.3126 | 74.6584 | 23.043 | 0 | 7.2692 | FALSE | FALSE
2025-02-10 21:00 | 16.55 | 77 | 101495 | 100 | 3000 | 17.0272 | 75.4887 | 21.4674 | 0 | 7.2692 | FALSE | FALSE
2025-02-10 22:00 | 15.9 | 79.5 | 101495 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-10 23:00 | 15.15 | 83.5 | 101485 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-11 | 14.1 | 88.5 | 101465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-11 01:00 | 13.2 | 91.5 | 101465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-11 02:00 | 12.8 | 91.5 | 101455 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-11 03:00 | 12.75 | 91 | 101440 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-11 04:00 | 13.15 | 87 | 101435 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-11 05:00 | 13.35 | 84 | 101450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-11 06:00 | 12.75 | 87 | 101505 | 100 | 3000 | 15.3219 | 79.5429 | 10.798 | 0 | 7.2692 | FALSE | FALSE
2025-02-11 07:00 | 12.9 | 86 | 101570 | 100 | 3000 | 15.3902 | 79.1283 | 10.9876 | 0 | 7.2692 | FALSE | FALSE
2025-02-11 08:00 | 15.15 | 76.5 | 101635 | 100 | 3000 | 16.4054 | 75.1435 | 15.7223 | 0 | 7.2692 | FALSE | FALSE
2025-02-11 09:00 | 18.25 | 65 | 101680 | 100 | 3000 | 17.7704 | 70.0069 | 21.8177 | 0 | 7.2692 | FALSE | FALSE
2025-02-11 10:00 | 20.6 | 56 | 101680 | 100 | 3000 | 18.7801 | 65.6484 | 25.2572 | 0 | 7.2692 | FALSE | FALSE
2025-02-11 11:00 | 22.4 | 47.5 | 101625 | 100 | 3000 | 19.541 | 61.174 | 26.0651 | 0 | 7.2692 | FALSE | FALSE
2025-02-11 12:00 | 24.05 | 40 | 101530 | 100 | 3000 | 20.2297 | 56.924 | 26.1896 | 0 | 7.2692 | FALSE | FALSE
2025-02-11 13:00 | 25 | 38 | 101430 | 100 | 3000 | 20.6197 | 55.7249 | 27.6863 | 0 | 7.2692 | FALSE | FALSE
2025-02-11 14:00 | 25 | 41 | 101345 | 100 | 3000 | 20.6156 | 57.5305 | 30.0145 | 0 | 7.2692 | FALSE | FALSE
2025-02-11 15:00 | 24.45 | 42.5 | 101300 | 100 | 3000 | 20.3902 | 58.4094 | 29.3445 | 0 | 7.2692 | FALSE | FALSE
2025-02-11 16:00 | 23.85 | 45.5 | 101280 | 100 | 3000 | 20.1417 | 60.1345 | 29.5606 | 0 | 7.2692 | FALSE | FALSE
2025-02-11 17:00 | 22.7 | 53.5 | 101285 | 100 | 3000 | 19.6607 | 64.5551 | 31.1996 | 0 | 7.2692 | FALSE | FALSE
2025-02-11 18:00 | 21.2 | 61.5 | 101320 | 100 | 3000 | 19.0303 | 68.6485 | 30.9078 | 0 | 7.2692 | FALSE | FALSE
2025-02-11 19:00 | 20.2 | 66.5 | 101370 | 100 | 3000 | 18.6063 | 71.0502 | 30.1399 | 0 | 7.2692 | FALSE | FALSE
2025-02-11 20:00 | 19.45 | 70.5 | 101410 | 100 | 3000 | 18.286 | 72.9088 | 29.5404 | 0 | 7.2692 | FALSE | FALSE
2025-02-11 21:00 | 18.75 | 73.5 | 101420 | 100 | 3000 | 17.9853 | 74.2339 | 28.4381 | 0 | 7.2692 | FALSE | FALSE
2025-02-11 22:00 | 18.15 | 70.5 | 101420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-11 23:00 | 17.45 | 64 | 101410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-12 | 16.55 | 62 | 101380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-12 01:00 | 16.1 | 64.5 | 101350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-12 02:00 | 16.3 | 64.5 | 101330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-12 03:00 | 16.5 | 59.5 | 101305 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-12 04:00 | 16.55 | 57.5 | 101305 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-12 05:00 | 16.35 | 58.5 | 101340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-12 06:00 | 15.9 | 57.5 | 101395 | 100 | 3000 | 16.7368 | 66.7163 | 13.84 | 0 | 7.2692 | FALSE | FALSE
2025-02-12 07:00 | 16.35 | 55 | 101455 | 100 | 3000 | 16.9366 | 65.4899 | 14.567 | 0 | 7.2692 | FALSE | FALSE
2025-02-12 08:00 | 18.7 | 50.5 | 101510 | 100 | 3000 | 17.9674 | 62.9607 | 18.2383 | 0 | 7.2692 | FALSE | FALSE
2025-02-12 09:00 | 22.05 | 44 | 101550 | 100 | 3000 | 19.3974 | 59.27 | 23.2234 | 0 | 7.2692 | FALSE | FALSE
2025-02-12 10:00 | 24.65 | 38.5 | 101565 | 100 | 3000 | 20.4767 | 56.0196 | 26.9791 | 0 | 7.2692 | FALSE | FALSE
2025-02-12 11:00 | 26.9 | 38 | 101520 | 100 | 3000 | 21.3818 | 55.7467 | 33.7909 | 0 | 7.2692 | FALSE | FALSE
2025-02-12 12:00 | 29 | 33.5 | 101415 | 100 | 3000 | 22.2152 | 52.9269 | 36.4003 | 0 | 7.2692 | FALSE | FALSE
2025-02-12 13:00 | 30 | 27 | 101325 | 100 | 3000 | 22.6205 | 48.4645 | 33.938 | 0 | 7.2692 | FALSE | FALSE
2025-02-12 14:00 | 29.8 | 28.5 | 101270 | 100 | 3000 | 22.5388 | 49.5222 | 33.9353 | 0 | 7.2692 | FALSE | FALSE
2025-02-12 15:00 | 28.85 | 34 | 101230 | 100 | 3000 | 22.1558 | 53.2736 | 36.3707 | 0 | 7.2692 | FALSE | FALSE
2025-02-12 16:00 | 28.2 | 38.5 | 101185 | 100 | 3000 | 21.8917 | 56.2237 | 38.4375 | 0 | 7.2692 | FALSE | FALSE
2025-02-12 17:00 | 26.35 | 45 | 101170 | 100 | 3000 | 21.1507 | 60.1254 | 37.7822 | 0 | 7.2692 | FALSE | FALSE
2025-02-12 18:00 | 23.9 | 54.5 | 101210 | 100 | 3000 | 20.1521 | 65.3417 | 36.3185 | 0 | 7.2692 | FALSE | FALSE
2025-02-12 19:00 | 22.9 | 60 | 101280 | 100 | 3000 | 19.7375 | 68.2162 | 36.4386 | 0 | 7.2692 | FALSE | FALSE
2025-02-12 20:00 | 22.55 | 57 | 101340 | 100 | 3000 | 19.5957 | 66.4648 | 33.0505 | 0 | 7.2692 | FALSE | FALSE
2025-02-12 21:00 | 21.9 | 54.5 | 101350 | 100 | 3000 | 19.3275 | 64.9993 | 28.9772 | 0 | 7.2692 | FALSE | FALSE
2025-02-12 22:00 | 21 | 56 | 101335 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-12 23:00 | 20.25 | 55 | 101315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-13 | 19.55 | 55.5 | 101295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-13 01:00 | 19.2 | 59 | 101260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-13 02:00 | 19.1 | 63 | 101215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-13 03:00 | 19.3 | 62 | 101200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-13 04:00 | 19.15 | 59.5 | 101215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-13 05:00 | 18.6 | 60 | 101260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-13 06:00 | 18.2 | 61 | 101320 | 100 | 3000 | 17.7491 | 68.1216 | 19.4414 | 0 | 7.2692 | FALSE | FALSE
2025-02-13 07:00 | 19.1 | 59 | 101390 | 100 | 3000 | 18.1386 | 67.1437 | 21.5958 | 0 | 7.2692 | FALSE | FALSE
2025-02-13 08:00 | 21.75 | 51 | 101455 | 100 | 3000 | 19.2671 | 63.0833 | 26.1434 | 0 | 7.2692 | FALSE | FALSE
2025-02-13 09:00 | 24.7 | 42 | 101490 | 100 | 3000 | 20.4925 | 58.1023 | 29.8161 | 0 | 7.2692 | FALSE | FALSE
2025-02-13 10:00 | 27.1 | 37.5 | 101500 | 100 | 3000 | 21.462 | 55.4417 | 34.0046 | 0 | 7.2692 | FALSE | FALSE
2025-02-13 11:00 | 28.9 | 35.5 | 101455 | 100 | 3000 | 22.1711 | 54.2699 | 37.9855 | 0 | 7.2692 | FALSE | FALSE
2025-02-13 12:00 | 30.2 | 33.5 | 101350 | 100 | 3000 | 22.6764 | 53.0323 | 40.1626 | 0 | 7.2692 | FALSE | FALSE
2025-02-13 13:00 | 30.95 | 32.5 | 101240 | 100 | 3000 | 22.9645 | 52.4141 | 41.4839 | 0 | 7.2692 | FALSE | FALSE
2025-02-13 14:00 | 31.2 | 32 | 101170 | 100 | 3000 | 23.0607 | 52.0876 | 41.7295 | 0 | 7.2692 | FALSE | FALSE
2025-02-13 15:00 | 30.2 | 35 | 101135 | 100 | 3000 | 22.6717 | 54.1076 | 41.6277 | 0 | 7.2692 | FALSE | FALSE
2025-02-13 16:00 | 28.4 | 38.5 | 101160 | 100 | 3000 | 21.9695 | 56.2522 | 39.0962 | 0 | 7.2692 | FALSE | FALSE
2025-02-13 17:00 | 26.4 | 45.5 | 101230 | 100 | 3000 | 21.1696 | 60.4403 | 38.3814 | 0 | 7.2692 | FALSE | FALSE
2025-02-13 18:00 | 24.5 | 55.5 | 101290 | 100 | 3000 | 20.3942 | 66.0619 | 39.3288 | 0 | 7.2692 | FALSE | FALSE
2025-02-13 19:00 | 23.65 | 58.5 | 101325 | 100 | 3000 | 20.0459 | 67.5648 | 38.2821 | 0 | 7.2692 | FALSE | FALSE
2025-02-13 20:00 | 23.65 | 56 | 101320 | 100 | 3000 | 20.0486 | 66.1355 | 36.4813 | 0 | 7.2692 | FALSE | FALSE
2025-02-13 21:00 | 23.85 | 53 | 101305 | 100 | 3000 | 20.1334 | 64.4567 | 35.0492 | 0 | 7.2692 | FALSE | FALSE
2025-02-13 22:00 | 23.85 | 51 | 101280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-13 23:00 | 23.25 | 50.5 | 101245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-14 | 22.55 | 51.5 | 101230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-14 01:00 | 22.05 | 53.5 | 101210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-14 02:00 | 21.05 | 57 | 101185 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-14 03:00 | 20.3 | 59.5 | 101175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-14 04:00 | 21 | 67 | 101235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-14 05:00 | 21.65 | 77.5 | 101335 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-14 06:00 | 21.15 | 81.5 | 101410 | 100 | 3000 | 18.9985 | 79.1719 | 43.3266 | 0 | 7.2692 | FALSE | FALSE
2025-02-14 07:00 | 21.45 | 77 | 101480 | 100 | 3000 | 19.1258 | 76.9312 | 41.8048 | 0 | 7.2692 | FALSE | FALSE
2025-02-14 08:00 | 23.15 | 66 | 101530 | 100 | 3000 | 19.8345 | 71.6299 | 41.6314 | 0 | 7.2692 | FALSE | FALSE
2025-02-14 09:00 | 25 | 55 | 101565 | 100 | 3000 | 20.596 | 65.8769 | 40.8873 | 0 | 7.2692 | FALSE | FALSE
2025-02-14 10:00 | 26.35 | 46.5 | 101570 | 100 | 3000 | 21.1479 | 61.021 | 39.0833 | 0 | 7.2692 | FALSE | FALSE
2025-02-14 11:00 | 27.5 | 38.5 | 101510 | 100 | 3000 | 21.6177 | 56.1147 | 36.1823 | 0 | 7.2692 | FALSE | FALSE
2025-02-14 12:00 | 28.15 | 33.5 | 101410 | 100 | 3000 | 21.8841 | 52.8929 | 33.756 | 0 | 7.2692 | FALSE | FALSE
2025-02-14 13:00 | 28 | 34 | 101335 | 100 | 3000 | 21.8242 | 53.226 | 33.7326 | 0 | 7.2692 | FALSE | FALSE
2025-02-14 14:00 | 27.1 | 38 | 101285 | 100 | 3000 | 21.4611 | 55.7823 | 34.4034 | 0 | 7.2692 | FALSE | FALSE
2025-02-14 15:00 | 26.3 | 42.5 | 101230 | 100 | 3000 | 21.1352 | 58.5537 | 35.5464 | 0 | 7.2692 | FALSE | FALSE
2025-02-14 16:00 | 25.75 | 49.5 | 101230 | 100 | 3000 | 20.9043 | 62.7809 | 39.3175 | 0 | 7.2692 | FALSE | FALSE
2025-02-14 17:00 | 24.55 | 59 | 101270 | 100 | 3000 | 20.4099 | 68.1362 | 42.1501 | 0 | 7.2692 | FALSE | FALSE
2025-02-14 18:00 | 23.35 | 65.5 | 101295 | 100 | 3000 | 19.9165 | 71.4496 | 42.0738 | 0 | 7.2692 | FALSE | FALSE
2025-02-14 19:00 | 22.45 | 69.5 | 101325 | 100 | 3000 | 19.5445 | 73.3248 | 41.1234 | 0 | 7.2692 | FALSE | FALSE
2025-02-14 20:00 | 21.7 | 71.5 | 101360 | 100 | 3000 | 19.2331 | 74.1139 | 39.3237 | 0 | 7.2692 | FALSE | FALSE
2025-02-14 21:00 | 21.1 | 73.5 | 101375 | 100 | 3000 | 18.982 | 74.9462 | 38.0916 | 0 | 7.2692 | FALSE | FALSE
2025-02-14 22:00 | 20.4 | 77.5 | 101370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-14 23:00 | 19.75 | 82.5 | 101355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-15 | 19.25 | 87.5 | 101315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-15 01:00 | 18.85 | 92.5 | 101270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-15 02:00 | 18.55 | 96.5 | 101230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-15 03:00 | 18.35 | 98 | 101185 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-15 04:00 | 18.6 | 96.5 | 101150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-15 05:00 | 18.6 | 96 | 101170 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-15 06:00 | 18.2 | 97.5 | 101230 | 100 | 3000 | 17.7457 | 85.6346 | 39.1432 | 0 | 7.2692 | FALSE | FALSE
2025-02-15 07:00 | 18.85 | 96.5 | 101310 | 100 | 3000 | 18.0241 | 85.5109 | 41.6393 | 0 | 7.2692 | FALSE | FALSE
2025-02-15 08:00 | 20.35 | 91 | 101370 | 100 | 3000 | 18.6599 | 83.6539 | 45.4943 | 0 | 7.2692 | FALSE | FALSE
2025-02-15 09:00 | 21.85 | 82 | 101380 | 100 | 3000 | 19.2882 | 79.8198 | 46.7802 | 0 | 7.2692 | FALSE | FALSE
2025-02-15 10:00 | 23 | 74 | 101355 | 100 | 3000 | 19.7658 | 76.0623 | 46.5309 | 0 | 7.2692 | FALSE | FALSE
2025-02-15 11:00 | 23.6 | 70.5 | 101300 | 100 | 3000 | 20.013 | 74.3944 | 46.6616 | 0 | 7.2692 | FALSE | FALSE
2025-02-15 12:00 | 24 | 68.5 | 101230 | 100 | 3000 | 20.1768 | 73.4485 | 46.9178 | 0 | 7.2692 | FALSE | FALSE
2025-02-15 13:00 | 24.25 | 67 | 101155 | 100 | 3000 | 20.2792 | 72.7054 | 46.8663 | 0 | 7.2692 | FALSE | FALSE
2025-02-15 14:00 | 24.6 | 64 | 101080 | 100 | 3000 | 20.4235 | 71.1156 | 46.0826 | 0 | 7.2692 | FALSE | FALSE
2025-02-15 15:00 | 24.9 | 60 | 101020 | 100 | 3000 | 20.549 | 68.8777 | 44.2628 | 0 | 7.2692 | FALSE | FALSE
2025-02-15 16:00 | 24.25 | 62.5 | 101040 | 100 | 3000 | 20.2846 | 70.1 | 43.5347 | 0 | 7.2692 | FALSE | FALSE
2025-02-15 17:00 | 22.85 | 72.5 | 101105 | 100 | 3000 | 19.706 | 75.1803 | 44.8279 | 0 | 7.2692 | FALSE | FALSE
2025-02-15 18:00 | 21.95 | 81 | 101130 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-15 19:00 | 21.45 | 85 | 101145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-15 20:00 | 20.8 | 87 | 101190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-15 21:00 | 20.4 | 88 | 101235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-15 22:00 | 20.35 | 89.5 | 101265 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-15 23:00 | 20.1 | 89.5 | 101260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 | 19.85 | 88 | 101215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 01:00 | 19.65 | 85.5 | 101165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 02:00 | 19.65 | 83.5 | 101135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 03:00 | 19.75 | 83.5 | 101095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 04:00 | 19.7 | 87 | 101055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 05:00 | 19.7 | 90.5 | 101070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 06:00 | 19.6 | 90.5 | 101130 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 07:00 | 20.05 | 85.5 | 101200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 08:00 | 21.45 | 75 | 101270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 09:00 | 23.1 | 66 | 101320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 10:00 | 24.1 | 63.5 | 101330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 11:00 | 24.25 | 64 | 101295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 12:00 | 24.85 | 60.5 | 101215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 13:00 | 25.35 | 57 | 101150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 14:00 | 24.9 | 58 | 101100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 15:00 | 24.45 | 60.5 | 101050 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 16:00 | 24.6 | 54.5 | 101000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 17:00 | 24.75 | 47.5 | 100995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 18:00 | 24.1 | 49.5 | 100995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 19:00 | 23.05 | 53 | 101000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 20:00 | 22.4 | 55.5 | 101100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 21:00 | 22 | 59.5 | 101160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 22:00 | 21.2 | 68.5 | 101160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-16 23:00 | 20.8 | 75.5 | 101140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-17 | 20.5 | 81.5 | 101105 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-17 01:00 | 20.1 | 88 | 101085 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-17 02:00 | 19.9 | 90.5 | 101060 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-17 03:00 | 19.5 | 91.5 | 101055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-17 04:00 | 20.1 | 85 | 101040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-17 05:00 | 20.9 | 77 | 101010 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-17 06:00 | 20.65 | 74 | 101075 | 100 | 3000 | 18.7931 | 75.0764 | 36.4994 | 0 | 7.2692 | FALSE | FALSE
2025-02-17 07:00 | 20.95 | 68.5 | 101165 | 100 | 3000 | 18.9217 | 72.2945 | 34.3284 | 0 | 7.2692 | FALSE | FALSE
2025-02-17 08:00 | 22.1 | 63.5 | 101205 | 100 | 3000 | 19.4045 | 69.9407 | 35.6849 | 0 | 7.2692 | FALSE | FALSE
2025-02-17 09:00 | 24.7 | 57 | 101235 | 100 | 3000 | 20.4728 | 67.0093 | 41.2214 | 0 | 7.2692 | FALSE | FALSE
2025-02-17 10:00 | 27.4 | 48 | 101225 | 100 | 3000 | 21.5581 | 62.2562 | 44.1015 | 0 | 7.2692 | FALSE | FALSE
2025-02-17 11:00 | 29.1 | 40.5 | 101175 | 100 | 3000 | 22.2346 | 57.7156 | 43.331 | 0 | 7.2692 | FALSE | FALSE
2025-02-17 12:00 | 30.2 | 36.5 | 101105 | 100 | 3000 | 22.6668 | 55.1656 | 43.1265 | 0 | 7.2692 | FALSE | FALSE
2025-02-17 13:00 | 29.65 | 39 | 101045 | 100 | 3000 | 22.4496 | 56.8121 | 43.7438 | 0 | 7.2692 | FALSE | FALSE
2025-02-17 14:00 | 28.95 | 40.5 | 100985 | 100 | 3000 | 22.177 | 57.7029 | 42.7819 | 0 | 7.2692 | FALSE | FALSE
2025-02-17 15:00 | 28.45 | 39.5 | 100955 | 100 | 3000 | 21.9865 | 56.9448 | 40.148 | 0 | 7.2692 | FALSE | FALSE
2025-02-17 16:00 | 27.65 | 40.5 | 100960 | 100 | 3000 | 21.6723 | 57.4828 | 38.359 | 0 | 7.2692 | FALSE | FALSE
2025-02-17 17:00 | 26.7 | 42.5 | 100975 | 100 | 3000 | 21.2941 | 58.6299 | 36.8701 | 0 | 7.2692 | FALSE | FALSE
2025-02-17 18:00 | 25.45 | 44.5 | 101000 | 100 | 3000 | 20.7921 | 59.7074 | 34.2333 | 0 | 7.2692 | FALSE | FALSE
2025-02-17 19:00 | 24.3 | 49.5 | 101105 | 100 | 3000 | 20.3206 | 62.5224 | 34.0713 | 0 | 7.2692 | FALSE | FALSE
2025-02-17 20:00 | 24 | 53.5 | 101190 | 100 | 3000 | 20.1939 | 64.7872 | 35.9553 | 0 | 7.2692 | FALSE | FALSE
2025-02-17 21:00 | 23.7 | 55 | 101205 | 100 | 3000 | 20.0701 | 65.5862 | 35.9345 | 0 | 7.2692 | FALSE | FALSE
2025-02-17 22:00 | 23 | 58 | 101205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-17 23:00 | 22.55 | 62 | 101155 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-18 | 21.5 | 68 | 101135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-18 01:00 | 20.5 | 73 | 101115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-18 02:00 | 19.65 | 77.5 | 101090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-18 03:00 | 19 | 79.5 | 101070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-18 04:00 | 19.15 | 84.5 | 101055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-18 05:00 | 19.45 | 89.5 | 101075 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-18 06:00 | 19.55 | 88 | 101125 | 100 | 3000 | 18.3237 | 81.7209 | 40.051 | 0 | 7.2692 | FALSE | FALSE
2025-02-18 07:00 | 20.05 | 84.5 | 101210 | 100 | 3000 | 18.5363 | 80.196 | 40.2499 | 0 | 7.2692 | FALSE | FALSE
2025-02-18 08:00 | 21.6 | 76 | 101295 | 100 | 3000 | 19.1887 | 76.4876 | 41.7977 | 0 | 7.2692 | FALSE | FALSE
2025-02-18 09:00 | 22.8 | 69.5 | 101360 | 100 | 3000 | 19.6881 | 73.4636 | 42.5865 | 0 | 7.2692 | FALSE | FALSE
2025-02-18 10:00 | 23.4 | 65 | 101380 | 100 | 3000 | 19.9374 | 71.1765 | 41.9335 | 0 | 7.2692 | FALSE | FALSE
2025-02-18 11:00 | 24.45 | 55.5 | 101310 | 100 | 3000 | 20.374 | 66.0464 | 39.1412 | 0 | 7.2692 | FALSE | FALSE
2025-02-18 12:00 | 26.05 | 43.5 | 101215 | 100 | 3000 | 21.0339 | 59.1454 | 35.515 | 0 | 7.2692 | FALSE | FALSE
2025-02-18 13:00 | 26.65 | 40.5 | 101165 | 100 | 3000 | 21.278 | 57.3442 | 35.041 | 0 | 7.2692 | FALSE | FALSE
2025-02-18 14:00 | 25.15 | 56.5 | 101140 | 100 | 3000 | 20.654 | 66.8638 | 42.5686 | 0 | 7.2692 | FALSE | FALSE
2025-02-18 15:00 | 24.05 | 69.5 | 101145 | 100 | 3000 | 20.1957 | 74.0588 | 47.8478 | 0 | 7.2692 | FALSE | FALSE
2025-02-18 16:00 | 23.45 | 72 | 101245 | 100 | 3000 | 19.9506 | 75.1777 | 47.0742 | 0 | 7.2692 | FALSE | FALSE
2025-02-18 17:00 | 22.7 | 75.5 | 101290 | 100 | 3000 | 19.6421 | 76.7487 | 46.2418 | 0 | 7.2692 | FALSE | FALSE
2025-02-18 18:00 | 22.25 | 77 | 101260 | 100 | 3000 | 19.4564 | 77.344 | 45.2734 | 0 | 7.2692 | FALSE | FALSE
2025-02-18 19:00 | 21.7 | 78 | 101315 | 100 | 3000 | 19.2289 | 77.6019 | 43.5213 | 0 | 7.2692 | FALSE | FALSE
2025-02-18 20:00 | 21.35 | 81 | 101375 | 100 | 3000 | 19.0819 | 79.0152 | 43.8983 | 0 | 7.2692 | FALSE | FALSE
2025-02-18 21:00 | 21.2 | 82.5 | 101410 | 100 | 3000 | 19.0188 | 79.7242 | 44.1766 | 0 | 7.2692 | FALSE | FALSE
2025-02-18 22:00 | 20.7 | 85 | 101410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-18 23:00 | 20.3 | 88.5 | 101360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-19 | 19.75 | 90.5 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-19 01:00 | 18.8 | 93 | 101265 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-19 02:00 | 18.2 | 93.5 | 101220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-19 03:00 | 18 | 91.5 | 101200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-19 04:00 | 18.85 | 89.5 | 101190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-19 05:00 | 19.5 | 89 | 101205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-19 06:00 | 19.3 | 88 | 101255 | 100 | 3000 | 18.2176 | 81.5819 | 38.9336 | 0 | 7.2692 | FALSE | FALSE
2025-02-19 07:00 | 19.9 | 83 | 101305 | 100 | 3000 | 18.4734 | 79.3552 | 38.7082 | 0 | 7.2692 | FALSE | FALSE
2025-02-19 08:00 | 21.35 | 71.5 | 101365 | 100 | 3000 | 19.0874 | 73.9831 | 37.8687 | 0 | 7.2692 | FALSE | FALSE
2025-02-19 09:00 | 22.9 | 58 | 101420 | 100 | 3000 | 19.7393 | 67.084 | 35.0664 | 0 | 7.2692 | FALSE | FALSE
2025-02-19 10:00 | 24.1 | 48.5 | 101425 | 100 | 3000 | 20.2404 | 61.8789 | 32.6551 | 0 | 7.2692 | FALSE | FALSE
2025-02-19 11:00 | 24.95 | 44 | 101360 | 100 | 3000 | 20.5912 | 59.3205 | 32.1804 | 0 | 7.2692 | FALSE | FALSE
2025-02-19 12:00 | 25.3 | 43 | 101255 | 100 | 3000 | 20.7339 | 58.7588 | 32.5694 | 0 | 7.2692 | FALSE | FALSE
2025-02-19 13:00 | 25.2 | 44 | 101165 | 100 | 3000 | 20.6922 | 59.3624 | 33.0055 | 0 | 7.2692 | FALSE | FALSE
2025-02-19 14:00 | 24.85 | 46.5 | 101100 | 100 | 3000 | 20.5474 | 60.8278 | 33.7344 | 0 | 7.2692 | FALSE | FALSE
2025-02-19 15:00 | 24.3 | 50 | 101055 | 100 | 3000 | 20.32 | 62.82 | 34.4392 | 0 | 7.2692 | FALSE | FALSE
2025-02-19 16:00 | 23.7 | 52 | 101035 | 100 | 3000 | 20.0733 | 63.884 | 33.7441 | 0 | 7.2692 | FALSE | FALSE
2025-02-19 17:00 | 22.75 | 55.5 | 101025 | 100 | 3000 | 19.6797 | 65.7031 | 32.7359 | 0 | 7.2692 | FALSE | FALSE
2025-02-19 18:00 | 21.45 | 64 | 101020 | 100 | 3000 | 19.1336 | 70.0635 | 33.4476 | 0 | 7.2692 | FALSE | FALSE
2025-02-19 19:00 | 20.3 | 73.5 | 101030 | 100 | 3000 | 18.6459 | 74.7045 | 34.7399 | 0 | 7.2692 | FALSE | FALSE
2025-02-19 20:00 | 19.5 | 80.5 | 101060 | 100 | 3000 | 18.3046 | 77.9613 | 35.5054 | 0 | 7.2692 | FALSE | FALSE
2025-02-19 21:00 | 18.95 | 84.5 | 101085 | 100 | 3000 | 18.0691 | 79.721 | 35.4045 | 0 | 7.2692 | FALSE | FALSE
2025-02-19 22:00 | 18.4 | 87.5 | 101085 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-19 23:00 | 17.65 | 90.5 | 101045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-20 | 16.85 | 93 | 100995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-20 01:00 | 16.2 | 95 | 100960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-20 02:00 | 15.8 | 96.5 | 100920 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-20 03:00 | 16 | 96.5 | 100910 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-20 04:00 | 16.4 | 95 | 100905 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-20 05:00 | 16.3 | 94.5 | 100900 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-20 06:00 | 15.85 | 95 | 100935 | 100 | 3000 | 16.7203 | 83.4875 | 27.2598 | 0 | 7.2692 | FALSE | FALSE
2025-02-20 07:00 | 16.25 | 91 | 100980 | 100 | 3000 | 16.8964 | 81.823 | 27.0827 | 0 | 7.2692 | FALSE | FALSE
2025-02-20 08:00 | 18.15 | 80.5 | 101030 | 100 | 3000 | 17.7257 | 77.5121 | 29.7939 | 0 | 7.2692 | FALSE | FALSE
2025-02-20 09:00 | 20.65 | 66 | 101080 | 100 | 3000 | 18.7968 | 70.9226 | 31.5793 | 0 | 7.2692 | FALSE | FALSE
2025-02-20 10:00 | 23.15 | 48.5 | 101090 | 100 | 3000 | 19.851 | 61.8225 | 29.291 | 0 | 7.2692 | FALSE | FALSE
2025-02-20 11:00 | 25.25 | 34.5 | 101055 | 100 | 3000 | 20.7262 | 53.6431 | 27.6202 | 0 | 7.2692 | FALSE | FALSE
2025-02-20 12:00 | 26.35 | 30 | 100980 | 100 | 3000 | 21.1775 | 50.7718 | 29.1158 | 0 | 7.2692 | FALSE | FALSE
2025-02-20 13:00 | 26.55 | 31.5 | 100895 | 100 | 3000 | 21.255 | 51.7012 | 29.3387 | 0 | 7.2692 | FALSE | FALSE
2025-02-20 14:00 | 26.4 | 31.5 | 100845 | 100 | 3000 | 21.1949 | 51.7192 | 29.1267 | 0 | 7.2692 | FALSE | FALSE
2025-02-20 15:00 | 25.7 | 30 | 100810 | 100 | 3000 | 20.9155 | 50.876 | 28.2021 | 0 | 7.2692 | FALSE | FALSE
2025-02-20 16:00 | 25.15 | 34.5 | 100755 | 100 | 3000 | 20.6858 | 53.6818 | 27.4045 | 0 | 7.2692 | FALSE | FALSE
2025-02-20 17:00 | 24.65 | 39.5 | 100735 | 100 | 3000 | 20.4757 | 56.6974 | 27.6418 | 0 | 7.2692 | FALSE | FALSE
2025-02-20 18:00 | 23.7 | 47 | 100770 | 100 | 3000 | 20.0787 | 61.0422 | 30.0849 | 0 | 7.2692 | FALSE | FALSE
2025-02-20 19:00 | 23 | 55 | 100840 | 100 | 3000 | 19.7832 | 65.4874 | 33.2948 | 0 | 7.2692 | FALSE | FALSE
2025-02-20 20:00 | 22.15 | 56 | 100905 | 100 | 3000 | 19.4307 | 65.896 | 30.8493 | 0 | 7.2692 | FALSE | FALSE
2025-02-20 21:00 | 21.3 | 56.5 | 100940 | 100 | 3000 | 19.0751 | 66.0535 | 28.0613 | 0 | 7.2692 | FALSE | FALSE
2025-02-20 22:00 | 20.95 | 57.5 | 100965 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-20 23:00 | 20.8 | 56 | 100955 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-21 | 20.75 | 54 | 100920 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-21 01:00 | 20.35 | 58 | 100925 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-21 02:00 | 19.5 | 66 | 100965 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-21 03:00 | 18.55 | 72.5 | 100950 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-21 04:00 | 19.65 | 74 | 100920 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-21 05:00 | 20.95 | 73.5 | 100960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-21 06:00 | 20.2 | 72 | 101035 | 100 | 3000 | 18.6042 | 73.9046 | 33.4272 | 0 | 7.2692 | FALSE | FALSE
2025-02-21 07:00 | 20.45 | 64.5 | 101100 | 100 | 3000 | 18.713 | 70.1017 | 29.8817 | 0 | 7.2692 | FALSE | FALSE
2025-02-21 08:00 | 22.5 | 54.5 | 101175 | 100 | 3000 | 19.5771 | 65.0934 | 31.1454 | 0 | 7.2692 | FALSE | FALSE
2025-02-21 09:00 | 25.5 | 45.5 | 101225 | 100 | 3000 | 20.8106 | 60.298 | 35.2311 | 0 | 7.2692 | FALSE | FALSE
2025-02-21 10:00 | 28.05 | 36 | 101220 | 100 | 3000 | 21.8391 | 54.5558 | 35.6835 | 0 | 7.2692 | FALSE | FALSE
2025-02-21 11:00 | 29.65 | 28 | 101170 | 100 | 3000 | 22.4825 | 49.1877 | 33.4359 | 0 | 7.2692 | FALSE | FALSE
2025-02-21 12:00 | 30.7 | 23 | 101090 | 100 | 3000 | 22.9028 | 45.6038 | 34.7953 | 0 | 7.2692 | FALSE | FALSE
2025-02-21 13:00 | 30.95 | 21 | 101015 | 100 | 3000 | 23.0057 | 44.1431 | 35.1151 | 0 | 7.2692 | FALSE | FALSE
2025-02-21 14:00 | 30.4 | 21.5 | 100960 | 100 | 3000 | 22.7926 | 44.5831 | 34.4117 | 0 | 7.2692 | FALSE | FALSE
2025-02-21 15:00 | 29.4 | 24.5 | 100945 | 100 | 3000 | 22.3959 | 46.8103 | 33.1104 | 0 | 7.2692 | FALSE | FALSE
2025-02-21 16:00 | 27.95 | 32 | 100965 | 100 | 3000 | 21.8094 | 51.9459 | 31.7052 | 0 | 7.2692 | FALSE | FALSE
2025-02-21 17:00 | 26.05 | 44.5 | 101010 | 100 | 3000 | 21.0322 | 59.7841 | 36.3035 | 0 | 7.2692 | FALSE | FALSE
2025-02-21 18:00 | 24.25 | 59.5 | 101060 | 100 | 3000 | 20.2883 | 68.3512 | 41.3186 | 0 | 7.2692 | FALSE | FALSE
2025-02-21 19:00 | 23.15 | 68.5 | 101110 | 100 | 3000 | 19.8321 | 73.0796 | 43.3327 | 0 | 7.2692 | FALSE | FALSE
2025-02-21 20:00 | 22.35 | 72.5 | 101165 | 100 | 3000 | 19.501 | 74.9451 | 42.7006 | 0 | 7.2692 | FALSE | FALSE
2025-02-21 21:00 | 21.55 | 77 | 101200 | 100 | 3000 | 19.1673 | 77.0088 | 42.2158 | 0 | 7.2692 | FALSE | FALSE
2025-02-21 22:00 | 20.9 | 80 | 101205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-21 23:00 | 20.2 | 82 | 101195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-22 | 19.4 | 84.5 | 101175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-22 01:00 | 18.6 | 87 | 101160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-22 02:00 | 17.95 | 88 | 101150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-22 03:00 | 17.35 | 88.5 | 101145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-22 04:00 | 17.15 | 87.5 | 101145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-22 05:00 | 17.15 | 87 | 101175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-22 06:00 | 16.95 | 89 | 101245 | 100 | 3000 | 17.2037 | 81.1022 | 29.1204 | 0 | 7.2692 | FALSE | FALSE
2025-02-22 07:00 | 17.6 | 88.5 | 101325 | 100 | 3000 | 17.4869 | 81.0871 | 31.6884 | 0 | 7.2692 | FALSE | FALSE
2025-02-22 08:00 | 19.7 | 81.5 | 101410 | 100 | 3000 | 18.3892 | 78.5008 | 36.9644 | 0 | 7.2692 | FALSE | FALSE
2025-02-22 09:00 | 22.2 | 72 | 101455 | 100 | 3000 | 19.4396 | 74.5753 | 41.7583 | 0 | 7.2692 | FALSE | FALSE
2025-02-22 10:00 | 24.35 | 58 | 101445 | 100 | 3000 | 20.3305 | 67.4674 | 40.6412 | 0 | 7.2692 | FALSE | FALSE
2025-02-22 11:00 | 26.25 | 43.5 | 101390 | 100 | 3000 | 21.1135 | 59.154 | 36.2263 | 0 | 7.2692 | FALSE | FALSE
2025-02-22 12:00 | 27.35 | 40.5 | 101305 | 100 | 3000 | 21.5545 | 57.4089 | 37.4048 | 0 | 7.2692 | FALSE | FALSE
2025-02-22 13:00 | 27.45 | 41.5 | 101225 | 100 | 3000 | 21.5917 | 58.0756 | 38.6052 | 0 | 7.2692 | FALSE | FALSE
2025-02-22 14:00 | 27.1 | 39.5 | 101160 | 100 | 3000 | 21.4581 | 56.7534 | 35.68 | 0 | 7.2692 | FALSE | FALSE
2025-02-22 15:00 | 26.6 | 39.5 | 101115 | 100 | 3000 | 21.26 | 56.7151 | 34.0244 | 0 | 7.2692 | FALSE | FALSE
2025-02-22 16:00 | 26 | 44 | 101105 | 100 | 3000 | 21.0131 | 59.4588 | 35.7361 | 0 | 7.2692 | FALSE | FALSE
2025-02-22 17:00 | 25.1 | 50 | 101120 | 100 | 3000 | 20.6433 | 62.9567 | 37.3335 | 0 | 7.2692 | FALSE | FALSE
2025-02-22 18:00 | 23.6 | 58.5 | 101140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-22 19:00 | 22.2 | 66.5 | 101185 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-22 20:00 | 21.45 | 68 | 101240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-22 21:00 | 20.85 | 65.5 | 101255 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-22 22:00 | 20.3 | 64.5 | 101235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-22 23:00 | 19.7 | 67 | 101195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 | 19.05 | 69.5 | 101140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 01:00 | 18.6 | 70 | 101090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 02:00 | 18.25 | 71.5 | 101050 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 03:00 | 18 | 74 | 101015 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 04:00 | 18.15 | 77 | 100995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 05:00 | 18.45 | 77.5 | 101000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 06:00 | 18.45 | 76 | 101040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 07:00 | 19.5 | 72 | 101100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 08:00 | 22.5 | 59.5 | 101165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 09:00 | 26.55 | 46.5 | 101195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 10:00 | 29.85 | 42.5 | 101150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 11:00 | 31.9 | 39 | 101055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 12:00 | 33.55 | 32.5 | 100920 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 13:00 | 34.9 | 27 | 100790 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 14:00 | 35.7 | 22 | 100695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 15:00 | 34.85 | 24.5 | 100635 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 16:00 | 31.95 | 36.5 | 100645 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 17:00 | 29.25 | 45 | 100695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 18:00 | 27.9 | 49 | 100750 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 19:00 | 27.05 | 51.5 | 100820 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 20:00 | 26.6 | 50.5 | 100865 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 21:00 | 26.2 | 51.5 | 100865 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 22:00 | 25.4 | 57.5 | 100830 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-23 23:00 | 24.4 | 67 | 100795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-24 | 23.3 | 75.5 | 100770 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-24 01:00 | 22.35 | 80.5 | 100735 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-24 02:00 | 21.65 | 81 | 100710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-24 03:00 | 21.1 | 75.5 | 100710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-24 04:00 | 21.45 | 59 | 100745 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-24 05:00 | 21.9 | 48 | 100820 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-24 06:00 | 21.3 | 54.5 | 100915 | 100 | 3000 | 19.0763 | 64.9928 | 26.777 | 0 | 7.2692 | FALSE | FALSE
2025-02-24 07:00 | 21.15 | 60 | 101005 | 100 | 3000 | 19.0102 | 67.8819 | 29.7419 | 0 | 7.2692 | FALSE | FALSE
2025-02-24 08:00 | 22.6 | 61 | 101075 | 100 | 3000 | 19.6131 | 68.7164 | 35.944 | 0 | 7.2692 | FALSE | FALSE
2025-02-24 09:00 | 24.75 | 60 | 101105 | 100 | 3000 | 20.4889 | 68.8134 | 43.6759 | 0 | 7.2692 | FALSE | FALSE
2025-02-24 10:00 | 26.6 | 56.5 | 101095 | 100 | 3000 | 21.2281 | 67.3959 | 48.2466 | 0 | 7.2692 | FALSE | FALSE
2025-02-24 11:00 | 27.85 | 54.5 | 101070 | 100 | 3000 | 21.7182 | 66.6428 | 51.4863 | 0 | 7.2692 | FALSE | FALSE
2025-02-24 12:00 | 27.25 | 61.5 | 101020 | 100 | 3000 | 21.4711 | 70.8741 | 55.0964 | 0 | 7.2692 | FALSE | FALSE
2025-02-24 13:00 | 25.7 | 70 | 100955 | 100 | 3000 | 20.8513 | 75.2866 | 55.366 | 0 | 7.2692 | FALSE | FALSE
2025-02-24 14:00 | 25.45 | 70 | 100905 | 100 | 3000 | 20.7529 | 75.1416 | 54.2586 | 0 | 7.2692 | FALSE | FALSE
2025-02-24 15:00 | 25.4 | 70 | 100875 | 100 | 3000 | 20.7332 | 75.1151 | 54.0351 | 0 | 7.2692 | FALSE | FALSE
2025-02-24 16:00 | 25.25 | 69.5 | 100830 | 100 | 3000 | 20.6747 | 74.7324 | 52.9866 | 0 | 7.2692 | FALSE | FALSE
2025-02-24 17:00 | 24.7 | 71.5 | 100835 | 100 | 3000 | 20.4535 | 75.6053 | 52.1021 | 0 | 7.2692 | FALSE | FALSE
2025-02-24 18:00 | 23.65 | 77 | 100895 | 100 | 3000 | 20.0262 | 78.1647 | 51.456 | 0 | 7.2692 | FALSE | FALSE
2025-02-24 19:00 | 23.1 | 80.5 | 100940 | 100 | 3000 | 19.8004 | 79.795 | 51.4162 | 0 | 7.2692 | FALSE | FALSE
2025-02-24 20:00 | 22.85 | 82 | 101000 | 100 | 3000 | 19.6975 | 80.4652 | 51.3038 | 0 | 7.2692 | FALSE | FALSE
2025-02-24 21:00 | 22.9 | 79 | 101050 | 100 | 3000 | 19.7206 | 78.8252 | 49.4902 | 0 | 7.2692 | FALSE | FALSE
2025-02-24 22:00 | 22.95 | 74 | 101070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-24 23:00 | 22.6 | 73 | 101055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-25 | 22.35 | 76 | 101035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-25 01:00 | 22.2 | 83.5 | 101015 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-25 02:00 | 21.8 | 91.5 | 100970 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-25 03:00 | 21.6 | 94 | 100945 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-25 04:00 | 21.95 | 87 | 100985 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-25 05:00 | 22.05 | 77 | 101090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-25 06:00 | 21.7 | 72 | 101185 | 100 | 3000 | 19.2327 | 74.4015 | 39.6331 | 0 | 7.2692 | FALSE | FALSE
2025-02-25 07:00 | 21.85 | 67.5 | 101285 | 100 | 3000 | 19.298 | 72.0241 | 37.3303 | 0 | 7.2692 | FALSE | FALSE
2025-02-25 08:00 | 22.3 | 62.5 | 101405 | 100 | 3000 | 19.488 | 69.4268 | 35.8202 | 0 | 7.2692 | FALSE | FALSE
2025-02-25 09:00 | 22.6 | 59.5 | 101480 | 100 | 3000 | 19.6143 | 67.8426 | 34.9592 | 0 | 7.2692 | FALSE | FALSE
2025-02-25 10:00 | 23.05 | 57.5 | 101510 | 100 | 3000 | 19.8014 | 66.8281 | 35.2967 | 0 | 7.2692 | FALSE | FALSE
2025-02-25 11:00 | 23.35 | 55.5 | 101500 | 100 | 3000 | 19.9264 | 65.7658 | 35.0162 | 0 | 7.2692 | FALSE | FALSE
2025-02-25 12:00 | 23.1 | 54.5 | 101465 | 100 | 3000 | 19.8247 | 65.157 | 33.3775 | 0 | 7.2692 | FALSE | FALSE
2025-02-25 13:00 | 22.95 | 52 | 101425 | 100 | 3000 | 19.7652 | 63.7353 | 31.0767 | 0 | 7.2692 | FALSE | FALSE
2025-02-25 14:00 | 23.3 | 45 | 101390 | 100 | 3000 | 19.9161 | 59.8167 | 27.3497 | 0 | 7.2692 | FALSE | FALSE
2025-02-25 15:00 | 23.2 | 40 | 101385 | 100 | 3000 | 19.8795 | 56.9855 | 24.8401 | 0 | 7.2692 | FALSE | FALSE
2025-02-25 16:00 | 21.95 | 46 | 101435 | 100 | 3000 | 19.3542 | 60.377 | 23.5162 | 0 | 7.2692 | FALSE | FALSE
2025-02-25 17:00 | 20.55 | 53.5 | 101490 | 100 | 3000 | 18.76 | 64.3684 | 23.5206 | 0 | 7.2692 | FALSE | FALSE
2025-02-25 18:00 | 19.75 | 55.5 | 101530 | 100 | 3000 | 18.4184 | 65.3815 | 21.9 | 0 | 7.2692 | FALSE | FALSE
2025-02-25 19:00 | 19.1 | 58 | 101575 | 100 | 3000 | 18.1388 | 66.6262 | 21.0329 | 0 | 7.2692 | FALSE | FALSE
2025-02-25 20:00 | 18.55 | 61.5 | 101615 | 100 | 3000 | 17.9008 | 68.3325 | 21.0059 | 0 | 7.2692 | FALSE | FALSE
2025-02-25 21:00 | 18.15 | 65.5 | 101635 | 100 | 3000 | 17.727 | 70.2466 | 21.7117 | 0 | 7.2692 | FALSE | FALSE
2025-02-25 22:00 | 17.8 | 69 | 101645 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-25 23:00 | 17.6 | 71 | 101630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-26 | 17.4 | 73 | 101590 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-26 01:00 | 17.15 | 74.5 | 101535 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-26 02:00 | 16.9 | 75.5 | 101480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-26 03:00 | 16.65 | 76.5 | 101465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-26 04:00 | 16.75 | 75 | 101480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-26 05:00 | 16.75 | 74 | 101520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-26 06:00 | 16.45 | 75 | 101595 | 100 | 3000 | 16.9829 | 74.5557 | 20.0838 | 0 | 7.2692 | FALSE | FALSE
2025-02-26 07:00 | 17.25 | 71.5 | 101675 | 100 | 3000 | 17.3344 | 73.0099 | 21.4424 | 0 | 7.2692 | FALSE | FALSE
2025-02-26 08:00 | 18.9 | 62.5 | 101755 | 100 | 3000 | 18.0518 | 68.8212 | 22.8654 | 0 | 7.2692 | FALSE | FALSE
2025-02-26 09:00 | 20.1 | 55.5 | 101800 | 100 | 3000 | 18.5678 | 65.3554 | 23.1632 | 0 | 7.2692 | FALSE | FALSE
2025-02-26 10:00 | 20.85 | 52 | 101785 | 100 | 3000 | 18.8877 | 63.5558 | 23.6613 | 0 | 7.2692 | FALSE | FALSE
2025-02-26 11:00 | 21.45 | 49 | 101725 | 100 | 3000 | 19.1424 | 61.9736 | 23.8202 | 0 | 7.2692 | FALSE | FALSE
2025-02-26 12:00 | 21.8 | 47.5 | 101620 | 100 | 3000 | 19.2903 | 61.1741 | 24.0226 | 0 | 7.2692 | FALSE | FALSE
2025-02-26 13:00 | 21.7 | 48.5 | 101535 | 100 | 3000 | 19.2477 | 61.7246 | 24.3338 | 0 | 7.2692 | FALSE | FALSE
2025-02-26 14:00 | 21.55 | 49.5 | 101495 | 100 | 3000 | 19.1842 | 62.2669 | 24.4701 | 0 | 7.2692 | FALSE | FALSE
2025-02-26 15:00 | 21.4 | 49.5 | 101465 | 100 | 3000 | 19.1211 | 62.27 | 23.9514 | 0 | 7.2692 | FALSE | FALSE
2025-02-26 16:00 | 20.55 | 54 | 101475 | 100 | 3000 | 18.7598 | 64.6299 | 23.8284 | 0 | 7.2692 | FALSE | FALSE
2025-02-26 17:00 | 19.6 | 60 | 101510 | 100 | 3000 | 18.3529 | 67.651 | 24.0073 | 0 | 7.2692 | FALSE | FALSE
2025-02-26 18:00 | 19.1 | 63 | 101525 | 100 | 3000 | 18.1378 | 69.11 | 23.8855 | 0 | 7.2692 | FALSE | FALSE
2025-02-26 19:00 | 18.65 | 66 | 101550 | 100 | 3000 | 17.9434 | 70.5401 | 23.8767 | 0 | 7.2692 | FALSE | FALSE
2025-02-26 20:00 | 18.15 | 70 | 101585 | 100 | 3000 | 17.7266 | 72.4131 | 24.1465 | 0 | 7.2692 | FALSE | FALSE
2025-02-26 21:00 | 18.05 | 70.5 | 101610 | 100 | 3000 | 17.6832 | 72.6364 | 24.0273 | 0 | 7.2692 | FALSE | FALSE
2025-02-26 22:00 | 17.95 | 71 | 101610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-26 23:00 | 17.55 | 73.5 | 101580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-27 | 17.5 | 73 | 101545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-27 01:00 | 17.7 | 71 | 101520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-27 02:00 | 17.55 | 69 | 101485 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-27 03:00 | 17.35 | 68.5 | 101445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-27 04:00 | 18 | 64 | 101440 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-27 05:00 | 18.55 | 60 | 101470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-27 06:00 | 18.7 | 58 | 101520 | 100 | 3000 | 17.9662 | 66.6353 | 19.5956 | 0 | 7.2692 | FALSE | FALSE
2025-02-27 07:00 | 19.6 | 54 | 101575 | 100 | 3000 | 18.3546 | 64.6202 | 20.4884 | 0 | 7.2692 | FALSE | FALSE
2025-02-27 08:00 | 20.85 | 52 | 101645 | 100 | 3000 | 18.8877 | 63.5716 | 23.6511 | 0 | 7.2692 | FALSE | FALSE
2025-02-27 09:00 | 21.5 | 52.5 | 101700 | 100 | 3000 | 19.1613 | 63.8508 | 26.2627 | 0 | 7.2692 | FALSE | FALSE
2025-02-27 10:00 | 21.7 | 54 | 101685 | 100 | 3000 | 19.2442 | 64.6723 | 27.9538 | 0 | 7.2692 | FALSE | FALSE
2025-02-27 11:00 | 21.85 | 56 | 101630 | 100 | 3000 | 19.3056 | 65.7745 | 29.8089 | 0 | 7.2692 | FALSE | FALSE
2025-02-27 12:00 | 21.9 | 58 | 101570 | 100 | 3000 | 19.3251 | 66.871 | 31.308 | 0 | 7.2692 | FALSE | FALSE
2025-02-27 13:00 | 21.95 | 56.5 | 101495 | 100 | 3000 | 19.347 | 66.0741 | 30.4962 | 0 | 7.2692 | FALSE | FALSE
2025-02-27 14:00 | 21.7 | 55 | 101430 | 100 | 3000 | 19.2436 | 65.2391 | 28.5871 | 0 | 7.2692 | FALSE | FALSE
2025-02-27 15:00 | 21 | 57 | 101405 | 100 | 3000 | 18.9486 | 66.2349 | 27.317 | 0 | 7.2692 | FALSE | FALSE
2025-02-27 16:00 | 20.3 | 61.5 | 101390 | 100 | 3000 | 18.6506 | 68.4978 | 27.5015 | 0 | 7.2692 | FALSE | FALSE
2025-02-27 17:00 | 19.65 | 65 | 101365 | 100 | 3000 | 18.3729 | 70.1913 | 27.118 | 0 | 7.2692 | FALSE | FALSE
2025-02-27 18:00 | 19.15 | 67.5 | 101365 | 100 | 3000 | 18.1583 | 71.3641 | 26.6352 | 0 | 7.2692 | FALSE | FALSE
2025-02-27 19:00 | 18.95 | 67.5 | 101410 | 100 | 3000 | 18.0724 | 71.3288 | 25.8627 | 0 | 7.2692 | FALSE | FALSE
2025-02-27 20:00 | 18.95 | 63.5 | 101485 | 100 | 3000 | 18.0731 | 69.3494 | 23.6055 | 0 | 7.2692 | FALSE | FALSE
2025-02-27 21:00 | 19.05 | 60.5 | 101540 | 100 | 3000 | 18.1168 | 67.8675 | 22.2762 | 0 | 7.2692 | FALSE | FALSE
2025-02-27 22:00 | 19.05 | 59.5 | 101525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-27 23:00 | 18.8 | 60 | 101470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-28 | 18.25 | 64 | 101405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-28 01:00 | 17.6 | 70 | 101345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-28 02:00 | 17.2 | 74 | 101290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-28 03:00 | 17 | 72.5 | 101245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-28 04:00 | 17.05 | 70.5 | 101250 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-28 05:00 | 17.25 | 71 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-28 06:00 | 17.35 | 70.5 | 101380 | 100 | 3000 | 17.3781 | 72.5883 | 21.3065 | 0 | 7.2692 | FALSE | FALSE
2025-02-28 07:00 | 18.2 | 65 | 101440 | 100 | 3000 | 17.7487 | 70.0328 | 21.6219 | 0 | 7.2692 | FALSE | FALSE
2025-02-28 08:00 | 19.8 | 57 | 101510 | 100 | 3000 | 18.4393 | 66.1448 | 22.9667 | 0 | 7.2692 | FALSE | FALSE
2025-02-28 09:00 | 21.05 | 52.5 | 101565 | 100 | 3000 | 18.972 | 63.8475 | 24.6625 | 0 | 7.2692 | FALSE | FALSE
2025-02-28 10:00 | 21.85 | 49.5 | 101560 | 100 | 3000 | 19.31 | 62.2637 | 25.5111 | 0 | 7.2692 | FALSE | FALSE
2025-02-28 11:00 | 22.4 | 46 | 101500 | 100 | 3000 | 19.5421 | 60.3603 | 25.0311 | 0 | 7.2692 | FALSE | FALSE
2025-02-28 12:00 | 22.6 | 42.5 | 101405 | 100 | 3000 | 19.6282 | 58.4262 | 23.9827 | 0 | 7.2692 | FALSE | FALSE
2025-02-28 13:00 | 22.55 | 41 | 101300 | 100 | 3000 | 19.6086 | 57.6084 | 23.8962 | 0 | 7.2692 | FALSE | FALSE
2025-02-28 14:00 | 22.35 | 41.5 | 101215 | 100 | 3000 | 19.5248 | 57.912 | 23.5893 | 0 | 7.2692 | FALSE | FALSE
2025-02-28 15:00 | 21.9 | 43.5 | 101170 | 100 | 3000 | 19.335 | 59.0496 | 22.9254 | 0 | 7.2692 | FALSE | FALSE
2025-02-28 16:00 | 21.4 | 47 | 101190 | 100 | 3000 | 19.1226 | 60.9646 | 22.3114 | 0 | 7.2692 | FALSE | FALSE
2025-02-28 17:00 | 20.7 | 51 | 101235 | 100 | 3000 | 18.8247 | 63.0948 | 22.4751 | 0 | 7.2692 | FALSE | FALSE
2025-02-28 18:00 | 19.75 | 55.5 | 101270 | 100 | 3000 | 18.4185 | 65.4116 | 21.8854 | 0 | 7.2692 | FALSE | FALSE
2025-02-28 19:00 | 19.05 | 58.5 | 101300 | 100 | 3000 | 18.1172 | 66.9059 | 21.1255 | 0 | 7.2692 | FALSE | FALSE
2025-02-28 20:00 | 18.55 | 59 | 101330 | 100 | 3000 | 17.9012 | 67.1487 | 19.6076 | 0 | 7.2692 | FALSE | FALSE
2025-02-28 21:00 | 18.15 | 59.5 | 101355 | 100 | 3000 | 17.7275 | 67.3961 | 18.4457 | 0 | 7.2692 | FALSE | FALSE
2025-02-28 22:00 | 17.85 | 61.5 | 101360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-02-28 23:00 | 17.55 | 64.5 | 101330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-01 | 17.2 | 68.5 | 101270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-01 01:00 | 16.8 | 72.5 | 101225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-01 02:00 | 16.2 | 77.5 | 101190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-01 03:00 | 15.6 | 83.5 | 101170 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-01 04:00 | 15.3 | 85.5 | 101185 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-01 05:00 | 15.05 | 86 | 101230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-01 06:00 | 14.85 | 87.5 | 101290 | 100 | 3000 | 16.2735 | 79.9245 | 19.5327 | 0 | 7.2692 | FALSE | FALSE
2025-03-01 07:00 | 15.9 | 83 | 101345 | 100 | 3000 | 16.7406 | 78.1144 | 21.7614 | 0 | 7.2692 | FALSE | FALSE
2025-03-01 08:00 | 18.1 | 73 | 101395 | 100 | 3000 | 17.7047 | 73.8663 | 25.5632 | 0 | 7.2692 | FALSE | FALSE
2025-03-01 09:00 | 20.15 | 63 | 101420 | 100 | 3000 | 18.5864 | 69.2432 | 27.8425 | 0 | 7.2692 | FALSE | FALSE
2025-03-01 10:00 | 21.75 | 55 | 101400 | 100 | 3000 | 19.2645 | 65.2478 | 28.7663 | 0 | 7.2692 | FALSE | FALSE
2025-03-01 11:00 | 22.7 | 50.5 | 101350 | 100 | 3000 | 19.6632 | 62.8801 | 29.1375 | 0 | 7.2692 | FALSE | FALSE
2025-03-01 12:00 | 22.95 | 48 | 101260 | 100 | 3000 | 19.7688 | 61.5105 | 28.2637 | 0 | 7.2692 | FALSE | FALSE
2025-03-01 13:00 | 22.8 | 47 | 101150 | 100 | 3000 | 19.7076 | 60.9567 | 27.0403 | 0 | 7.2692 | FALSE | FALSE
2025-03-01 14:00 | 22.6 | 47 | 101070 | 100 | 3000 | 19.6246 | 60.9608 | 26.3514 | 0 | 7.2692 | FALSE | FALSE
2025-03-01 15:00 | 22.3 | 47.5 | 101025 | 100 | 3000 | 19.4994 | 61.2379 | 25.668 | 0 | 7.2692 | FALSE | FALSE
2025-03-01 16:00 | 21.7 | 50 | 101045 | 100 | 3000 | 19.2469 | 62.5875 | 25.2776 | 0 | 7.2692 | FALSE | FALSE
2025-03-01 17:00 | 20.85 | 55 | 101085 | 100 | 3000 | 18.8863 | 65.2082 | 25.4926 | 0 | 7.2692 | FALSE | FALSE
2025-03-01 18:00 | 20.05 | 62.5 | 101090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-01 19:00 | 19.4 | 70 | 101105 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-01 20:00 | 18.85 | 74.5 | 101160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-01 21:00 | 18.35 | 77.5 | 101200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-01 22:00 | 17.9 | 80 | 101190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-01 23:00 | 17.3 | 82.5 | 101165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 | 16.5 | 85.5 | 101125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 01:00 | 15.85 | 88.5 | 101090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 02:00 | 15.5 | 90.5 | 101055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 03:00 | 15.3 | 91 | 101025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 04:00 | 15.6 | 89.5 | 101030 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 05:00 | 16 | 88.5 | 101070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 06:00 | 15.85 | 89.5 | 101150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 07:00 | 16.55 | 85.5 | 101235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 08:00 | 18.9 | 75 | 101300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 09:00 | 21.25 | 60.5 | 101360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 10:00 | 22.6 | 45.5 | 101380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 11:00 | 23.25 | 39.5 | 101340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 12:00 | 23.55 | 37.5 | 101270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 13:00 | 23.6 | 37 | 101195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 14:00 | 23.4 | 40 | 101130 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 15:00 | 23 | 43 | 101095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 16:00 | 22.25 | 47.5 | 101110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 17:00 | 21.3 | 55.5 | 101150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 18:00 | 20.5 | 60.5 | 101180 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 19:00 | 20.1 | 56 | 101215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 20:00 | 19.65 | 55.5 | 101260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 21:00 | 19.1 | 60.5 | 101300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 22:00 | 18.9 | 60 | 101320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-02 23:00 | 18.85 | 55.5 | 101325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-03 | 18.6 | 56 | 101315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-03 01:00 | 18.25 | 58 | 101290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-03 02:00 | 17.9 | 56 | 101285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-03 03:00 | 17.5 | 56 | 101300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-03 04:00 | 17.1 | 58 | 101325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-03 05:00 | 16.6 | 60 | 101385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-03 06:00 | 16.15 | 62.5 | 101480 | 100 | 3000 | 16.8487 | 68.9152 | 14.247 | 0 | 7.2692 | FALSE | FALSE
2025-03-03 07:00 | 17 | 61.5 | 101570 | 100 | 3000 | 17.2243 | 68.3709 | 15.6025 | 0 | 7.2692 | FALSE | FALSE
2025-03-03 08:00 | 19 | 54.5 | 101640 | 100 | 3000 | 18.0964 | 64.8874 | 18.7073 | 0 | 7.2692 | FALSE | FALSE
2025-03-03 09:00 | 20.5 | 48.5 | 101685 | 100 | 3000 | 18.7408 | 61.75 | 20.9771 | 0 | 7.2692 | FALSE | FALSE
2025-03-03 10:00 | 21.4 | 45 | 101690 | 100 | 3000 | 19.1237 | 59.84 | 22.3112 | 0 | 7.2692 | FALSE | FALSE
2025-03-03 11:00 | 22.2 | 41.5 | 101645 | 100 | 3000 | 19.462 | 57.8795 | 23.4738 | 0 | 7.2692 | FALSE | FALSE
2025-03-03 12:00 | 22.85 | 39 | 101565 | 100 | 3000 | 19.7352 | 56.4352 | 24.3963 | 0 | 7.2692 | FALSE | FALSE
2025-03-03 13:00 | 23.15 | 38.5 | 101490 | 100 | 3000 | 19.8602 | 56.1299 | 24.8053 | 0 | 7.2692 | FALSE | FALSE
2025-03-03 14:00 | 23.15 | 39 | 101420 | 100 | 3000 | 19.8598 | 56.4201 | 24.785 | 0 | 7.2692 | FALSE | FALSE
2025-03-03 15:00 | 22.9 | 39 | 101355 | 100 | 3000 | 19.756 | 56.4522 | 24.4171 | 0 | 7.2692 | FALSE | FALSE
2025-03-03 16:00 | 22.45 | 39 | 101350 | 100 | 3000 | 19.5685 | 56.5056 | 23.7775 | 0 | 7.2692 | FALSE | FALSE
2025-03-03 17:00 | 21.65 | 41 | 101370 | 100 | 3000 | 19.2315 | 57.7006 | 22.6229 | 0 | 7.2692 | FALSE | FALSE
2025-03-03 18:00 | 20.45 | 46 | 101360 | 100 | 3000 | 18.7207 | 60.4933 | 20.8467 | 0 | 7.2692 | FALSE | FALSE
2025-03-03 19:00 | 19.35 | 51.5 | 101370 | 100 | 3000 | 18.2479 | 63.4019 | 19.1932 | 0 | 7.2692 | FALSE | FALSE
2025-03-03 20:00 | 18.45 | 56.5 | 101410 | 100 | 3000 | 17.8582 | 65.9261 | 17.8695 | 0 | 7.2692 | FALSE | FALSE
2025-03-03 21:00 | 17.75 | 59.5 | 101440 | 100 | 3000 | 17.5532 | 67.4024 | 17.0154 | 0 | 7.2692 | FALSE | FALSE
2025-03-03 22:00 | 16.95 | 61 | 101465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-03 23:00 | 15.9 | 62.5 | 101465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-04 | 14.8 | 65 | 101420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-04 01:00 | 13.7 | 68.5 | 101370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-04 02:00 | 12.85 | 71.5 | 101345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-04 03:00 | 12.45 | 70 | 101325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-04 04:00 | 12.85 | 67 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-04 05:00 | 13.5 | 65.5 | 101345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-04 06:00 | 13.8 | 62.5 | 101430 | 100 | 3000 | 15.7926 | 69.3573 | 10.4246 | 0 | 7.2692 | FALSE | FALSE
2025-03-04 07:00 | 15.05 | 56.5 | 101510 | 100 | 3000 | 16.3561 | 66.4552 | 12.485 | 0 | 7.2692 | FALSE | FALSE
2025-03-04 08:00 | 17.9 | 45.5 | 101570 | 100 | 3000 | 17.6194 | 60.6867 | 17.0293 | 0 | 7.2692 | FALSE | FALSE
2025-03-04 09:00 | 21.6 | 32 | 101620 | 100 | 3000 | 19.2159 | 52.8272 | 22.6501 | 0 | 7.2692 | FALSE | FALSE
2025-03-04 10:00 | 25.05 | 22.5 | 101635 | 100 | 3000 | 20.6615 | 46.3849 | 27.6143 | 0 | 7.2692 | FALSE | FALSE
2025-03-04 11:00 | 27.3 | 17 | 101580 | 100 | 3000 | 21.5835 | 42.2293 | 30.7046 | 0 | 7.2692 | FALSE | FALSE
2025-03-04 12:00 | 28.85 | 14 | 101475 | 100 | 3000 | 22.2084 | 39.72 | 32.748 | 0 | 7.2692 | FALSE | FALSE
2025-03-04 13:00 | 29.9 | 14.5 | 101365 | 100 | 3000 | 22.6203 | 39.7278 | 34.049 | 0 | 7.2692 | FALSE | FALSE
2025-03-04 14:00 | 30.2 | 16.5 | 101275 | 100 | 3000 | 22.7311 | 41.0564 | 34.3612 | 0 | 7.2692 | FALSE | FALSE
2025-03-04 15:00 | 29.85 | 19.5 | 101210 | 100 | 3000 | 22.5857 | 43.2491 | 33.8468 | 0 | 7.2692 | FALSE | FALSE
2025-03-04 16:00 | 28.55 | 22.5 | 101200 | 100 | 3000 | 22.0684 | 45.5565 | 32.1456 | 0 | 7.2692 | FALSE | FALSE
2025-03-04 17:00 | 27.15 | 25.5 | 101215 | 100 | 3000 | 21.5063 | 47.7774 | 30.2921 | 0 | 7.2692 | FALSE | FALSE
2025-03-04 18:00 | 25.8 | 32.5 | 101225 | 100 | 3000 | 20.9517 | 52.3581 | 28.4255 | 0 | 7.2692 | FALSE | FALSE
2025-03-04 19:00 | 24.1 | 45 | 101265 | 100 | 3000 | 20.2445 | 59.8604 | 30.0399 | 0 | 7.2692 | FALSE | FALSE
2025-03-04 20:00 | 22.85 | 55.5 | 101315 | 100 | 3000 | 19.7209 | 65.6893 | 33.135 | 0 | 7.2692 | FALSE | FALSE
2025-03-04 21:00 | 22.15 | 62 | 101355 | 100 | 3000 | 19.4263 | 69.1202 | 34.8959 | 0 | 7.2692 | FALSE | FALSE
2025-03-04 22:00 | 21.65 | 67.5 | 101375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-04 23:00 | 21.1 | 71.5 | 101370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-05 | 20.55 | 74.5 | 101340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-05 01:00 | 20.1 | 76.5 | 101305 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-05 02:00 | 19.85 | 76.5 | 101285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-05 03:00 | 19.5 | 76.5 | 101300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-05 04:00 | 19.7 | 65.5 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-05 05:00 | 20.35 | 49.5 | 101355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-05 06:00 | 20.4 | 42.5 | 101435 | 100 | 3000 | 18.7008 | 58.6763 | 20.8014 | 0 | 7.2692 | FALSE | FALSE
2025-03-05 07:00 | 21 | 37.5 | 101490 | 100 | 3000 | 18.9585 | 55.9333 | 21.7179 | 0 | 7.2692 | FALSE | FALSE
2025-03-05 08:00 | 22.65 | 33.5 | 101550 | 100 | 3000 | 19.6564 | 53.3948 | 24.1423 | 0 | 7.2692 | FALSE | FALSE
2025-03-05 09:00 | 24.75 | 30.5 | 101595 | 100 | 3000 | 20.5279 | 51.2532 | 27.1194 | 0 | 7.2692 | FALSE | FALSE
2025-03-05 10:00 | 26.85 | 28 | 101590 | 100 | 3000 | 21.3813 | 49.3859 | 29.9761 | 0 | 7.2692 | FALSE | FALSE
2025-03-05 11:00 | 28.85 | 25.5 | 101525 | 100 | 3000 | 22.1782 | 47.5019 | 32.5853 | 0 | 7.2692 | FALSE | FALSE
2025-03-05 12:00 | 30.35 | 23 | 101450 | 100 | 3000 | 22.768 | 45.6093 | 34.486 | 0 | 7.2692 | FALSE | FALSE
2025-03-05 13:00 | 30.3 | 27.5 | 101385 | 100 | 3000 | 22.7341 | 48.8022 | 34.4048 | 0 | 7.2692 | FALSE | FALSE
2025-03-05 14:00 | 28.35 | 40.5 | 101340 | 100 | 3000 | 21.9451 | 57.5567 | 40.7941 | 0 | 7.2692 | FALSE | FALSE
2025-03-05 15:00 | 27.15 | 45 | 101305 | 100 | 3000 | 21.4665 | 60.2627 | 40.6171 | 0 | 7.2692 | FALSE | FALSE
2025-03-05 16:00 | 27.45 | 40.5 | 101290 | 100 | 3000 | 21.5938 | 57.4234 | 37.7388 | 0 | 7.2692 | FALSE | FALSE
2025-03-05 17:00 | 27.3 | 37 | 101305 | 100 | 3000 | 21.5421 | 55.1514 | 34.1833 | 0 | 7.2692 | FALSE | FALSE
2025-03-05 18:00 | 26.5 | 37 | 101330 | 100 | 3000 | 21.2248 | 55.1177 | 31.6283 | 0 | 7.2692 | FALSE | FALSE
2025-03-05 19:00 | 25.15 | 45.5 | 101360 | 100 | 3000 | 20.6698 | 60.2394 | 34.0342 | 0 | 7.2692 | FALSE | FALSE
2025-03-05 20:00 | 23.65 | 56 | 101375 | 100 | 3000 | 20.0486 | 66.1296 | 36.4874 | 0 | 7.2692 | FALSE | FALSE
2025-03-05 21:00 | 22.55 | 62 | 101370 | 100 | 3000 | 19.5917 | 69.2234 | 36.458 | 0 | 7.2692 | FALSE | FALSE
2025-03-05 22:00 | 21.8 | 67.5 | 101330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-05 23:00 | 21.2 | 71 | 101275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-06 | 20.8 | 71 | 101245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-06 01:00 | 20.3 | 71.5 | 101225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-06 02:00 | 19.75 | 73 | 101200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-06 03:00 | 19.15 | 75 | 101195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-06 04:00 | 19.2 | 70 | 101210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-06 05:00 | 19.65 | 60.5 | 101250 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-06 06:00 | 19.7 | 55 | 101295 | 100 | 3000 | 18.3972 | 65.1558 | 21.414 | 0 | 7.2692 | FALSE | FALSE
2025-03-06 07:00 | 20.65 | 50 | 101350 | 100 | 3000 | 18.804 | 62.561 | 21.6886 | 0 | 7.2692 | FALSE | FALSE
2025-03-06 08:00 | 22.95 | 44 | 101420 | 100 | 3000 | 19.7723 | 59.2488 | 25.4762 | 0 | 7.2692 | FALSE | FALSE
2025-03-06 09:00 | 25.55 | 39 | 101445 | 100 | 3000 | 20.8406 | 56.3249 | 30.2396 | 0 | 7.2692 | FALSE | FALSE
2025-03-06 10:00 | 27.9 | 34.5 | 101455 | 100 | 3000 | 21.7838 | 53.5399 | 33.8925 | 0 | 7.2692 | FALSE | FALSE
2025-03-06 11:00 | 29.9 | 30 | 101445 | 100 | 3000 | 22.5726 | 50.5517 | 35.7553 | 0 | 7.2692 | FALSE | FALSE
2025-03-06 12:00 | 31.05 | 28 | 101370 | 100 | 3000 | 23.0185 | 49.162 | 37.1011 | 0 | 7.2692 | FALSE | FALSE
2025-03-06 13:00 | 30.85 | 30 | 101280 | 100 | 3000 | 22.9355 | 50.6036 | 38.5803 | 0 | 7.2692 | FALSE | FALSE
2025-03-06 14:00 | 29.8 | 32 | 101210 | 100 | 3000 | 22.5282 | 51.9625 | 37.3905 | 0 | 7.2692 | FALSE | FALSE
2025-03-06 15:00 | 28.65 | 34 | 101175 | 100 | 3000 | 22.0782 | 53.2672 | 35.7338 | 0 | 7.2692 | FALSE | FALSE
2025-03-06 16:00 | 28.2 | 36.5 | 101175 | 100 | 3000 | 21.8966 | 54.9017 | 36.6124 | 0 | 7.2692 | FALSE | FALSE
2025-03-06 17:00 | 27.65 | 38 | 101200 | 100 | 3000 | 21.6778 | 55.8344 | 36.1813 | 0 | 7.2692 | FALSE | FALSE
2025-03-06 18:00 | 26.4 | 40 | 101245 | 100 | 3000 | 21.1795 | 57.0011 | 33.8044 | 0 | 7.2692 | FALSE | FALSE
2025-03-06 19:00 | 25.55 | 40.5 | 101290 | 100 | 3000 | 20.8384 | 57.2543 | 31.4197 | 0 | 7.2692 | FALSE | FALSE
2025-03-06 20:00 | 25 | 39 | 101300 | 100 | 3000 | 20.6184 | 56.3372 | 28.4498 | 0 | 7.2692 | FALSE | FALSE
2025-03-06 21:00 | 24.45 | 37.5 | 101295 | 100 | 3000 | 20.3964 | 55.4659 | 26.5696 | 0 | 7.2692 | FALSE | FALSE
2025-03-06 22:00 | 23.85 | 37 | 101280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-06 23:00 | 23.2 | 35 | 101220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-07 | 23.2 | 26.5 | 101150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-07 01:00 | 23.65 | 18.5 | 101085 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-07 02:00 | 23.85 | 18 | 101035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-07 03:00 | 23.35 | 21.5 | 101025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-07 04:00 | 21.85 | 25.5 | 101060 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-07 05:00 | 20.8 | 27.5 | 101110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-07 06:00 | 20.65 | 29 | 101150 | 100 | 3000 | 18.8134 | 51.6002 | 21.1658 | 0 | 7.2692 | FALSE | FALSE
2025-03-07 07:00 | 21.8 | 28.5 | 101205 | 100 | 3000 | 19.3028 | 50.9139 | 22.8669 | 0 | 7.2692 | FALSE | FALSE
2025-03-07 08:00 | 24.95 | 24.5 | 101265 | 100 | 3000 | 20.6179 | 47.6539 | 27.3599 | 0 | 7.2692 | FALSE | FALSE
2025-03-07 09:00 | 28.5 | 20 | 101295 | 100 | 3000 | 22.0548 | 43.8827 | 32.1482 | 0 | 7.2692 | FALSE | FALSE
2025-03-07 10:00 | 31 | 17.5 | 101290 | 100 | 3000 | 23.0372 | 41.5819 | 35.3411 | 0 | 7.2692 | FALSE | FALSE
2025-03-07 11:00 | 32.65 | 16.5 | 101250 | 100 | 3000 | 23.6702 | 40.5178 | 37.3486 | 0 | 7.2692 | FALSE | FALSE
2025-03-07 12:00 | 33.4 | 17 | 101160 | 100 | 3000 | 23.9498 | 40.784 | 38.189 | 0 | 7.2692 | FALSE | FALSE
2025-03-07 13:00 | 33.25 | 20 | 101050 | 100 | 3000 | 23.8795 | 43.1378 | 37.8941 | 0 | 7.2692 | FALSE | FALSE
2025-03-07 14:00 | 33.25 | 22 | 100955 | 100 | 3000 | 23.87 | 44.6931 | 37.8067 | 0 | 7.2692 | FALSE | FALSE
2025-03-07 15:00 | 33.35 | 22.5 | 100880 | 100 | 3000 | 23.9048 | 45.0836 | 37.8813 | 0 | 7.2692 | FALSE | FALSE
2025-03-07 16:00 | 32.9 | 25.5 | 100820 | 100 | 3000 | 23.7236 | 47.3988 | 39.5817 | 0 | 7.2692 | FALSE | FALSE
2025-03-07 17:00 | 31.5 | 30.5 | 100775 | 100 | 3000 | 23.1794 | 51.06 | 40.9808 | 0 | 7.2692 | FALSE | FALSE
2025-03-07 18:00 | 29.45 | 34 | 100755 | 100 | 3000 | 22.3879 | 53.3624 | 38.1724 | 0 | 7.2692 | FALSE | FALSE
2025-03-07 19:00 | 27.95 | 37.5 | 100785 | 100 | 3000 | 21.7966 | 55.5755 | 36.6436 | 0 | 7.2692 | FALSE | FALSE
2025-03-07 20:00 | 27.45 | 35.5 | 100850 | 100 | 3000 | 21.6047 | 54.2345 | 33.2712 | 0 | 7.2692 | FALSE | FALSE
2025-03-07 21:00 | 26.85 | 30.5 | 100870 | 100 | 3000 | 21.3768 | 51.0449 | 29.7368 | 0 | 7.2692 | FALSE | FALSE
2025-03-07 22:00 | 25.75 | 31 | 100845 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-07 23:00 | 24.8 | 31.5 | 100815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-08 | 24.9 | 28.5 | 100790 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-08 01:00 | 25.3 | 24 | 100760 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-08 02:00 | 24.25 | 23 | 100735 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-08 03:00 | 22.85 | 24.5 | 100730 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-08 04:00 | 22.6 | 24 | 100710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-08 05:00 | 22.8 | 23.5 | 100720 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-08 06:00 | 22.6 | 28 | 100780 | 100 | 3000 | 19.6402 | 50.4236 | 23.9235 | 0 | 7.2692 | FALSE | FALSE
2025-03-08 07:00 | 23.2 | 33.5 | 100845 | 100 | 3000 | 19.8858 | 53.3583 | 24.7529 | 0 | 7.2692 | FALSE | FALSE
2025-03-08 08:00 | 25.15 | 33 | 100910 | 100 | 3000 | 20.6879 | 52.7622 | 27.4601 | 0 | 7.2692 | FALSE | FALSE
2025-03-08 09:00 | 27.4 | 28 | 100940 | 100 | 3000 | 21.6009 | 49.3778 | 30.5056 | 0 | 7.2692 | FALSE | FALSE
2025-03-08 10:00 | 29.7 | 21.5 | 100905 | 100 | 3000 | 22.5215 | 44.6973 | 33.524 | 0 | 7.2692 | FALSE | FALSE
2025-03-08 11:00 | 32 | 15.5 | 100815 | 100 | 3000 | 23.4282 | 39.9355 | 36.4369 | 0 | 7.2692 | FALSE | FALSE
2025-03-08 12:00 | 34 | 11 | 100705 | 100 | 3000 | 24.2052 | 35.9843 | 38.8846 | 0 | 7.2692 | FALSE | FALSE
2025-03-08 13:00 | 35.4 | 9 | 100590 | 100 | 3000 | 24.7381 | 33.9785 | 40.5178 | 0 | 7.2692 | FALSE | FALSE
2025-03-08 14:00 | 36.15 | 9 | 100490 | 100 | 3000 | 25.0146 | 33.7741 | 41.3271 | 0 | 7.2692 | FALSE | FALSE
2025-03-08 15:00 | 36.2 | 9.5 | 100420 | 100 | 3000 | 25.0297 | 34.1888 | 41.3374 | 0 | 7.2692 | FALSE | FALSE
2025-03-08 16:00 | 35.75 | 11 | 100400 | 100 | 3000 | 24.8548 | 35.5621 | 40.7727 | 0 | 7.2692 | FALSE | FALSE
2025-03-08 17:00 | 34.2 | 15.5 | 100410 | 100 | 3000 | 24.2563 | 39.539 | 38.876 | 0 | 7.2692 | FALSE | FALSE
2025-03-08 18:00 | 31.3 | 20 | 100415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-08 19:00 | 28.75 | 22.5 | 100450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-08 20:00 | 27.1 | 23.5 | 100505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-08 21:00 | 25.8 | 24 | 100535 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-08 22:00 | 24.45 | 28 | 100535 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-08 23:00 | 23.7 | 30.5 | 100510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 | 23.5 | 30 | 100480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 01:00 | 23.05 | 32 | 100455 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 02:00 | 22.65 | 35.5 | 100425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 03:00 | 22.35 | 39 | 100420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 04:00 | 22.1 | 36.5 | 100455 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 05:00 | 22 | 33 | 100510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 06:00 | 22.4 | 34 | 100575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 07:00 | 24.2 | 31 | 100660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 08:00 | 26.9 | 26.5 | 100745 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 09:00 | 28.5 | 26 | 100845 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 10:00 | 29.75 | 25 | 100895 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 11:00 | 31.35 | 21.5 | 100850 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 12:00 | 32.4 | 19.5 | 100795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 13:00 | 31 | 28.5 | 100770 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 14:00 | 28.8 | 39 | 100770 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 15:00 | 28.2 | 41 | 100765 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 16:00 | 27.95 | 39.5 | 100765 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 17:00 | 27.2 | 40.5 | 100820 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 18:00 | 25.85 | 47 | 100890 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 19:00 | 24.85 | 52 | 100945 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 20:00 | 24.25 | 55.5 | 101025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 21:00 | 23.7 | 58.5 | 101085 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 22:00 | 22.95 | 62 | 101085 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-09 23:00 | 22.05 | 66.5 | 101065 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-10 | 21.4 | 70 | 101045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-10 01:00 | 20.95 | 72 | 101005 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-10 02:00 | 20.5 | 74 | 100965 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-10 03:00 | 20.05 | 76 | 100950 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-10 04:00 | 20.45 | 69 | 100905 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-10 05:00 | 21.3 | 60 | 100895 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-10 06:00 | 21.35 | 59 | 100965 | 100 | 3000 | 19.0947 | 67.3868 | 29.8508 | 0 | 7.2692 | FALSE | FALSE
2025-03-10 07:00 | 22.3 | 56 | 101045 | 100 | 3000 | 19.493 | 65.9034 | 31.4152 | 0 | 7.2692 | FALSE | FALSE
2025-03-10 08:00 | 23.85 | 53 | 101135 | 100 | 3000 | 20.1334 | 64.4747 | 35.03 | 0 | 7.2692 | FALSE | FALSE
2025-03-10 09:00 | 25.85 | 49 | 101170 | 100 | 3000 | 20.945 | 62.5029 | 39.2707 | 0 | 7.2692 | FALSE | FALSE
2025-03-10 10:00 | 28.4 | 42 | 101165 | 100 | 3000 | 21.9608 | 58.5797 | 42.3097 | 0 | 7.2692 | FALSE | FALSE
2025-03-10 11:00 | 30.15 | 36.5 | 101130 | 100 | 3000 | 22.6478 | 55.1548 | 42.9662 | 0 | 7.2692 | FALSE | FALSE
2025-03-10 12:00 | 31.4 | 32.5 | 101040 | 100 | 3000 | 23.134 | 52.4881 | 42.861 | 0 | 7.2692 | FALSE | FALSE
2025-03-10 13:00 | 31.85 | 31.5 | 100955 | 100 | 3000 | 23.3065 | 51.8193 | 43.1813 | 0 | 7.2692 | FALSE | FALSE
2025-03-10 14:00 | 31.5 | 32.5 | 100895 | 100 | 3000 | 23.1716 | 52.5145 | 43.1466 | 0 | 7.2692 | FALSE | FALSE
2025-03-10 15:00 | 30.45 | 35.5 | 100870 | 100 | 3000 | 22.765 | 54.5224 | 42.8927 | 0 | 7.2692 | FALSE | FALSE
2025-03-10 16:00 | 30.05 | 36 | 100855 | 100 | 3000 | 22.6114 | 54.8132 | 42.0854 | 0 | 7.2692 | FALSE | FALSE
2025-03-10 17:00 | 29 | 41 | 100870 | 100 | 3000 | 22.1949 | 58.0626 | 43.4046 | 0 | 7.2692 | FALSE | FALSE
2025-03-10 18:00 | 26.65 | 51.5 | 100935 | 100 | 3000 | 21.2572 | 64.2908 | 44.2495 | 0 | 7.2692 | FALSE | FALSE
2025-03-10 19:00 | 25.4 | 55.5 | 101015 | 100 | 3000 | 20.7554 | 66.3551 | 42.7381 | 0 | 7.2692 | FALSE | FALSE
2025-03-10 20:00 | 25 | 56 | 101085 | 100 | 3000 | 20.5947 | 66.5232 | 41.5961 | 0 | 7.2692 | FALSE | FALSE
2025-03-10 21:00 | 24.65 | 56 | 101090 | 100 | 3000 | 20.454 | 66.4189 | 40.2537 | 0 | 7.2692 | FALSE | FALSE
2025-03-10 22:00 | 24.25 | 55 | 101030 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-10 23:00 | 24.05 | 52.5 | 100990 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-11 | 23.75 | 49 | 100975 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-11 01:00 | 23.25 | 46.5 | 100955 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-11 02:00 | 23 | 46 | 100940 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-11 03:00 | 22.5 | 48 | 100935 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-11 04:00 | 22.9 | 50.5 | 100915 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-11 05:00 | 23.35 | 53 | 100930 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-11 06:00 | 22.9 | 55 | 101015 | 100 | 3000 | 19.742 | 65.4512 | 32.9431 | 0 | 7.2692 | FALSE | FALSE
2025-03-11 07:00 | 23.75 | 52 | 101115 | 100 | 3000 | 20.0937 | 63.8838 | 33.9345 | 0 | 7.2692 | FALSE | FALSE
2025-03-11 08:00 | 25.35 | 46.5 | 101185 | 100 | 3000 | 20.7489 | 60.8867 | 35.4938 | 0 | 7.2692 | FALSE | FALSE
2025-03-11 09:00 | 26.35 | 45 | 101265 | 100 | 3000 | 21.1506 | 60.116 | 37.7961 | 0 | 7.2692 | FALSE | FALSE
2025-03-11 10:00 | 27.4 | 42.5 | 101305 | 100 | 3000 | 21.5699 | 58.705 | 39.3217 | 0 | 7.2692 | FALSE | FALSE
2025-03-11 11:00 | 28.45 | 37.5 | 101255 | 100 | 3000 | 21.9914 | 55.5835 | 38.3566 | 0 | 7.2692 | FALSE | FALSE
2025-03-11 12:00 | 29.25 | 34 | 101165 | 100 | 3000 | 22.3106 | 53.3078 | 37.6174 | 0 | 7.2692 | FALSE | FALSE
2025-03-11 13:00 | 30.1 | 30.5 | 101050 | 100 | 3000 | 22.648 | 50.9436 | 36.7801 | 0 | 7.2692 | FALSE | FALSE
2025-03-11 14:00 | 31.2 | 27 | 100980 | 100 | 3000 | 23.0793 | 48.4738 | 36.3996 | 0 | 7.2692 | FALSE | FALSE
2025-03-11 15:00 | 32.3 | 23.5 | 100935 | 100 | 3000 | 23.5083 | 45.8741 | 36.6523 | 0 | 7.2692 | FALSE | FALSE
2025-03-11 16:00 | 32.3 | 25.5 | 100885 | 100 | 3000 | 23.4998 | 47.3813 | 37.8903 | 0 | 7.2692 | FALSE | FALSE
2025-03-11 17:00 | 29.9 | 35.5 | 100900 | 100 | 3000 | 22.5558 | 54.4379 | 41.1092 | 0 | 7.2692 | FALSE | FALSE
2025-03-11 18:00 | 27.5 | 44.5 | 100965 | 100 | 3000 | 21.6048 | 60.0484 | 41.3659 | 0 | 7.2692 | FALSE | FALSE
2025-03-11 19:00 | 26.95 | 49 | 101030 | 100 | 3000 | 21.3799 | 62.7898 | 43.2746 | 0 | 7.2692 | FALSE | FALSE
2025-03-11 20:00 | 26.6 | 49.5 | 101085 | 100 | 3000 | 21.2413 | 63.0048 | 42.4135 | 0 | 7.2692 | FALSE | FALSE
2025-03-11 21:00 | 26.4 | 47 | 101115 | 100 | 3000 | 21.1669 | 61.3886 | 39.6096 | 0 | 7.2692 | FALSE | FALSE
2025-03-11 22:00 | 26 | 45.5 | 101120 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-11 23:00 | 25.25 | 47.5 | 101100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-12 | 24.4 | 53 | 101065 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-12 01:00 | 23.8 | 56.5 | 101025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-12 02:00 | 23.4 | 58 | 100965 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-12 03:00 | 23 | 62 | 100930 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-12 04:00 | 23.5 | 58.5 | 101025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-12 05:00 | 24.85 | 46.5 | 101095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-12 06:00 | 25.5 | 41 | 101100 | 100 | 3000 | 20.8175 | 57.5754 | 31.6288 | 0 | 7.2692 | FALSE | FALSE
2025-03-12 07:00 | 25.9 | 42 | 101145 | 100 | 3000 | 20.9765 | 58.211 | 33.7728 | 0 | 7.2692 | FALSE | FALSE
2025-03-12 08:00 | 27.1 | 41 | 101195 | 100 | 3000 | 21.455 | 57.7085 | 36.9799 | 0 | 7.2692 | FALSE | FALSE
2025-03-12 09:00 | 28.15 | 43 | 101250 | 100 | 3000 | 21.8614 | 59.181 | 42.3631 | 0 | 7.2692 | FALSE | FALSE
2025-03-12 10:00 | 28.45 | 46.5 | 101265 | 100 | 3000 | 21.9688 | 61.5757 | 46.6243 | 0 | 7.2692 | FALSE | FALSE
2025-03-12 11:00 | 29.2 | 41 | 101215 | 100 | 3000 | 22.2716 | 58.0737 | 44.1585 | 0 | 7.2692 | FALSE | FALSE
2025-03-12 12:00 | 30.8 | 32.5 | 101120 | 100 | 3000 | 22.9078 | 52.408 | 40.9882 | 0 | 7.2692 | FALSE | FALSE
2025-03-12 13:00 | 31.5 | 29.5 | 101020 | 100 | 3000 | 23.1832 | 50.3055 | 39.9602 | 0 | 7.2692 | FALSE | FALSE
2025-03-12 14:00 | 30.5 | 34 | 100935 | 100 | 3000 | 22.789 | 53.4592 | 41.5415 | 0 | 7.2692 | FALSE | FALSE
2025-03-12 15:00 | 29.15 | 41.5 | 100875 | 100 | 3000 | 22.2511 | 58.4349 | 44.3985 | 0 | 7.2692 | FALSE | FALSE
2025-03-12 16:00 | 28.8 | 41.5 | 100850 | 100 | 3000 | 22.1166 | 58.3594 | 43.1789 | 0 | 7.2692 | FALSE | FALSE
2025-03-12 17:00 | 27.9 | 44 | 100860 | 100 | 3000 | 21.762 | 59.8209 | 42.318 | 0 | 7.2692 | FALSE | FALSE
2025-03-12 18:00 | 25.55 | 59.5 | 100910 | 100 | 3000 | 20.8089 | 68.8412 | 46.4601 | 0 | 7.2692 | FALSE | FALSE
2025-03-12 19:00 | 23.85 | 72 | 100975 | 100 | 3000 | 20.1123 | 75.4129 | 48.7759 | 0 | 7.2692 | FALSE | FALSE
2025-03-12 20:00 | 23.15 | 76.5 | 101035 | 100 | 3000 | 19.8245 | 77.5757 | 48.8859 | 0 | 7.2692 | FALSE | FALSE
2025-03-12 21:00 | 22.7 | 78 | 101075 | 100 | 3000 | 19.6399 | 78.1537 | 47.9163 | 0 | 7.2692 | FALSE | FALSE
2025-03-12 22:00 | 22.25 | 78.5 | 101085 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-12 23:00 | 21.75 | 80.5 | 101075 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-13 | 21.25 | 83 | 101060 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-13 01:00 | 20.95 | 84.5 | 101025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-13 02:00 | 20.85 | 85 | 101005 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-13 03:00 | 20.7 | 84.5 | 100985 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-13 04:00 | 21.1 | 81.5 | 100965 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-13 05:00 | 21.6 | 78.5 | 100995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-13 06:00 | 21.45 | 78 | 101045 | 100 | 3000 | 19.1252 | 77.5113 | 42.408 | 0 | 7.2692 | FALSE | FALSE
2025-03-13 07:00 | 22.25 | 73.5 | 101110 | 100 | 3000 | 19.459 | 75.4527 | 42.9362 | 0 | 7.2692 | FALSE | FALSE
2025-03-13 08:00 | 24 | 61.5 | 101175 | 100 | 3000 | 20.1848 | 69.4144 | 41.813 | 0 | 7.2692 | FALSE | FALSE
2025-03-13 09:00 | 25.4 | 50 | 101210 | 100 | 3000 | 20.7637 | 63.0099 | 38.4365 | 0 | 7.2692 | FALSE | FALSE
2025-03-13 10:00 | 26.5 | 43 | 101210 | 100 | 3000 | 21.2138 | 58.8937 | 36.642 | 0 | 7.2692 | FALSE | FALSE
2025-03-13 11:00 | 27.3 | 37 | 101175 | 100 | 3000 | 21.5422 | 55.164 | 34.1626 | 0 | 7.2692 | FALSE | FALSE
2025-03-13 12:00 | 27.35 | 35 | 101110 | 100 | 3000 | 21.5662 | 53.884 | 32.5594 | 0 | 7.2692 | FALSE | FALSE
2025-03-13 13:00 | 26.8 | 39 | 101025 | 100 | 3000 | 21.3404 | 56.423 | 34.2432 | 0 | 7.2692 | FALSE | FALSE
2025-03-13 14:00 | 26.25 | 44 | 100940 | 100 | 3000 | 21.1128 | 59.5099 | 36.5739 | 0 | 7.2692 | FALSE | FALSE
2025-03-13 15:00 | 25.55 | 50 | 100890 | 100 | 3000 | 20.8237 | 63.0755 | 38.9407 | 0 | 7.2692 | FALSE | FALSE
2025-03-13 16:00 | 24.9 | 54.5 | 100890 | 100 | 3000 | 20.5566 | 65.6206 | 40.0372 | 0 | 7.2692 | FALSE | FALSE
2025-03-13 17:00 | 23.95 | 61.5 | 100900 | 100 | 3000 | 20.1646 | 69.4261 | 41.5826 | 0 | 7.2692 | FALSE | FALSE
2025-03-13 18:00 | 22.7 | 71 | 100915 | 100 | 3000 | 19.6459 | 74.3009 | 43.1473 | 0 | 7.2692 | FALSE | FALSE
2025-03-13 19:00 | 22 | 75.5 | 100970 | 100 | 3000 | 19.3545 | 76.4392 | 43.1707 | 0 | 7.2692 | FALSE | FALSE
2025-03-13 20:00 | 21.5 | 78 | 101025 | 100 | 3000 | 19.146 | 77.5374 | 42.6242 | 0 | 7.2692 | FALSE | FALSE
2025-03-13 21:00 | 20.9 | 81 | 101045 | 100 | 3000 | 18.8945 | 78.8265 | 41.8825 | 0 | 7.2692 | FALSE | FALSE
2025-03-13 22:00 | 20.3 | 85 | 101035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-13 23:00 | 19.75 | 88.5 | 101020 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-14 | 19.25 | 90.5 | 101005 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-14 01:00 | 18.7 | 92 | 100975 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-14 02:00 | 18.1 | 93.5 | 100955 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-14 03:00 | 17.45 | 95 | 100955 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-14 04:00 | 17 | 95 | 100975 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-14 05:00 | 16.7 | 94.5 | 101015 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-14 06:00 | 16.5 | 95 | 101080 | 100 | 3000 | 17.0069 | 83.7005 | 30.1285 | 0 | 7.2692 | FALSE | FALSE
2025-03-14 07:00 | 17.55 | 89.5 | 101150 | 100 | 3000 | 17.4652 | 81.5588 | 31.9861 | 0 | 7.2692 | FALSE | FALSE
2025-03-14 08:00 | 20.05 | 77.5 | 101220 | 100 | 3000 | 18.5388 | 76.6385 | 36.1 | 0 | 7.2692 | FALSE | FALSE
2025-03-14 09:00 | 22.6 | 66.5 | 101255 | 100 | 3000 | 19.6086 | 71.7364 | 39.705 | 0 | 7.2692 | FALSE | FALSE
2025-03-14 10:00 | 24.6 | 58.5 | 101240 | 100 | 3000 | 20.4306 | 67.8618 | 41.9665 | 0 | 7.2692 | FALSE | FALSE
2025-03-14 11:00 | 26.2 | 52 | 101195 | 100 | 3000 | 21.0788 | 64.4408 | 43.0056 | 0 | 7.2692 | FALSE | FALSE
2025-03-14 12:00 | 27.45 | 47.5 | 101100 | 100 | 3000 | 21.5787 | 61.9601 | 43.8295 | 0 | 7.2692 | FALSE | FALSE
2025-03-14 13:00 | 28.1 | 48 | 100995 | 100 | 3000 | 21.83 | 62.4864 | 46.6471 | 0 | 7.2692 | FALSE | FALSE
2025-03-14 14:00 | 27.9 | 51.5 | 100920 | 100 | 3000 | 21.7445 | 64.7196 | 49.0033 | 0 | 7.2692 | FALSE | FALSE
2025-03-14 15:00 | 27.15 | 53.5 | 100885 | 100 | 3000 | 21.449 | 65.7335 | 47.8442 | 0 | 7.2692 | FALSE | FALSE
2025-03-14 16:00 | 26.15 | 56.5 | 100895 | 100 | 3000 | 21.0512 | 67.24 | 46.4402 | 0 | 7.2692 | FALSE | FALSE
2025-03-14 17:00 | 24.9 | 62 | 100920 | 100 | 3000 | 20.5463 | 70.0763 | 45.7763 | 0 | 7.2692 | FALSE | FALSE
2025-03-14 18:00 | 23.6 | 69 | 100950 | 100 | 3000 | 20.0145 | 73.5779 | 45.5558 | 0 | 7.2692 | FALSE | FALSE
2025-03-14 19:00 | 22.5 | 77.5 | 100990 | 100 | 3000 | 19.5586 | 77.7782 | 46.6835 | 0 | 7.2692 | FALSE | FALSE
2025-03-14 20:00 | 21.55 | 87 | 101035 | 100 | 3000 | 19.1611 | 82.3509 | 48.5889 | 0 | 7.2692 | FALSE | FALSE
2025-03-14 21:00 | 20.75 | 94 | 101045 | 100 | 3000 | 18.8256 | 85.4943 | 49.1755 | 0 | 7.2692 | FALSE | FALSE
2025-03-14 22:00 | 19.95 | 97.5 | 101040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-14 23:00 | 19.25 | 98.5 | 101050 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-15 | 18.75 | 98.5 | 101025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-15 01:00 | 18.2 | 99 | 100980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-15 02:00 | 17.7 | 99.5 | 100945 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-15 03:00 | 17.05 | 100 | 100945 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-15 04:00 | 17.65 | 100 | 100980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-15 05:00 | 18.75 | 100 | 101035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-15 06:00 | 18.7 | 99.5 | 101095 | 100 | 3000 | 17.9596 | 86.9045 | 42.5748 | 0 | 7.2692 | FALSE | FALSE
2025-03-15 07:00 | 18.75 | 97 | 101165 | 100 | 3000 | 17.9814 | 85.7131 | 41.4404 | 0 | 7.2692 | FALSE | FALSE
2025-03-15 08:00 | 20.1 | 86.5 | 101235 | 100 | 3000 | 18.5566 | 81.234 | 41.6595 | 0 | 7.2692 | FALSE | FALSE
2025-03-15 09:00 | 23.15 | 66.5 | 101285 | 100 | 3000 | 19.834 | 71.9373 | 41.9554 | 0 | 7.2692 | FALSE | FALSE
2025-03-15 10:00 | 26.4 | 45.5 | 101290 | 100 | 3000 | 21.1696 | 60.4343 | 38.3902 | 0 | 7.2692 | FALSE | FALSE
2025-03-15 11:00 | 28.8 | 31 | 101245 | 100 | 3000 | 22.1443 | 51.2459 | 33.3886 | 0 | 7.2692 | FALSE | FALSE
2025-03-15 12:00 | 30.4 | 24 | 101175 | 100 | 3000 | 22.7842 | 46.3376 | 34.4366 | 0 | 7.2692 | FALSE | FALSE
2025-03-15 13:00 | 31 | 24 | 101085 | 100 | 3000 | 23.0141 | 46.2978 | 35.1392 | 0 | 7.2692 | FALSE | FALSE
2025-03-15 14:00 | 30.3 | 30 | 101010 | 100 | 3000 | 22.7262 | 50.6025 | 36.8698 | 0 | 7.2692 | FALSE | FALSE
2025-03-15 15:00 | 29.1 | 38.5 | 100975 | 100 | 3000 | 22.2403 | 56.375 | 41.3964 | 0 | 7.2692 | FALSE | FALSE
2025-03-15 16:00 | 27.6 | 41.5 | 101000 | 100 | 3000 | 21.6505 | 58.1208 | 39.0802 | 0 | 7.2692 | FALSE | FALSE
2025-03-15 17:00 | 25.85 | 49 | 101050 | 100 | 3000 | 20.945 | 62.515 | 39.254 | 0 | 7.2692 | FALSE | FALSE
2025-03-15 18:00 | 24.5 | 64 | 101090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-15 19:00 | 23.75 | 69.5 | 101145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-15 20:00 | 23.25 | 69.5 | 101200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-15 21:00 | 22.4 | 70 | 101230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-15 22:00 | 21.35 | 71 | 101225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-15 23:00 | 20.3 | 73 | 101185 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 | 19.4 | 71 | 101150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 01:00 | 18.65 | 63 | 101120 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 02:00 | 17.95 | 51 | 101100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 03:00 | 17.05 | 38.5 | 101110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 04:00 | 16.75 | 45 | 101160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 05:00 | 16.9 | 56 | 101230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 06:00 | 16.9 | 52 | 101285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 07:00 | 18.5 | 45 | 101340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 08:00 | 22.1 | 37.5 | 101390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 09:00 | 26.05 | 28.5 | 101425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 10:00 | 29.2 | 20 | 101415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 11:00 | 31.75 | 14 | 101340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 12:00 | 33.5 | 9 | 101230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 13:00 | 33.6 | 8 | 101140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 14:00 | 32.2 | 16.5 | 101065 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 15:00 | 30.85 | 28.5 | 100980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 16:00 | 28.75 | 38.5 | 100970 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 17:00 | 26.25 | 47.5 | 101010 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 18:00 | 25 | 54.5 | 101035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 19:00 | 24.05 | 60 | 101080 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 20:00 | 23.35 | 65 | 101135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 21:00 | 22.8 | 69.5 | 101165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 22:00 | 22.35 | 71.5 | 101165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-16 23:00 | 22.05 | 74.5 | 101175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-17 | 21.45 | 80 | 101160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-17 01:00 | 21.15 | 81 | 101135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-17 02:00 | 21.1 | 78 | 101120 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-17 03:00 | 20.6 | 77.5 | 101075 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-17 04:00 | 20.95 | 84.5 | 101045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-17 05:00 | 21.6 | 90 | 101065 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-17 06:00 | 21.6 | 87 | 101115 | 100 | 3000 | 19.1818 | 82.3736 | 48.8277 | 0 | 7.2692 | FALSE | FALSE
2025-03-17 07:00 | 22.15 | 81 | 101185 | 100 | 3000 | 19.4123 | 79.4729 | 47.4645 | 0 | 7.2692 | FALSE | FALSE
2025-03-17 08:00 | 24 | 65.5 | 101255 | 100 | 3000 | 20.1802 | 71.7153 | 44.7388 | 0 | 7.2692 | FALSE | FALSE
2025-03-17 09:00 | 26.1 | 46 | 101310 | 100 | 3000 | 21.0495 | 60.6897 | 37.7479 | 0 | 7.2692 | FALSE | FALSE
2025-03-17 10:00 | 27.3 | 35 | 101340 | 100 | 3000 | 21.5463 | 53.8609 | 32.4397 | 0 | 7.2692 | FALSE | FALSE
2025-03-17 11:00 | 27.05 | 36.5 | 101335 | 100 | 3000 | 21.4443 | 54.8164 | 32.9541 | 0 | 7.2692 | FALSE | FALSE
2025-03-17 12:00 | 25.8 | 47 | 101295 | 100 | 3000 | 20.9283 | 61.2537 | 37.4961 | 0 | 7.2692 | FALSE | FALSE
2025-03-17 13:00 | 25.65 | 48.5 | 101200 | 100 | 3000 | 20.866 | 62.1519 | 38.1503 | 0 | 7.2692 | FALSE | FALSE
2025-03-17 14:00 | 26.4 | 42 | 101100 | 100 | 3000 | 21.1759 | 58.2661 | 35.4507 | 0 | 7.2692 | FALSE | FALSE
2025-03-17 15:00 | 26.85 | 37.5 | 101045 | 100 | 3000 | 21.3631 | 55.4731 | 33.1286 | 0 | 7.2692 | FALSE | FALSE
2025-03-17 16:00 | 27.15 | 34.5 | 101045 | 100 | 3000 | 21.4881 | 53.567 | 31.4894 | 0 | 7.2692 | FALSE | FALSE
2025-03-17 17:00 | 26.45 | 38 | 101075 | 100 | 3000 | 21.2031 | 55.7686 | 32.2697 | 0 | 7.2692 | FALSE | FALSE
2025-03-17 18:00 | 24.55 | 50.5 | 101100 | 100 | 3000 | 20.4208 | 63.1512 | 35.7213 | 0 | 7.2692 | FALSE | FALSE
2025-03-17 19:00 | 22.85 | 66 | 101115 | 100 | 3000 | 19.7117 | 71.5638 | 40.3662 | 0 | 7.2692 | FALSE | FALSE
2025-03-17 20:00 | 21.9 | 76.5 | 101135 | 100 | 3000 | 19.3125 | 76.9134 | 43.4056 | 0 | 7.2692 | FALSE | FALSE
2025-03-17 21:00 | 21.3 | 82.5 | 101150 | 100 | 3000 | 19.0603 | 79.8071 | 44.6053 | 0 | 7.2692 | FALSE | FALSE
2025-03-17 22:00 | 20.7 | 86.5 | 101145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-17 23:00 | 19.85 | 90 | 101115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-18 | 18.85 | 94 | 101090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-18 01:00 | 18.1 | 97 | 101070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-18 02:00 | 17.7 | 98.5 | 101025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-18 03:00 | 17.5 | 99.5 | 100985 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-18 04:00 | 17.7 | 100 | 100995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-18 05:00 | 17.7 | 100 | 101040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-18 06:00 | 17.25 | 100 | 101095 | 100 | 3000 | 17.3349 | 86.3224 | 36.0303 | 0 | 7.2692 | FALSE | FALSE
2025-03-18 07:00 | 17.7 | 99 | 101165 | 100 | 3000 | 17.53 | 86.0824 | 37.6064 | 0 | 7.2692 | FALSE | FALSE
2025-03-18 08:00 | 18.9 | 96.5 | 101225 | 100 | 3000 | 18.0455 | 85.5503 | 41.8703 | 0 | 7.2692 | FALSE | FALSE
2025-03-18 09:00 | 21.5 | 81.5 | 101240 | 100 | 3000 | 19.1439 | 79.3747 | 44.8741 | 0 | 7.2692 | FALSE | FALSE
2025-03-18 10:00 | 25.05 | 54.5 | 101215 | 100 | 3000 | 20.6168 | 65.6286 | 40.6471 | 0 | 7.2692 | FALSE | FALSE
2025-03-18 11:00 | 27.4 | 35 | 101165 | 100 | 3000 | 21.5859 | 53.8797 | 32.7247 | 0 | 7.2692 | FALSE | FALSE
2025-03-18 12:00 | 28.2 | 29.5 | 101100 | 100 | 3000 | 21.9135 | 50.2744 | 31.5642 | 0 | 7.2692 | FALSE | FALSE
2025-03-18 13:00 | 27.9 | 31.5 | 101040 | 100 | 3000 | 21.7908 | 51.6116 | 31.1341 | 0 | 7.2692 | FALSE | FALSE
2025-03-18 14:00 | 27.4 | 32.5 | 101005 | 100 | 3000 | 21.5913 | 52.2803 | 30.4973 | 0 | 7.2692 | FALSE | FALSE
2025-03-18 15:00 | 26.9 | 32 | 100995 | 100 | 3000 | 21.3938 | 51.9828 | 29.8206 | 0 | 7.2692 | FALSE | FALSE
2025-03-18 16:00 | 26.25 | 34.5 | 100995 | 100 | 3000 | 21.1294 | 53.5891 | 28.9382 | 0 | 7.2692 | FALSE | FALSE
2025-03-18 17:00 | 25 | 45.5 | 101010 | 100 | 3000 | 20.6094 | 60.2579 | 33.4701 | 0 | 7.2692 | FALSE | FALSE
2025-03-18 18:00 | 23.55 | 58.5 | 101020 | 100 | 3000 | 20.0052 | 67.57 | 37.8634 | 0 | 7.2692 | FALSE | FALSE
2025-03-18 19:00 | 22.6 | 65.5 | 101030 | 100 | 3000 | 19.6094 | 71.2086 | 39.004 | 0 | 7.2692 | FALSE | FALSE
2025-03-18 20:00 | 21.85 | 70.5 | 101065 | 100 | 3000 | 19.2959 | 73.666 | 39.2724 | 0 | 7.2692 | FALSE | FALSE
2025-03-18 21:00 | 21.1 | 75.5 | 101090 | 100 | 3000 | 18.9809 | 76.0302 | 39.3254 | 0 | 7.2692 | FALSE | FALSE
2025-03-18 22:00 | 20.25 | 79.5 | 101085 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-18 23:00 | 19.45 | 83 | 101075 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-19 | 18.75 | 85.5 | 101060 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-19 01:00 | 18 | 86.5 | 101045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-19 02:00 | 17.15 | 88 | 101030 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-19 03:00 | 16.3 | 90 | 101020 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-19 04:00 | 16.3 | 86 | 101035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-19 05:00 | 16.45 | 80.5 | 101090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-19 06:00 | 16.25 | 78 | 101150 | 100 | 3000 | 16.8949 | 75.9484 | 20.7621 | 0 | 7.2692 | FALSE | FALSE
2025-03-19 07:00 | 17.7 | 68 | 101200 | 100 | 3000 | 17.531 | 71.4613 | 21.3339 | 0 | 7.2692 | FALSE | FALSE
2025-03-19 08:00 | 21 | 52 | 101255 | 100 | 3000 | 18.9512 | 63.6173 | 24.1471 | 0 | 7.2692 | FALSE | FALSE
2025-03-19 09:00 | 24.35 | 38.5 | 101290 | 100 | 3000 | 20.3543 | 56.0601 | 26.4229 | 0 | 7.2692 | FALSE | FALSE
2025-03-19 10:00 | 26.85 | 29.5 | 101285 | 100 | 3000 | 21.3785 | 50.369 | 29.8695 | 0 | 7.2692 | FALSE | FALSE
2025-03-19 11:00 | 28.55 | 24 | 101240 | 100 | 3000 | 22.0646 | 46.5586 | 32.1357 | 0 | 7.2692 | FALSE | FALSE
2025-03-19 12:00 | 29.45 | 22.5 | 101170 | 100 | 3000 | 22.421 | 45.4057 | 33.2795 | 0 | 7.2692 | FALSE | FALSE
2025-03-19 13:00 | 29.5 | 23 | 101095 | 100 | 3000 | 22.4391 | 45.75 | 33.3096 | 0 | 7.2692 | FALSE | FALSE
2025-03-19 14:00 | 28.9 | 25 | 101035 | 100 | 3000 | 22.1994 | 47.2028 | 32.5014 | 0 | 7.2692 | FALSE | FALSE
2025-03-19 15:00 | 28.05 | 29.5 | 101005 | 100 | 3000 | 21.8545 | 50.2923 | 31.3433 | 0 | 7.2692 | FALSE | FALSE
2025-03-19 16:00 | 27.05 | 35 | 101015 | 100 | 3000 | 21.4474 | 53.8895 | 31.6075 | 0 | 7.2692 | FALSE | FALSE
2025-03-19 17:00 | 25.65 | 43.5 | 101040 | 100 | 3000 | 20.8739 | 59.1167 | 34.1244 | 0 | 7.2692 | FALSE | FALSE
2025-03-19 18:00 | 24.05 | 56 | 101055 | 100 | 3000 | 20.2114 | 66.2605 | 37.9641 | 0 | 7.2692 | FALSE | FALSE
2025-03-19 19:00 | 22.85 | 67.5 | 101085 | 100 | 3000 | 19.7104 | 72.4019 | 41.3949 | 0 | 7.2692 | FALSE | FALSE
2025-03-19 20:00 | 22 | 74.5 | 101135 | 100 | 3000 | 19.3552 | 75.8801 | 42.529 | 0 | 7.2692 | FALSE | FALSE
2025-03-19 21:00 | 21.2 | 78 | 101180 | 100 | 3000 | 19.0212 | 77.3796 | 41.3318 | 0 | 7.2692 | FALSE | FALSE
2025-03-19 22:00 | 20.35 | 80 | 101200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-19 23:00 | 19.25 | 83 | 101175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-20 | 18.2 | 85.5 | 101135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-20 01:00 | 17.3 | 86.5 | 101105 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-20 02:00 | 16.35 | 87 | 101090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-20 03:00 | 15.6 | 86.5 | 101100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-20 04:00 | 15.9 | 83 | 101115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-20 05:00 | 16.35 | 78.5 | 101170 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-20 06:00 | 16.25 | 74 | 101250 | 100 | 3000 | 16.8944 | 74.1312 | 18.8106 | 0 | 7.2692 | FALSE | FALSE
2025-03-20 07:00 | 17.7 | 64.5 | 101305 | 100 | 3000 | 17.5312 | 69.7913 | 19.4844 | 0 | 7.2692 | FALSE | FALSE
2025-03-20 08:00 | 21.4 | 49.5 | 101350 | 100 | 3000 | 19.1211 | 62.2828 | 23.9422 | 0 | 7.2692 | FALSE | FALSE
2025-03-20 09:00 | 25.7 | 34 | 101370 | 100 | 3000 | 20.9089 | 53.2729 | 28.3163 | 0 | 7.2692 | FALSE | FALSE
2025-03-20 10:00 | 29.2 | 22.5 | 101360 | 100 | 3000 | 22.3233 | 45.4282 | 33.025 | 0 | 7.2692 | FALSE | FALSE
2025-03-20 11:00 | 31.7 | 16 | 101315 | 100 | 3000 | 23.3112 | 40.3313 | 36.2386 | 0 | 7.2692 | FALSE | FALSE
2025-03-20 12:00 | 33.1 | 14.5 | 101235 | 100 | 3000 | 23.849 | 38.8978 | 37.9283 | 0 | 7.2692 | FALSE | FALSE
2025-03-20 13:00 | 33.3 | 17.5 | 101155 | 100 | 3000 | 23.91 | 41.1872 | 38.0568 | 0 | 7.2692 | FALSE | FALSE
2025-03-20 14:00 | 32.6 | 21 | 101075 | 100 | 3000 | 23.6317 | 43.9566 | 37.1163 | 0 | 7.2692 | FALSE | FALSE
2025-03-20 15:00 | 31.55 | 23.5 | 101010 | 100 | 3000 | 23.2252 | 45.9042 | 35.7872 | 0 | 7.2692 | FALSE | FALSE
2025-03-20 16:00 | 30.25 | 29.5 | 101000 | 100 | 3000 | 22.7087 | 50.249 | 36.2117 | 0 | 7.2692 | FALSE | FALSE
2025-03-20 17:00 | 28.3 | 40.5 | 101020 | 100 | 3000 | 21.9258 | 57.5787 | 40.5691 | 0 | 7.2692 | FALSE | FALSE
2025-03-20 18:00 | 26.35 | 50.5 | 101045 | 100 | 3000 | 21.1408 | 63.5665 | 42.3126 | 0 | 7.2692 | FALSE | FALSE
2025-03-20 19:00 | 25.05 | 58.5 | 101105 | 100 | 3000 | 20.6112 | 68.03 | 43.7182 | 0 | 7.2692 | FALSE | FALSE
2025-03-20 20:00 | 24.1 | 63.5 | 101175 | 100 | 3000 | 20.2229 | 70.6083 | 43.6785 | 0 | 7.2692 | FALSE | FALSE
2025-03-20 21:00 | 23.3 | 64 | 101225 | 100 | 3000 | 19.8976 | 70.591 | 40.8062 | 0 | 7.2692 | FALSE | FALSE
2025-03-20 22:00 | 22.4 | 64.5 | 101260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-20 23:00 | 21.5 | 65.5 | 101250 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-21 | 20.7 | 64 | 101215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-21 01:00 | 19.95 | 59 | 101185 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-21 02:00 | 19.15 | 54 | 101155 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-21 03:00 | 18.45 | 52.5 | 101135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-21 04:00 | 18.1 | 53.5 | 101130 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-21 05:00 | 17.7 | 56.5 | 101155 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-21 06:00 | 17.8 | 56 | 101205 | 100 | 3000 | 17.5752 | 65.7624 | 16.7956 | 0 | 7.2692 | FALSE | FALSE
2025-03-21 07:00 | 20.4 | 42.5 | 101265 | 100 | 3000 | 18.7008 | 58.6956 | 20.7669 | 0 | 7.2692 | FALSE | FALSE
2025-03-21 08:00 | 25.4 | 26 | 101335 | 100 | 3000 | 20.7996 | 48.4375 | 27.9802 | 0 | 7.2692 | FALSE | FALSE
2025-03-21 09:00 | 30 | 17.5 | 101375 | 100 | 3000 | 22.65 | 41.8012 | 34.1252 | 0 | 7.2692 | FALSE | FALSE
2025-03-21 10:00 | 33.05 | 15 | 101370 | 100 | 3000 | 23.8277 | 39.2822 | 37.9057 | 0 | 7.2692 | FALSE | FALSE
2025-03-21 11:00 | 35.1 | 13.5 | 101345 | 100 | 3000 | 24.5992 | 37.6903 | 40.3265 | 0 | 7.2692 | FALSE | FALSE
2025-03-21 12:00 | 36.3 | 11.5 | 101280 | 100 | 3000 | 25.0514 | 35.793 | 41.7246 | 0 | 7.2692 | FALSE | FALSE
2025-03-21 13:00 | 36.95 | 11 | 101195 | 100 | 3000 | 25.291 | 35.2378 | 42.4311 | 0 | 7.2692 | FALSE | FALSE
2025-03-21 14:00 | 37.45 | 11 | 101125 | 100 | 3000 | 25.4713 | 35.144 | 42.9514 | 0 | 7.2692 | FALSE | FALSE
2025-03-21 15:00 | 36.65 | 14 | 101075 | 100 | 3000 | 25.1613 | 37.8806 | 41.9385 | 0 | 7.2692 | FALSE | FALSE
2025-03-21 16:00 | 33.55 | 25 | 101095 | 100 | 3000 | 23.9662 | 47.0124 | 40.9132 | 0 | 7.2692 | FALSE | FALSE
2025-03-21 17:00 | 30.6 | 35.5 | 101135 | 100 | 3000 | 22.8217 | 54.5227 | 43.4356 | 0 | 7.2692 | FALSE | FALSE
2025-03-21 18:00 | 29.1 | 40.5 | 101155 | 100 | 3000 | 22.2347 | 57.7175 | 43.3274 | 0 | 7.2692 | FALSE | FALSE
2025-03-21 19:00 | 28.05 | 42 | 101200 | 100 | 3000 | 21.8249 | 58.5068 | 41.1038 | 0 | 7.2692 | FALSE | FALSE
2025-03-21 20:00 | 27.4 | 38.5 | 101245 | 100 | 3000 | 21.5784 | 56.1311 | 35.8113 | 0 | 7.2692 | FALSE | FALSE
2025-03-21 21:00 | 26.95 | 34 | 101260 | 100 | 3000 | 21.4096 | 53.2284 | 30.4729 | 0 | 7.2692 | FALSE | FALSE
2025-03-21 22:00 | 26.45 | 30 | 101240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-21 23:00 | 25.75 | 27 | 101190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-22 | 25.5 | 27 | 101125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-22 01:00 | 25.45 | 31.5 | 101055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-22 02:00 | 25.15 | 32.5 | 100995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-22 03:00 | 24.7 | 30 | 100965 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-22 04:00 | 23.45 | 33.5 | 100980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-22 05:00 | 22.25 | 37.5 | 101035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-22 06:00 | 22.5 | 35 | 101095 | 100 | 3000 | 19.5926 | 54.3085 | 23.813 | 0 | 7.2692 | FALSE | FALSE
2025-03-22 07:00 | 24.6 | 28 | 101165 | 100 | 3000 | 20.4699 | 49.8413 | 26.8215 | 0 | 7.2692 | FALSE | FALSE
2025-03-22 08:00 | 27.6 | 21.5 | 101215 | 100 | 3000 | 21.6942 | 45.0966 | 30.9333 | 0 | 7.2692 | FALSE | FALSE
2025-03-22 09:00 | 30.4 | 16.5 | 101205 | 100 | 3000 | 22.8088 | 41.0117 | 34.588 | 0 | 7.2692 | FALSE | FALSE
2025-03-22 10:00 | 32.7 | 12.5 | 101195 | 100 | 3000 | 23.7069 | 37.4672 | 37.4863 | 0 | 7.2692 | FALSE | FALSE
2025-03-22 11:00 | 34.45 | 10.5 | 101180 | 100 | 3000 | 24.3755 | 35.4229 | 39.6048 | 0 | 7.2692 | FALSE | FALSE
2025-03-22 12:00 | 35.7 | 10 | 101125 | 100 | 3000 | 24.8418 | 34.6837 | 41.0378 | 0 | 7.2692 | FALSE | FALSE
2025-03-22 13:00 | 36.1 | 10.5 | 101045 | 100 | 3000 | 24.9854 | 35.0099 | 41.4411 | 0 | 7.2692 | FALSE | FALSE
2025-03-22 14:00 | 35 | 15 | 100965 | 100 | 3000 | 24.554 | 38.9635 | 40.0173 | 0 | 7.2692 | FALSE | FALSE
2025-03-22 15:00 | 33.1 | 20 | 100915 | 100 | 3000 | 23.8236 | 43.1623 | 37.6695 | 0 | 7.2692 | FALSE | FALSE
2025-03-22 16:00 | 31.2 | 23.5 | 100920 | 100 | 3000 | 23.0923 | 45.9358 | 35.3348 | 0 | 7.2692 | FALSE | FALSE
2025-03-22 17:00 | 29.45 | 29.5 | 100930 | 100 | 3000 | 22.4009 | 50.2496 | 33.8273 | 0 | 7.2692 | FALSE | FALSE
2025-03-22 18:00 | 27.9 | 35 | 100940 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-22 19:00 | 26.8 | 36.5 | 100975 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-22 20:00 | 26.3 | 34.5 | 101015 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-22 21:00 | 25.9 | 32 | 101035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-22 22:00 | 25.4 | 30.5 | 101015 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-22 23:00 | 24.9 | 30 | 100985 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 | 24.4 | 29.5 | 100945 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 01:00 | 24 | 28.5 | 100890 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 02:00 | 23.65 | 27.5 | 100835 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 03:00 | 23.05 | 27 | 100825 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 04:00 | 23 | 31 | 100840 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 05:00 | 23.5 | 34 | 100890 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 06:00 | 23.9 | 32.5 | 100990 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 07:00 | 24.9 | 28.5 | 101110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 08:00 | 26.05 | 28 | 101215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 09:00 | 27.1 | 27.5 | 101240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 10:00 | 29.4 | 22 | 101215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 11:00 | 31.65 | 19.5 | 101150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 12:00 | 32.75 | 18.5 | 101070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 13:00 | 33.65 | 17.5 | 101005 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 14:00 | 32.85 | 21.5 | 100975 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 15:00 | 31.05 | 26.5 | 100985 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 16:00 | 29.8 | 31 | 101005 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 17:00 | 27.85 | 45.5 | 101020 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 18:00 | 26 | 62.5 | 101030 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 19:00 | 25.15 | 71 | 101065 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 20:00 | 24.45 | 76 | 101120 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 21:00 | 23.7 | 79.5 | 101150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 22:00 | 23.05 | 82 | 101145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-23 23:00 | 22.45 | 85.5 | 101135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-24 | 22 | 87.5 | 101120 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-24 01:00 | 21.75 | 87.5 | 101105 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-24 02:00 | 21.45 | 88.5 | 101090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-24 03:00 | 21.1 | 91 | 101100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-24 04:00 | 21.25 | 91.5 | 101115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-24 05:00 | 21.45 | 90.5 | 101150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-24 06:00 | 21.7 | 88.5 | 101230 | 100 | 3000 | 19.2221 | 83.2257 | 50.2642 | 0 | 7.2692 | FALSE | FALSE
2025-03-24 07:00 | 23.15 | 81.5 | 101320 | 100 | 3000 | 19.8197 | 80.3451 | 52.3745 | 0 | 7.2692 | FALSE | FALSE
2025-03-24 08:00 | 24.75 | 72 | 101390 | 100 | 3000 | 20.4728 | 75.8708 | 52.7659 | 0 | 7.2692 | FALSE | FALSE
2025-03-24 09:00 | 25.5 | 65.5 | 101410 | 100 | 3000 | 20.7797 | 72.4 | 51.0322 | 0 | 7.2692 | FALSE | FALSE
2025-03-24 10:00 | 26.4 | 58 | 101390 | 100 | 3000 | 21.1469 | 68.2209 | 48.731 | 0 | 7.2692 | FALSE | FALSE
2025-03-24 11:00 | 27.1 | 52 | 101350 | 100 | 3000 | 21.4326 | 64.7129 | 46.4426 | 0 | 7.2692 | FALSE | FALSE
2025-03-24 12:00 | 27.1 | 51 | 101300 | 100 | 3000 | 21.4346 | 64.0804 | 45.5808 | 0 | 7.2692 | FALSE | FALSE
2025-03-24 13:00 | 26.85 | 49 | 101225 | 100 | 3000 | 21.3407 | 62.7431 | 42.9358 | 0 | 7.2692 | FALSE | FALSE
2025-03-24 14:00 | 26.5 | 47 | 101165 | 100 | 3000 | 21.2065 | 61.4048 | 39.9752 | 0 | 7.2692 | FALSE | FALSE
2025-03-24 15:00 | 25.9 | 47 | 101145 | 100 | 3000 | 20.9682 | 61.287 | 37.8305 | 0 | 7.2692 | FALSE | FALSE
2025-03-24 16:00 | 25.1 | 48 | 101170 | 100 | 3000 | 20.6462 | 61.7525 | 35.7844 | 0 | 7.2692 | FALSE | FALSE
2025-03-24 17:00 | 24.15 | 51 | 101220 | 100 | 3000 | 20.2579 | 63.3615 | 34.6627 | 0 | 7.2692 | FALSE | FALSE
2025-03-24 18:00 | 23.05 | 58 | 101270 | 100 | 3000 | 19.801 | 67.1346 | 35.6218 | 0 | 7.2692 | FALSE | FALSE
2025-03-24 19:00 | 22.2 | 65 | 101320 | 100 | 3000 | 19.4448 | 70.7742 | 37.0896 | 0 | 7.2692 | FALSE | FALSE
2025-03-24 20:00 | 21.65 | 67 | 101345 | 100 | 3000 | 19.2151 | 71.6856 | 36.2025 | 0 | 7.2692 | FALSE | FALSE
2025-03-24 21:00 | 21.05 | 68 | 101355 | 100 | 3000 | 18.9639 | 72.0389 | 34.4306 | 0 | 7.2692 | FALSE | FALSE
2025-03-24 22:00 | 20.35 | 70.5 | 101340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-24 23:00 | 19.8 | 73.5 | 101295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-25 | 19.5 | 75 | 101235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-25 01:00 | 19.3 | 75 | 101175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-25 02:00 | 19.2 | 75.5 | 101125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-25 03:00 | 19.2 | 75.5 | 101100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-25 04:00 | 19.1 | 72.5 | 101115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-25 05:00 | 19.1 | 68 | 101150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-25 06:00 | 19.5 | 64.5 | 101185 | 100 | 3000 | 18.3089 | 69.9401 | 26.2433 | 0 | 7.2692 | FALSE | FALSE
2025-03-25 07:00 | 20.65 | 59.5 | 101215 | 100 | 3000 | 18.7997 | 67.5267 | 27.5738 | 0 | 7.2692 | FALSE | FALSE
2025-03-25 08:00 | 22 | 54 | 101255 | 100 | 3000 | 19.3696 | 64.749 | 28.9994 | 0 | 7.2692 | FALSE | FALSE
2025-03-25 09:00 | 22.9 | 50 | 101270 | 100 | 3000 | 19.7464 | 62.6266 | 29.4877 | 0 | 7.2692 | FALSE | FALSE
2025-03-25 10:00 | 23.55 | 47.5 | 101255 | 100 | 3000 | 20.0165 | 61.2663 | 29.9826 | 0 | 7.2692 | FALSE | FALSE
2025-03-25 11:00 | 24 | 46.5 | 101230 | 100 | 3000 | 20.2019 | 60.7282 | 30.8046 | 0 | 7.2692 | FALSE | FALSE
2025-03-25 12:00 | 24.2 | 46 | 101170 | 100 | 3000 | 20.2841 | 60.4598 | 31.1148 | 0 | 7.2692 | FALSE | FALSE
2025-03-25 13:00 | 24.15 | 47 | 101085 | 100 | 3000 | 20.2626 | 61.0472 | 31.6769 | 0 | 7.2692 | FALSE | FALSE
2025-03-25 14:00 | 23.9 | 49 | 101010 | 100 | 3000 | 20.1583 | 62.188 | 32.2701 | 0 | 7.2692 | FALSE | FALSE
2025-03-25 15:00 | 23.4 | 51 | 100975 | 100 | 3000 | 19.9514 | 63.2757 | 31.9373 | 0 | 7.2692 | FALSE | FALSE
2025-03-25 16:00 | 22.55 | 52.5 | 100980 | 100 | 3000 | 19.5994 | 64.0153 | 29.9423 | 0 | 7.2692 | FALSE | FALSE
2025-03-25 17:00 | 21.6 | 55 | 101000 | 100 | 3000 | 19.2018 | 65.2765 | 28.1887 | 0 | 7.2692 | FALSE | FALSE
2025-03-25 18:00 | 20.85 | 59.5 | 101020 | 100 | 3000 | 18.8842 | 67.5739 | 28.3049 | 0 | 7.2692 | FALSE | FALSE
2025-03-25 19:00 | 20.3 | 62.5 | 101040 | 100 | 3000 | 18.6503 | 69.0523 | 28.0862 | 0 | 7.2692 | FALSE | FALSE
2025-03-25 20:00 | 20 | 63.5 | 101065 | 100 | 3000 | 18.5225 | 69.5176 | 27.5504 | 0 | 7.2692 | FALSE | FALSE
2025-03-25 21:00 | 19.8 | 64.5 | 101090 | 100 | 3000 | 18.437 | 69.9931 | 27.3829 | 0 | 7.2692 | FALSE | FALSE
2025-03-25 22:00 | 19.55 | 66.5 | 101085 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-25 23:00 | 19.25 | 69 | 101035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-26 | 18.95 | 70.5 | 100965 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-26 01:00 | 18.6 | 72.5 | 100915 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-26 02:00 | 18.05 | 76.5 | 100875 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-26 03:00 | 17.65 | 79 | 100850 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-26 04:00 | 17.25 | 79 | 100840 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-26 05:00 | 16.65 | 80 | 100860 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-26 06:00 | 16.35 | 81 | 100930 | 100 | 3000 | 16.9394 | 77.3451 | 22.6294 | 0 | 7.2692 | FALSE | FALSE
2025-03-26 07:00 | 17.25 | 76.5 | 101020 | 100 | 3000 | 17.3345 | 75.4203 | 24.0051 | 0 | 7.2692 | FALSE | FALSE
2025-03-26 08:00 | 19.45 | 67 | 101100 | 100 | 3000 | 18.2869 | 71.1947 | 27.4984 | 0 | 7.2692 | FALSE | FALSE
2025-03-26 09:00 | 21.65 | 59.5 | 101130 | 100 | 3000 | 19.2199 | 67.6852 | 31.3141 | 0 | 7.2692 | FALSE | FALSE
2025-03-26 10:00 | 23.35 | 54.5 | 101115 | 100 | 3000 | 19.9274 | 65.2399 | 34.2648 | 0 | 7.2692 | FALSE | FALSE
2025-03-26 11:00 | 24.7 | 49 | 101060 | 100 | 3000 | 20.4834 | 62.2949 | 35.1161 | 0 | 7.2692 | FALSE | FALSE
2025-03-26 12:00 | 25.8 | 43.5 | 100965 | 100 | 3000 | 20.934 | 59.1407 | 34.6252 | 0 | 7.2692 | FALSE | FALSE
2025-03-26 13:00 | 26.4 | 42 | 100865 | 100 | 3000 | 21.176 | 58.2894 | 35.4161 | 0 | 7.2692 | FALSE | FALSE
2025-03-26 14:00 | 26.1 | 46.5 | 100795 | 100 | 3000 | 21.0488 | 61.0507 | 38.0835 | 0 | 7.2692 | FALSE | FALSE
2025-03-26 15:00 | 25.35 | 51 | 100780 | 100 | 3000 | 20.7422 | 63.6471 | 38.9836 | 0 | 7.2692 | FALSE | FALSE
2025-03-26 16:00 | 24.45 | 53 | 100815 | 100 | 3000 | 20.3772 | 64.631 | 37.2051 | 0 | 7.2692 | FALSE | FALSE
2025-03-26 17:00 | 23.35 | 56.5 | 100850 | 100 | 3000 | 19.9255 | 66.402 | 35.6576 | 0 | 7.2692 | FALSE | FALSE
2025-03-26 18:00 | 22.35 | 62 | 100870 | 100 | 3000 | 19.5091 | 69.2246 | 35.6305 | 0 | 7.2692 | FALSE | FALSE
2025-03-26 19:00 | 21.55 | 67.5 | 100910 | 100 | 3000 | 19.1732 | 71.9712 | 36.088 | 0 | 7.2692 | FALSE | FALSE
2025-03-26 20:00 | 20.7 | 73.5 | 100975 | 100 | 3000 | 18.8144 | 74.8459 | 36.3935 | 0 | 7.2692 | FALSE | FALSE
2025-03-26 21:00 | 19.75 | 78.5 | 101010 | 100 | 3000 | 18.4114 | 77.0579 | 35.4063 | 0 | 7.2692 | FALSE | FALSE
2025-03-26 22:00 | 18.8 | 82 | 101015 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-26 23:00 | 17.95 | 85.5 | 101020 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-27 | 17.35 | 88.5 | 101015 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-27 01:00 | 16.9 | 90.5 | 101005 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-27 02:00 | 16.4 | 92 | 100980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-27 03:00 | 15.85 | 94 | 100960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-27 04:00 | 15.95 | 93.5 | 100985 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-27 05:00 | 15.85 | 93 | 101035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-27 06:00 | 15.4 | 95 | 101100 | 100 | 3000 | 16.5207 | 83.3251 | 25.2927 | 0 | 7.2692 | FALSE | FALSE
2025-03-27 07:00 | 16.8 | 90 | 101170 | 100 | 3000 | 17.138 | 81.5207 | 28.9714 | 0 | 7.2692 | FALSE | FALSE
2025-03-27 08:00 | 19.7 | 77 | 101225 | 100 | 3000 | 18.3906 | 76.2601 | 34.3306 | 0 | 7.2692 | FALSE | FALSE
2025-03-27 09:00 | 22.25 | 63 | 101250 | 100 | 3000 | 19.4669 | 69.7039 | 35.9452 | 0 | 7.2692 | FALSE | FALSE
2025-03-27 10:00 | 24.5 | 50 | 101245 | 100 | 3000 | 20.4011 | 62.833 | 35.1807 | 0 | 7.2692 | FALSE | FALSE
2025-03-27 11:00 | 26.8 | 40 | 101205 | 100 | 3000 | 21.3384 | 57.0386 | 35.1218 | 0 | 7.2692 | FALSE | FALSE
2025-03-27 12:00 | 28.4 | 34.5 | 101120 | 100 | 3000 | 21.9795 | 53.5933 | 35.4041 | 0 | 7.2692 | FALSE | FALSE
2025-03-27 13:00 | 28.5 | 38 | 101025 | 100 | 3000 | 22.0097 | 55.945 | 38.9428 | 0 | 7.2692 | FALSE | FALSE
2025-03-27 14:00 | 27.45 | 45.5 | 100950 | 100 | 3000 | 21.5831 | 60.6845 | 42.0607 | 0 | 7.2692 | FALSE | FALSE
2025-03-27 15:00 | 26.4 | 49.5 | 100910 | 100 | 3000 | 21.1624 | 62.9697 | 41.6513 | 0 | 7.2692 | FALSE | FALSE
2025-03-27 16:00 | 25.7 | 48.5 | 100905 | 100 | 3000 | 20.886 | 62.1918 | 38.2899 | 0 | 7.2692 | FALSE | FALSE
2025-03-27 17:00 | 24.75 | 51.5 | 100915 | 100 | 3000 | 20.5003 | 63.8003 | 37.1864 | 0 | 7.2692 | FALSE | FALSE
2025-03-27 18:00 | 23.55 | 63.5 | 100930 | 100 | 3000 | 20 | 70.428 | 41.427 | 0 | 7.2692 | FALSE | FALSE
2025-03-27 19:00 | 22.75 | 72.5 | 100965 | 100 | 3000 | 19.6651 | 75.1486 | 44.3863 | 0 | 7.2692 | FALSE | FALSE
2025-03-27 20:00 | 22.2 | 76.5 | 101020 | 100 | 3000 | 19.4362 | 77.073 | 44.7019 | 0 | 7.2692 | FALSE | FALSE
2025-03-27 21:00 | 21.55 | 79.5 | 101055 | 100 | 3000 | 19.1658 | 78.3572 | 43.8046 | 0 | 7.2692 | FALSE | FALSE
2025-03-27 22:00 | 20.65 | 82.5 | 101060 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-27 23:00 | 19.55 | 85.5 | 101060 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-28 | 18.55 | 86.5 | 101035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-28 01:00 | 17.7 | 86 | 100995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-28 02:00 | 17 | 85.5 | 100965 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-28 03:00 | 16.5 | 86.5 | 100955 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-28 04:00 | 16.65 | 92 | 100975 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-28 05:00 | 16.6 | 94.5 | 101025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-28 06:00 | 16.25 | 93.5 | 101100 | 100 | 3000 | 16.8967 | 82.9312 | 28.2945 | 0 | 7.2692 | FALSE | FALSE
2025-03-28 07:00 | 17.1 | 89.5 | 101165 | 100 | 3000 | 17.2692 | 81.3933 | 30.0222 | 0 | 7.2692 | FALSE | FALSE
2025-03-28 08:00 | 19.55 | 70.5 | 101240 | 100 | 3000 | 18.3286 | 72.9512 | 29.9306 | 0 | 7.2692 | FALSE | FALSE
2025-03-28 09:00 | 22.75 | 44.5 | 101290 | 100 | 3000 | 19.689 | 59.546 | 25.1485 | 0 | 7.2692 | FALSE | FALSE
2025-03-28 10:00 | 25.7 | 29 | 101280 | 100 | 3000 | 20.9169 | 50.2158 | 28.3419 | 0 | 7.2692 | FALSE | FALSE
2025-03-28 11:00 | 28.15 | 24 | 101220 | 100 | 3000 | 21.9069 | 46.6255 | 31.6155 | 0 | 7.2692 | FALSE | FALSE
2025-03-28 12:00 | 29.9 | 22.5 | 101115 | 100 | 3000 | 22.596 | 45.3444 | 33.8251 | 0 | 7.2692 | FALSE | FALSE
2025-03-28 13:00 | 30.65 | 23.5 | 101010 | 100 | 3000 | 22.882 | 45.9735 | 34.6973 | 0 | 7.2692 | FALSE | FALSE
2025-03-28 14:00 | 30.1 | 28.5 | 100920 | 100 | 3000 | 22.6544 | 49.551 | 34.7441 | 0 | 7.2692 | FALSE | FALSE
2025-03-28 15:00 | 28.8 | 34 | 100870 | 100 | 3000 | 22.1366 | 53.3044 | 36.1496 | 0 | 7.2692 | FALSE | FALSE
2025-03-28 16:00 | 27.7 | 41.5 | 100870 | 100 | 3000 | 21.6897 | 58.1496 | 39.4002 | 0 | 7.2692 | FALSE | FALSE
2025-03-28 17:00 | 26.5 | 48.5 | 100890 | 100 | 3000 | 21.2037 | 62.3716 | 41.1841 | 0 | 7.2692 | FALSE | FALSE
2025-03-28 18:00 | 25.05 | 57 | 100915 | 100 | 3000 | 20.6133 | 67.1536 | 42.538 | 0 | 7.2692 | FALSE | FALSE
2025-03-28 19:00 | 24.1 | 65.5 | 100945 | 100 | 3000 | 20.2206 | 71.7906 | 45.1164 | 0 | 7.2692 | FALSE | FALSE
2025-03-28 20:00 | 23.35 | 69.5 | 100980 | 100 | 3000 | 19.9126 | 73.7443 | 44.8584 | 0 | 7.2692 | FALSE | FALSE
2025-03-28 21:00 | 22.45 | 77 | 101015 | 100 | 3000 | 19.5385 | 77.4746 | 46.1301 | 0 | 7.2692 | FALSE | FALSE
2025-03-28 22:00 | 21.6 | 86.5 | 101020 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-28 23:00 | 20.9 | 93 | 101000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-29 | 20.4 | 95 | 100975 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-29 01:00 | 20.05 | 94.5 | 100950 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-29 02:00 | 19.7 | 94 | 100925 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-29 03:00 | 19.3 | 94.5 | 100900 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-29 04:00 | 19.3 | 95 | 100900 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-29 05:00 | 19.1 | 93 | 100935 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-29 06:00 | 18.6 | 85 | 100990 | 100 | 3000 | 17.919 | 79.8371 | 34.1566 | 0 | 7.2692 | FALSE | FALSE
2025-03-29 07:00 | 19.7 | 71 | 101055 | 100 | 3000 | 18.3924 | 73.2597 | 30.8129 | 0 | 7.2692 | FALSE | FALSE
2025-03-29 08:00 | 22.5 | 56 | 101120 | 100 | 3000 | 19.5759 | 65.9275 | 32.162 | 0 | 7.2692 | FALSE | FALSE
2025-03-29 09:00 | 25.45 | 44 | 101155 | 100 | 3000 | 20.7928 | 59.3883 | 33.8571 | 0 | 7.2692 | FALSE | FALSE
2025-03-29 10:00 | 27.85 | 35.5 | 101150 | 100 | 3000 | 21.7619 | 54.2222 | 34.584 | 0 | 7.2692 | FALSE | FALSE
2025-03-29 11:00 | 29.75 | 29 | 101115 | 100 | 3000 | 22.5181 | 49.8846 | 34.2547 | 0 | 7.2692 | FALSE | FALSE
2025-03-29 12:00 | 31.15 | 24.5 | 101040 | 100 | 3000 | 23.0695 | 46.6546 | 35.2951 | 0 | 7.2692 | FALSE | FALSE
2025-03-29 13:00 | 31.9 | 23 | 100930 | 100 | 3000 | 23.3597 | 45.5205 | 36.1883 | 0 | 7.2692 | FALSE | FALSE
2025-03-29 14:00 | 31.85 | 24.5 | 100845 | 100 | 3000 | 23.3349 | 46.643 | 36.0652 | 0 | 7.2692 | FALSE | FALSE
2025-03-29 15:00 | 30.85 | 28 | 100795 | 100 | 3000 | 22.9428 | 49.21 | 36.3981 | 0 | 7.2692 | FALSE | FALSE
2025-03-29 16:00 | 28.9 | 36 | 100795 | 100 | 3000 | 22.17 | 54.67 | 38.3392 | 0 | 7.2692 | FALSE | FALSE
2025-03-29 17:00 | 26.65 | 46.5 | 100840 | 100 | 3000 | 21.2667 | 61.1552 | 40.045 | 0 | 7.2692 | FALSE | FALSE
2025-03-29 18:00 | 24.95 | 54.5 | 100860 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-29 19:00 | 23.95 | 60 | 100885 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-29 20:00 | 23.2 | 63.5 | 100935 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-29 21:00 | 22.45 | 64 | 100980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-29 22:00 | 21.75 | 64.5 | 101000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-29 23:00 | 21.05 | 69.5 | 100980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 | 20.25 | 76 | 100940 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 01:00 | 19.4 | 82.5 | 100900 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 02:00 | 18.75 | 87 | 100865 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 03:00 | 18.25 | 88 | 100845 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 04:00 | 18.05 | 84 | 100840 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 05:00 | 17.95 | 78.5 | 100885 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 06:00 | 18 | 74 | 100960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 07:00 | 19.55 | 63 | 101035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 08:00 | 22.75 | 47 | 101105 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 09:00 | 26.6 | 33 | 101140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 10:00 | 30.3 | 23.5 | 101125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 11:00 | 32.85 | 18.5 | 101070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 12:00 | 33.95 | 18 | 101000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 13:00 | 34.15 | 19.5 | 100915 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 14:00 | 33.55 | 21 | 100850 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 15:00 | 32.25 | 24 | 100820 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 16:00 | 30.85 | 29.5 | 100825 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 17:00 | 29.1 | 37.5 | 100850 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 18:00 | 27.05 | 50 | 100870 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 19:00 | 25.9 | 56.5 | 100905 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 20:00 | 25.35 | 53 | 100960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 21:00 | 24.55 | 50.5 | 101010 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 22:00 | 23.75 | 50 | 101035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-30 23:00 | 23.05 | 50.5 | 101025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-31 | 22.2 | 50.5 | 100995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-31 01:00 | 21.35 | 48.5 | 100975 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-31 02:00 | 20.65 | 46 | 100945 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-31 03:00 | 19.9 | 44 | 100915 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-31 04:00 | 19.5 | 40.5 | 100905 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-31 05:00 | 19.45 | 37.5 | 100935 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-31 06:00 | 19.85 | 36 | 101005 | 100 | 3000 | 18.4675 | 55.5119 | 19.9205 | 0 | 7.2692 | FALSE | FALSE
2025-03-31 07:00 | 22.1 | 31.5 | 101080 | 100 | 3000 | 19.4274 | 52.4735 | 23.2566 | 0 | 7.2692 | FALSE | FALSE
2025-03-31 08:00 | 26.05 | 24.5 | 101140 | 100 | 3000 | 21.0659 | 47.3815 | 28.8204 | 0 | 7.2692 | FALSE | FALSE
2025-03-31 09:00 | 29.9 | 19 | 101150 | 100 | 3000 | 22.6067 | 42.8947 | 33.8986 | 0 | 7.2692 | FALSE | FALSE
2025-03-31 10:00 | 32.65 | 15.5 | 101125 | 100 | 3000 | 23.6748 | 39.7681 | 37.3277 | 0 | 7.2692 | FALSE | FALSE
2025-03-31 11:00 | 34.3 | 14 | 101080 | 100 | 3000 | 24.3008 | 38.2696 | 39.2897 | 0 | 7.2692 | FALSE | FALSE
2025-03-31 12:00 | 35.2 | 14 | 101000 | 100 | 3000 | 24.6334 | 38.1097 | 40.2896 | 0 | 7.2692 | FALSE | FALSE
2025-03-31 13:00 | 35.6 | 14 | 100910 | 100 | 3000 | 24.7802 | 38.0497 | 40.7055 | 0 | 7.2692 | FALSE | FALSE
2025-03-31 14:00 | 35.45 | 13.5 | 100830 | 100 | 3000 | 24.7285 | 37.6672 | 40.5217 | 0 | 7.2692 | FALSE | FALSE
2025-03-31 15:00 | 34.6 | 14 | 100775 | 100 | 3000 | 24.4124 | 38.2364 | 39.5184 | 0 | 7.2692 | FALSE | FALSE
2025-03-31 16:00 | 32.9 | 18 | 100780 | 100 | 3000 | 23.7581 | 41.661 | 37.4366 | 0 | 7.2692 | FALSE | FALSE
2025-03-31 17:00 | 30.35 | 27.5 | 100825 | 100 | 3000 | 22.7536 | 48.8518 | 34.4382 | 0 | 7.2692 | FALSE | FALSE
2025-03-31 18:00 | 27.65 | 42.5 | 100860 | 100 | 3000 | 21.6679 | 58.7922 | 40.1125 | 0 | 7.2692 | FALSE | FALSE
2025-03-31 19:00 | 25.95 | 54.5 | 100885 | 100 | 3000 | 20.9756 | 65.9372 | 44.0411 | 0 | 7.2692 | FALSE | FALSE
2025-03-31 20:00 | 25 | 61 | 100930 | 100 | 3000 | 20.5876 | 69.5208 | 45.4175 | 0 | 7.2692 | FALSE | FALSE
2025-03-31 21:00 | 24.3 | 63.5 | 100955 | 100 | 3000 | 20.3036 | 70.7109 | 44.4667 | 0 | 7.2692 | FALSE | FALSE
2025-03-31 22:00 | 23.95 | 61.5 | 100945 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-03-31 23:00 | 23.4 | 59.5 | 100930 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-01 | 22.75 | 58.5 | 100900 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-01 01:00 | 22.15 | 57.5 | 100865 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-01 02:00 | 21.45 | 57 | 100850 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-01 03:00 | 20.55 | 58 | 100835 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-01 04:00 | 19.8 | 59.5 | 100835 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-01 05:00 | 19.25 | 61 | 100860 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-01 06:00 | 19.1 | 59.5 | 100890 | 100 | 3000 | 18.1386 | 67.4504 | 21.8581 | 0 | 7.2692 | FALSE | FALSE
2025-04-01 07:00 | 21.05 | 49.5 | 100925 | 100 | 3000 | 18.9736 | 62.3347 | 22.7102 | 0 | 7.2692 | FALSE | FALSE
2025-04-01 08:00 | 25.15 | 35.5 | 100965 | 100 | 3000 | 20.6843 | 54.263 | 27.4517 | 0 | 7.2692 | FALSE | FALSE
2025-04-01 09:00 | 29.2 | 23.5 | 100995 | 100 | 3000 | 22.3208 | 46.1455 | 32.8916 | 0 | 7.2692 | FALSE | FALSE
2025-04-01 10:00 | 31.9 | 15 | 100990 | 100 | 3000 | 23.3919 | 39.5717 | 36.3892 | 0 | 7.2692 | FALSE | FALSE
2025-04-01 11:00 | 33.45 | 12 | 100960 | 100 | 3000 | 23.9931 | 36.8986 | 38.3064 | 0 | 7.2692 | FALSE | FALSE
2025-04-01 12:00 | 33.65 | 13.5 | 100900 | 100 | 3000 | 24.061 | 38.0262 | 38.4791 | 0 | 7.2692 | FALSE | FALSE
2025-04-01 13:00 | 33.05 | 14.5 | 100825 | 100 | 3000 | 23.8307 | 38.9429 | 37.7185 | 0 | 7.2692 | FALSE | FALSE
2025-04-01 14:00 | 32.4 | 15.5 | 100755 | 100 | 3000 | 23.5804 | 39.8522 | 36.8957 | 0 | 7.2692 | FALSE | FALSE
2025-04-01 15:00 | 31.25 | 19 | 100705 | 100 | 3000 | 23.1282 | 42.6738 | 35.4147 | 0 | 7.2692 | FALSE | FALSE
2025-04-01 16:00 | 29.9 | 24.5 | 100685 | 100 | 3000 | 22.5901 | 46.7806 | 33.6479 | 0 | 7.2692 | FALSE | FALSE
2025-04-01 17:00 | 28.25 | 35 | 100700 | 100 | 3000 | 21.9199 | 53.9571 | 35.3191 | 0 | 7.2692 | FALSE | FALSE
2025-04-01 18:00 | 26.4 | 48.5 | 100735 | 100 | 3000 | 21.1642 | 62.3631 | 40.7975 | 0 | 7.2692 | FALSE | FALSE
2025-04-01 19:00 | 25.2 | 57 | 100780 | 100 | 3000 | 20.6733 | 67.2172 | 43.104 | 0 | 7.2692 | FALSE | FALSE
2025-04-01 20:00 | 24.35 | 61 | 100825 | 100 | 3000 | 20.3268 | 69.2852 | 42.7992 | 0 | 7.2692 | FALSE | FALSE
2025-04-01 21:00 | 23.55 | 64 | 100835 | 100 | 3000 | 19.9995 | 70.7228 | 41.7734 | 0 | 7.2692 | FALSE | FALSE
2025-04-01 22:00 | 22.7 | 65.5 | 100815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-01 23:00 | 21.75 | 66 | 100810 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-02 | 20.9 | 65.5 | 100800 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-02 01:00 | 20.05 | 65 | 100755 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-02 02:00 | 19.15 | 63.5 | 100700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-02 03:00 | 18.3 | 60 | 100665 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-02 04:00 | 17.9 | 56 | 100655 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-02 05:00 | 17.65 | 52 | 100675 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-02 06:00 | 17.75 | 46.5 | 100740 | 100 | 3000 | 17.5537 | 61.3025 | 16.6585 | 0 | 7.2692 | FALSE | FALSE
2025-04-02 07:00 | 19.85 | 37.5 | 100805 | 100 | 3000 | 18.467 | 56.3003 | 19.8765 | 0 | 7.2692 | FALSE | FALSE
2025-04-02 08:00 | 23.85 | 28 | 100855 | 100 | 3000 | 20.1609 | 50.0569 | 25.7032 | 0 | 7.2692 | FALSE | FALSE
2025-04-02 09:00 | 27.65 | 24 | 100890 | 100 | 3000 | 21.7089 | 46.7463 | 30.8677 | 0 | 7.2692 | FALSE | FALSE
2025-04-02 10:00 | 30.25 | 23 | 100870 | 100 | 3000 | 22.7299 | 45.6727 | 34.1686 | 0 | 7.2692 | FALSE | FALSE
2025-04-02 11:00 | 32.1 | 21 | 100800 | 100 | 3000 | 23.4436 | 44.0259 | 36.4257 | 0 | 7.2692 | FALSE | FALSE
2025-04-02 12:00 | 33.4 | 20 | 100725 | 100 | 3000 | 23.9356 | 43.1525 | 37.948 | 0 | 7.2692 | FALSE | FALSE
2025-04-02 13:00 | 33.85 | 20 | 100655 | 100 | 3000 | 24.1027 | 43.1248 | 38.4397 | 0 | 7.2692 | FALSE | FALSE
2025-04-02 14:00 | 33.05 | 20.5 | 100600 | 100 | 3000 | 23.8029 | 43.5781 | 37.4827 | 0 | 7.2692 | FALSE | FALSE
2025-04-02 15:00 | 31.65 | 25 | 100565 | 100 | 3000 | 23.2575 | 47.0424 | 35.7182 | 0 | 7.2692 | FALSE | FALSE
2025-04-02 16:00 | 30.15 | 34 | 100565 | 100 | 3000 | 22.6561 | 53.4502 | 40.3531 | 0 | 7.2692 | FALSE | FALSE
2025-04-02 17:00 | 28.15 | 45 | 100605 | 100 | 3000 | 21.8567 | 60.5622 | 44.0619 | 0 | 7.2692 | FALSE | FALSE
2025-04-02 18:00 | 26.15 | 58.5 | 100645 | 100 | 3000 | 21.0477 | 68.5016 | 48.0291 | 0 | 7.2692 | FALSE | FALSE
2025-04-02 19:00 | 24.9 | 71 | 100680 | 100 | 3000 | 20.5337 | 75.4412 | 52.5833 | 0 | 7.2692 | FALSE | FALSE
2025-04-02 20:00 | 24.15 | 76.5 | 100720 | 100 | 3000 | 20.2276 | 78.2046 | 53.3305 | 0 | 7.2692 | FALSE | FALSE
2025-04-02 21:00 | 23.45 | 77 | 100745 | 100 | 3000 | 19.9455 | 78.0614 | 50.5425 | 0 | 7.2692 | FALSE | FALSE
2025-04-02 22:00 | 22.7 | 78 | 100735 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-02 23:00 | 21.95 | 79 | 100695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-03 | 21.15 | 79.5 | 100645 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-03 01:00 | 20.3 | 80 | 100610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-03 02:00 | 19.45 | 80 | 100585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-03 03:00 | 18.7 | 79.5 | 100590 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-03 04:00 | 18.6 | 75.5 | 100630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-03 05:00 | 18.5 | 72.5 | 100695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-03 06:00 | 18.5 | 71 | 100765 | 100 | 3000 | 17.8779 | 73.0463 | 26.0333 | 0 | 7.2692 | FALSE | FALSE
2025-04-03 07:00 | 20.55 | 63 | 100815 | 100 | 3000 | 18.7559 | 69.3759 | 29.328 | 0 | 7.2692 | FALSE | FALSE
2025-04-03 08:00 | 24.5 | 50 | 100855 | 100 | 3000 | 20.4012 | 62.8735 | 35.1332 | 0 | 7.2692 | FALSE | FALSE
2025-04-03 09:00 | 28.6 | 37 | 100865 | 100 | 3000 | 22.0511 | 55.3036 | 38.3158 | 0 | 7.2692 | FALSE | FALSE
2025-04-03 10:00 | 32.2 | 26 | 100835 | 100 | 3000 | 23.4603 | 47.7594 | 38.1524 | 0 | 7.2692 | FALSE | FALSE
2025-04-03 11:00 | 35.2 | 18.5 | 100775 | 100 | 3000 | 24.6066 | 41.8211 | 40.0569 | 0 | 7.2692 | FALSE | FALSE
2025-04-03 12:00 | 37.3 | 14.5 | 100700 | 100 | 3000 | 25.3914 | 38.2641 | 42.4727 | 0 | 7.2692 | FALSE | FALSE
2025-04-03 13:00 | 38.15 | 13.5 | 100630 | 100 | 3000 | 25.7017 | 37.2926 | 43.393 | 0 | 7.2692 | FALSE | FALSE
2025-04-03 14:00 | 36.35 | 22 | 100590 | 100 | 3000 | 24.9983 | 44.756 | 44.8196 | 0 | 7.2692 | FALSE | FALSE
2025-04-03 15:00 | 32.35 | 36 | 100590 | 100 | 3000 | 23.4732 | 55.3029 | 49.6601 | 0 | 7.2692 | FALSE | FALSE
2025-04-03 16:00 | 29.95 | 44 | 100605 | 100 | 3000 | 22.5481 | 60.4025 | 49.6061 | 0 | 7.2692 | FALSE | FALSE
2025-04-03 17:00 | 29 | 51 | 100625 | 100 | 3000 | 22.1673 | 64.8535 | 52.7453 | 0 | 7.2692 | FALSE | FALSE
2025-04-03 18:00 | 27.4 | 60.5 | 100650 | 100 | 3000 | 21.5311 | 70.3503 | 54.8107 | 0 | 7.2692 | FALSE | FALSE
2025-04-03 19:00 | 26.35 | 63 | 100700 | 100 | 3000 | 21.1182 | 71.3772 | 52.5195 | 0 | 7.2692 | FALSE | FALSE
2025-04-03 20:00 | 26.25 | 58.5 | 100765 | 100 | 3000 | 21.0871 | 68.5314 | 48.4475 | 0 | 7.2692 | FALSE | FALSE
2025-04-03 21:00 | 26.2 | 55 | 100805 | 100 | 3000 | 21.0736 | 66.3391 | 45.4009 | 0 | 7.2692 | FALSE | FALSE
2025-04-03 22:00 | 25.7 | 52.5 | 100800 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-03 23:00 | 25 | 49.5 | 100765 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-04 | 24.25 | 47 | 100730 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-04 01:00 | 23.4 | 46 | 100705 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-04 02:00 | 22.65 | 46.5 | 100690 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-04 03:00 | 22.1 | 46.5 | 100685 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-04 04:00 | 22.2 | 41 | 100680 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-04 05:00 | 22.65 | 32 | 100705 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-04 06:00 | 24.05 | 24 | 100775 | 100 | 3000 | 20.2482 | 47.6799 | 25.9919 | 0 | 7.2692 | FALSE | FALSE
2025-04-04 07:00 | 27 | 17 | 100850 | 100 | 3000 | 21.4634 | 42.4017 | 30.0908 | 0 | 7.2692 | FALSE | FALSE
2025-04-04 08:00 | 30.45 | 13 | 100910 | 100 | 3000 | 22.8401 | 38.5347 | 34.6173 | 0 | 7.2692 | FALSE | FALSE
2025-04-04 09:00 | 33.85 | 10 | 100940 | 100 | 3000 | 24.1537 | 35.2184 | 38.8251 | 0 | 7.2692 | FALSE | FALSE
2025-04-04 10:00 | 36.65 | 7.5 | 100940 | 100 | 3000 | 25.2073 | 32.3197 | 42.1244 | 0 | 7.2692 | FALSE | FALSE
2025-04-04 11:00 | 38.6 | 7 | 100900 | 100 | 3000 | 25.9167 | 31.323 | 44.2743 | 0 | 7.2692 | FALSE | FALSE
2025-04-04 12:00 | 39.95 | 7 | 100825 | 100 | 3000 | 26.3959 | 30.9779 | 45.6784 | 0 | 7.2692 | FALSE | FALSE
2025-04-04 13:00 | 40.65 | 7 | 100735 | 100 | 3000 | 26.6413 | 30.8166 | 46.3667 | 0 | 7.2692 | FALSE | FALSE
2025-04-04 14:00 | 40.2 | 9 | 100660 | 100 | 3000 | 26.4636 | 32.8318 | 45.7627 | 0 | 7.2692 | FALSE | FALSE
2025-04-04 15:00 | 38.7 | 12.5 | 100625 | 100 | 3000 | 25.9046 | 36.325 | 44.0155 | 0 | 7.2692 | FALSE | FALSE
2025-04-04 16:00 | 35.95 | 17 | 100625 | 100 | 3000 | 24.8885 | 40.5352 | 40.8792 | 0 | 7.2692 | FALSE | FALSE
2025-04-04 17:00 | 33.15 | 24 | 100645 | 100 | 3000 | 23.8235 | 46.2659 | 38.509 | 0 | 7.2692 | FALSE | FALSE
2025-04-04 18:00 | 31.25 | 31 | 100670 | 100 | 3000 | 23.0834 | 51.4111 | 40.724 | 0 | 7.2692 | FALSE | FALSE
2025-04-04 19:00 | 29.7 | 34 | 100710 | 100 | 3000 | 22.4839 | 53.3894 | 38.9538 | 0 | 7.2692 | FALSE | FALSE
2025-04-04 20:00 | 28.95 | 30.5 | 100770 | 100 | 3000 | 22.2043 | 50.9514 | 33.2781 | 0 | 7.2692 | FALSE | FALSE
2025-04-04 21:00 | 28.5 | 26 | 100805 | 100 | 3000 | 22.0401 | 47.9454 | 31.9062 | 0 | 7.2692 | FALSE | FALSE
2025-04-04 22:00 | 27.75 | 24 | 100810 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-04 23:00 | 26.75 | 22 | 100800 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-05 | 25.75 | 20.5 | 100765 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-05 01:00 | 25 | 22 | 100735 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-05 02:00 | 24.35 | 27 | 100715 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-05 03:00 | 23.65 | 31 | 100705 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-05 04:00 | 23.4 | 30 | 100700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-05 05:00 | 23.85 | 22.5 | 100720 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-05 06:00 | 25.45 | 15 | 100785 | 100 | 3000 | 20.8368 | 41.77 | 28.0044 | 0 | 7.2692 | FALSE | FALSE
2025-04-05 07:00 | 27.9 | 12.5 | 100870 | 100 | 3000 | 21.8344 | 39.1349 | 31.3429 | 0 | 7.2692 | FALSE | FALSE
2025-04-05 08:00 | 30.5 | 11 | 100955 | 100 | 3000 | 22.8662 | 37.0886 | 34.7329 | 0 | 7.2692 | FALSE | FALSE
2025-04-05 09:00 | 33.5 | 9 | 101005 | 100 | 3000 | 24.0266 | 34.5404 | 38.4622 | 0 | 7.2692 | FALSE | FALSE
2025-04-05 10:00 | 36.3 | 7.5 | 101015 | 100 | 3000 | 25.0788 | 32.4204 | 41.7606 | 0 | 7.2692 | FALSE | FALSE
2025-04-05 11:00 | 38.15 | 6.5 | 100990 | 100 | 3000 | 25.7592 | 30.9934 | 43.8457 | 0 | 7.2692 | FALSE | FALSE
2025-04-05 12:00 | 39.25 | 5.5 | 100930 | 100 | 3000 | 26.1621 | 29.7598 | 45.0556 | 0 | 7.2692 | FALSE | FALSE
2025-04-05 13:00 | 39.9 | 5 | 100840 | 100 | 3000 | 26.398 | 29.1033 | 45.7334 | 0 | 7.2692 | FALSE | FALSE
2025-04-05 14:00 | 39.3 | 8 | 100750 | 100 | 3000 | 26.157 | 32.0744 | 44.9116 | 0 | 7.2692 | FALSE | FALSE
2025-04-05 15:00 | 37.15 | 14.5 | 100705 | 100 | 3000 | 25.3378 | 38.2798 | 42.3128 | 0 | 7.2692 | FALSE | FALSE
2025-04-05 16:00 | 34.5 | 21 | 100700 | 100 | 3000 | 24.3365 | 43.8872 | 39.1657 | 0 | 7.2692 | FALSE | FALSE
2025-04-05 17:00 | 32.25 | 30 | 100710 | 100 | 3000 | 23.462 | 50.771 | 42.7177 | 0 | 7.2692 | FALSE | FALSE
2025-04-05 18:00 | 30.2 | 39 | 100740 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-05 19:00 | 28.85 | 40.5 | 100790 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-05 20:00 | 28.2 | 39 | 100845 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-05 21:00 | 27.15 | 39 | 100875 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-05 22:00 | 26.05 | 39 | 100875 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-05 23:00 | 25.2 | 37.5 | 100860 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 | 24.45 | 33.5 | 100825 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 01:00 | 23.75 | 30 | 100780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 02:00 | 23.05 | 27.5 | 100735 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 03:00 | 22.45 | 24.5 | 100715 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 04:00 | 21.95 | 23.5 | 100710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 05:00 | 21.4 | 24.5 | 100720 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 06:00 | 21.85 | 24 | 100785 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 07:00 | 24.65 | 19.5 | 100870 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 08:00 | 29.2 | 13.5 | 100935 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 09:00 | 33.5 | 10.5 | 100970 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 10:00 | 36.35 | 9.5 | 100970 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 11:00 | 38 | 8.5 | 100925 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 12:00 | 38.95 | 8 | 100855 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 13:00 | 39.45 | 8.5 | 100780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 14:00 | 39.4 | 9.5 | 100700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 15:00 | 38.45 | 11 | 100650 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 16:00 | 36.45 | 15.5 | 100645 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 17:00 | 33.3 | 28 | 100660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 18:00 | 30.3 | 41.5 | 100680 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 19:00 | 28.9 | 45 | 100715 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 20:00 | 28.1 | 47 | 100780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 21:00 | 27.05 | 52 | 100840 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 22:00 | 26 | 53 | 100870 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-06 23:00 | 25 | 52 | 100875 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-07 | 24.15 | 51.5 | 100850 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-07 01:00 | 23.35 | 52 | 100815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-07 02:00 | 22.6 | 53 | 100780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-07 03:00 | 22.25 | 51.5 | 100745 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-07 04:00 | 22 | 45.5 | 100720 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-07 05:00 | 21.5 | 41 | 100740 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-07 06:00 | 21.75 | 38.5 | 100795 | 100 | 3000 | 19.2753 | 56.3971 | 22.6523 | 0 | 7.2692 | FALSE | FALSE
2025-04-07 07:00 | 24.4 | 31.5 | 100855 | 100 | 3000 | 20.3835 | 51.9823 | 26.4366 | 0 | 7.2692 | FALSE | FALSE
2025-04-07 08:00 | 29 | 23 | 100905 | 100 | 3000 | 22.244 | 45.8432 | 32.6182 | 0 | 7.2692 | FALSE | FALSE
2025-04-07 09:00 | 33 | 17 | 100925 | 100 | 3000 | 23.8001 | 40.8664 | 37.6326 | 0 | 7.2692 | FALSE | FALSE
2025-04-07 10:00 | 35.55 | 13.5 | 100910 | 100 | 3000 | 24.765 | 37.6431 | 40.666 | 0 | 7.2692 | FALSE | FALSE
2025-04-07 11:00 | 37.45 | 11 | 100875 | 100 | 3000 | 25.4717 | 35.163 | 42.8474 | 0 | 7.2692 | FALSE | FALSE
2025-04-07 12:00 | 38.45 | 10 | 100825 | 100 | 3000 | 25.8375 | 34.0815 | 43.9479 | 0 | 7.2692 | FALSE | FALSE
2025-04-07 13:00 | 37.8 | 12 | 100770 | 100 | 3000 | 25.5894 | 35.9917 | 43.1417 | 0 | 7.2692 | FALSE | FALSE
2025-04-07 14:00 | 36.4 | 16 | 100730 | 100 | 3000 | 25.0576 | 39.6436 | 41.4508 | 0 | 7.2692 | FALSE | FALSE
2025-04-07 15:00 | 35.25 | 20.5 | 100705 | 100 | 3000 | 24.6127 | 43.4673 | 40.0205 | 0 | 7.2692 | FALSE | FALSE
2025-04-07 16:00 | 34.3 | 22.5 | 100700 | 100 | 3000 | 24.255 | 45.0903 | 39.8891 | 0 | 7.2692 | FALSE | FALSE
2025-04-07 17:00 | 32.55 | 27.5 | 100710 | 100 | 3000 | 23.5845 | 48.9138 | 40.8209 | 0 | 7.2692 | FALSE | FALSE
2025-04-07 18:00 | 30.05 | 40 | 100735 | 100 | 3000 | 22.5987 | 57.6245 | 46.0371 | 0 | 7.2692 | FALSE | FALSE
2025-04-07 19:00 | 28.5 | 49 | 100775 | 100 | 3000 | 21.9816 | 63.3033 | 49.0112 | 0 | 7.2692 | FALSE | FALSE
2025-04-07 20:00 | 27.75 | 53 | 100835 | 100 | 3000 | 21.683 | 65.6478 | 49.7339 | 0 | 7.2692 | FALSE | FALSE
2025-04-07 21:00 | 27 | 56.5 | 100885 | 100 | 3000 | 21.3844 | 67.5828 | 49.8055 | 0 | 7.2692 | FALSE | FALSE
2025-04-07 22:00 | 26.3 | 59.5 | 100880 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-07 23:00 | 25.5 | 60.5 | 100835 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-08 | 24.6 | 59 | 100780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-08 01:00 | 23.85 | 57 | 100720 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-08 02:00 | 23.45 | 54.5 | 100665 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-08 03:00 | 23.3 | 51.5 | 100650 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-08 04:00 | 22.8 | 47.5 | 100630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-08 05:00 | 22.3 | 43 | 100630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-08 06:00 | 22.5 | 39.5 | 100695 | 100 | 3000 | 19.5891 | 56.8468 | 23.6933 | 0 | 7.2692 | FALSE | FALSE
2025-04-08 07:00 | 24.4 | 34 | 100755 | 100 | 3000 | 20.3805 | 53.4649 | 26.3902 | 0 | 7.2692 | FALSE | FALSE
2025-04-08 08:00 | 27.65 | 28.5 | 100810 | 100 | 3000 | 21.699 | 49.6876 | 30.7838 | 0 | 7.2692 | FALSE | FALSE
2025-04-08 09:00 | 30.55 | 30 | 100855 | 100 | 3000 | 22.8217 | 50.6266 | 37.5901 | 0 | 7.2692 | FALSE | FALSE
2025-04-08 10:00 | 32.85 | 33 | 100855 | 100 | 3000 | 23.6705 | 53.1213 | 48.0074 | 0 | 7.2692 | FALSE | FALSE
2025-04-08 11:00 | 34.4 | 32.5 | 100810 | 100 | 3000 | 24.2359 | 53.0871 | 52.4535 | 0 | 7.2692 | FALSE | FALSE
2025-04-08 12:00 | 34.95 | 32.5 | 100755 | 100 | 3000 | 24.4325 | 53.2366 | 54.2456 | 0 | 7.2692 | FALSE | FALSE
2025-04-08 13:00 | 35.1 | 32.5 | 100690 | 100 | 3000 | 24.4858 | 53.2836 | 54.7239 | 0 | 7.2692 | FALSE | FALSE
2025-04-08 14:00 | 35.15 | 31.5 | 100620 | 100 | 3000 | 24.5097 | 52.4849 | 53.6123 | 0 | 7.2692 | FALSE | FALSE
2025-04-08 15:00 | 34.85 | 31 | 100580 | 100 | 3000 | 24.4058 | 52.0073 | 52.0083 | 0 | 7.2692 | FALSE | FALSE
2025-04-08 16:00 | 33.6 | 33.5 | 100595 | 100 | 3000 | 23.9419 | 53.6973 | 50.9724 | 0 | 7.2692 | FALSE | FALSE
2025-04-08 17:00 | 31.5 | 40.5 | 100635 | 100 | 3000 | 23.1405 | 58.3941 | 51.6021 | 0 | 7.2692 | FALSE | FALSE
2025-04-08 18:00 | 29.8 | 46.5 | 100665 | 100 | 3000 | 22.4836 | 62.0837 | 51.5099 | 0 | 7.2692 | FALSE | FALSE
2025-04-08 19:00 | 28.85 | 48.5 | 100705 | 100 | 3000 | 22.117 | 63.1005 | 49.857 | 0 | 7.2692 | FALSE | FALSE
2025-04-08 20:00 | 28.05 | 51 | 100745 | 100 | 3000 | 21.8035 | 64.4652 | 49.1043 | 0 | 7.2692 | FALSE | FALSE
2025-04-08 21:00 | 27.25 | 55 | 100775 | 100 | 3000 | 21.4848 | 66.7422 | 49.502 | 0 | 7.2692 | FALSE | FALSE
2025-04-08 22:00 | 26.55 | 59.5 | 100790 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-08 23:00 | 25.7 | 64.5 | 100790 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-09 | 24.75 | 68.5 | 100765 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-09 01:00 | 24 | 70 | 100715 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-09 02:00 | 23.4 | 71 | 100675 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-09 03:00 | 22.9 | 72.5 | 100650 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-09 04:00 | 22.85 | 70 | 100640 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-09 05:00 | 22.7 | 68 | 100655 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-09 06:00 | 22.75 | 67.5 | 100695 | 100 | 3000 | 19.6694 | 72.406 | 40.9459 | 0 | 7.2692 | FALSE | FALSE
2025-04-09 07:00 | 24.35 | 61.5 | 100745 | 100 | 3000 | 20.3262 | 69.5856 | 43.1612 | 0 | 7.2692 | FALSE | FALSE
2025-04-09 08:00 | 26.95 | 52.5 | 100785 | 100 | 3000 | 21.373 | 65.0353 | 46.2076 | 0 | 7.2692 | FALSE | FALSE
2025-04-09 09:00 | 29.3 | 45 | 100795 | 100 | 3000 | 22.2985 | 60.8695 | 48.2467 | 0 | 7.2692 | FALSE | FALSE
2025-04-09 10:00 | 31.05 | 40 | 100780 | 100 | 3000 | 22.9749 | 57.8825 | 49.5229 | 0 | 7.2692 | FALSE | FALSE
2025-04-09 11:00 | 32.15 | 37 | 100745 | 100 | 3000 | 23.3951 | 55.9865 | 50.1173 | 0 | 7.2692 | FALSE | FALSE
2025-04-09 12:00 | 32.6 | 36 | 100685 | 100 | 3000 | 23.5651 | 55.3586 | 50.5237 | 0 | 7.2692 | FALSE | FALSE
2025-04-09 13:00 | 32.6 | 37 | 100610 | 100 | 3000 | 23.5606 | 56.1223 | 51.6248 | 0 | 7.2692 | FALSE | FALSE
2025-04-09 14:00 | 32.2 | 39 | 100535 | 100 | 3000 | 23.405 | 57.5139 | 52.4336 | 0 | 7.2692 | FALSE | FALSE
2025-04-09 15:00 | 31.5 | 41.5 | 100470 | 100 | 3000 | 23.1366 | 59.1405 | 52.6254 | 0 | 7.2692 | FALSE | FALSE
2025-04-09 16:00 | 30.45 | 47.5 | 100435 | 100 | 3000 | 22.7243 | 63.0614 | 54.9041 | 0 | 7.2692 | FALSE | FALSE
2025-04-09 17:00 | 29.1 | 54 | 100445 | 100 | 3000 | 22.1968 | 66.9469 | 55.9103 | 0 | 7.2692 | FALSE | FALSE
2025-04-09 18:00 | 27.75 | 59.5 | 100470 | 100 | 3000 | 21.6681 | 69.9068 | 55.3719 | 0 | 7.2692 | FALSE | FALSE
2025-04-09 19:00 | 26.7 | 64 | 100505 | 100 | 3000 | 21.2527 | 72.2084 | 54.7919 | 0 | 7.2692 | FALSE | FALSE
2025-04-09 20:00 | 25.75 | 67.5 | 100550 | 100 | 3000 | 20.875 | 73.8367 | 53.5577 | 0 | 7.2692 | FALSE | FALSE
2025-04-09 21:00 | 24.75 | 72 | 100575 | 100 | 3000 | 20.4727 | 75.9562 | 52.6649 | 0 | 7.2692 | FALSE | FALSE
2025-04-09 22:00 | 23.85 | 75.5 | 100575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-09 23:00 | 22.95 | 78.5 | 100560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-10 | 22.1 | 81.5 | 100515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-10 01:00 | 21.4 | 83.5 | 100450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-10 02:00 | 20.75 | 84.5 | 100400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-10 03:00 | 20 | 86 | 100375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-10 04:00 | 19.85 | 87 | 100375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-10 05:00 | 19.95 | 86.5 | 100410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-10 06:00 | 20.3 | 82.5 | 100455 | 100 | 3000 | 18.6423 | 79.3828 | 40.1176 | 0 | 7.2692 | FALSE | FALSE
2025-04-10 07:00 | 22.2 | 72.5 | 100495 | 100 | 3000 | 19.4392 | 74.9535 | 42.0046 | 0 | 7.2692 | FALSE | FALSE
2025-04-10 08:00 | 25.15 | 60 | 100540 | 100 | 3000 | 20.6489 | 69.0227 | 45.1998 | 0 | 7.2692 | FALSE | FALSE
2025-04-10 09:00 | 28.1 | 48.5 | 100555 | 100 | 3000 | 21.8289 | 62.858 | 47.0223 | 0 | 7.2692 | FALSE | FALSE
2025-04-10 10:00 | 30.8 | 38 | 100525 | 100 | 3000 | 22.8885 | 56.4036 | 46.5432 | 0 | 7.2692 | FALSE | FALSE
2025-04-10 11:00 | 32.85 | 31 | 100465 | 100 | 3000 | 23.6798 | 51.6285 | 45.6448 | 0 | 7.2692 | FALSE | FALSE
2025-04-10 12:00 | 33.45 | 34 | 100385 | 100 | 3000 | 23.885 | 54.0679 | 51.0132 | 0 | 7.2692 | FALSE | FALSE
2025-04-10 13:00 | 32.9 | 40 | 100285 | 100 | 3000 | 23.6561 | 58.5298 | 55.9704 | 0 | 7.2692 | FALSE | FALSE
2025-04-10 14:00 | 32.35 | 40 | 100195 | 100 | 3000 | 23.4557 | 58.3427 | 53.9863 | 0 | 7.2692 | FALSE | FALSE
2025-04-10 15:00 | 32.15 | 38.5 | 100130 | 100 | 3000 | 23.3888 | 57.1612 | 51.6243 | 0 | 7.2692 | FALSE | FALSE
2025-04-10 16:00 | 31.45 | 35 | 100105 | 100 | 3000 | 23.1434 | 54.4066 | 45.4854 | 0 | 7.2692 | FALSE | FALSE
2025-04-10 17:00 | 30.05 | 35 | 100105 | 100 | 3000 | 22.6149 | 54.1817 | 40.9442 | 0 | 7.2692 | FALSE | FALSE
2025-04-10 18:00 | 28.15 | 51.5 | 100105 | 100 | 3000 | 21.8408 | 64.8941 | 49.8284 | 0 | 7.2692 | FALSE | FALSE
2025-04-10 19:00 | 26.45 | 71.5 | 100135 | 100 | 3000 | 21.1413 | 76.7772 | 59.7984 | 0 | 7.2692 | FALSE | FALSE
2025-04-10 20:00 | 25.5 | 81.5 | 100190 | 100 | 3000 | 20.7543 | 82.1808 | 63.3004 | 0 | 7.2692 | FALSE | FALSE
2025-04-10 21:00 | 24.7 | 87.5 | 100240 | 100 | 3000 | 20.4317 | 85.0712 | 63.9425 | 0 | 7.2692 | FALSE | FALSE
2025-04-10 22:00 | 23.9 | 91.5 | 100255 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-10 23:00 | 23 | 94.5 | 100235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-11 | 22.05 | 96.5 | 100195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-11 01:00 | 21.4 | 97 | 100140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-11 02:00 | 20.9 | 97 | 100090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-11 03:00 | 20.35 | 95.5 | 100060 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-11 04:00 | 20.4 | 89.5 | 100040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-11 05:00 | 20.55 | 79.5 | 100055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-11 06:00 | 21.15 | 68.5 | 100100 | 100 | 3000 | 19.0056 | 72.4728 | 35.0543 | 0 | 7.2692 | FALSE | FALSE
2025-04-11 07:00 | 23.85 | 55 | 100140 | 100 | 3000 | 20.1313 | 65.7318 | 36.3759 | 0 | 7.2692 | FALSE | FALSE
2025-04-11 08:00 | 28.05 | 39.5 | 100180 | 100 | 3000 | 21.8312 | 56.9598 | 38.6763 | 0 | 7.2692 | FALSE | FALSE
2025-04-11 09:00 | 31.55 | 28.5 | 100210 | 100 | 3000 | 23.2063 | 49.6466 | 38.8634 | 0 | 7.2692 | FALSE | FALSE
2025-04-11 10:00 | 33.8 | 22.5 | 100200 | 100 | 3000 | 24.0717 | 45.133 | 38.4108 | 0 | 7.2692 | FALSE | FALSE
2025-04-11 11:00 | 35.25 | 20 | 100150 | 100 | 3000 | 24.6162 | 43.1015 | 39.8192 | 0 | 7.2692 | FALSE | FALSE
2025-04-11 12:00 | 35.9 | 21.5 | 100085 | 100 | 3000 | 24.8413 | 44.354 | 42.7943 | 0 | 7.2692 | FALSE | FALSE
2025-04-11 13:00 | 35.45 | 25.5 | 100020 | 100 | 3000 | 24.6542 | 47.655 | 46.7382 | 0 | 7.2692 | FALSE | FALSE
2025-04-11 14:00 | 34.1 | 28 | 99955 | 100 | 3000 | 24.1525 | 49.5168 | 45.8435 | 0 | 7.2692 | FALSE | FALSE
2025-04-11 15:00 | 32.55 | 31.5 | 99910 | 100 | 3000 | 23.567 | 52.0104 | 45.1452 | 0 | 7.2692 | FALSE | FALSE
2025-04-11 16:00 | 31.15 | 38 | 99920 | 100 | 3000 | 23.0199 | 56.5413 | 47.6088 | 0 | 7.2692 | FALSE | FALSE
2025-04-11 17:00 | 29.95 | 44 | 99940 | 100 | 3000 | 22.5481 | 60.4645 | 49.4793 | 0 | 7.2692 | FALSE | FALSE
2025-04-11 18:00 | 28.6 | 52 | 99950 | 100 | 3000 | 22.0121 | 65.422 | 51.9961 | 0 | 7.2692 | FALSE | FALSE
2025-04-11 19:00 | 27.55 | 59 | 99975 | 100 | 3000 | 21.5922 | 69.5289 | 54.0305 | 0 | 7.2692 | FALSE | FALSE
2025-04-11 20:00 | 26.75 | 62 | 100020 | 100 | 3000 | 21.276 | 71.0271 | 53.2692 | 0 | 7.2692 | FALSE | FALSE
2025-04-11 21:00 | 26.05 | 61 | 100060 | 100 | 3000 | 21.0039 | 70.0595 | 49.5634 | 0 | 7.2692 | FALSE | FALSE
2025-04-11 22:00 | 25.55 | 57.5 | 100065 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-11 23:00 | 24.8 | 54.5 | 100055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-12 | 24.05 | 51 | 100030 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-12 01:00 | 23.35 | 49 | 100000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-12 02:00 | 22.6 | 48 | 99975 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-12 03:00 | 22.2 | 45 | 99970 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-12 04:00 | 22.25 | 42.5 | 99970 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-12 05:00 | 22.3 | 40.5 | 99985 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-12 06:00 | 22.95 | 34.5 | 100035 | 100 | 3000 | 19.7812 | 54.0561 | 24.2011 | 0 | 7.2692 | FALSE | FALSE
2025-04-12 07:00 | 25.65 | 26 | 100090 | 100 | 3000 | 20.9019 | 48.5034 | 27.9768 | 0 | 7.2692 | FALSE | FALSE
2025-04-12 08:00 | 30 | 18.5 | 100155 | 100 | 3000 | 22.648 | 42.6116 | 33.7039 | 0 | 7.2692 | FALSE | FALSE
2025-04-12 09:00 | 34.3 | 12.5 | 100195 | 100 | 3000 | 24.31 | 37.1425 | 38.9961 | 0 | 7.2692 | FALSE | FALSE
2025-04-12 10:00 | 37.5 | 9.5 | 100190 | 100 | 3000 | 25.5024 | 33.8864 | 42.6771 | 0 | 7.2692 | FALSE | FALSE
2025-04-12 11:00 | 39.2 | 9.5 | 100170 | 100 | 3000 | 26.1087 | 33.5262 | 44.4828 | 0 | 7.2692 | FALSE | FALSE
2025-04-12 12:00 | 39.35 | 10.5 | 100150 | 100 | 3000 | 26.1522 | 34.4273 | 44.5829 | 0 | 7.2692 | FALSE | FALSE
2025-04-12 13:00 | 38.1 | 12 | 100125 | 100 | 3000 | 25.6972 | 35.9937 | 43.1908 | 0 | 7.2692 | FALSE | FALSE
2025-04-12 14:00 | 37.05 | 14.5 | 100085 | 100 | 3000 | 25.3027 | 38.3388 | 41.9495 | 0 | 7.2692 | FALSE | FALSE
2025-04-12 15:00 | 36.25 | 17.5 | 100060 | 100 | 3000 | 24.994 | 40.9811 | 40.9627 | 0 | 7.2692 | FALSE | FALSE
2025-04-12 16:00 | 34.8 | 23 | 100070 | 100 | 3000 | 24.4349 | 45.5549 | 41.7253 | 0 | 7.2692 | FALSE | FALSE
2025-04-12 17:00 | 33.1 | 31.5 | 100095 | 100 | 3000 | 23.7695 | 52.0853 | 46.9195 | 0 | 7.2692 | FALSE | FALSE
2025-04-12 18:00 | 31 | 40.5 | 100110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-12 19:00 | 29.4 | 46 | 100125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-12 20:00 | 28.7 | 42 | 100165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-12 21:00 | 28.3 | 36.5 | 100200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-12 22:00 | 27.9 | 34.5 | 100210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-12 23:00 | 27.3 | 34 | 100200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 | 26.6 | 36 | 100180 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 01:00 | 25.95 | 36.5 | 100150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 02:00 | 25.15 | 35.5 | 100120 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 03:00 | 24.3 | 34.5 | 100125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 04:00 | 25.1 | 32 | 100130 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 05:00 | 26.5 | 30 | 100160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 06:00 | 27.75 | 26 | 100270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 07:00 | 30.35 | 23 | 100390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 08:00 | 33.25 | 25 | 100460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 09:00 | 35.75 | 24.5 | 100495 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 10:00 | 37.95 | 21 | 100515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 11:00 | 39.8 | 18 | 100515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 12:00 | 41.2 | 15.5 | 100490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 13:00 | 42.15 | 13 | 100440 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 14:00 | 41.6 | 15 | 100390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 15:00 | 39.35 | 18 | 100360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 16:00 | 37.65 | 16 | 100380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 17:00 | 36.15 | 16 | 100415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 18:00 | 33.85 | 20.5 | 100435 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 19:00 | 31.95 | 26 | 100470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 20:00 | 30.8 | 29 | 100520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 21:00 | 30.05 | 28.5 | 100585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 22:00 | 29.25 | 27.5 | 100610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-13 23:00 | 28.35 | 28 | 100590 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-14 | 27.45 | 30 | 100545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-14 01:00 | 26.75 | 32 | 100495 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-14 02:00 | 26.2 | 34 | 100470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-14 03:00 | 25.35 | 37.5 | 100475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-14 04:00 | 24.9 | 38.5 | 100490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-14 05:00 | 24.75 | 37 | 100520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-14 06:00 | 25.1 | 34 | 100600 | 100 | 3000 | 20.6662 | 53.4011 | 27.3001 | 0 | 7.2692 | FALSE | FALSE
2025-04-14 07:00 | 27.9 | 27.5 | 100670 | 100 | 3000 | 21.8002 | 49.0206 | 31.0766 | 0 | 7.2692 | FALSE | FALSE
2025-04-14 08:00 | 32.35 | 21.5 | 100700 | 100 | 3000 | 23.5358 | 44.387 | 36.6743 | 0 | 7.2692 | FALSE | FALSE
2025-04-14 09:00 | 36.2 | 18.5 | 100715 | 100 | 3000 | 24.9685 | 41.7778 | 41.1363 | 0 | 7.2692 | FALSE | FALSE
2025-04-14 10:00 | 38.95 | 16.5 | 100700 | 100 | 3000 | 25.956 | 39.9605 | 44.1237 | 0 | 7.2692 | FALSE | FALSE
2025-04-14 11:00 | 40.85 | 13.5 | 100665 | 100 | 3000 | 26.6399 | 37.0818 | 46.1819 | 0 | 7.2692 | FALSE | FALSE
2025-04-14 12:00 | 41.9 | 12 | 100605 | 100 | 3000 | 27.0135 | 35.5513 | 47.2764 | 0 | 7.2692 | FALSE | FALSE
2025-04-14 13:00 | 42.05 | 12.5 | 100530 | 100 | 3000 | 27.058 | 36.0502 | 47.357 | 0 | 7.2692 | FALSE | FALSE
2025-04-14 14:00 | 40.7 | 14.5 | 100465 | 100 | 3000 | 26.5781 | 38.0698 | 45.8878 | 0 | 7.2692 | FALSE | FALSE
2025-04-14 15:00 | 38.45 | 17.5 | 100420 | 100 | 3000 | 25.7734 | 40.894 | 43.9114 | 0 | 7.2692 | FALSE | FALSE
2025-04-14 16:00 | 36.45 | 21.5 | 100390 | 100 | 3000 | 25.0375 | 44.3522 | 44.363 | 0 | 7.2692 | FALSE | FALSE
2025-04-14 17:00 | 34.65 | 28 | 100370 | 100 | 3000 | 24.3515 | 49.5596 | 47.6065 | 0 | 7.2692 | FALSE | FALSE
2025-04-14 18:00 | 32.9 | 34.5 | 100400 | 100 | 3000 | 23.6819 | 54.3177 | 49.772 | 0 | 7.2692 | FALSE | FALSE
2025-04-14 19:00 | 31.85 | 36 | 100470 | 100 | 3000 | 23.2883 | 55.1934 | 47.9577 | 0 | 7.2692 | FALSE | FALSE
2025-04-14 20:00 | 31.55 | 34 | 100550 | 100 | 3000 | 23.1846 | 53.6525 | 44.8376 | 0 | 7.2692 | FALSE | FALSE
2025-04-14 21:00 | 31.05 | 32.5 | 100580 | 100 | 3000 | 23.0025 | 52.4851 | 41.6631 | 0 | 7.2692 | FALSE | FALSE
2025-04-14 22:00 | 30.5 | 32.5 | 100570 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-14 23:00 | 29.95 | 33.5 | 100560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-15 | 29.05 | 35.5 | 100530 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-15 01:00 | 28.1 | 39 | 100490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-15 02:00 | 27.25 | 40.5 | 100460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-15 03:00 | 26.55 | 39.5 | 100445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-15 04:00 | 26.25 | 41.5 | 100440 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-15 05:00 | 25.8 | 42 | 100450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-15 06:00 | 25.7 | 38.5 | 100500 | 100 | 3000 | 20.9021 | 56.1166 | 30.1895 | 0 | 7.2692 | FALSE | FALSE
2025-04-15 07:00 | 27.65 | 33.5 | 100560 | 100 | 3000 | 21.688 | 52.9681 | 32.0728 | 0 | 7.2692 | FALSE | FALSE
2025-04-15 08:00 | 31.75 | 25.5 | 100595 | 100 | 3000 | 23.2933 | 47.4069 | 36.2722 | 0 | 7.2692 | FALSE | FALSE
2025-04-15 09:00 | 35.75 | 18 | 100610 | 100 | 3000 | 24.8096 | 41.3871 | 40.6185 | 0 | 7.2692 | FALSE | FALSE
2025-04-15 10:00 | 37.75 | 16 | 100620 | 100 | 3000 | 25.5397 | 39.5538 | 42.8592 | 0 | 7.2692 | FALSE | FALSE
2025-04-15 11:00 | 37.2 | 21.5 | 100640 | 100 | 3000 | 25.3027 | 44.3788 | 46.4736 | 0 | 7.2692 | FALSE | FALSE
2025-04-15 12:00 | 35.7 | 29 | 100630 | 100 | 3000 | 24.7205 | 50.55 | 52.1735 | 0 | 7.2692 | FALSE | FALSE
2025-04-15 13:00 | 35.05 | 33 | 100575 | 100 | 3000 | 24.4651 | 53.6874 | 55.1562 | 0 | 7.2692 | FALSE | FALSE
2025-04-15 14:00 | 34.45 | 37 | 100515 | 100 | 3000 | 24.2285 | 56.7303 | 58.0172 | 0 | 7.2692 | FALSE | FALSE
2025-04-15 15:00 | 33.05 | 44 | 100475 | 100 | 3000 | 23.6913 | 61.6364 | 61.079 | 0 | 7.2692 | FALSE | FALSE
2025-04-15 16:00 | 32.35 | 46 | 100435 | 100 | 3000 | 23.4293 | 62.8247 | 60.6143 | 0 | 7.2692 | FALSE | FALSE
2025-04-15 17:00 | 31.35 | 51.5 | 100420 | 100 | 3000 | 23.0423 | 66.3693 | 62.5128 | 0 | 7.2692 | FALSE | FALSE
2025-04-15 18:00 | 29.15 | 66.5 | 100455 | 100 | 3000 | 22.1798 | 75.4436 | 67.7444 | 0 | 7.2692 | FALSE | FALSE
2025-04-15 19:00 | 27.8 | 76.5 | 100515 | 100 | 3000 | 21.6475 | 80.9607 | 70.3483 | 0 | 7.2692 | FALSE | FALSE
2025-04-15 20:00 | 27.1 | 80 | 100585 | 100 | 3000 | 21.3744 | 82.5771 | 69.9167 | 0 | 7.2692 | FALSE | FALSE
2025-04-15 21:00 | 26.45 | 81.5 | 100620 | 100 | 3000 | 21.1227 | 82.9381 | 67.9673 | 0 | 7.2692 | FALSE | FALSE
2025-04-15 22:00 | 25.75 | 83 | 100620 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-15 23:00 | 25 | 85.5 | 100610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-16 | 24.25 | 88.5 | 100580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-16 01:00 | 23.55 | 91 | 100540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-16 02:00 | 23.05 | 91.5 | 100510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-16 03:00 | 22.85 | 90.5 | 100505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-16 04:00 | 23.4 | 88 | 100510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-16 05:00 | 24 | 87.5 | 100525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-16 06:00 | 24.7 | 87.5 | 100580 | 100 | 3000 | 20.4319 | 85.0353 | 63.9847 | 0 | 7.2692 | FALSE | FALSE
2025-04-16 07:00 | 26.65 | 79 | 100650 | 100 | 3000 | 21.2043 | 81.5511 | 66.9167 | 0 | 7.2692 | FALSE | FALSE
2025-04-16 08:00 | 28.9 | 64.5 | 100715 | 100 | 3000 | 22.0921 | 73.8882 | 64.8283 | 0 | 7.2692 | FALSE | FALSE
2025-04-16 09:00 | 30.8 | 52 | 100765 | 100 | 3000 | 22.8385 | 66.3974 | 60.8717 | 0 | 7.2692 | FALSE | FALSE
2025-04-16 10:00 | 32.25 | 44.5 | 100775 | 100 | 3000 | 23.3996 | 61.6242 | 58.672 | 0 | 7.2692 | FALSE | FALSE
2025-04-16 11:00 | 33 | 40.5 | 100755 | 100 | 3000 | 23.6901 | 58.9081 | 57.0019 | 0 | 7.2692 | FALSE | FALSE
2025-04-16 12:00 | 33.3 | 38 | 100715 | 100 | 3000 | 23.8107 | 57.0961 | 55.2095 | 0 | 7.2692 | FALSE | FALSE
2025-04-16 13:00 | 33.3 | 36 | 100660 | 100 | 3000 | 23.8205 | 55.5542 | 52.8921 | 0 | 7.2692 | FALSE | FALSE
2025-04-16 14:00 | 33.2 | 34.5 | 100605 | 100 | 3000 | 23.7915 | 54.3733 | 50.814 | 0 | 7.2692 | FALSE | FALSE
2025-04-16 15:00 | 32.85 | 34 | 100565 | 100 | 3000 | 23.6659 | 53.9098 | 49.0768 | 0 | 7.2692 | FALSE | FALSE
2025-04-16 16:00 | 31.8 | 37.5 | 100550 | 100 | 3000 | 23.2637 | 56.283 | 49.4248 | 0 | 7.2692 | FALSE | FALSE
2025-04-16 17:00 | 30.15 | 45.5 | 100545 | 100 | 3000 | 22.6186 | 61.5251 | 51.8072 | 0 | 7.2692 | FALSE | FALSE
2025-04-16 18:00 | 28.35 | 56.5 | 100565 | 100 | 3000 | 21.9051 | 68.2389 | 55.1934 | 0 | 7.2692 | FALSE | FALSE
2025-04-16 19:00 | 27.35 | 61.5 | 100625 | 100 | 3000 | 21.5096 | 70.9675 | 55.4548 | 0 | 7.2692 | FALSE | FALSE
2025-04-16 20:00 | 27 | 60.5 | 100680 | 100 | 3000 | 21.3763 | 70.1411 | 53.1527 | 0 | 7.2692 | FALSE | FALSE
2025-04-16 21:00 | 26.6 | 59.5 | 100700 | 100 | 3000 | 21.2224 | 69.3158 | 50.6761 | 0 | 7.2692 | FALSE | FALSE
2025-04-16 22:00 | 26.15 | 57.5 | 100685 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-16 23:00 | 25.65 | 56 | 100645 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-17 | 25.15 | 55.5 | 100600 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-17 01:00 | 24.35 | 58 | 100565 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-17 02:00 | 23.55 | 67 | 100540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-17 03:00 | 23.3 | 76 | 100525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-17 04:00 | 23.1 | 81 | 100555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-17 05:00 | 22.9 | 85.5 | 100600 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-17 06:00 | 23.65 | 84 | 100640 | 100 | 3000 | 20.0186 | 82.1727 | 56.3837 | 0 | 7.2692 | FALSE | FALSE
2025-04-17 07:00 | 25.65 | 74.5 | 100695 | 100 | 3000 | 20.8244 | 78.012 | 58.635 | 0 | 7.2692 | FALSE | FALSE
2025-04-17 08:00 | 27.75 | 62 | 100750 | 100 | 3000 | 21.6624 | 71.5017 | 57.5992 | 0 | 7.2692 | FALSE | FALSE
2025-04-17 09:00 | 29.15 | 52 | 100785 | 100 | 3000 | 22.2214 | 65.5811 | 54.2967 | 0 | 7.2692 | FALSE | FALSE
2025-04-17 10:00 | 29.9 | 47.5 | 100785 | 100 | 3000 | 22.5182 | 62.805 | 52.8832 | 0 | 7.2692 | FALSE | FALSE
2025-04-17 11:00 | 30.45 | 44 | 100760 | 100 | 3000 | 22.7363 | 60.5543 | 51.4571 | 0 | 7.2692 | FALSE | FALSE
2025-04-17 12:00 | 30.85 | 41 | 100715 | 100 | 3000 | 22.8966 | 58.5496 | 49.8384 | 0 | 7.2692 | FALSE | FALSE
2025-04-17 13:00 | 30.85 | 41.5 | 100655 | 100 | 3000 | 22.8948 | 58.9136 | 50.3398 | 0 | 7.2692 | FALSE | FALSE
2025-04-17 14:00 | 30.7 | 41.5 | 100590 | 100 | 3000 | 22.8386 | 58.8738 | 49.7934 | 0 | 7.2692 | FALSE | FALSE
2025-04-17 15:00 | 30.25 | 42 | 100535 | 100 | 3000 | 22.6678 | 59.0998 | 48.6888 | 0 | 7.2692 | FALSE | FALSE
2025-04-17 16:00 | 29.35 | 43 | 100510 | 100 | 3000 | 22.3233 | 59.5432 | 46.4649 | 0 | 7.2692 | FALSE | FALSE
2025-04-17 17:00 | 28 | 48.5 | 100515 | 100 | 3000 | 21.7902 | 62.8297 | 46.6436 | 0 | 7.2692 | FALSE | FALSE
2025-04-17 18:00 | 26.75 | 57.5 | 100555 | 100 | 3000 | 21.2849 | 68.141 | 49.5969 | 0 | 7.2692 | FALSE | FALSE
2025-04-17 19:00 | 26 | 63.5 | 100600 | 100 | 3000 | 20.98 | 71.5181 | 51.4429 | 0 | 7.2692 | FALSE | FALSE
2025-04-17 20:00 | 25.55 | 66 | 100650 | 100 | 3000 | 20.7986 | 72.8067 | 51.534 | 0 | 7.2692 | FALSE | FALSE
2025-04-17 21:00 | 25.3 | 66 | 100695 | 100 | 3000 | 20.6997 | 72.6731 | 50.4798 | 0 | 7.2692 | FALSE | FALSE
2025-04-17 22:00 | 25 | 66.5 | 100695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-17 23:00 | 24.65 | 68 | 100665 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-18 | 24.4 | 69.5 | 100625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-18 01:00 | 24.2 | 71.5 | 100590 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-18 02:00 | 24 | 73.5 | 100555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-18 03:00 | 23.75 | 75 | 100540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-18 04:00 | 23.6 | 77 | 100560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-18 05:00 | 23.45 | 79.5 | 100600 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-18 06:00 | 23.85 | 79 | 100645 | 100 | 3000 | 20.1044 | 79.4588 | 53.7611 | 0 | 7.2692 | FALSE | FALSE
2025-04-18 07:00 | 25.2 | 71 | 100695 | 100 | 3000 | 20.6526 | 75.6154 | 53.9036 | 0 | 7.2692 | FALSE | FALSE
2025-04-18 08:00 | 26.5 | 61.5 | 100740 | 100 | 3000 | 21.1796 | 70.5147 | 51.9219 | 0 | 7.2692 | FALSE | FALSE
2025-04-18 09:00 | 27.45 | 55 | 100770 | 100 | 3000 | 21.5624 | 66.8256 | 50.2909 | 0 | 7.2692 | FALSE | FALSE
2025-04-18 10:00 | 28.25 | 50 | 100770 | 100 | 3000 | 21.883 | 63.8776 | 48.9729 | 0 | 7.2692 | FALSE | FALSE
2025-04-18 11:00 | 28.75 | 46.5 | 100730 | 100 | 3000 | 22.0841 | 61.7194 | 47.6325 | 0 | 7.2692 | FALSE | FALSE
2025-04-18 12:00 | 28.9 | 46 | 100675 | 100 | 3000 | 22.1429 | 61.4352 | 47.7078 | 0 | 7.2692 | FALSE | FALSE
2025-04-18 13:00 | 28.85 | 47 | 100610 | 100 | 3000 | 22.1211 | 62.0994 | 48.4448 | 0 | 7.2692 | FALSE | FALSE
2025-04-18 14:00 | 28.65 | 47 | 100550 | 100 | 3000 | 22.0444 | 62.0401 | 47.6951 | 0 | 7.2692 | FALSE | FALSE
2025-04-18 15:00 | 28.25 | 47.5 | 100515 | 100 | 3000 | 21.8892 | 62.2499 | 46.6701 | 0 | 7.2692 | FALSE | FALSE
2025-04-18 16:00 | 27.4 | 51 | 100505 | 100 | 3000 | 21.5517 | 64.258 | 46.5909 | 0 | 7.2692 | FALSE | FALSE
2025-04-18 17:00 | 26.3 | 55.5 | 100520 | 100 | 3000 | 21.1121 | 66.714 | 46.1576 | 0 | 7.2692 | FALSE | FALSE
2025-04-18 18:00 | 25.35 | 57.5 | 100540 | 100 | 3000 | 20.7324 | 67.5943 | 44.0479 | 0 | 7.2692 | FALSE | FALSE
2025-04-18 19:00 | 24.6 | 60.5 | 100575 | 100 | 3000 | 20.4281 | 69.1089 | 43.3912 | 0 | 7.2692 | FALSE | FALSE
2025-04-18 20:00 | 24.1 | 65 | 100625 | 100 | 3000 | 20.2212 | 71.535 | 44.7136 | 0 | 7.2692 | FALSE | FALSE
2025-04-18 21:00 | 23.65 | 68 | 100670 | 100 | 3000 | 20.0358 | 73.0605 | 45.0221 | 0 | 7.2692 | FALSE | FALSE
2025-04-18 22:00 | 23.05 | 71.5 | 100695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-18 23:00 | 22.45 | 75.5 | 100690 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-19 | 21.95 | 78 | 100670 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-19 01:00 | 21.45 | 80.5 | 100655 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-19 02:00 | 21.05 | 83 | 100640 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-19 03:00 | 20.7 | 85.5 | 100640 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-19 04:00 | 20.85 | 86.5 | 100635 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-19 05:00 | 21 | 86.5 | 100645 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-19 06:00 | 21.35 | 85 | 100700 | 100 | 3000 | 19.0796 | 81.2069 | 46.3742 | 0 | 7.2692 | FALSE | FALSE
2025-04-19 07:00 | 23.05 | 77.5 | 100755 | 100 | 3000 | 19.7829 | 78.1088 | 49.1036 | 0 | 7.2692 | FALSE | FALSE
2025-04-19 08:00 | 25.2 | 64.5 | 100800 | 100 | 3000 | 20.6623 | 71.713 | 48.9135 | 0 | 7.2692 | FALSE | FALSE
2025-04-19 09:00 | 26.9 | 51.5 | 100820 | 100 | 3000 | 21.3554 | 64.3812 | 45.176 | 0 | 7.2692 | FALSE | FALSE
2025-04-19 10:00 | 28.05 | 42.5 | 100815 | 100 | 3000 | 21.8238 | 58.8728 | 41.4898 | 0 | 7.2692 | FALSE | FALSE
2025-04-19 11:00 | 28.75 | 38.5 | 100790 | 100 | 3000 | 22.1053 | 56.3372 | 40.195 | 0 | 7.2692 | FALSE | FALSE
2025-04-19 12:00 | 29 | 39 | 100745 | 100 | 3000 | 22.2004 | 56.7192 | 41.4934 | 0 | 7.2692 | FALSE | FALSE
2025-04-19 13:00 | 29.05 | 40.5 | 100670 | 100 | 3000 | 22.2155 | 57.7529 | 43.0682 | 0 | 7.2692 | FALSE | FALSE
2025-04-19 14:00 | 29.05 | 41.5 | 100590 | 100 | 3000 | 22.2128 | 58.439 | 43.9994 | 0 | 7.2692 | FALSE | FALSE
2025-04-19 15:00 | 28.65 | 43.5 | 100540 | 100 | 3000 | 22.0536 | 59.6973 | 44.459 | 0 | 7.2692 | FALSE | FALSE
2025-04-19 16:00 | 27.75 | 47 | 100530 | 100 | 3000 | 21.6968 | 61.7738 | 44.3926 | 0 | 7.2692 | FALSE | FALSE
2025-04-19 17:00 | 26.5 | 54.5 | 100550 | 100 | 3000 | 21.1926 | 66.1602 | 46.1156 | 0 | 7.2692 | FALSE | FALSE
2025-04-19 18:00 | 25.3 | 62 | 100580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-19 19:00 | 24.55 | 64.5 | 100615 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-19 20:00 | 24 | 67.5 | 100655 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-19 21:00 | 23.5 | 70.5 | 100710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-19 22:00 | 23.05 | 72.5 | 100745 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-19 23:00 | 22.5 | 75.5 | 100745 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 | 21.85 | 78 | 100720 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 01:00 | 21.25 | 80 | 100670 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 02:00 | 20.75 | 81.5 | 100620 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 03:00 | 20.35 | 82.5 | 100605 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 04:00 | 20.55 | 81 | 100605 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 05:00 | 20.75 | 79.5 | 100615 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 06:00 | 21.2 | 77 | 100660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 07:00 | 23.15 | 67 | 100720 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 08:00 | 25.45 | 53.5 | 100775 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 09:00 | 27.15 | 43.5 | 100815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 10:00 | 28.5 | 37.5 | 100815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 11:00 | 29.5 | 34 | 100780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 12:00 | 30.15 | 32 | 100725 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 13:00 | 30.5 | 31 | 100665 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 14:00 | 30.45 | 31.5 | 100615 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 15:00 | 30 | 33.5 | 100580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 16:00 | 29.1 | 40.5 | 100575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 17:00 | 27.7 | 51.5 | 100590 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 18:00 | 26.25 | 61 | 100635 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 19:00 | 25.4 | 67 | 100695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 20:00 | 24.95 | 71.5 | 100760 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 21:00 | 24.8 | 72.5 | 100820 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 22:00 | 24.55 | 72.5 | 100835 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-20 23:00 | 24.05 | 75.5 | 100820 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-21 | 23.75 | 77.5 | 100785 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-21 01:00 | 23.15 | 79 | 100745 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-21 02:00 | 22.05 | 81 | 100710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-21 03:00 | 20.85 | 83 | 100690 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-21 04:00 | 20.85 | 83.5 | 100710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-21 05:00 | 21.15 | 84.5 | 100765 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-21 06:00 | 21.55 | 81.5 | 100825 | 100 | 3000 | 19.1645 | 79.4482 | 45.0647 | 0 | 7.2692 | FALSE | FALSE
2025-04-21 07:00 | 23.6 | 70.5 | 100900 | 100 | 3000 | 20.0129 | 74.4372 | 46.6182 | 0 | 7.2692 | FALSE | FALSE
2025-04-21 08:00 | 26.15 | 57 | 100980 | 100 | 3000 | 21.0503 | 67.5405 | 46.8587 | 0 | 7.2692 | FALSE | FALSE
2025-04-21 09:00 | 28.45 | 44 | 101005 | 100 | 3000 | 21.9751 | 59.937 | 44.2908 | 0 | 7.2692 | FALSE | FALSE
2025-04-21 10:00 | 30.8 | 32 | 100990 | 100 | 3000 | 22.9096 | 52.0612 | 40.4442 | 0 | 7.2692 | FALSE | FALSE
2025-04-21 11:00 | 33 | 22.5 | 100950 | 100 | 3000 | 23.7746 | 45.0882 | 37.5018 | 0 | 7.2692 | FALSE | FALSE
2025-04-21 12:00 | 34.5 | 17.5 | 100900 | 100 | 3000 | 24.3558 | 41.0584 | 39.3471 | 0 | 7.2692 | FALSE | FALSE
2025-04-21 13:00 | 35 | 15 | 100855 | 100 | 3000 | 24.5542 | 38.9723 | 39.9745 | 0 | 7.2692 | FALSE | FALSE
2025-04-21 14:00 | 34.55 | 14 | 100810 | 100 | 3000 | 24.3938 | 38.2431 | 39.4745 | 0 | 7.2692 | FALSE | FALSE
2025-04-21 15:00 | 33.4 | 17 | 100780 | 100 | 3000 | 23.9502 | 40.8156 | 38.0481 | 0 | 7.2692 | FALSE | FALSE
2025-04-21 16:00 | 32.1 | 23.5 | 100780 | 100 | 3000 | 23.4332 | 45.8955 | 36.361 | 0 | 7.2692 | FALSE | FALSE
2025-04-21 17:00 | 30.45 | 32 | 100810 | 100 | 3000 | 22.7768 | 52.0455 | 39.3211 | 0 | 7.2692 | FALSE | FALSE
2025-04-21 18:00 | 28.4 | 43.5 | 100855 | 100 | 3000 | 21.9571 | 59.6066 | 43.6298 | 0 | 7.2692 | FALSE | FALSE
2025-04-21 19:00 | 26.85 | 56 | 100915 | 100 | 3000 | 21.3269 | 67.2007 | 48.7923 | 0 | 7.2692 | FALSE | FALSE
2025-04-21 20:00 | 25.9 | 64.5 | 100985 | 100 | 3000 | 20.939 | 72.0411 | 51.8763 | 0 | 7.2692 | FALSE | FALSE
2025-04-21 21:00 | 25.2 | 68 | 101035 | 100 | 3000 | 20.6571 | 73.7848 | 51.6417 | 0 | 7.2692 | FALSE | FALSE
2025-04-21 22:00 | 24.45 | 69 | 101050 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-21 23:00 | 23.45 | 69.5 | 101035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-22 | 22.4 | 70 | 101000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-22 01:00 | 21.6 | 69 | 100955 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-22 02:00 | 21 | 66 | 100905 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-22 03:00 | 20.45 | 63 | 100880 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-22 04:00 | 20.85 | 67 | 100895 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-22 05:00 | 21.35 | 73.5 | 100940 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-22 06:00 | 21.85 | 71.5 | 101005 | 100 | 3000 | 19.2953 | 74.2115 | 39.9201 | 0 | 7.2692 | FALSE | FALSE
2025-04-22 07:00 | 24.15 | 61 | 101075 | 100 | 3000 | 20.2461 | 69.1879 | 42.0322 | 0 | 7.2692 | FALSE | FALSE
2025-04-22 08:00 | 27.7 | 44.5 | 101120 | 100 | 3000 | 21.6829 | 60.0771 | 42.0982 | 0 | 7.2692 | FALSE | FALSE
2025-04-22 09:00 | 31.05 | 28.5 | 101120 | 100 | 3000 | 23.0168 | 49.5458 | 37.5757 | 0 | 7.2692 | FALSE | FALSE
2025-04-22 10:00 | 33.45 | 20 | 101105 | 100 | 3000 | 23.9539 | 43.1166 | 38.147 | 0 | 7.2692 | FALSE | FALSE
2025-04-22 11:00 | 35.05 | 17.5 | 101070 | 100 | 3000 | 24.5575 | 40.99 | 40.0358 | 0 | 7.2692 | FALSE | FALSE
2025-04-22 12:00 | 35.6 | 17 | 101015 | 100 | 3000 | 24.7612 | 40.5333 | 40.6467 | 0 | 7.2692 | FALSE | FALSE
2025-04-22 13:00 | 35.1 | 17.5 | 100965 | 100 | 3000 | 24.5759 | 40.9939 | 40.0512 | 0 | 7.2692 | FALSE | FALSE
2025-04-22 14:00 | 34.35 | 20 | 100915 | 100 | 3000 | 24.2868 | 43.0735 | 39.1082 | 0 | 7.2692 | FALSE | FALSE
2025-04-22 15:00 | 33.75 | 23 | 100855 | 100 | 3000 | 24.0502 | 45.4713 | 39.0313 | 0 | 7.2692 | FALSE | FALSE
2025-04-22 16:00 | 33.3 | 24.5 | 100830 | 100 | 3000 | 23.8766 | 46.6384 | 39.5552 | 0 | 7.2692 | FALSE | FALSE
2025-04-22 17:00 | 32.2 | 28 | 100845 | 100 | 3000 | 23.4518 | 49.2564 | 40.3772 | 0 | 7.2692 | FALSE | FALSE
2025-04-22 18:00 | 30.5 | 35 | 100850 | 100 | 3000 | 22.7857 | 54.1772 | 42.5432 | 0 | 7.2692 | FALSE | FALSE
2025-04-22 19:00 | 29.25 | 40 | 100870 | 100 | 3000 | 22.2937 | 57.4346 | 43.3139 | 0 | 7.2692 | FALSE | FALSE
2025-04-22 20:00 | 28.4 | 42 | 100910 | 100 | 3000 | 21.9608 | 58.6041 | 42.2658 | 0 | 7.2692 | FALSE | FALSE
2025-04-22 21:00 | 27.7 | 44.5 | 100955 | 100 | 3000 | 21.6829 | 60.0932 | 42.0713 | 0 | 7.2692 | FALSE | FALSE
2025-04-22 22:00 | 26.95 | 48 | 100975 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-22 23:00 | 25.9 | 52.5 | 100965 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-23 | 24.9 | 55 | 100930 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-23 01:00 | 24.35 | 53 | 100880 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-23 02:00 | 24.1 | 50 | 100840 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-23 03:00 | 23.95 | 47.5 | 100800 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-23 04:00 | 24.05 | 44 | 100780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-23 05:00 | 24.05 | 41 | 100795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-23 06:00 | 24.75 | 36.5 | 100830 | 100 | 3000 | 20.5203 | 54.9023 | 26.8656 | 0 | 7.2692 | FALSE | FALSE
2025-04-23 07:00 | 27.7 | 28.5 | 100880 | 100 | 3000 | 21.7188 | 49.676 | 30.8694 | 0 | 7.2692 | FALSE | FALSE
2025-04-23 08:00 | 31.55 | 21.5 | 100915 | 100 | 3000 | 23.233 | 44.443 | 35.7973 | 0 | 7.2692 | FALSE | FALSE
2025-04-23 09:00 | 34.6 | 17.5 | 100915 | 100 | 3000 | 24.3926 | 41.0466 | 39.4666 | 0 | 7.2692 | FALSE | FALSE
2025-04-23 10:00 | 36.95 | 14.5 | 100880 | 100 | 3000 | 25.2659 | 38.2887 | 42.168 | 0 | 7.2692 | FALSE | FALSE
2025-04-23 11:00 | 38.65 | 13 | 100825 | 100 | 3000 | 25.8823 | 36.771 | 44.0261 | 0 | 7.2692 | FALSE | FALSE
2025-04-23 12:00 | 39.15 | 13 | 100780 | 100 | 3000 | 26.0578 | 36.7218 | 44.5295 | 0 | 7.2692 | FALSE | FALSE
2025-04-23 13:00 | 38.75 | 13.5 | 100715 | 100 | 3000 | 25.9132 | 37.2244 | 44.0611 | 0 | 7.2692 | FALSE | FALSE
2025-04-23 14:00 | 38.2 | 15 | 100630 | 100 | 3000 | 25.7068 | 38.6335 | 43.381 | 0 | 7.2692 | FALSE | FALSE
2025-04-23 15:00 | 37.6 | 16.5 | 100570 | 100 | 3000 | 25.4827 | 40.0071 | 42.6587 | 0 | 7.2692 | FALSE | FALSE
2025-04-23 16:00 | 36.75 | 18.5 | 100545 | 100 | 3000 | 25.1656 | 41.7772 | 41.6625 | 0 | 7.2692 | FALSE | FALSE
2025-04-23 17:00 | 35.05 | 23 | 100535 | 100 | 3000 | 24.5252 | 45.5263 | 42.5325 | 0 | 7.2692 | FALSE | FALSE
2025-04-23 18:00 | 33 | 29.5 | 100530 | 100 | 3000 | 23.7421 | 50.4961 | 44.4081 | 0 | 7.2692 | FALSE | FALSE
2025-04-23 19:00 | 31.45 | 36.5 | 100535 | 100 | 3000 | 23.1375 | 55.4646 | 47.169 | 0 | 7.2692 | FALSE | FALSE
2025-04-23 20:00 | 30 | 42.5 | 100570 | 100 | 3000 | 22.5718 | 59.3744 | 48.3024 | 0 | 7.2692 | FALSE | FALSE
2025-04-23 21:00 | 28.6 | 49 | 100600 | 100 | 3000 | 22.02 | 63.3558 | 49.3581 | 0 | 7.2692 | FALSE | FALSE
2025-04-23 22:00 | 27.55 | 54.5 | 100595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-23 23:00 | 26.6 | 58.5 | 100560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-24 | 25.65 | 64.5 | 100490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-24 01:00 | 24.65 | 70.5 | 100425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-24 02:00 | 23.65 | 75 | 100395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-24 03:00 | 22.9 | 78 | 100395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-24 04:00 | 22.95 | 72.5 | 100385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-24 05:00 | 23.1 | 66.5 | 100390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-24 06:00 | 23.7 | 65 | 100435 | 100 | 3000 | 20.0593 | 71.3931 | 43.0543 | 0 | 7.2692 | FALSE | FALSE
2025-04-24 07:00 | 25.95 | 59 | 100495 | 100 | 3000 | 20.968 | 68.7417 | 47.6097 | 0 | 7.2692 | FALSE | FALSE
2025-04-24 08:00 | 28.7 | 48.5 | 100550 | 100 | 3000 | 22.0596 | 63.0616 | 49.2654 | 0 | 7.2692 | FALSE | FALSE
2025-04-24 09:00 | 30.85 | 39.5 | 100565 | 100 | 3000 | 22.9019 | 57.4875 | 48.2659 | 0 | 7.2692 | FALSE | FALSE
2025-04-24 10:00 | 32.35 | 35.5 | 100545 | 100 | 3000 | 23.4754 | 54.9312 | 49.097 | 0 | 7.2692 | FALSE | FALSE
2025-04-24 11:00 | 33.4 | 32.5 | 100505 | 100 | 3000 | 23.8742 | 52.8809 | 49.1304 | 0 | 7.2692 | FALSE | FALSE
2025-04-24 12:00 | 34 | 31 | 100440 | 100 | 3000 | 24.1 | 51.8351 | 49.2631 | 0 | 7.2692 | FALSE | FALSE
2025-04-24 13:00 | 33.8 | 33 | 100370 | 100 | 3000 | 24.017 | 53.3735 | 50.9859 | 0 | 7.2692 | FALSE | FALSE
2025-04-24 14:00 | 32.9 | 37 | 100320 | 100 | 3000 | 23.6702 | 56.2351 | 52.589 | 0 | 7.2692 | FALSE | FALSE
2025-04-24 15:00 | 31.9 | 41 | 100290 | 100 | 3000 | 23.2862 | 58.9253 | 53.4887 | 0 | 7.2692 | FALSE | FALSE
2025-04-24 16:00 | 30.9 | 46 | 100285 | 100 | 3000 | 22.8971 | 62.1932 | 55.0609 | 0 | 7.2692 | FALSE | FALSE
2025-04-24 17:00 | 29.7 | 52.5 | 100295 | 100 | 3000 | 22.4273 | 66.2284 | 56.8601 | 0 | 7.2692 | FALSE | FALSE
2025-04-24 18:00 | 28.35 | 59 | 100310 | 100 | 3000 | 21.8987 | 69.9179 | 57.3992 | 0 | 7.2692 | FALSE | FALSE
2025-04-24 19:00 | 27.25 | 64.5 | 100340 | 100 | 3000 | 21.4646 | 72.8581 | 57.5426 | 0 | 7.2692 | FALSE | FALSE
2025-04-24 20:00 | 26.3 | 69.5 | 100390 | 100 | 3000 | 21.0867 | 75.4112 | 57.5414 | 0 | 7.2692 | FALSE | FALSE
2025-04-24 21:00 | 25.4 | 74.5 | 100435 | 100 | 3000 | 20.7262 | 77.8685 | 57.4606 | 0 | 7.2692 | FALSE | FALSE
2025-04-24 22:00 | 24.5 | 78.5 | 100450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-24 23:00 | 23.6 | 80.5 | 100430 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-25 | 22.8 | 81.5 | 100380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-25 01:00 | 22.05 | 84.5 | 100355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-25 02:00 | 21.35 | 88.5 | 100350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-25 03:00 | 20.75 | 90.5 | 100350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-25 04:00 | 20.9 | 87.5 | 100360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-25 05:00 | 21.2 | 83 | 100375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-25 06:00 | 22.05 | 75.5 | 100430 | 100 | 3000 | 19.3751 | 76.5226 | 43.3397 | 0 | 7.2692 | FALSE | FALSE
2025-04-25 07:00 | 24.95 | 60 | 100495 | 100 | 3000 | 20.5691 | 68.951 | 44.3958 | 0 | 7.2692 | FALSE | FALSE
2025-04-25 08:00 | 29.2 | 42.5 | 100540 | 100 | 3000 | 22.2675 | 59.1596 | 45.4629 | 0 | 7.2692 | FALSE | FALSE
2025-04-25 09:00 | 33.6 | 26.5 | 100565 | 100 | 3000 | 23.9774 | 48.2317 | 42.71 | 0 | 7.2692 | FALSE | FALSE
2025-04-25 10:00 | 37 | 15.5 | 100540 | 100 | 3000 | 25.2768 | 39.1755 | 42.0441 | 0 | 7.2692 | FALSE | FALSE
2025-04-25 11:00 | 38.85 | 11.5 | 100475 | 100 | 3000 | 25.9665 | 35.4028 | 44.1543 | 0 | 7.2692 | FALSE | FALSE
2025-04-25 12:00 | 39.1 | 15 | 100395 | 100 | 3000 | 26.0223 | 38.5993 | 44.2164 | 0 | 7.2692 | FALSE | FALSE
2025-04-25 13:00 | 37.65 | 24 | 100325 | 100 | 3000 | 25.4407 | 46.6482 | 51.1808 | 0 | 7.2692 | FALSE | FALSE
2025-04-25 14:00 | 35.85 | 29.5 | 100270 | 100 | 3000 | 24.7704 | 51.0306 | 53.2014 | 0 | 7.2692 | FALSE | FALSE
2025-04-25 15:00 | 35 | 30 | 100230 | 100 | 3000 | 24.4654 | 51.257 | 51.1484 | 0 | 7.2692 | FALSE | FALSE
2025-04-25 16:00 | 33.7 | 36.5 | 100235 | 100 | 3000 | 23.9627 | 56.1024 | 54.7456 | 0 | 7.2692 | FALSE | FALSE
2025-04-25 17:00 | 31.85 | 46 | 100265 | 100 | 3000 | 23.2472 | 62.606 | 58.66 | 0 | 7.2692 | FALSE | FALSE
2025-04-25 18:00 | 30.05 | 57 | 100265 | 100 | 3000 | 22.5436 | 69.5457 | 62.6404 | 0 | 7.2692 | FALSE | FALSE
2025-04-25 19:00 | 28.5 | 71 | 100285 | 100 | 3000 | 21.9244 | 77.9674 | 68.8097 | 0 | 7.2692 | FALSE | FALSE
2025-04-25 20:00 | 27.55 | 80 | 100360 | 100 | 3000 | 21.5449 | 83.0086 | 72.0933 | 0 | 7.2692 | FALSE | FALSE
2025-04-25 21:00 | 26.7 | 85 | 100405 | 100 | 3000 | 21.2116 | 85.3683 | 72.0096 | 0 | 7.2692 | FALSE | FALSE
2025-04-25 22:00 | 25.95 | 89 | 100405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-25 23:00 | 25.15 | 92 | 100380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-26 | 24.45 | 94 | 100325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-26 01:00 | 23.9 | 95.5 | 100275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-26 02:00 | 23.45 | 93 | 100250 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-26 03:00 | 22.9 | 90.5 | 100235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-26 04:00 | 22.7 | 77.5 | 100240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-26 05:00 | 22.8 | 62.5 | 100285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-26 06:00 | 23.75 | 55.5 | 100350 | 100 | 3000 | 20.09 | 65.9747 | 36.3887 | 0 | 7.2692 | FALSE | FALSE
2025-04-26 07:00 | 27.1 | 43 | 100410 | 100 | 3000 | 21.4511 | 59.0631 | 38.5807 | 0 | 7.2692 | FALSE | FALSE
2025-04-26 08:00 | 31.65 | 31 | 100465 | 100 | 3000 | 23.2339 | 51.4698 | 41.9139 | 0 | 7.2692 | FALSE | FALSE
2025-04-26 09:00 | 35.8 | 21 | 100495 | 100 | 3000 | 24.8083 | 43.9001 | 41.9728 | 0 | 7.2692 | FALSE | FALSE
2025-04-26 10:00 | 39.1 | 13.5 | 100495 | 100 | 3000 | 26.0361 | 37.2089 | 44.3305 | 0 | 7.2692 | FALSE | FALSE
2025-04-26 11:00 | 41.2 | 9 | 100460 | 100 | 3000 | 26.8104 | 32.6703 | 46.6924 | 0 | 7.2692 | FALSE | FALSE
2025-04-26 12:00 | 42.45 | 7 | 100395 | 100 | 3000 | 27.2629 | 30.4511 | 48.0304 | 0 | 7.2692 | FALSE | FALSE
2025-04-26 13:00 | 43.3 | 7 | 100310 | 100 | 3000 | 27.5512 | 30.294 | 48.823 | 0 | 7.2692 | FALSE | FALSE
2025-04-26 14:00 | 43.55 | 7 | 100235 | 100 | 3000 | 27.6355 | 30.2537 | 49.0289 | 0 | 7.2692 | FALSE | FALSE
2025-04-26 15:00 | 42.25 | 9 | 100205 | 100 | 3000 | 27.1698 | 32.5253 | 47.6189 | 0 | 7.2692 | FALSE | FALSE
2025-04-26 16:00 | 39.25 | 15 | 100210 | 100 | 3000 | 26.0747 | 38.6064 | 44.2898 | 0 | 7.2692 | FALSE | FALSE
2025-04-26 17:00 | 36.3 | 26 | 100225 | 100 | 3000 | 24.953 | 48.175 | 49.9498 | 0 | 7.2692 | FALSE | FALSE
2025-04-26 18:00 | 33.95 | 34.5 | 100245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-26 19:00 | 32.55 | 37 | 100280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-26 20:00 | 31.85 | 39.5 | 100345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-26 21:00 | 31.1 | 39.5 | 100405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-26 22:00 | 30.5 | 34.5 | 100420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-26 23:00 | 29.65 | 30.5 | 100400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 | 28.65 | 28.5 | 100350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 01:00 | 27.65 | 26 | 100295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 02:00 | 26.7 | 24 | 100265 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 03:00 | 25.9 | 23 | 100270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 04:00 | 26.05 | 23 | 100285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 05:00 | 26.25 | 22.5 | 100310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 06:00 | 26.5 | 21 | 100370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 07:00 | 29.15 | 18 | 100440 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 08:00 | 33.45 | 14 | 100505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 09:00 | 37.75 | 10 | 100555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 10:00 | 40.65 | 7.5 | 100545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 11:00 | 42.1 | 6.5 | 100505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 12:00 | 43.2 | 6 | 100460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 13:00 | 43.8 | 6 | 100400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 14:00 | 43.65 | 6.5 | 100345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 15:00 | 42.4 | 8 | 100295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 16:00 | 40.5 | 10 | 100270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 17:00 | 37.95 | 16 | 100285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 18:00 | 35 | 26 | 100330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 19:00 | 33.3 | 31.5 | 100380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 20:00 | 32.45 | 34.5 | 100420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 21:00 | 31.55 | 37 | 100450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 22:00 | 30.85 | 34 | 100460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-27 23:00 | 30.5 | 33.5 | 100440 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-28 | 29.9 | 32.5 | 100395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-28 01:00 | 29.2 | 29 | 100340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-28 02:00 | 28.55 | 27 | 100290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-28 03:00 | 27.7 | 25 | 100265 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-28 04:00 | 27.3 | 24.5 | 100265 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-28 05:00 | 26.9 | 24 | 100285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-28 06:00 | 27.15 | 22 | 100320 | 100 | 3000 | 21.514 | 45.6147 | 30.0715 | 0 | 7.2692 | FALSE | FALSE
2025-04-28 07:00 | 29.65 | 18 | 100375 | 100 | 3000 | 22.5129 | 42.3248 | 33.3486 | 0 | 7.2692 | FALSE | FALSE
2025-04-28 08:00 | 34.05 | 13 | 100425 | 100 | 3000 | 24.2138 | 37.5799 | 38.7804 | 0 | 7.2692 | FALSE | FALSE
2025-04-28 09:00 | 38 | 8.5 | 100450 | 100 | 3000 | 25.6898 | 32.8619 | 43.3695 | 0 | 7.2692 | FALSE | FALSE
2025-04-28 10:00 | 40.25 | 7 | 100440 | 100 | 3000 | 26.502 | 30.9322 | 45.8207 | 0 | 7.2692 | FALSE | FALSE
2025-04-28 11:00 | 41.8 | 6.5 | 100400 | 100 | 3000 | 27.0463 | 30.0859 | 47.415 | 0 | 7.2692 | FALSE | FALSE
2025-04-28 12:00 | 42.95 | 6 | 100345 | 100 | 3000 | 27.4463 | 29.3264 | 48.5651 | 0 | 7.2692 | FALSE | FALSE
2025-04-28 13:00 | 43.2 | 6.5 | 100280 | 100 | 3000 | 27.5244 | 29.7953 | 48.7456 | 0 | 7.2692 | FALSE | FALSE
2025-04-28 14:00 | 42.25 | 8 | 100220 | 100 | 3000 | 27.1824 | 31.5137 | 47.6884 | 0 | 7.2692 | FALSE | FALSE
2025-04-28 15:00 | 40.5 | 10.5 | 100170 | 100 | 3000 | 26.5529 | 34.2524 | 45.7718 | 0 | 7.2692 | FALSE | FALSE
2025-04-28 16:00 | 38.55 | 13.5 | 100140 | 100 | 3000 | 25.8436 | 37.2871 | 43.6056 | 0 | 7.2692 | FALSE | FALSE
2025-04-28 17:00 | 35.95 | 21.5 | 100140 | 100 | 3000 | 24.8591 | 44.3512 | 42.9436 | 0 | 7.2692 | FALSE | FALSE
2025-04-28 18:00 | 33.2 | 33 | 100160 | 100 | 3000 | 23.7989 | 53.2549 | 48.9831 | 0 | 7.2692 | FALSE | FALSE
2025-04-28 19:00 | 31.8 | 38 | 100180 | 100 | 3000 | 23.2617 | 56.6855 | 49.8842 | 0 | 7.2692 | FALSE | FALSE
2025-04-28 20:00 | 31.05 | 38.5 | 100210 | 100 | 3000 | 22.9805 | 56.8518 | 47.8483 | 0 | 7.2692 | FALSE | FALSE
2025-04-28 21:00 | 30.15 | 40.5 | 100235 | 100 | 3000 | 22.635 | 58.0459 | 46.7838 | 0 | 7.2692 | FALSE | FALSE
2025-04-28 22:00 | 29.55 | 39.5 | 100270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-28 23:00 | 29.15 | 32 | 100270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-29 | 28.45 | 25.5 | 100215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-29 01:00 | 27.7 | 23.5 | 100175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-29 02:00 | 27 | 22 | 100150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-29 03:00 | 26.4 | 21 | 100140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-29 04:00 | 26.5 | 20.5 | 100135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-29 05:00 | 26.55 | 20 | 100150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-29 06:00 | 27.15 | 18.5 | 100190 | 100 | 3000 | 21.5212 | 43.3769 | 30.0765 | 0 | 7.2692 | FALSE | FALSE
2025-04-29 07:00 | 29.95 | 15.5 | 100235 | 100 | 3000 | 22.6378 | 40.5135 | 33.7216 | 0 | 7.2692 | FALSE | FALSE
2025-04-29 08:00 | 34.35 | 11.5 | 100275 | 100 | 3000 | 24.334 | 36.3239 | 39.1135 | 0 | 7.2692 | FALSE | FALSE
2025-04-29 09:00 | 38.4 | 8 | 100280 | 100 | 3000 | 25.8377 | 32.3262 | 43.7501 | 0 | 7.2692 | FALSE | FALSE
2025-04-29 10:00 | 40.85 | 7 | 100265 | 100 | 3000 | 26.712 | 30.8033 | 46.3608 | 0 | 7.2692 | FALSE | FALSE
2025-04-29 11:00 | 42.35 | 6.5 | 100230 | 100 | 3000 | 27.2354 | 29.9759 | 47.886 | 0 | 7.2692 | FALSE | FALSE
2025-04-29 12:00 | 43.25 | 6.5 | 100175 | 100 | 3000 | 27.5415 | 29.7924 | 48.7445 | 0 | 7.2692 | FALSE | FALSE
2025-04-29 13:00 | 43.15 | 7.5 | 100125 | 100 | 3000 | 27.4941 | 30.8528 | 48.5559 | 0 | 7.2692 | FALSE | FALSE
2025-04-29 14:00 | 42.2 | 9 | 100075 | 100 | 3000 | 27.1531 | 32.5415 | 47.5094 | 0 | 7.2692 | FALSE | FALSE
2025-04-29 15:00 | 41.05 | 11 | 100035 | 100 | 3000 | 26.737 | 34.6775 | 46.236 | 0 | 7.2692 | FALSE | FALSE
2025-04-29 16:00 | 39.85 | 13.5 | 100010 | 100 | 3000 | 26.2974 | 37.1861 | 44.8864 | 0 | 7.2692 | FALSE | FALSE
2025-04-29 17:00 | 37.6 | 21 | 100010 | 100 | 3000 | 25.4475 | 44.0193 | 46.68 | 0 | 7.2692 | FALSE | FALSE
2025-04-29 18:00 | 34.35 | 36 | 100045 | 100 | 3000 | 24.1985 | 55.9359 | 56.345 | 0 | 7.2692 | FALSE | FALSE
2025-04-29 19:00 | 31.6 | 51.5 | 100090 | 100 | 3000 | 23.1334 | 66.54 | 63.4571 | 0 | 7.2692 | FALSE | FALSE
2025-04-29 20:00 | 30.35 | 55.5 | 100140 | 100 | 3000 | 22.6598 | 68.6853 | 62.4007 | 0 | 7.2692 | FALSE | FALSE
2025-04-29 21:00 | 29.95 | 51.5 | 100190 | 100 | 3000 | 22.5241 | 65.6662 | 56.8649 | 0 | 7.2692 | FALSE | FALSE
2025-04-29 22:00 | 29.5 | 47.5 | 100230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-29 23:00 | 28.9 | 44 | 100225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-30 | 28 | 42.5 | 100185 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-30 01:00 | 27.45 | 39 | 100170 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-30 02:00 | 27.05 | 34.5 | 100170 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-30 03:00 | 26.25 | 32.5 | 100185 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-30 04:00 | 25.9 | 31.5 | 100165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-30 05:00 | 25.85 | 28.5 | 100165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-30 06:00 | 26.45 | 23.5 | 100230 | 100 | 3000 | 21.2298 | 46.749 | 29.1068 | 0 | 7.2692 | FALSE | FALSE
2025-04-30 07:00 | 29.45 | 18 | 100305 | 100 | 3000 | 22.4347 | 42.3807 | 33.0748 | 0 | 7.2692 | FALSE | FALSE
2025-04-30 08:00 | 33.3 | 14.5 | 100375 | 100 | 3000 | 23.9253 | 38.9261 | 37.8471 | 0 | 7.2692 | FALSE | FALSE
2025-04-30 09:00 | 36.55 | 12.5 | 100390 | 100 | 3000 | 25.1366 | 36.6655 | 41.6054 | 0 | 7.2692 | FALSE | FALSE
2025-04-30 10:00 | 39.35 | 10 | 100375 | 100 | 3000 | 26.1565 | 33.9466 | 44.705 | 0 | 7.2692 | FALSE | FALSE
2025-04-30 11:00 | 41.15 | 9 | 100360 | 100 | 3000 | 26.7934 | 32.6856 | 46.5966 | 0 | 7.2692 | FALSE | FALSE
2025-04-30 12:00 | 42.25 | 9 | 100305 | 100 | 3000 | 27.1696 | 32.5184 | 47.6653 | 0 | 7.2692 | FALSE | FALSE
2025-04-30 13:00 | 42.75 | 8.5 | 100225 | 100 | 3000 | 27.3455 | 31.9415 | 48.1485 | 0 | 7.2692 | FALSE | FALSE
2025-04-30 14:00 | 42.5 | 8 | 100175 | 100 | 3000 | 27.2675 | 31.4739 | 47.9132 | 0 | 7.2692 | FALSE | FALSE
2025-04-30 15:00 | 41.5 | 8.5 | 100155 | 100 | 3000 | 26.9199 | 32.1485 | 46.8833 | 0 | 7.2692 | FALSE | FALSE
2025-04-30 16:00 | 38 | 23 | 100165 | 100 | 3000 | 25.5703 | 45.8239 | 50.7059 | 0 | 7.2692 | FALSE | FALSE
2025-04-30 17:00 | 34.45 | 38.5 | 100180 | 100 | 3000 | 24.2199 | 57.9607 | 59.7513 | 0 | 7.2692 | FALSE | FALSE
2025-04-30 18:00 | 32.75 | 44.5 | 100195 | 100 | 3000 | 23.5808 | 61.903 | 60.4375 | 0 | 7.2692 | FALSE | FALSE
2025-04-30 19:00 | 31.35 | 50 | 100235 | 100 | 3000 | 23.0481 | 65.2961 | 60.9174 | 0 | 7.2692 | FALSE | FALSE
2025-04-30 20:00 | 30.75 | 49.5 | 100275 | 100 | 3000 | 22.8288 | 64.6323 | 58.0449 | 0 | 7.2692 | FALSE | FALSE
2025-04-30 21:00 | 30.1 | 48.5 | 100310 | 100 | 3000 | 22.59 | 63.6289 | 54.5346 | 0 | 7.2692 | FALSE | FALSE
2025-04-30 22:00 | 29.25 | 48 | 100350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-04-30 23:00 | 28.4 | 48 | 100350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-01 | 27.6 | 48 | 100320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-01 01:00 | 26.8 | 46.5 | 100300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-01 02:00 | 26.2 | 43.5 | 100280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-01 03:00 | 25.65 | 39.5 | 100265 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-01 04:00 | 25.15 | 38 | 100265 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-01 05:00 | 25 | 35 | 100285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-01 06:00 | 25.75 | 29 | 100325 | 100 | 3000 | 20.9376 | 50.3022 | 28.1451 | 0 | 7.2692 | FALSE | FALSE
2025-05-01 07:00 | 29.05 | 22 | 100385 | 100 | 3000 | 22.2667 | 45.2019 | 32.5316 | 0 | 7.2692 | FALSE | FALSE
2025-05-01 08:00 | 33.95 | 15.5 | 100440 | 100 | 3000 | 24.1634 | 39.5786 | 38.5998 | 0 | 7.2692 | FALSE | FALSE
2025-05-01 09:00 | 37.6 | 12 | 100470 | 100 | 3000 | 25.5183 | 36.0466 | 42.8008 | 0 | 7.2692 | FALSE | FALSE
2025-05-01 10:00 | 39.65 | 10.5 | 100465 | 100 | 3000 | 26.2568 | 34.3563 | 45.0319 | 0 | 7.2692 | FALSE | FALSE
2025-05-01 11:00 | 40.9 | 10 | 100450 | 100 | 3000 | 26.696 | 33.6932 | 46.3292 | 0 | 7.2692 | FALSE | FALSE
2025-05-01 12:00 | 41.2 | 11 | 100425 | 100 | 3000 | 26.7878 | 34.6333 | 46.5624 | 0 | 7.2692 | FALSE | FALSE
2025-05-01 13:00 | 40.5 | 13 | 100375 | 100 | 3000 | 26.526 | 36.6394 | 45.7294 | 0 | 7.2692 | FALSE | FALSE
2025-05-01 14:00 | 38.85 | 17.5 | 100335 | 100 | 3000 | 25.9126 | 40.9044 | 44.891 | 0 | 7.2692 | FALSE | FALSE
2025-05-01 15:00 | 37.1 | 25 | 100310 | 100 | 3000 | 25.2412 | 47.4385 | 50.976 | 0 | 7.2692 | FALSE | FALSE
2025-05-01 16:00 | 35.65 | 30.5 | 100305 | 100 | 3000 | 24.6932 | 51.8132 | 53.8705 | 0 | 7.2692 | FALSE | FALSE
2025-05-01 17:00 | 33.95 | 36.5 | 100320 | 100 | 3000 | 24.0526 | 56.1762 | 55.6287 | 0 | 7.2692 | FALSE | FALSE
2025-05-01 18:00 | 32.05 | 45.5 | 100340 | 100 | 3000 | 23.3223 | 62.3197 | 58.9025 | 0 | 7.2692 | FALSE | FALSE
2025-05-01 19:00 | 30.8 | 49 | 100360 | 100 | 3000 | 22.8492 | 64.291 | 57.7505 | 0 | 7.2692 | FALSE | FALSE
2025-05-01 20:00 | 30.05 | 48 | 100400 | 100 | 3000 | 22.5729 | 63.25 | 53.869 | 0 | 7.2692 | FALSE | FALSE
2025-05-01 21:00 | 29.35 | 49.5 | 100445 | 100 | 3000 | 22.3044 | 63.9959 | 52.6507 | 0 | 7.2692 | FALSE | FALSE
2025-05-01 22:00 | 28.7 | 51 | 100470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-01 23:00 | 28.05 | 52 | 100460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-02 | 27.25 | 56.5 | 100415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-02 01:00 | 26.3 | 65 | 100380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-02 02:00 | 25.65 | 72 | 100375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-02 03:00 | 25.15 | 74 | 100370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-02 04:00 | 24.9 | 62 | 100345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-02 05:00 | 24.85 | 48.5 | 100345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-02 06:00 | 26 | 42.5 | 100400 | 100 | 3000 | 21.0158 | 58.6034 | 34.4115 | 0 | 7.2692 | FALSE | FALSE
2025-05-02 07:00 | 29.1 | 33.5 | 100490 | 100 | 3000 | 22.2543 | 53.0192 | 36.5446 | 0 | 7.2692 | FALSE | FALSE
2025-05-02 08:00 | 32.75 | 27 | 100560 | 100 | 3000 | 23.6612 | 48.5595 | 40.8067 | 0 | 7.2692 | FALSE | FALSE
2025-05-02 09:00 | 35.6 | 24.5 | 100565 | 100 | 3000 | 24.7139 | 46.798 | 46.0178 | 0 | 7.2692 | FALSE | FALSE
2025-05-02 10:00 | 37.45 | 23 | 100535 | 100 | 3000 | 25.3788 | 45.7234 | 49.2497 | 0 | 7.2692 | FALSE | FALSE
2025-05-02 11:00 | 38.6 | 21 | 100500 | 100 | 3000 | 25.7947 | 44.0692 | 49.5407 | 0 | 7.2692 | FALSE | FALSE
2025-05-02 12:00 | 39.2 | 20 | 100440 | 100 | 3000 | 26.0101 | 43.2163 | 49.6396 | 0 | 7.2692 | FALSE | FALSE
2025-05-02 13:00 | 39.5 | 20 | 100365 | 100 | 3000 | 26.1127 | 43.2516 | 50.4238 | 0 | 7.2692 | FALSE | FALSE
2025-05-02 14:00 | 39.55 | 20 | 100305 | 100 | 3000 | 26.1298 | 43.2613 | 50.5404 | 0 | 7.2692 | FALSE | FALSE
2025-05-02 15:00 | 39.05 | 21 | 100265 | 100 | 3000 | 25.9495 | 44.137 | 50.7051 | 0 | 7.2692 | FALSE | FALSE
2025-05-02 16:00 | 37.9 | 23.5 | 100240 | 100 | 3000 | 25.5315 | 46.2494 | 51.1626 | 0 | 7.2692 | FALSE | FALSE
2025-05-02 17:00 | 36.05 | 28.5 | 100235 | 100 | 3000 | 24.8476 | 50.2393 | 52.5089 | 0 | 7.2692 | FALSE | FALSE
2025-05-02 18:00 | 33.75 | 38.5 | 100250 | 100 | 3000 | 23.9703 | 57.6853 | 57.2706 | 0 | 7.2692 | FALSE | FALSE
2025-05-02 19:00 | 31.95 | 49 | 100295 | 100 | 3000 | 23.2711 | 64.8717 | 62.2596 | 0 | 7.2692 | FALSE | FALSE
2025-05-02 20:00 | 30.8 | 54 | 100345 | 100 | 3000 | 22.8311 | 67.8653 | 62.8076 | 0 | 7.2692 | FALSE | FALSE
2025-05-02 21:00 | 29.8 | 56.5 | 100375 | 100 | 3000 | 22.4522 | 69.0398 | 61.1314 | 0 | 7.2692 | FALSE | FALSE
2025-05-02 22:00 | 28.85 | 60.5 | 100380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-02 23:00 | 27.9 | 64 | 100345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-03 | 27 | 66.5 | 100315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-03 01:00 | 26.3 | 68.5 | 100300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-03 02:00 | 25.8 | 69.5 | 100280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-03 03:00 | 25.4 | 69.5 | 100270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-03 04:00 | 25.45 | 65 | 100250 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-03 05:00 | 25.65 | 60 | 100260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-03 06:00 | 26.6 | 54.5 | 100315 | 100 | 3000 | 21.2319 | 66.2199 | 46.4684 | 0 | 7.2692 | FALSE | FALSE
2025-05-03 07:00 | 29.3 | 44.5 | 100375 | 100 | 3000 | 22.2999 | 60.5676 | 47.6935 | 0 | 7.2692 | FALSE | FALSE
2025-05-03 08:00 | 32.7 | 35 | 100415 | 100 | 3000 | 23.6063 | 54.6492 | 49.6768 | 0 | 7.2692 | FALSE | FALSE
2025-05-03 09:00 | 35.6 | 28.5 | 100400 | 100 | 3000 | 24.6884 | 50.1326 | 51.1565 | 0 | 7.2692 | FALSE | FALSE
2025-05-03 10:00 | 37.7 | 24.5 | 100355 | 100 | 3000 | 25.454 | 47.0958 | 52.0461 | 0 | 7.2692 | FALSE | FALSE
2025-05-03 11:00 | 39.05 | 21.5 | 100305 | 100 | 3000 | 25.9448 | 44.5945 | 51.4755 | 0 | 7.2692 | FALSE | FALSE
2025-05-03 12:00 | 39.45 | 20.5 | 100240 | 100 | 3000 | 26.0909 | 43.7221 | 51.0251 | 0 | 7.2692 | FALSE | FALSE
2025-05-03 13:00 | 39.1 | 21.5 | 100170 | 100 | 3000 | 25.9619 | 44.6114 | 51.5746 | 0 | 7.2692 | FALSE | FALSE
2025-05-03 14:00 | 38.5 | 23 | 100110 | 100 | 3000 | 25.7428 | 45.9015 | 52.1146 | 0 | 7.2692 | FALSE | FALSE
2025-05-03 15:00 | 37.85 | 24.5 | 100075 | 100 | 3000 | 25.506 | 47.1437 | 52.4067 | 0 | 7.2692 | FALSE | FALSE
2025-05-03 16:00 | 36.85 | 25 | 100085 | 100 | 3000 | 25.1538 | 47.4172 | 50.1813 | 0 | 7.2692 | FALSE | FALSE
2025-05-03 17:00 | 35.2 | 28.5 | 100105 | 100 | 3000 | 24.546 | 50.0806 | 49.8473 | 0 | 7.2692 | FALSE | FALSE
2025-05-03 18:00 | 33.25 | 36 | 100115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-03 19:00 | 31.8 | 42 | 100140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-03 20:00 | 30.7 | 47.5 | 100175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-03 21:00 | 29.6 | 53 | 100210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-03 22:00 | 28.95 | 54 | 100205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-03 23:00 | 28.3 | 52.5 | 100155 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 | 27.35 | 50.5 | 100110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 01:00 | 26.85 | 46.5 | 100090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 02:00 | 26.55 | 43.5 | 100090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 03:00 | 26.25 | 43 | 100085 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 04:00 | 26.5 | 38.5 | 100075 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 05:00 | 26.65 | 33 | 100095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 06:00 | 27.6 | 29 | 100145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 07:00 | 30.7 | 22.5 | 100200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 08:00 | 34.75 | 16.5 | 100260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 09:00 | 38.2 | 12 | 100285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 10:00 | 40.6 | 9.5 | 100270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 11:00 | 42.25 | 9 | 100215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 12:00 | 42.95 | 9.5 | 100130 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 13:00 | 42.55 | 10.5 | 100055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 14:00 | 41.45 | 12 | 99995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 15:00 | 40 | 15.5 | 99960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 16:00 | 37.85 | 22.5 | 99950 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 17:00 | 35.35 | 31 | 99960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 18:00 | 33.3 | 39 | 99985 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 19:00 | 31.85 | 45 | 100015 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 20:00 | 30.85 | 49.5 | 100060 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 21:00 | 30.15 | 51.5 | 100110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 22:00 | 29.55 | 50.5 | 100125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-04 23:00 | 28.9 | 49.5 | 100085 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-05 | 28.3 | 48.5 | 100015 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-05 01:00 | 27.85 | 46.5 | 99965 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-05 02:00 | 27.5 | 43 | 99940 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-05 03:00 | 27.2 | 39.5 | 99940 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-05 04:00 | 27.05 | 37 | 99955 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-05 05:00 | 26.9 | 35.5 | 99990 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-05 06:00 | 27.7 | 32.5 | 100050 | 100 | 3000 | 21.7102 | 52.3648 | 31.2479 | 0 | 7.2692 | FALSE | FALSE
2025-05-05 07:00 | 30.45 | 27 | 100115 | 100 | 3000 | 22.794 | 48.5591 | 34.0848 | 0 | 7.2692 | FALSE | FALSE
2025-05-05 08:00 | 34.1 | 21.5 | 100170 | 100 | 3000 | 24.1874 | 44.34 | 38.4983 | 0 | 7.2692 | FALSE | FALSE
2025-05-05 09:00 | 37.35 | 16.5 | 100185 | 100 | 3000 | 25.3945 | 40.0491 | 42.2331 | 0 | 7.2692 | FALSE | FALSE
2025-05-05 10:00 | 39.8 | 13 | 100170 | 100 | 3000 | 26.2849 | 36.7072 | 44.9314 | 0 | 7.2692 | FALSE | FALSE
2025-05-05 11:00 | 41.25 | 12 | 100140 | 100 | 3000 | 26.7938 | 35.6303 | 46.4252 | 0 | 7.2692 | FALSE | FALSE
2025-05-05 12:00 | 41.45 | 13 | 100100 | 100 | 3000 | 26.8501 | 36.606 | 46.5454 | 0 | 7.2692 | FALSE | FALSE
2025-05-05 13:00 | 40.7 | 15 | 100055 | 100 | 3000 | 26.5731 | 38.5831 | 45.6762 | 0 | 7.2692 | FALSE | FALSE
2025-05-05 14:00 | 39.15 | 18 | 100025 | 100 | 3000 | 26.012 | 41.3956 | 46.3213 | 0 | 7.2692 | FALSE | FALSE
2025-05-05 15:00 | 37.7 | 20.5 | 100015 | 100 | 3000 | 25.4865 | 43.5839 | 46.2355 | 0 | 7.2692 | FALSE | FALSE
2025-05-05 16:00 | 37.35 | 21 | 99985 | 100 | 3000 | 25.3598 | 44.0041 | 45.9972 | 0 | 7.2692 | FALSE | FALSE
2025-05-05 17:00 | 36.55 | 24 | 99975 | 100 | 3000 | 25.0555 | 46.5271 | 47.9198 | 0 | 7.2692 | FALSE | FALSE
2025-05-05 18:00 | 34.75 | 30 | 99995 | 100 | 3000 | 24.376 | 51.2245 | 50.303 | 0 | 7.2692 | FALSE | FALSE
2025-05-05 19:00 | 33.2 | 34.5 | 100015 | 100 | 3000 | 23.7916 | 54.4247 | 50.6785 | 0 | 7.2692 | FALSE | FALSE
2025-05-05 20:00 | 32.15 | 37.5 | 100060 | 100 | 3000 | 23.3931 | 56.4208 | 50.5157 | 0 | 7.2692 | FALSE | FALSE
2025-05-05 21:00 | 31.25 | 38.5 | 100105 | 100 | 3000 | 23.0553 | 56.9123 | 48.5121 | 0 | 7.2692 | FALSE | FALSE
2025-05-05 22:00 | 30.4 | 37 | 100115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-05 23:00 | 29.6 | 39.5 | 100090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-06 | 28.85 | 50 | 100055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-06 01:00 | 28.3 | 61.5 | 100025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-06 02:00 | 27.85 | 66 | 100005 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-06 03:00 | 27.5 | 66 | 100000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-06 04:00 | 27.5 | 62 | 100010 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-06 05:00 | 27.45 | 59 | 100040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-06 06:00 | 28.3 | 57 | 100095 | 100 | 3000 | 21.8847 | 68.5902 | 55.3593 | 0 | 7.2692 | FALSE | FALSE
2025-05-06 07:00 | 30.75 | 51 | 100170 | 100 | 3000 | 22.8234 | 65.7126 | 59.5408 | 0 | 7.2692 | FALSE | FALSE
2025-05-06 08:00 | 33.25 | 46 | 100220 | 100 | 3000 | 23.7531 | 63.2964 | 64.0538 | 0 | 7.2692 | FALSE | FALSE
2025-05-06 09:00 | 34.85 | 42 | 100235 | 100 | 3000 | 24.3403 | 60.9568 | 65.4961 | 0 | 7.2692 | FALSE | FALSE
2025-05-06 10:00 | 35.65 | 39.5 | 100230 | 100 | 3000 | 24.6345 | 59.2993 | 65.3734 | 0 | 7.2692 | FALSE | FALSE
2025-05-06 11:00 | 36.05 | 39 | 100200 | 100 | 3000 | 24.776 | 59.0764 | 66.2029 | 0 | 7.2692 | FALSE | FALSE
2025-05-06 12:00 | 36.2 | 39 | 100155 | 100 | 3000 | 24.8275 | 59.1533 | 66.7455 | 0 | 7.2692 | FALSE | FALSE
2025-05-06 13:00 | 36.05 | 39.5 | 100100 | 100 | 3000 | 24.7725 | 59.5054 | 66.8232 | 0 | 7.2692 | FALSE | FALSE
2025-05-06 14:00 | 35.6 | 41.5 | 100040 | 100 | 3000 | 24.604 | 60.9506 | 67.6715 | 0 | 7.2692 | FALSE | FALSE
2025-05-06 15:00 | 35.05 | 43 | 99990 | 100 | 3000 | 24.4039 | 61.8954 | 67.4263 | 0 | 7.2692 | FALSE | FALSE
2025-05-06 16:00 | 34.85 | 43.5 | 99955 | 100 | 3000 | 24.3312 | 62.1968 | 67.2593 | 0 | 7.2692 | FALSE | FALSE
2025-05-06 17:00 | 34.1 | 46.5 | 99960 | 100 | 3000 | 24.0515 | 64.1791 | 67.9163 | 0 | 7.2692 | FALSE | FALSE
2025-05-06 18:00 | 32.65 | 52 | 100000 | 100 | 3000 | 23.51 | 67.5514 | 68.283 | 0 | 7.2692 | FALSE | FALSE
2025-05-06 19:00 | 31.95 | 53 | 100045 | 100 | 3000 | 23.2542 | 67.8564 | 66.4673 | 0 | 7.2692 | FALSE | FALSE
2025-05-06 20:00 | 31.85 | 50.5 | 100090 | 100 | 3000 | 23.2285 | 65.9453 | 63.4131 | 0 | 7.2692 | FALSE | FALSE
2025-05-06 21:00 | 31.65 | 49.5 | 100120 | 100 | 3000 | 23.1598 | 65.0983 | 61.5622 | 0 | 7.2692 | FALSE | FALSE
2025-05-06 22:00 | 31.4 | 49 | 100135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-06 23:00 | 31.15 | 49 | 100110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-07 | 30.55 | 51.5 | 100070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-07 01:00 | 29.6 | 57 | 100060 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-07 02:00 | 28.75 | 62 | 100075 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-07 03:00 | 28.2 | 64.5 | 100095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-07 04:00 | 28.05 | 68 | 100110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-07 05:00 | 28.15 | 69 | 100150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-07 06:00 | 28.75 | 64.5 | 100210 | 100 | 3000 | 22.0356 | 73.8336 | 64.0738 | 0 | 7.2692 | FALSE | FALSE
2025-05-07 07:00 | 29.75 | 60.5 | 100280 | 100 | 3000 | 22.421 | 71.7833 | 64.7363 | 0 | 7.2692 | FALSE | FALSE
2025-05-07 08:00 | 30.8 | 54 | 100340 | 100 | 3000 | 22.8311 | 67.8658 | 62.8066 | 0 | 7.2692 | FALSE | FALSE
2025-05-07 09:00 | 31.85 | 45 | 100365 | 100 | 3000 | 23.2513 | 61.8581 | 57.6129 | 0 | 7.2692 | FALSE | FALSE
2025-05-07 10:00 | 32.55 | 41 | 100355 | 100 | 3000 | 23.5243 | 59.1533 | 55.8435 | 0 | 7.2692 | FALSE | FALSE
2025-05-07 11:00 | 33 | 39.5 | 100310 | 100 | 3000 | 23.6948 | 58.1815 | 55.7685 | 0 | 7.2692 | FALSE | FALSE
2025-05-07 12:00 | 33.1 | 38 | 100255 | 100 | 3000 | 23.7382 | 57.0697 | 54.4036 | 0 | 7.2692 | FALSE | FALSE
2025-05-07 13:00 | 32.8 | 39 | 100195 | 100 | 3000 | 23.6245 | 57.7398 | 54.4687 | 0 | 7.2692 | FALSE | FALSE
2025-05-07 14:00 | 32.35 | 41 | 100140 | 100 | 3000 | 23.4513 | 59.0985 | 55.0738 | 0 | 7.2692 | FALSE | FALSE
2025-05-07 15:00 | 31.75 | 44 | 100115 | 100 | 3000 | 23.2187 | 61.1009 | 56.1178 | 0 | 7.2692 | FALSE | FALSE
2025-05-07 16:00 | 30.9 | 44.5 | 100130 | 100 | 3000 | 22.9026 | 61.131 | 53.493 | 0 | 7.2692 | FALSE | FALSE
2025-05-07 17:00 | 29.8 | 46.5 | 100155 | 100 | 3000 | 22.4836 | 62.1316 | 51.4137 | 0 | 7.2692 | FALSE | FALSE
2025-05-07 18:00 | 28.65 | 53 | 100165 | 100 | 3000 | 22.0286 | 66.091 | 53.1454 | 0 | 7.2692 | FALSE | FALSE
2025-05-07 19:00 | 27.85 | 56 | 100175 | 100 | 3000 | 21.7146 | 67.7084 | 52.6614 | 0 | 7.2692 | FALSE | FALSE
2025-05-07 20:00 | 27.35 | 58 | 100205 | 100 | 3000 | 21.5171 | 68.7649 | 52.3871 | 0 | 7.2692 | FALSE | FALSE
2025-05-07 21:00 | 26.9 | 61.5 | 100230 | 100 | 3000 | 21.3354 | 70.7683 | 53.5091 | 0 | 7.2692 | FALSE | FALSE
2025-05-07 22:00 | 26.5 | 63 | 100200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-07 23:00 | 26.1 | 64 | 100135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-08 | 25.7 | 66 | 100060 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-08 01:00 | 25.3 | 67.5 | 99995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-08 02:00 | 24.9 | 68.5 | 99970 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-08 03:00 | 24.6 | 70 | 99960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-08 04:00 | 24.1 | 69 | 99975 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-08 05:00 | 23.65 | 67.5 | 100020 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-08 06:00 | 24.55 | 65.5 | 100075 | 100 | 3000 | 20.4015 | 72.0802 | 46.8773 | 0 | 7.2692 | FALSE | FALSE
2025-05-08 07:00 | 27.05 | 59 | 100130 | 100 | 3000 | 21.3987 | 69.2684 | 52.0068 | 0 | 7.2692 | FALSE | FALSE
2025-05-08 08:00 | 29.6 | 52.5 | 100175 | 100 | 3000 | 22.3897 | 66.1912 | 56.4396 | 0 | 7.2692 | FALSE | FALSE
2025-05-08 09:00 | 31 | 49 | 100200 | 100 | 3000 | 22.9231 | 64.4009 | 58.4989 | 0 | 7.2692 | FALSE | FALSE
2025-05-08 10:00 | 31.7 | 47 | 100190 | 100 | 3000 | 23.1882 | 63.2804 | 59.1317 | 0 | 7.2692 | FALSE | FALSE
2025-05-08 11:00 | 32.2 | 45.5 | 100175 | 100 | 3000 | 23.377 | 62.4033 | 59.4385 | 0 | 7.2692 | FALSE | FALSE
2025-05-08 12:00 | 32.4 | 45.5 | 100155 | 100 | 3000 | 23.4496 | 62.4984 | 60.1982 | 0 | 7.2692 | FALSE | FALSE
2025-05-08 13:00 | 32.35 | 46.5 | 100115 | 100 | 3000 | 23.427 | 63.2287 | 61.0897 | 0 | 7.2692 | FALSE | FALSE
2025-05-08 14:00 | 32.05 | 48.5 | 100070 | 100 | 3000 | 23.3095 | 64.5739 | 62.0715 | 0 | 7.2692 | FALSE | FALSE
2025-05-08 15:00 | 31.45 | 50 | 100060 | 100 | 3000 | 23.0847 | 65.3645 | 61.2788 | 0 | 7.2692 | FALSE | FALSE
2025-05-08 16:00 | 30.75 | 48.5 | 100080 | 100 | 3000 | 22.8324 | 63.9366 | 56.993 | 0 | 7.2692 | FALSE | FALSE
2025-05-08 17:00 | 29.75 | 49.5 | 100095 | 100 | 3000 | 22.4554 | 64.1961 | 54.124 | 0 | 7.2692 | FALSE | FALSE
2025-05-08 18:00 | 28.55 | 54 | 100120 | 100 | 3000 | 21.9878 | 66.7177 | 53.656 | 0 | 7.2692 | FALSE | FALSE
2025-05-08 19:00 | 27.75 | 57 | 100170 | 100 | 3000 | 21.6738 | 68.3127 | 53.136 | 0 | 7.2692 | FALSE | FALSE
2025-05-08 20:00 | 27.25 | 60.5 | 100235 | 100 | 3000 | 21.4731 | 70.3132 | 54.1209 | 0 | 7.2692 | FALSE | FALSE
2025-05-08 21:00 | 26.7 | 65.5 | 100295 | 100 | 3000 | 21.2498 | 73.1711 | 56.0027 | 0 | 7.2692 | FALSE | FALSE
2025-05-08 22:00 | 26.05 | 70 | 100315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-08 23:00 | 25.35 | 73 | 100290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-09 | 24.6 | 75.5 | 100245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-09 01:00 | 23.9 | 77.5 | 100210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-09 02:00 | 23.3 | 78.5 | 100195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-09 03:00 | 22.7 | 79.5 | 100200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-09 04:00 | 22.3 | 76.5 | 100205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-09 05:00 | 22.1 | 73 | 100220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-09 06:00 | 22.8 | 69.5 | 100285 | 100 | 3000 | 19.6881 | 73.5806 | 42.4817 | 0 | 7.2692 | FALSE | FALSE
2025-05-09 07:00 | 25.1 | 60 | 100355 | 100 | 3000 | 20.629 | 69.0225 | 44.9762 | 0 | 7.2692 | FALSE | FALSE
2025-05-09 08:00 | 27.95 | 51 | 100400 | 100 | 3000 | 21.765 | 64.4619 | 48.6647 | 0 | 7.2692 | FALSE | FALSE
2025-05-09 09:00 | 30.25 | 46 | 100425 | 100 | 3000 | 22.6545 | 61.9244 | 52.6517 | 0 | 7.2692 | FALSE | FALSE
2025-05-09 10:00 | 32.15 | 40.5 | 100410 | 100 | 3000 | 23.3802 | 58.6291 | 53.8676 | 0 | 7.2692 | FALSE | FALSE
2025-05-09 11:00 | 33.9 | 34.5 | 100360 | 100 | 3000 | 24.0452 | 54.5806 | 53.0938 | 0 | 7.2692 | FALSE | FALSE
2025-05-09 12:00 | 35.15 | 31.5 | 100295 | 100 | 3000 | 24.5097 | 52.5122 | 53.5305 | 0 | 7.2692 | FALSE | FALSE
2025-05-09 13:00 | 35.35 | 35.5 | 100235 | 100 | 3000 | 24.5555 | 55.8638 | 59.2323 | 0 | 7.2692 | FALSE | FALSE
2025-05-09 14:00 | 34.45 | 44 | 100190 | 100 | 3000 | 24.1885 | 62.3637 | 66.3753 | 0 | 7.2692 | FALSE | FALSE
2025-05-09 15:00 | 33.3 | 48.5 | 100170 | 100 | 3000 | 23.7585 | 65.258 | 67.0762 | 0 | 7.2692 | FALSE | FALSE
2025-05-09 16:00 | 32.2 | 51.5 | 100195 | 100 | 3000 | 23.3509 | 66.8804 | 65.9269 | 0 | 7.2692 | FALSE | FALSE
2025-05-09 17:00 | 30.7 | 59 | 100220 | 100 | 3000 | 22.7764 | 71.3777 | 67.3776 | 0 | 7.2692 | FALSE | FALSE
2025-05-09 18:00 | 29.05 | 70 | 100240 | 100 | 3000 | 22.1325 | 77.7504 | 70.4655 | 0 | 7.2692 | FALSE | FALSE
2025-05-09 19:00 | 27.8 | 80 | 100290 | 100 | 3000 | 21.6391 | 83.2488 | 73.3184 | 0 | 7.2692 | FALSE | FALSE
2025-05-09 20:00 | 27.05 | 85.5 | 100360 | 100 | 3000 | 21.3437 | 86.0297 | 74.1861 | 0 | 7.2692 | FALSE | FALSE
2025-05-09 21:00 | 26.55 | 88.5 | 100425 | 100 | 3000 | 21.1475 | 87.3973 | 74.0769 | 0 | 7.2692 | FALSE | FALSE
2025-05-09 22:00 | 25.95 | 91.5 | 100450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-09 23:00 | 25.15 | 95 | 100430 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-10 | 24.3 | 98 | 100385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-10 01:00 | 23.55 | 99.5 | 100340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-10 02:00 | 22.85 | 100 | 100325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-10 03:00 | 22.3 | 100 | 100345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-10 04:00 | 22.65 | 100 | 100360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-10 05:00 | 23.35 | 99.5 | 100390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-10 06:00 | 23.7 | 99 | 100460 | 100 | 3000 | 20.0221 | 90.747 | 67.1556 | 0 | 7.2692 | FALSE | FALSE
2025-05-10 07:00 | 23.95 | 98.5 | 100530 | 100 | 3000 | 20.1219 | 90.7054 | 68.12 | 0 | 7.2692 | FALSE | FALSE
2025-05-10 08:00 | 25.3 | 89.5 | 100590 | 100 | 3000 | 20.664 | 86.7611 | 68.4896 | 0 | 7.2692 | FALSE | FALSE
2025-05-10 09:00 | 28.1 | 72 | 100630 | 100 | 3000 | 21.7716 | 78.2706 | 67.8844 | 0 | 7.2692 | FALSE | FALSE
2025-05-10 10:00 | 31.1 | 56 | 100615 | 100 | 3000 | 22.9338 | 69.4581 | 66.1452 | 0 | 7.2692 | FALSE | FALSE
2025-05-10 11:00 | 33.6 | 46.5 | 100555 | 100 | 3000 | 23.8753 | 63.8431 | 66.0769 | 0 | 7.2692 | FALSE | FALSE
2025-05-10 12:00 | 34.8 | 45.5 | 100470 | 100 | 3000 | 24.3021 | 63.7429 | 69.6253 | 0 | 7.2692 | FALSE | FALSE
2025-05-10 13:00 | 34.8 | 49.5 | 100370 | 100 | 3000 | 24.2781 | 66.9866 | 74.4401 | 0 | 7.2692 | FALSE | FALSE
2025-05-10 14:00 | 34.2 | 51 | 100285 | 100 | 3000 | 24.0616 | 67.7807 | 73.6902 | 0 | 7.2692 | FALSE | FALSE
2025-05-10 15:00 | 33.4 | 51.5 | 100230 | 100 | 3000 | 23.7788 | 67.6346 | 70.9004 | 0 | 7.2692 | FALSE | FALSE
2025-05-10 16:00 | 32.15 | 53.5 | 100225 | 100 | 3000 | 23.3242 | 68.3374 | 67.8736 | 0 | 7.2692 | FALSE | FALSE
2025-05-10 17:00 | 30.9 | 56.5 | 100245 | 100 | 3000 | 22.8587 | 69.7236 | 65.7296 | 0 | 7.2692 | FALSE | FALSE
2025-05-10 18:00 | 30 | 62.5 | 100260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-10 19:00 | 29.25 | 66.5 | 100310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-10 20:00 | 28.85 | 68 | 100370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-10 21:00 | 28.55 | 70 | 100410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-10 22:00 | 28.15 | 72.5 | 100435 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-10 23:00 | 27.55 | 75 | 100410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 | 26.9 | 78 | 100360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 01:00 | 26.3 | 82 | 100320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 02:00 | 25.8 | 85 | 100295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 03:00 | 25.25 | 87.5 | 100295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 04:00 | 24.95 | 84 | 100300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 05:00 | 24.8 | 78 | 100310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 06:00 | 25.5 | 72 | 100345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 07:00 | 27.9 | 60 | 100405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 08:00 | 30.85 | 47 | 100470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 09:00 | 33.7 | 35.5 | 100490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 10:00 | 35.9 | 28.5 | 100460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 11:00 | 36.95 | 29 | 100400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 12:00 | 37.25 | 31 | 100325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 13:00 | 37.35 | 29.5 | 100245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 14:00 | 37.05 | 27.5 | 100170 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 15:00 | 36.4 | 28 | 100125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 16:00 | 34.95 | 35 | 100115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 17:00 | 33 | 45.5 | 100125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 18:00 | 31.55 | 55.5 | 100135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 19:00 | 30.5 | 63.5 | 100165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 20:00 | 29.95 | 64.5 | 100220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 21:00 | 29.5 | 62.5 | 100280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 22:00 | 28.9 | 62 | 100305 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-11 23:00 | 28.15 | 64 | 100260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-12 | 27.3 | 68.5 | 100195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-12 01:00 | 26.5 | 73 | 100150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-12 02:00 | 25.85 | 75 | 100125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-12 03:00 | 25.3 | 75 | 100125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-12 04:00 | 25.2 | 71.5 | 100125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-12 05:00 | 25.2 | 67 | 100130 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-12 06:00 | 25.95 | 61 | 100165 | 100 | 3000 | 20.9646 | 70.0033 | 49.1695 | 0 | 7.2692 | FALSE | FALSE
2025-05-12 07:00 | 28.6 | 50 | 100215 | 100 | 3000 | 22.0174 | 64.0608 | 50.2091 | 0 | 7.2692 | FALSE | FALSE
2025-05-12 08:00 | 31.9 | 38 | 100265 | 100 | 3000 | 23.2987 | 56.7053 | 50.246 | 0 | 7.2692 | FALSE | FALSE
2025-05-12 09:00 | 34.85 | 28 | 100290 | 100 | 3000 | 24.4235 | 49.5973 | 48.1938 | 0 | 7.2692 | FALSE | FALSE
2025-05-12 10:00 | 37.15 | 22 | 100270 | 100 | 3000 | 25.2816 | 44.8395 | 46.9337 | 0 | 7.2692 | FALSE | FALSE
2025-05-12 11:00 | 38.8 | 19.5 | 100230 | 100 | 3000 | 25.8773 | 42.74 | 47.7532 | 0 | 7.2692 | FALSE | FALSE
2025-05-12 12:00 | 39.75 | 19.5 | 100170 | 100 | 3000 | 26.2029 | 42.8228 | 50.2547 | 0 | 7.2692 | FALSE | FALSE
2025-05-12 13:00 | 40.1 | 18.5 | 100105 | 100 | 3000 | 26.332 | 41.9128 | 49.5745 | 0 | 7.2692 | FALSE | FALSE
2025-05-12 14:00 | 39.9 | 16.5 | 100045 | 100 | 3000 | 26.2844 | 40.013 | 45.8658 | 0 | 7.2692 | FALSE | FALSE
2025-05-12 15:00 | 39.15 | 17 | 100005 | 100 | 3000 | 26.0214 | 40.4734 | 44.7801 | 0 | 7.2692 | FALSE | FALSE
2025-05-12 16:00 | 37.9 | 19 | 99990 | 100 | 3000 | 25.5688 | 42.2639 | 44.5916 | 0 | 7.2692 | FALSE | FALSE
2025-05-12 17:00 | 36.15 | 22.5 | 99975 | 100 | 3000 | 24.924 | 45.2164 | 44.7771 | 0 | 7.2692 | FALSE | FALSE
2025-05-12 18:00 | 34.15 | 31 | 99990 | 100 | 3000 | 24.1543 | 51.9039 | 49.6311 | 0 | 7.2692 | FALSE | FALSE
2025-05-12 19:00 | 32.5 | 38 | 100030 | 100 | 3000 | 23.5195 | 56.9001 | 52.2656 | 0 | 7.2692 | FALSE | FALSE
2025-05-12 20:00 | 31.6 | 38 | 100085 | 100 | 3000 | 23.1875 | 56.6405 | 49.1785 | 0 | 7.2692 | FALSE | FALSE
2025-05-12 21:00 | 31.05 | 36 | 100140 | 100 | 3000 | 22.9898 | 55.0531 | 45.2306 | 0 | 7.2692 | FALSE | FALSE
2025-05-12 22:00 | 30.25 | 36 | 100155 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-12 23:00 | 29.05 | 41 | 100135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-13 | 28 | 47 | 100095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-13 01:00 | 27.2 | 47 | 100060 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-13 02:00 | 26.4 | 44.5 | 100065 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-13 03:00 | 25.65 | 44 | 100090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-13 04:00 | 25.65 | 42.5 | 100100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-13 05:00 | 25.95 | 39.5 | 100120 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-13 06:00 | 27 | 34.5 | 100160 | 100 | 3000 | 21.4289 | 53.6535 | 30.8867 | 0 | 7.2692 | FALSE | FALSE
2025-05-13 07:00 | 30.25 | 27.5 | 100215 | 100 | 3000 | 22.7156 | 48.9088 | 34.0299 | 0 | 7.2692 | FALSE | FALSE
2025-05-13 08:00 | 34.15 | 21 | 100280 | 100 | 3000 | 24.2084 | 43.9321 | 38.6108 | 0 | 7.2692 | FALSE | FALSE
2025-05-13 09:00 | 37.1 | 17.5 | 100305 | 100 | 3000 | 25.2979 | 40.9227 | 41.9771 | 0 | 7.2692 | FALSE | FALSE
2025-05-13 10:00 | 39.25 | 16 | 100285 | 100 | 3000 | 26.0652 | 39.5271 | 44.2745 | 0 | 7.2692 | FALSE | FALSE
2025-05-13 11:00 | 40.9 | 14.5 | 100240 | 100 | 3000 | 26.6464 | 38.0828 | 45.984 | 0 | 7.2692 | FALSE | FALSE
2025-05-13 12:00 | 42.05 | 12.5 | 100170 | 100 | 3000 | 27.0585 | 36.0756 | 47.1904 | 0 | 7.2692 | FALSE | FALSE
2025-05-13 13:00 | 42.45 | 11.5 | 100095 | 100 | 3000 | 27.2055 | 35.047 | 47.6037 | 0 | 7.2692 | FALSE | FALSE
2025-05-13 14:00 | 42.05 | 12.5 | 100035 | 100 | 3000 | 27.0587 | 36.0851 | 47.1279 | 0 | 7.2692 | FALSE | FALSE
2025-05-13 15:00 | 40.7 | 15 | 99990 | 100 | 3000 | 26.5732 | 38.5879 | 45.6469 | 0 | 7.2692 | FALSE | FALSE
2025-05-13 16:00 | 38.95 | 20 | 99970 | 100 | 3000 | 25.9246 | 43.2296 | 48.831 | 0 | 7.2692 | FALSE | FALSE
2025-05-13 17:00 | 36.65 | 27.5 | 99985 | 100 | 3000 | 25.0654 | 49.5382 | 52.9605 | 0 | 7.2692 | FALSE | FALSE
2025-05-13 18:00 | 34.15 | 36.5 | 100015 | 100 | 3000 | 24.1242 | 56.2694 | 56.248 | 0 | 7.2692 | FALSE | FALSE
2025-05-13 19:00 | 32.55 | 46 | 100065 | 100 | 3000 | 23.5016 | 62.9551 | 61.3036 | 0 | 7.2692 | FALSE | FALSE
2025-05-13 20:00 | 31.75 | 48 | 100140 | 100 | 3000 | 23.2024 | 64.0449 | 60.375 | 0 | 7.2692 | FALSE | FALSE
2025-05-13 21:00 | 31.2 | 46 | 100185 | 100 | 3000 | 23.0082 | 62.3274 | 56.1727 | 0 | 7.2692 | FALSE | FALSE
2025-05-13 22:00 | 30.35 | 46.5 | 100190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-13 23:00 | 29.5 | 45.5 | 100165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-14 | 28.6 | 46.5 | 100120 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-14 01:00 | 27.75 | 47 | 100095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-14 02:00 | 26.95 | 44.5 | 100090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-14 03:00 | 26.3 | 41.5 | 100105 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-14 04:00 | 26.55 | 38 | 100135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-14 05:00 | 27.35 | 33 | 100160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-14 06:00 | 29.3 | 23.5 | 100215 | 100 | 3000 | 22.3603 | 46.2027 | 32.7664 | 0 | 7.2692 | FALSE | FALSE
2025-05-14 07:00 | 32.5 | 17.5 | 100290 | 100 | 3000 | 23.6101 | 41.3839 | 36.7995 | 0 | 7.2692 | FALSE | FALSE
2025-05-14 08:00 | 35.25 | 22 | 100345 | 100 | 3000 | 24.6038 | 44.7294 | 41.7547 | 0 | 7.2692 | FALSE | FALSE
2025-05-14 09:00 | 37.6 | 25 | 100375 | 100 | 3000 | 25.4153 | 47.5185 | 52.4675 | 0 | 7.2692 | FALSE | FALSE
2025-05-14 10:00 | 39.85 | 21.5 | 100370 | 100 | 3000 | 26.2166 | 44.7042 | 53.7253 | 0 | 7.2692 | FALSE | FALSE
2025-05-14 11:00 | 41.7 | 16.5 | 100350 | 100 | 3000 | 26.8921 | 40.0633 | 50.4261 | 0 | 7.2692 | FALSE | FALSE
2025-05-14 12:00 | 42.75 | 13 | 100305 | 100 | 3000 | 27.2857 | 36.5535 | 47.8911 | 0 | 7.2692 | FALSE | FALSE
2025-05-14 13:00 | 42.5 | 15 | 100235 | 100 | 3000 | 27.1766 | 38.6017 | 49.7309 | 0 | 7.2692 | FALSE | FALSE
2025-05-14 14:00 | 41.2 | 21.5 | 100180 | 100 | 3000 | 26.6672 | 44.9571 | 57.4684 | 0 | 7.2692 | FALSE | FALSE
2025-05-14 15:00 | 39.85 | 25.5 | 100135 | 100 | 3000 | 26.176 | 48.4972 | 59.902 | 0 | 7.2692 | FALSE | FALSE
2025-05-14 16:00 | 38.35 | 29 | 100105 | 100 | 3000 | 25.6389 | 51.2925 | 60.4411 | 0 | 7.2692 | FALSE | FALSE
2025-05-14 17:00 | 36.15 | 36 | 100115 | 100 | 3000 | 24.8312 | 56.6009 | 62.6435 | 0 | 7.2692 | FALSE | FALSE
2025-05-14 18:00 | 33.9 | 44 | 100145 | 100 | 3000 | 23.9946 | 62.0807 | 64.2453 | 0 | 7.2692 | FALSE | FALSE
2025-05-14 19:00 | 32.7 | 48.5 | 100185 | 100 | 3000 | 23.5442 | 64.9139 | 64.6757 | 0 | 7.2692 | FALSE | FALSE
2025-05-14 20:00 | 32.2 | 47.5 | 100240 | 100 | 3000 | 23.3683 | 63.8909 | 61.6198 | 0 | 7.2692 | FALSE | FALSE
2025-05-14 21:00 | 31.45 | 45.5 | 100290 | 100 | 3000 | 23.1024 | 62.0604 | 56.6173 | 0 | 7.2692 | FALSE | FALSE
2025-05-14 22:00 | 30.75 | 44.5 | 100305 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-14 23:00 | 30.05 | 44.5 | 100285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-15 | 29.3 | 45 | 100255 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-15 01:00 | 28.45 | 46 | 100230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-15 02:00 | 27.65 | 47 | 100215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-15 03:00 | 27.05 | 47 | 100225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-15 04:00 | 26.95 | 45.5 | 100270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-15 05:00 | 27.2 | 42.5 | 100330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-15 06:00 | 28.7 | 33 | 100385 | 100 | 3000 | 22.1005 | 52.6719 | 34.8132 | 0 | 7.2692 | FALSE | FALSE
2025-05-15 07:00 | 31.9 | 22 | 100445 | 100 | 3000 | 23.3642 | 44.8199 | 36.0394 | 0 | 7.2692 | FALSE | FALSE
2025-05-15 08:00 | 34.9 | 19 | 100500 | 100 | 3000 | 24.4944 | 42.2703 | 39.5986 | 0 | 7.2692 | FALSE | FALSE
2025-05-15 09:00 | 37.25 | 18.5 | 100515 | 100 | 3000 | 25.3433 | 41.7743 | 42.3536 | 0 | 7.2692 | FALSE | FALSE
2025-05-15 10:00 | 39.25 | 17 | 100505 | 100 | 3000 | 26.0555 | 40.4368 | 45.1774 | 0 | 7.2692 | FALSE | FALSE
2025-05-15 11:00 | 40.65 | 15.5 | 100485 | 100 | 3000 | 26.5502 | 39.0348 | 46.2138 | 0 | 7.2692 | FALSE | FALSE
2025-05-15 12:00 | 40.35 | 18 | 100445 | 100 | 3000 | 26.4217 | 41.4292 | 49.5241 | 0 | 7.2692 | FALSE | FALSE
2025-05-15 13:00 | 39.5 | 20.5 | 100400 | 100 | 3000 | 26.1078 | 43.7157 | 51.2091 | 0 | 7.2692 | FALSE | FALSE
2025-05-15 14:00 | 39 | 21 | 100355 | 100 | 3000 | 25.9323 | 44.1242 | 50.5943 | 0 | 7.2692 | FALSE | FALSE
2025-05-15 15:00 | 38.2 | 23 | 100310 | 100 | 3000 | 25.6394 | 45.8409 | 51.3163 | 0 | 7.2692 | FALSE | FALSE
2025-05-15 16:00 | 37.45 | 24.5 | 100290 | 100 | 3000 | 25.3672 | 47.0598 | 51.2971 | 0 | 7.2692 | FALSE | FALSE
2025-05-15 17:00 | 36.1 | 29 | 100275 | 100 | 3000 | 24.8618 | 50.6683 | 53.3343 | 0 | 7.2692 | FALSE | FALSE
2025-05-15 18:00 | 33.95 | 39.5 | 100255 | 100 | 3000 | 24.0365 | 58.5483 | 59.1652 | 0 | 7.2692 | FALSE | FALSE
2025-05-15 19:00 | 32.35 | 45.5 | 100260 | 100 | 3000 | 23.4315 | 62.4654 | 60.03 | 0 | 7.2692 | FALSE | FALSE
2025-05-15 20:00 | 31.45 | 46.5 | 100290 | 100 | 3000 | 23.0985 | 62.7902 | 57.6662 | 0 | 7.2692 | FALSE | FALSE
2025-05-15 21:00 | 30.55 | 49.5 | 100320 | 100 | 3000 | 22.7546 | 64.5334 | 57.2716 | 0 | 7.2692 | FALSE | FALSE
2025-05-15 22:00 | 30.05 | 50.5 | 100330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-15 23:00 | 29.8 | 50.5 | 100320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-16 | 29.15 | 53.5 | 100295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-16 01:00 | 28.25 | 55 | 100265 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-16 02:00 | 27.4 | 54.5 | 100245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-16 03:00 | 26.75 | 55 | 100230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-16 04:00 | 26.4 | 52 | 100225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-16 05:00 | 26 | 49 | 100245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-16 06:00 | 26.85 | 46 | 100290 | 100 | 3000 | 21.3467 | 60.9362 | 40.2518 | 0 | 7.2692 | FALSE | FALSE
2025-05-16 07:00 | 29.5 | 38.5 | 100370 | 100 | 3000 | 22.3939 | 56.5013 | 42.6258 | 0 | 7.2692 | FALSE | FALSE
2025-05-16 08:00 | 32.45 | 31.5 | 100440 | 100 | 3000 | 23.5298 | 51.9487 | 44.9489 | 0 | 7.2692 | FALSE | FALSE
2025-05-16 09:00 | 35.1 | 27.5 | 100435 | 100 | 3000 | 24.5162 | 49.2172 | 48.3587 | 0 | 7.2692 | FALSE | FALSE
2025-05-16 10:00 | 37.45 | 22.5 | 100390 | 100 | 3000 | 25.3828 | 45.2959 | 48.5031 | 0 | 7.2692 | FALSE | FALSE
2025-05-16 11:00 | 38.95 | 19.5 | 100350 | 100 | 3000 | 25.9289 | 42.7414 | 48.185 | 0 | 7.2692 | FALSE | FALSE
2025-05-16 12:00 | 39.3 | 20.5 | 100295 | 100 | 3000 | 26.0397 | 43.7009 | 50.6334 | 0 | 7.2692 | FALSE | FALSE
2025-05-16 13:00 | 39.15 | 19.5 | 100235 | 100 | 3000 | 25.9978 | 42.7653 | 48.6806 | 0 | 7.2692 | FALSE | FALSE
2025-05-16 14:00 | 37.95 | 21 | 100185 | 100 | 3000 | 25.5696 | 44.0328 | 47.6783 | 0 | 7.2692 | FALSE | FALSE
2025-05-16 15:00 | 36.6 | 24 | 100160 | 100 | 3000 | 25.0731 | 46.5181 | 48.1125 | 0 | 7.2692 | FALSE | FALSE
2025-05-16 16:00 | 35.6 | 26.5 | 100155 | 100 | 3000 | 24.7013 | 48.4923 | 48.507 | 0 | 7.2692 | FALSE | FALSE
2025-05-16 17:00 | 33.65 | 38 | 100155 | 100 | 3000 | 23.9369 | 57.266 | 56.3094 | 0 | 7.2692 | FALSE | FALSE
2025-05-16 18:00 | 31.6 | 53 | 100175 | 100 | 3000 | 23.1274 | 67.6307 | 65.0461 | 0 | 7.2692 | FALSE | FALSE
2025-05-16 19:00 | 30.4 | 61.5 | 100210 | 100 | 3000 | 22.6576 | 72.9372 | 68.5372 | 0 | 7.2692 | FALSE | FALSE
2025-05-16 20:00 | 29.65 | 66 | 100235 | 100 | 3000 | 22.3668 | 75.5055 | 69.5106 | 0 | 7.2692 | FALSE | FALSE
2025-05-16 21:00 | 28.85 | 71.5 | 100245 | 100 | 3000 | 22.0538 | 78.5922 | 70.8948 | 0 | 7.2692 | FALSE | FALSE
2025-05-16 22:00 | 28.05 | 76.5 | 100240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-16 23:00 | 27.3 | 78.5 | 100210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-17 | 26.55 | 81 | 100160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-17 01:00 | 26.05 | 84 | 100105 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-17 02:00 | 25.8 | 85.5 | 100065 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-17 03:00 | 25.75 | 85.5 | 100040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-17 04:00 | 25.95 | 83.5 | 100055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-17 05:00 | 26.2 | 80.5 | 100090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-17 06:00 | 27.4 | 73.5 | 100125 | 100 | 3000 | 21.5024 | 78.7371 | 65.8223 | 0 | 7.2692 | FALSE | FALSE
2025-05-17 07:00 | 30.2 | 62 | 100170 | 100 | 3000 | 22.5824 | 73.1478 | 68.1331 | 0 | 7.2692 | FALSE | FALSE
2025-05-17 08:00 | 32.85 | 51.5 | 100195 | 100 | 3000 | 23.5838 | 67.2811 | 68.6049 | 0 | 7.2692 | FALSE | FALSE
2025-05-17 09:00 | 34.25 | 44.5 | 100200 | 100 | 3000 | 24.1154 | 62.6545 | 66.1991 | 0 | 7.2692 | FALSE | FALSE
2025-05-17 10:00 | 35.15 | 41 | 100210 | 100 | 3000 | 24.4511 | 60.2945 | 65.389 | 0 | 7.2692 | FALSE | FALSE
2025-05-17 11:00 | 35.85 | 38.5 | 100205 | 100 | 3000 | 24.7103 | 58.5621 | 64.8252 | 0 | 7.2692 | FALSE | FALSE
2025-05-17 12:00 | 36.15 | 37.5 | 100160 | 100 | 3000 | 24.8208 | 57.8628 | 64.6111 | 0 | 7.2692 | FALSE | FALSE
2025-05-17 13:00 | 36.1 | 37.5 | 100100 | 100 | 3000 | 24.8035 | 57.8455 | 64.4147 | 0 | 7.2692 | FALSE | FALSE
2025-05-17 14:00 | 35.8 | 37.5 | 100060 | 100 | 3000 | 24.6996 | 57.7166 | 63.3231 | 0 | 7.2692 | FALSE | FALSE
2025-05-17 15:00 | 35.1 | 38.5 | 100040 | 100 | 3000 | 24.4491 | 58.2421 | 62.0568 | 0 | 7.2692 | FALSE | FALSE
2025-05-17 16:00 | 33.95 | 42 | 100035 | 100 | 3000 | 24.023 | 60.539 | 62.0607 | 0 | 7.2692 | FALSE | FALSE
2025-05-17 17:00 | 32.35 | 50 | 100070 | 100 | 3000 | 23.4115 | 65.8578 | 64.8884 | 0 | 7.2692 | FALSE | FALSE
2025-05-17 18:00 | 30.65 | 60.5 | 100115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-17 19:00 | 29.6 | 67.5 | 100150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-17 20:00 | 29.05 | 69.5 | 100190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-17 21:00 | 28.5 | 71.5 | 100215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-17 22:00 | 27.85 | 74 | 100220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-17 23:00 | 27 | 76.5 | 100215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 | 26.15 | 79 | 100190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 01:00 | 25.45 | 80.5 | 100165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 02:00 | 24.9 | 81 | 100155 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 03:00 | 24.5 | 81.5 | 100135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 04:00 | 24.5 | 79.5 | 100135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 05:00 | 24.6 | 77.5 | 100170 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 06:00 | 25.25 | 74.5 | 100230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 07:00 | 27.3 | 66 | 100290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 08:00 | 29.85 | 56.5 | 100330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 09:00 | 32.1 | 47 | 100340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 10:00 | 33.95 | 38 | 100310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 11:00 | 35.45 | 31.5 | 100275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 12:00 | 36.5 | 28 | 100220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 13:00 | 36.9 | 27.5 | 100145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 14:00 | 36.45 | 30 | 100080 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 15:00 | 35.15 | 37.5 | 100035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 16:00 | 33.5 | 45 | 100030 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 17:00 | 32 | 49.5 | 100035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 18:00 | 30.6 | 55 | 100040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 19:00 | 29.4 | 63 | 100065 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 20:00 | 28.45 | 71.5 | 100090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 21:00 | 27.5 | 78 | 100095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 22:00 | 26.55 | 83.5 | 100080 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-18 23:00 | 25.7 | 88.5 | 100060 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-19 | 24.95 | 93 | 100025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-19 01:00 | 24.35 | 95.5 | 99980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-19 02:00 | 23.8 | 96 | 99965 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-19 03:00 | 23.25 | 96 | 99970 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-19 04:00 | 23.35 | 94.5 | 99965 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-19 05:00 | 23.6 | 93.5 | 99975 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-19 06:00 | 24.35 | 90 | 100030 | 100 | 3000 | 20.2903 | 86.2453 | 64.0119 | 0 | 7.2692 | FALSE | FALSE
2025-05-19 07:00 | 26.65 | 78.5 | 100090 | 100 | 3000 | 21.205 | 81.2959 | 66.425 | 0 | 7.2692 | FALSE | FALSE
2025-05-19 08:00 | 29.6 | 64 | 100135 | 100 | 3000 | 22.3544 | 74.1033 | 67.3756 | 0 | 7.2692 | FALSE | FALSE
2025-05-19 09:00 | 32.65 | 50.5 | 100160 | 100 | 3000 | 23.517 | 66.402 | 66.6719 | 0 | 7.2692 | FALSE | FALSE
2025-05-19 10:00 | 35.4 | 40.5 | 100140 | 100 | 3000 | 24.5412 | 60.0131 | 65.6836 | 0 | 7.2692 | FALSE | FALSE
2025-05-19 11:00 | 37.1 | 36.5 | 100095 | 100 | 3000 | 25.1533 | 57.4466 | 66.6938 | 0 | 7.2692 | FALSE | FALSE
2025-05-19 12:00 | 37.7 | 34 | 100030 | 100 | 3000 | 25.3765 | 55.5268 | 65.36 | 0 | 7.2692 | FALSE | FALSE
2025-05-19 13:00 | 37.45 | 31 | 99960 | 100 | 3000 | 25.3157 | 52.7938 | 60.3062 | 0 | 7.2692 | FALSE | FALSE
2025-05-19 14:00 | 36.6 | 34.5 | 99905 | 100 | 3000 | 24.9971 | 55.5244 | 62.1829 | 0 | 7.2692 | FALSE | FALSE
2025-05-19 15:00 | 35.45 | 43.5 | 99865 | 100 | 3000 | 24.5391 | 62.5383 | 69.5645 | 0 | 7.2692 | FALSE | FALSE
2025-05-19 16:00 | 33.8 | 54.5 | 99855 | 100 | 3000 | 23.9029 | 70.289 | 75.9375 | 0 | 7.2692 | FALSE | FALSE
2025-05-19 17:00 | 32.15 | 66 | 99865 | 100 | 3000 | 23.2692 | 77.6691 | 81.0679 | 0 | 7.2692 | FALSE | FALSE
2025-05-19 18:00 | 30.75 | 74.5 | 99875 | 100 | 3000 | 22.7379 | 82.47 | 82.881 | 0 | 7.2692 | FALSE | FALSE
2025-05-19 19:00 | 29.7 | 79.5 | 99900 | 100 | 3000 | 22.3424 | 84.8593 | 82.362 | 0 | 7.2692 | FALSE | FALSE
2025-05-19 20:00 | 29.1 | 83 | 99945 | 100 | 3000 | 22.1131 | 86.5864 | 82.4959 | 0 | 7.2692 | FALSE | FALSE
2025-05-19 21:00 | 28.45 | 87 | 99970 | 100 | 3000 | 21.8634 | 88.5253 | 82.6581 | 0 | 7.2692 | FALSE | FALSE
2025-05-19 22:00 | 27.75 | 91.5 | 99950 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-19 23:00 | 27.05 | 95 | 99920 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-20 | 26.55 | 97 | 99885 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-20 01:00 | 25.95 | 99 | 99865 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-20 02:00 | 25.35 | 100 | 99875 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-20 03:00 | 24.9 | 100 | 99885 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-20 04:00 | 25.2 | 96.5 | 99885 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-20 05:00 | 25.85 | 90 | 99895 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-20 06:00 | 27.15 | 78 | 99915 | 100 | 3000 | 21.3973 | 81.4209 | 68.3888 | 0 | 7.2692 | FALSE | FALSE
2025-05-20 07:00 | 30.3 | 59.5 | 99940 | 100 | 3000 | 22.6276 | 71.4862 | 66.0844 | 0 | 7.2692 | FALSE | FALSE
2025-05-20 08:00 | 33.55 | 47.5 | 99990 | 100 | 3000 | 23.8521 | 64.6441 | 66.8958 | 0 | 7.2692 | FALSE | FALSE
2025-05-20 09:00 | 35.85 | 41.5 | 100020 | 100 | 3000 | 24.6901 | 61.0856 | 68.6183 | 0 | 7.2692 | FALSE | FALSE
2025-05-20 10:00 | 37.75 | 36.5 | 100005 | 100 | 3000 | 25.3727 | 57.7653 | 69.0223 | 0 | 7.2692 | FALSE | FALSE
2025-05-20 11:00 | 38.6 | 37 | 99965 | 100 | 3000 | 25.651 | 58.658 | 72.8407 | 0 | 7.2692 | FALSE | FALSE
2025-05-20 12:00 | 38.4 | 36.5 | 99915 | 100 | 3000 | 25.5894 | 58.1023 | 71.3703 | 0 | 7.2692 | FALSE | FALSE
2025-05-20 13:00 | 37.95 | 36.5 | 99855 | 100 | 3000 | 25.4396 | 57.8771 | 69.7082 | 0 | 7.2692 | FALSE | FALSE
2025-05-20 14:00 | 37.15 | 39.5 | 99795 | 100 | 3000 | 25.1467 | 60.1049 | 70.8617 | 0 | 7.2692 | FALSE | FALSE
2025-05-20 15:00 | 36.45 | 40 | 99745 | 100 | 3000 | 24.9057 | 60.1635 | 68.8771 | 0 | 7.2692 | FALSE | FALSE
2025-05-20 16:00 | 35.65 | 41 | 99735 | 100 | 3000 | 24.6244 | 60.5878 | 67.1497 | 0 | 7.2692 | FALSE | FALSE
2025-05-20 17:00 | 34.4 | 45 | 99745 | 100 | 3000 | 24.165 | 63.1752 | 67.269 | 0 | 7.2692 | FALSE | FALSE
2025-05-20 18:00 | 32.8 | 53 | 99740 | 100 | 3000 | 23.5586 | 68.4308 | 69.9505 | 0 | 7.2692 | FALSE | FALSE
2025-05-20 19:00 | 31.05 | 65 | 99770 | 100 | 3000 | 22.8811 | 75.9753 | 74.866 | 0 | 7.2692 | FALSE | FALSE
2025-05-20 20:00 | 29.75 | 75.5 | 99825 | 100 | 3000 | 22.3732 | 82.1682 | 78.8574 | 0 | 7.2692 | FALSE | FALSE
2025-05-20 21:00 | 29.05 | 80 | 99850 | 100 | 3000 | 22.1034 | 84.5237 | 79.506 | 0 | 7.2692 | FALSE | FALSE
2025-05-20 22:00 | 28.25 | 83 | 99840 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-20 23:00 | 27.2 | 87.5 | 99815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-21 | 26.35 | 91.5 | 99770 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-21 01:00 | 25.7 | 93.5 | 99720 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-21 02:00 | 25.15 | 93 | 99695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-21 03:00 | 24.6 | 91.5 | 99700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-21 04:00 | 24.45 | 90 | 99725 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-21 05:00 | 24.45 | 87.5 | 99765 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-21 06:00 | 25.4 | 78 | 99835 | 100 | 3000 | 20.7206 | 80.0349 | 60.0812 | 0 | 7.2692 | FALSE | FALSE
2025-05-21 07:00 | 28.35 | 62 | 99905 | 100 | 3000 | 21.8909 | 71.9414 | 60.0216 | 0 | 7.2692 | FALSE | FALSE
2025-05-21 08:00 | 32.25 | 45.5 | 99975 | 100 | 3000 | 23.3951 | 62.4445 | 59.5857 | 0 | 7.2692 | FALSE | FALSE
2025-05-21 09:00 | 35.95 | 31 | 100010 | 100 | 3000 | 24.7956 | 52.3341 | 55.4104 | 0 | 7.2692 | FALSE | FALSE
2025-05-21 10:00 | 38.9 | 22.5 | 99990 | 100 | 3000 | 25.8844 | 45.5166 | 52.4724 | 0 | 7.2692 | FALSE | FALSE
2025-05-21 11:00 | 40.9 | 19.5 | 99945 | 100 | 3000 | 26.5906 | 42.9696 | 53.2612 | 0 | 7.2692 | FALSE | FALSE
2025-05-21 12:00 | 42 | 20 | 99870 | 100 | 3000 | 26.9483 | 43.6386 | 57.0679 | 0 | 7.2692 | FALSE | FALSE
2025-05-21 13:00 | 42.6 | 22 | 99790 | 100 | 3000 | 27.1169 | 45.8053 | 62.2122 | 0 | 7.2692 | FALSE | FALSE
2025-05-21 14:00 | 42.3 | 22 | 99730 | 100 | 3000 | 27.0203 | 45.7343 | 61.3226 | 0 | 7.2692 | FALSE | FALSE
2025-05-21 15:00 | 40.8 | 22.5 | 99705 | 100 | 3000 | 26.5238 | 45.8874 | 57.8192 | 0 | 7.2692 | FALSE | FALSE
2025-05-21 16:00 | 38.35 | 32.5 | 99700 | 100 | 3000 | 25.608 | 54.4837 | 65.3855 | 0 | 7.2692 | FALSE | FALSE
2025-05-21 17:00 | 35.75 | 46 | 99710 | 100 | 3000 | 24.6253 | 64.8079 | 73.8572 | 0 | 7.2692 | FALSE | FALSE
2025-05-21 18:00 | 33.65 | 55.5 | 99735 | 100 | 3000 | 23.8453 | 70.9669 | 76.3976 | 0 | 7.2692 | FALSE | FALSE
2025-05-21 19:00 | 32.1 | 63 | 99780 | 100 | 3000 | 23.2646 | 75.4043 | 77.6542 | 0 | 7.2692 | FALSE | FALSE
2025-05-21 20:00 | 31.15 | 68 | 99830 | 100 | 3000 | 22.9056 | 78.2145 | 78.3652 | 0 | 7.2692 | FALSE | FALSE
2025-05-21 21:00 | 30.45 | 70.5 | 99855 | 100 | 3000 | 22.6443 | 79.3508 | 77.4981 | 0 | 7.2692 | FALSE | FALSE
2025-05-21 22:00 | 29.65 | 71.5 | 99860 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-21 23:00 | 28.85 | 73 | 99835 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-22 | 28 | 76.5 | 99790 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-22 01:00 | 27.1 | 85 | 99755 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-22 02:00 | 26.35 | 93 | 99730 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-22 03:00 | 25.6 | 95 | 99720 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-22 04:00 | 25.6 | 93 | 99725 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-22 05:00 | 25.55 | 92.5 | 99740 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-22 06:00 | 25.95 | 88.5 | 99770 | 100 | 3000 | 20.9171 | 86.867 | 70.908 | 0 | 7.2692 | FALSE | FALSE
2025-05-22 07:00 | 28.75 | 73 | 99840 | 100 | 3000 | 22.0122 | 79.55 | 71.7048 | 0 | 7.2692 | FALSE | FALSE
2025-05-22 08:00 | 32.5 | 53.5 | 99910 | 100 | 3000 | 23.4495 | 68.5944 | 69.274 | 0 | 7.2692 | FALSE | FALSE
2025-05-22 09:00 | 36.3 | 34.5 | 99930 | 100 | 3000 | 24.8935 | 55.4069 | 61.1515 | 0 | 7.2692 | FALSE | FALSE
2025-05-22 10:00 | 39.85 | 19.5 | 99915 | 100 | 3000 | 26.2371 | 42.8518 | 50.4438 | 0 | 7.2692 | FALSE | FALSE
2025-05-22 11:00 | 42.3 | 12.5 | 99865 | 100 | 3000 | 27.1428 | 36.0864 | 47.2892 | 0 | 7.2692 | FALSE | FALSE
2025-05-22 12:00 | 43.65 | 10.5 | 99790 | 100 | 3000 | 27.6194 | 33.9508 | 48.665 | 0 | 7.2692 | FALSE | FALSE
2025-05-22 13:00 | 44.05 | 11.5 | 99720 | 100 | 3000 | 27.7364 | 34.9952 | 48.9303 | 0 | 7.2692 | FALSE | FALSE
2025-05-22 14:00 | 43.8 | 13 | 99665 | 100 | 3000 | 27.6323 | 36.5959 | 48.9111 | 0 | 7.2692 | FALSE | FALSE
2025-05-22 15:00 | 42.95 | 12.5 | 99620 | 100 | 3000 | 27.3597 | 36.0825 | 47.7905 | 0 | 7.2692 | FALSE | FALSE
2025-05-22 16:00 | 41.45 | 14.5 | 99585 | 100 | 3000 | 26.8331 | 38.1257 | 46.2222 | 0 | 7.2692 | FALSE | FALSE
2025-05-22 17:00 | 38.95 | 23.5 | 99565 | 100 | 3000 | 25.8924 | 46.4759 | 53.9954 | 0 | 7.2692 | FALSE | FALSE
2025-05-22 18:00 | 36 | 36.5 | 99565 | 100 | 3000 | 24.7756 | 57.0061 | 62.6192 | 0 | 7.2692 | FALSE | FALSE
2025-05-22 19:00 | 34.05 | 46 | 99585 | 100 | 3000 | 24.0364 | 63.7882 | 67.0408 | 0 | 7.2692 | FALSE | FALSE
2025-05-22 20:00 | 32.65 | 54 | 99620 | 100 | 3000 | 23.5005 | 69.0989 | 70.3882 | 0 | 7.2692 | FALSE | FALSE
2025-05-22 21:00 | 31.35 | 61.5 | 99645 | 100 | 3000 | 23.0027 | 73.703 | 72.6546 | 0 | 7.2692 | FALSE | FALSE
2025-05-22 22:00 | 30.35 | 62.5 | 99635 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-22 23:00 | 29.8 | 56.5 | 99590 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-23 | 29.45 | 49.5 | 99535 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-23 01:00 | 28.75 | 46.5 | 99500 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-23 02:00 | 28 | 45 | 99475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-23 03:00 | 27.45 | 43 | 99470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-23 04:00 | 27 | 45.5 | 99480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-23 05:00 | 26.65 | 49.5 | 99515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-23 06:00 | 27.55 | 44 | 99580 | 100 | 3000 | 21.6257 | 59.8702 | 40.8798 | 0 | 7.2692 | FALSE | FALSE
2025-05-23 07:00 | 30.8 | 31.5 | 99625 | 100 | 3000 | 22.912 | 51.8256 | 39.6497 | 0 | 7.2692 | FALSE | FALSE
2025-05-23 08:00 | 35.25 | 20.5 | 99635 | 100 | 3000 | 24.6136 | 43.5542 | 39.6445 | 0 | 7.2692 | FALSE | FALSE
2025-05-23 09:00 | 39.3 | 13.5 | 99625 | 100 | 3000 | 26.107 | 37.2564 | 44.1585 | 0 | 7.2692 | FALSE | FALSE
2025-05-23 10:00 | 42.45 | 9.5 | 99585 | 100 | 3000 | 27.2323 | 33.048 | 47.4934 | 0 | 7.2692 | FALSE | FALSE
2025-05-23 11:00 | 44.9 | 7 | 99520 | 100 | 3000 | 28.0865 | 30.0747 | 49.9595 | 0 | 7.2692 | FALSE | FALSE
2025-05-23 12:00 | 46.3 | 6.5 | 99465 | 100 | 3000 | 28.5532 | 29.3093 | 51.2528 | 0 | 7.2692 | FALSE | FALSE
2025-05-23 13:00 | 46.55 | 7.5 | 99405 | 100 | 3000 | 28.6154 | 30.4213 | 51.3569 | 0 | 7.2692 | FALSE | FALSE
2025-05-23 14:00 | 45.8 | 8.5 | 99340 | 100 | 3000 | 28.3555 | 31.634 | 50.5686 | 0 | 7.2692 | FALSE | FALSE
2025-05-23 15:00 | 43.5 | 14 | 99305 | 100 | 3000 | 27.5201 | 37.6692 | 49.9701 | 0 | 7.2692 | FALSE | FALSE
2025-05-23 16:00 | 40.9 | 21 | 99305 | 100 | 3000 | 26.574 | 44.4779 | 55.5261 | 0 | 7.2692 | FALSE | FALSE
2025-05-23 17:00 | 38.35 | 29 | 99315 | 100 | 3000 | 25.6389 | 51.3557 | 60.2151 | 0 | 7.2692 | FALSE | FALSE
2025-05-23 18:00 | 35.6 | 42 | 99340 | 100 | 3000 | 24.6003 | 61.4256 | 68.1234 | 0 | 7.2692 | FALSE | FALSE
2025-05-23 19:00 | 34 | 48.5 | 99375 | 100 | 3000 | 24.005 | 65.7519 | 69.7188 | 0 | 7.2692 | FALSE | FALSE
2025-05-23 20:00 | 33.15 | 47.5 | 99420 | 100 | 3000 | 23.7097 | 64.4691 | 65.1745 | 0 | 7.2692 | FALSE | FALSE
2025-05-23 21:00 | 32.3 | 47.5 | 99460 | 100 | 3000 | 23.4043 | 64.0126 | 61.8406 | 0 | 7.2692 | FALSE | FALSE
2025-05-23 22:00 | 31.5 | 47 | 99465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-23 23:00 | 30.6 | 45 | 99450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-24 | 29.75 | 44 | 99415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-24 01:00 | 28.95 | 45 | 99385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-24 02:00 | 28.2 | 48 | 99385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-24 03:00 | 27.55 | 50 | 99400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-24 04:00 | 27.3 | 45.5 | 99380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-24 05:00 | 27.35 | 37 | 99385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-24 06:00 | 28.9 | 28 | 99465 | 100 | 3000 | 22.1923 | 49.3804 | 31.9566 | 0 | 7.2692 | FALSE | FALSE
2025-05-24 07:00 | 32.95 | 18 | 99535 | 100 | 3000 | 23.7781 | 41.7585 | 37.04 | 0 | 7.2692 | FALSE | FALSE
2025-05-24 08:00 | 37.6 | 12 | 99570 | 100 | 3000 | 25.5196 | 36.1149 | 42.4251 | 0 | 7.2692 | FALSE | FALSE
2025-05-24 09:00 | 41.55 | 9.5 | 99560 | 100 | 3000 | 26.9263 | 33.1717 | 46.602 | 0 | 7.2692 | FALSE | FALSE
2025-05-24 10:00 | 44.1 | 7.5 | 99510 | 100 | 3000 | 27.8136 | 30.7389 | 49.1692 | 0 | 7.2692 | FALSE | FALSE
2025-05-24 11:00 | 45.7 | 6 | 99450 | 100 | 3000 | 28.3666 | 28.8437 | 50.7434 | 0 | 7.2692 | FALSE | FALSE
2025-05-24 12:00 | 46.85 | 5 | 99380 | 100 | 3000 | 28.7601 | 27.5056 | 51.8394 | 0 | 7.2692 | FALSE | FALSE
2025-05-24 13:00 | 46.9 | 5.5 | 99310 | 100 | 3000 | 28.7668 | 28.0781 | 51.8026 | 0 | 7.2692 | FALSE | FALSE
2025-05-24 14:00 | 45.8 | 7 | 99265 | 100 | 3000 | 28.3821 | 29.958 | 50.6583 | 0 | 7.2692 | FALSE | FALSE
2025-05-24 15:00 | 44.05 | 9 | 99255 | 100 | 3000 | 27.7749 | 32.3615 | 48.8895 | 0 | 7.2692 | FALSE | FALSE
2025-05-24 16:00 | 41.25 | 17 | 99265 | 100 | 3000 | 26.7369 | 40.6077 | 49.7998 | 0 | 7.2692 | FALSE | FALSE
2025-05-24 17:00 | 38.2 | 28.5 | 99275 | 100 | 3000 | 25.5923 | 50.8632 | 59.0011 | 0 | 7.2692 | FALSE | FALSE
2025-05-24 18:00 | 35.65 | 39.5 | 99290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-24 19:00 | 33.55 | 51.5 | 99325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-24 20:00 | 32.25 | 59 | 99375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-24 21:00 | 31.25 | 64 | 99435 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-24 22:00 | 30.5 | 66 | 99470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-24 23:00 | 29.75 | 65 | 99450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 | 28.85 | 66.5 | 99415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 01:00 | 28.05 | 66 | 99385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 02:00 | 27.35 | 61 | 99375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 03:00 | 26.75 | 53.5 | 99380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 04:00 | 27.05 | 44.5 | 99385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 05:00 | 27.7 | 35 | 99405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 06:00 | 29.3 | 24.5 | 99465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 07:00 | 33.2 | 15 | 99540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 08:00 | 37.25 | 11 | 99605 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 09:00 | 40.3 | 15.5 | 99635 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 10:00 | 42.85 | 18 | 99620 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 11:00 | 44.6 | 15 | 99590 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 12:00 | 45.15 | 14 | 99550 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 13:00 | 44.05 | 15.5 | 99510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 14:00 | 42.4 | 19 | 99480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 15:00 | 40.85 | 23.5 | 99475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 16:00 | 38.85 | 30.5 | 99470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 17:00 | 36.75 | 41 | 99470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 18:00 | 34.75 | 53 | 99500 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 19:00 | 33.2 | 62.5 | 99545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 20:00 | 32.1 | 68.5 | 99610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 21:00 | 31.1 | 74 | 99685 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 22:00 | 30.2 | 79 | 99720 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-25 23:00 | 29.35 | 83 | 99710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-26 | 28.55 | 85.5 | 99670 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-26 01:00 | 27.9 | 85.5 | 99630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-26 02:00 | 27.4 | 82.5 | 99630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-26 03:00 | 27.05 | 77.5 | 99650 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-26 04:00 | 27.35 | 77.5 | 99660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-26 05:00 | 28 | 78.5 | 99680 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-26 06:00 | 29.1 | 72 | 99745 | 100 | 3000 | 22.1449 | 79.1903 | 72.4439 | 0 | 7.2692 | FALSE | FALSE
2025-05-26 07:00 | 31.5 | 61.5 | 99820 | 100 | 3000 | 23.0568 | 73.804 | 73.3653 | 0 | 7.2692 | FALSE | FALSE
2025-05-26 08:00 | 34.25 | 52 | 99880 | 100 | 3000 | 24.073 | 68.6465 | 74.977 | 0 | 7.2692 | FALSE | FALSE
2025-05-26 09:00 | 36.7 | 44.5 | 99915 | 100 | 3000 | 24.9573 | 64.1431 | 75.81 | 0 | 7.2692 | FALSE | FALSE
2025-05-26 10:00 | 39.35 | 34.5 | 99900 | 100 | 3000 | 25.9208 | 56.7572 | 71.8893 | 0 | 7.2692 | FALSE | FALSE
2025-05-26 11:00 | 42.1 | 22.5 | 99855 | 100 | 3000 | 26.9492 | 46.1812 | 61.6437 | 0 | 7.2692 | FALSE | FALSE
2025-05-26 12:00 | 43.7 | 16 | 99795 | 100 | 3000 | 27.5554 | 39.756 | 54.34 | 0 | 7.2692 | FALSE | FALSE
2025-05-26 13:00 | 43.8 | 14 | 99735 | 100 | 3000 | 27.6174 | 37.6505 | 50.8181 | 0 | 7.2692 | FALSE | FALSE
2025-05-26 14:00 | 43.6 | 12.5 | 99680 | 100 | 3000 | 27.5741 | 36.0669 | 48.4243 | 0 | 7.2692 | FALSE | FALSE
2025-05-26 15:00 | 43.35 | 12 | 99635 | 100 | 3000 | 27.499 | 35.5507 | 48.2059 | 0 | 7.2692 | FALSE | FALSE
2025-05-26 16:00 | 42.35 | 13.5 | 99615 | 100 | 3000 | 27.147 | 37.117 | 47.1572 | 0 | 7.2692 | FALSE | FALSE
2025-05-26 17:00 | 39.85 | 22.5 | 99610 | 100 | 3000 | 26.2067 | 45.7059 | 55.0625 | 0 | 7.2692 | FALSE | FALSE
2025-05-26 18:00 | 36.55 | 39 | 99635 | 100 | 3000 | 24.947 | 59.3717 | 67.9047 | 0 | 7.2692 | FALSE | FALSE
2025-05-26 19:00 | 34.55 | 47 | 99695 | 100 | 3000 | 24.2058 | 64.8693 | 70.2442 | 0 | 7.2692 | FALSE | FALSE
2025-05-26 20:00 | 33.8 | 47 | 99765 | 100 | 3000 | 23.943 | 64.4173 | 67.2617 | 0 | 7.2692 | FALSE | FALSE
2025-05-26 21:00 | 33.3 | 48 | 99820 | 100 | 3000 | 23.7608 | 64.9032 | 66.4285 | 0 | 7.2692 | FALSE | FALSE
2025-05-26 22:00 | 32.95 | 47 | 99840 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-26 23:00 | 32.45 | 47.5 | 99825 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-27 | 31.65 | 50.5 | 99790 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-27 01:00 | 31 | 51.5 | 99755 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-27 02:00 | 30.6 | 50.5 | 99735 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-27 03:00 | 30.2 | 49 | 99730 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-27 04:00 | 29.95 | 46.5 | 99730 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-27 05:00 | 29.9 | 45.5 | 99740 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-27 06:00 | 31.05 | 44.5 | 99775 | 100 | 3000 | 22.9583 | 61.2205 | 53.9756 | 0 | 7.2692 | FALSE | FALSE
2025-05-27 07:00 | 33.15 | 41 | 99820 | 100 | 3000 | 23.7417 | 59.4336 | 57.9012 | 0 | 7.2692 | FALSE | FALSE
2025-05-27 08:00 | 34.9 | 35.5 | 99860 | 100 | 3000 | 24.3968 | 55.736 | 57.5829 | 0 | 7.2692 | FALSE | FALSE
2025-05-27 09:00 | 36.05 | 31 | 99870 | 100 | 3000 | 24.8307 | 52.3734 | 55.6983 | 0 | 7.2692 | FALSE | FALSE
2025-05-27 10:00 | 36.7 | 29.5 | 99845 | 100 | 3000 | 25.0683 | 51.277 | 55.7846 | 0 | 7.2692 | FALSE | FALSE
2025-05-27 11:00 | 37.1 | 29.5 | 99810 | 100 | 3000 | 25.207 | 51.3887 | 57.052 | 0 | 7.2692 | FALSE | FALSE
2025-05-27 12:00 | 37.2 | 31 | 99760 | 100 | 3000 | 25.2299 | 52.7281 | 59.427 | 0 | 7.2692 | FALSE | FALSE
2025-05-27 13:00 | 37.1 | 34 | 99700 | 100 | 3000 | 25.1724 | 55.3075 | 63.1845 | 0 | 7.2692 | FALSE | FALSE
2025-05-27 14:00 | 36.8 | 36.5 | 99655 | 100 | 3000 | 25.0509 | 57.3459 | 65.4959 | 0 | 7.2692 | FALSE | FALSE
2025-05-27 15:00 | 36.15 | 39 | 99620 | 100 | 3000 | 24.8101 | 59.1742 | 66.4202 | 0 | 7.2692 | FALSE | FALSE
2025-05-27 16:00 | 35.35 | 41.5 | 99605 | 100 | 3000 | 24.5172 | 60.8578 | 66.6125 | 0 | 7.2692 | FALSE | FALSE
2025-05-27 17:00 | 34.5 | 44 | 99610 | 100 | 3000 | 24.2057 | 62.4413 | 66.4272 | 0 | 7.2692 | FALSE | FALSE
2025-05-27 18:00 | 33.25 | 49.5 | 99620 | 100 | 3000 | 23.7354 | 66.0491 | 67.8786 | 0 | 7.2692 | FALSE | FALSE
2025-05-27 19:00 | 31.8 | 58 | 99635 | 100 | 3000 | 23.1788 | 71.4843 | 71.0182 | 0 | 7.2692 | FALSE | FALSE
2025-05-27 20:00 | 30.75 | 67 | 99670 | 100 | 3000 | 22.7652 | 77.1592 | 75.4471 | 0 | 7.2692 | FALSE | FALSE
2025-05-27 21:00 | 30.05 | 73 | 99725 | 100 | 3000 | 22.4905 | 80.7384 | 77.9459 | 0 | 7.2692 | FALSE | FALSE
2025-05-27 22:00 | 29.35 | 74.5 | 99755 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-27 23:00 | 28.4 | 74 | 99745 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-28 | 27.65 | 71.5 | 99705 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-28 01:00 | 27.25 | 67 | 99660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-28 02:00 | 26.75 | 64 | 99640 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-28 03:00 | 26.2 | 63.5 | 99650 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-28 04:00 | 26.4 | 62 | 99645 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-28 05:00 | 26.9 | 60 | 99655 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-28 06:00 | 27.7 | 58 | 99710 | 100 | 3000 | 21.6522 | 68.9829 | 53.7325 | 0 | 7.2692 | FALSE | FALSE
2025-05-28 07:00 | 29.8 | 52 | 99775 | 100 | 3000 | 22.4663 | 65.9804 | 56.6776 | 0 | 7.2692 | FALSE | FALSE
2025-05-28 08:00 | 32.6 | 44 | 99820 | 100 | 3000 | 23.5288 | 61.4893 | 59.232 | 0 | 7.2692 | FALSE | FALSE
2025-05-28 09:00 | 35.35 | 36.5 | 99820 | 100 | 3000 | 24.5491 | 56.7225 | 60.3889 | 0 | 7.2692 | FALSE | FALSE
2025-05-28 10:00 | 37.5 | 30.5 | 99795 | 100 | 3000 | 25.3368 | 52.3841 | 59.7281 | 0 | 7.2692 | FALSE | FALSE
2025-05-28 11:00 | 38.9 | 28 | 99770 | 100 | 3000 | 25.8336 | 50.5794 | 60.6347 | 0 | 7.2692 | FALSE | FALSE
2025-05-28 12:00 | 39.35 | 30.5 | 99740 | 100 | 3000 | 25.9599 | 53.0485 | 65.8378 | 0 | 7.2692 | FALSE | FALSE
2025-05-28 13:00 | 39.1 | 34 | 99685 | 100 | 3000 | 25.8435 | 56.1878 | 70.1888 | 0 | 7.2692 | FALSE | FALSE
2025-05-28 14:00 | 38.4 | 36.5 | 99620 | 100 | 3000 | 25.5891 | 58.1265 | 71.2857 | 0 | 7.2692 | FALSE | FALSE
2025-05-28 15:00 | 37.4 | 41 | 99580 | 100 | 3000 | 25.2184 | 61.5761 | 73.794 | 0 | 7.2692 | FALSE | FALSE
2025-05-28 16:00 | 36.15 | 44 | 99585 | 100 | 3000 | 24.775 | 63.3955 | 72.8762 | 0 | 7.2692 | FALSE | FALSE
2025-05-28 17:00 | 34.55 | 49 | 99600 | 100 | 3000 | 24.194 | 66.483 | 72.6132 | 0 | 7.2692 | FALSE | FALSE
2025-05-28 18:00 | 32.65 | 62 | 99610 | 100 | 3000 | 23.463 | 75.146 | 79.0841 | 0 | 7.2692 | FALSE | FALSE
2025-05-28 19:00 | 31.2 | 73.5 | 99635 | 100 | 3000 | 22.9018 | 82.2428 | 84.0877 | 0 | 7.2692 | FALSE | FALSE
2025-05-28 20:00 | 30.5 | 77.5 | 99655 | 100 | 3000 | 22.6373 | 84.3493 | 84.4959 | 0 | 7.2692 | FALSE | FALSE
2025-05-28 21:00 | 29.85 | 79 | 99685 | 100 | 3000 | 22.3981 | 84.6958 | 82.6181 | 0 | 7.2692 | FALSE | FALSE
2025-05-28 22:00 | 29.15 | 81.5 | 99715 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-28 23:00 | 28.4 | 84 | 99695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-29 | 27.7 | 85.5 | 99660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-29 01:00 | 26.95 | 87.5 | 99635 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-29 02:00 | 26.2 | 91 | 99615 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-29 03:00 | 25.65 | 93 | 99615 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-29 04:00 | 25.9 | 89.5 | 99630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-29 05:00 | 26.3 | 84.5 | 99660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-29 06:00 | 27.1 | 78 | 99700 | 100 | 3000 | 21.3781 | 81.4 | 68.1144 | 0 | 7.2692 | FALSE | FALSE
2025-05-29 07:00 | 29.9 | 63.5 | 99750 | 100 | 3000 | 22.4667 | 74.0146 | 68.1667 | 0 | 7.2692 | FALSE | FALSE
2025-05-29 08:00 | 33.6 | 45.5 | 99790 | 100 | 3000 | 23.8801 | 63.1314 | 64.7454 | 0 | 7.2692 | FALSE | FALSE
2025-05-29 09:00 | 36.75 | 32 | 99800 | 100 | 3000 | 25.0672 | 53.4432 | 59.311 | 0 | 7.2692 | FALSE | FALSE
2025-05-29 10:00 | 39.4 | 23 | 99785 | 100 | 3000 | 26.0498 | 46.0787 | 54.5995 | 0 | 7.2692 | FALSE | FALSE
2025-05-29 11:00 | 41.4 | 19.5 | 99735 | 100 | 3000 | 26.757 | 43.0536 | 54.5409 | 0 | 7.2692 | FALSE | FALSE
2025-05-29 12:00 | 42.35 | 20.5 | 99655 | 100 | 3000 | 27.0561 | 44.2265 | 58.8331 | 0 | 7.2692 | FALSE | FALSE
2025-05-29 13:00 | 42.7 | 20.5 | 99575 | 100 | 3000 | 27.1693 | 44.305 | 59.785 | 0 | 7.2692 | FALSE | FALSE
2025-05-29 14:00 | 42.05 | 21.5 | 99525 | 100 | 3000 | 26.9458 | 45.1848 | 59.675 | 0 | 7.2692 | FALSE | FALSE
2025-05-29 15:00 | 40.15 | 25.5 | 99500 | 100 | 3000 | 26.2758 | 48.6285 | 60.6271 | 0 | 7.2692 | FALSE | FALSE
2025-05-29 16:00 | 37.8 | 33.5 | 99485 | 100 | 3000 | 25.4142 | 55.1702 | 64.854 | 0 | 7.2692 | FALSE | FALSE
2025-05-29 17:00 | 35.2 | 46.5 | 99475 | 100 | 3000 | 24.4335 | 64.8886 | 72.1996 | 0 | 7.2692 | FALSE | FALSE
2025-05-29 18:00 | 32.9 | 58.5 | 99485 | 100 | 3000 | 23.5674 | 72.7116 | 76.3767 | 0 | 7.2692 | FALSE | FALSE
2025-05-29 19:00 | 31.6 | 68 | 99535 | 100 | 3000 | 23.0658 | 78.659 | 80.4506 | 0 | 7.2692 | FALSE | FALSE
2025-05-29 20:00 | 31.1 | 72.5 | 99600 | 100 | 3000 | 22.8701 | 81.4246 | 82.5843 | 0 | 7.2692 | FALSE | FALSE
2025-05-29 21:00 | 30.65 | 72 | 99655 | 100 | 3000 | 22.7109 | 80.6182 | 79.8913 | 0 | 7.2692 | FALSE | FALSE
2025-05-29 22:00 | 29.85 | 73.5 | 99665 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-29 23:00 | 29.1 | 74 | 99625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-30 | 28.55 | 73 | 99575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-30 01:00 | 28 | 74 | 99540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-30 02:00 | 27.3 | 76 | 99530 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-30 03:00 | 26.6 | 77.5 | 99545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-30 04:00 | 26.55 | 72 | 99555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-30 05:00 | 26.8 | 63 | 99565 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-30 06:00 | 27.95 | 53 | 99615 | 100 | 3000 | 21.7602 | 65.8473 | 50.3117 | 0 | 7.2692 | FALSE | FALSE
2025-05-30 07:00 | 31.4 | 38.5 | 99690 | 100 | 3000 | 23.1113 | 56.9892 | 48.9408 | 0 | 7.2692 | FALSE | FALSE
2025-05-30 08:00 | 35.75 | 25 | 99740 | 100 | 3000 | 24.7648 | 47.2976 | 46.8882 | 0 | 7.2692 | FALSE | FALSE
2025-05-30 09:00 | 39.5 | 15.5 | 99745 | 100 | 3000 | 26.157 | 39.0978 | 44.3167 | 0 | 7.2692 | FALSE | FALSE
2025-05-30 10:00 | 41.75 | 12.5 | 99735 | 100 | 3000 | 26.958 | 36.1211 | 46.6996 | 0 | 7.2692 | FALSE | FALSE
2025-05-30 11:00 | 42.35 | 16 | 99710 | 100 | 3000 | 27.1145 | 39.6489 | 50.963 | 0 | 7.2692 | FALSE | FALSE
2025-05-30 12:00 | 42.05 | 21.5 | 99655 | 100 | 3000 | 26.9458 | 45.1751 | 59.7171 | 0 | 7.2692 | FALSE | FALSE
2025-05-30 13:00 | 41.35 | 22.5 | 99595 | 100 | 3000 | 26.705 | 46.018 | 59.3757 | 0 | 7.2692 | FALSE | FALSE
2025-05-30 14:00 | 40.45 | 22.5 | 99550 | 100 | 3000 | 26.4076 | 45.8262 | 56.7634 | 0 | 7.2692 | FALSE | FALSE
2025-05-30 15:00 | 39.4 | 27 | 99525 | 100 | 3000 | 26.0108 | 49.8243 | 60.6349 | 0 | 7.2692 | FALSE | FALSE
2025-05-30 16:00 | 37.55 | 37 | 99530 | 100 | 3000 | 25.3011 | 58.1474 | 68.8554 | 0 | 7.2692 | FALSE | FALSE
2025-05-30 17:00 | 35.7 | 44.5 | 99540 | 100 | 3000 | 24.6181 | 63.5425 | 71.72 | 0 | 7.2692 | FALSE | FALSE
2025-05-30 18:00 | 34.55 | 48.5 | 99555 | 100 | 3000 | 24.1969 | 66.0857 | 72.0048 | 0 | 7.2692 | FALSE | FALSE
2025-05-30 19:00 | 33.3 | 55.5 | 99590 | 100 | 3000 | 23.7228 | 70.7131 | 74.8352 | 0 | 7.2692 | FALSE | FALSE
2025-05-30 20:00 | 32.3 | 58.5 | 99640 | 100 | 3000 | 23.3554 | 72.2275 | 73.7454 | 0 | 7.2692 | FALSE | FALSE
2025-05-30 21:00 | 31.4 | 60 | 99690 | 100 | 3000 | 23.0267 | 72.6477 | 71.3483 | 0 | 7.2692 | FALSE | FALSE
2025-05-30 22:00 | 30.45 | 65.5 | 99695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-30 23:00 | 29.75 | 70.5 | 99660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-31 | 29.45 | 71.5 | 99625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-31 01:00 | 29.3 | 70 | 99595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-31 02:00 | 29.15 | 68 | 99585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-31 03:00 | 28.5 | 67.5 | 99610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-31 04:00 | 27.8 | 70 | 99645 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-31 05:00 | 27.65 | 71.5 | 99675 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-31 06:00 | 28.7 | 65.5 | 99720 | 100 | 3000 | 22.0139 | 74.515 | 64.6738 | 0 | 7.2692 | FALSE | FALSE
2025-05-31 07:00 | 31.55 | 54.5 | 99785 | 100 | 3000 | 23.103 | 68.7334 | 66.3224 | 0 | 7.2692 | FALSE | FALSE
2025-05-31 08:00 | 34.8 | 44.5 | 99840 | 100 | 3000 | 24.3077 | 62.989 | 68.2544 | 0 | 7.2692 | FALSE | FALSE
2025-05-31 09:00 | 37.25 | 37 | 99860 | 100 | 3000 | 25.2001 | 57.9727 | 67.8533 | 0 | 7.2692 | FALSE | FALSE
2025-05-31 10:00 | 38.5 | 33 | 99860 | 100 | 3000 | 25.6539 | 54.9858 | 66.6706 | 0 | 7.2692 | FALSE | FALSE
2025-05-31 11:00 | 38.65 | 32.5 | 99855 | 100 | 3000 | 25.7084 | 54.5955 | 66.4604 | 0 | 7.2692 | FALSE | FALSE
2025-05-31 12:00 | 38.5 | 33 | 99835 | 100 | 3000 | 25.6539 | 54.9878 | 66.6634 | 0 | 7.2692 | FALSE | FALSE
2025-05-31 13:00 | 38.35 | 34 | 99805 | 100 | 3000 | 25.5948 | 55.8289 | 67.5735 | 0 | 7.2692 | FALSE | FALSE
2025-05-31 14:00 | 38.1 | 34 | 99775 | 100 | 3000 | 25.5111 | 55.7202 | 66.6872 | 0 | 7.2692 | FALSE | FALSE
2025-05-31 15:00 | 37.55 | 34.5 | 99755 | 100 | 3000 | 25.3215 | 55.9268 | 65.4553 | 0 | 7.2692 | FALSE | FALSE
2025-05-31 16:00 | 36.65 | 38 | 99745 | 100 | 3000 | 24.9885 | 58.5564 | 66.9783 | 0 | 7.2692 | FALSE | FALSE
2025-05-31 17:00 | 35.3 | 44.5 | 99750 | 100 | 3000 | 24.4809 | 63.285 | 70.1941 | 0 | 7.2692 | FALSE | FALSE
2025-05-31 18:00 | 33.5 | 53 | 99795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-31 19:00 | 32.15 | 58.5 | 99855 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-31 20:00 | 31.35 | 60 | 99905 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-31 21:00 | 30.6 | 60.5 | 99960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-31 22:00 | 29.85 | 61.5 | 99980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-05-31 23:00 | 29.15 | 62.5 | 99955 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 | 28.35 | 66 | 99925 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 01:00 | 27.55 | 71 | 99905 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 02:00 | 26.85 | 74 | 99910 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 03:00 | 26.25 | 75.5 | 99935 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 04:00 | 26.1 | 76 | 99950 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 05:00 | 26 | 77 | 99960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 06:00 | 26.45 | 74.5 | 99990 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 07:00 | 28.35 | 65 | 100035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 08:00 | 30.6 | 53.5 | 100070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 09:00 | 32.6 | 44.5 | 100085 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 10:00 | 34.6 | 37.5 | 100080 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 11:00 | 36.75 | 30 | 100035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 12:00 | 39.1 | 22.5 | 99960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 13:00 | 40.45 | 19.5 | 99885 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 14:00 | 39.3 | 29 | 99815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 15:00 | 37.35 | 37.5 | 99765 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 16:00 | 36.4 | 38.5 | 99755 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 17:00 | 35 | 45 | 99765 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 18:00 | 33 | 54 | 99770 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 19:00 | 31.7 | 62 | 99785 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 20:00 | 31 | 69 | 99830 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 21:00 | 30.45 | 73 | 99875 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 22:00 | 29.85 | 74.5 | 99885 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-01 23:00 | 28.95 | 77.5 | 99865 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-02 | 28 | 81.5 | 99835 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-02 01:00 | 27.3 | 82.5 | 99810 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-02 02:00 | 26.65 | 80.5 | 99800 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-02 03:00 | 26.35 | 74.5 | 99795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-02 04:00 | 26.55 | 69.5 | 99785 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-02 05:00 | 26.85 | 64 | 99795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-02 06:00 | 28.35 | 51.5 | 99835 | 100 | 3000 | 21.9177 | 64.9985 | 50.5527 | 0 | 7.2692 | FALSE | FALSE
2025-06-02 07:00 | 31.65 | 37.5 | 99875 | 100 | 3000 | 23.2081 | 56.3049 | 48.7706 | 0 | 7.2692 | FALSE | FALSE
2025-06-02 08:00 | 35.35 | 27 | 99890 | 100 | 3000 | 24.609 | 48.8903 | 48.3364 | 0 | 7.2692 | FALSE | FALSE
2025-06-02 09:00 | 38.5 | 20 | 99875 | 100 | 3000 | 25.7694 | 43.2011 | 47.6022 | 0 | 7.2692 | FALSE | FALSE
2025-06-02 10:00 | 41 | 15 | 99845 | 100 | 3000 | 26.6751 | 38.5979 | 46.0222 | 0 | 7.2692 | FALSE | FALSE
2025-06-02 11:00 | 41.1 | 23.5 | 99820 | 100 | 3000 | 26.6112 | 46.9243 | 60.3689 | 0 | 7.2692 | FALSE | FALSE
2025-06-02 12:00 | 39.1 | 37.5 | 99775 | 100 | 3000 | 25.8099 | 59.4128 | 75.3798 | 0 | 7.2692 | FALSE | FALSE
2025-06-02 13:00 | 38.3 | 38 | 99710 | 100 | 3000 | 25.5428 | 59.4191 | 73.0814 | 0 | 7.2692 | FALSE | FALSE
2025-06-02 14:00 | 38.75 | 31.5 | 99650 | 100 | 3000 | 25.7509 | 53.7408 | 65.2791 | 0 | 7.2692 | FALSE | FALSE
2025-06-02 15:00 | 38.7 | 29 | 99590 | 100 | 3000 | 25.7571 | 51.4454 | 61.4216 | 0 | 7.2692 | FALSE | FALSE
2025-06-02 16:00 | 37.7 | 34 | 99570 | 100 | 3000 | 25.3763 | 55.5645 | 65.2316 | 0 | 7.2692 | FALSE | FALSE
2025-06-02 17:00 | 35.95 | 42.5 | 99580 | 100 | 3000 | 24.7173 | 62.0158 | 70.1665 | 0 | 7.2692 | FALSE | FALSE
2025-06-02 18:00 | 33.7 | 52 | 99585 | 100 | 3000 | 23.8811 | 68.2847 | 72.578 | 0 | 7.2692 | FALSE | FALSE
2025-06-02 19:00 | 31.95 | 61.5 | 99600 | 100 | 3000 | 23.2177 | 74.1847 | 75.3505 | 0 | 7.2692 | FALSE | FALSE
2025-06-02 20:00 | 31.05 | 67 | 99610 | 100 | 3000 | 22.8733 | 77.4267 | 76.842 | 0 | 7.2692 | FALSE | FALSE
2025-06-02 21:00 | 30.1 | 71.5 | 99640 | 100 | 3000 | 22.5136 | 79.7497 | 76.7379 | 0 | 7.2692 | FALSE | FALSE
2025-06-02 22:00 | 29.15 | 75.5 | 99645 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-02 23:00 | 28.35 | 76 | 99595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-03 | 27.5 | 78 | 99565 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-03 01:00 | 26.85 | 81.5 | 99545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-03 02:00 | 26.3 | 84.5 | 99530 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-03 03:00 | 25.8 | 87.5 | 99540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-03 04:00 | 25.5 | 89.5 | 99565 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-03 05:00 | 25.4 | 89.5 | 99600 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-03 06:00 | 26.45 | 83.5 | 99655 | 100 | 3000 | 21.1184 | 84.2771 | 69.435 | 0 | 7.2692 | FALSE | FALSE
2025-06-03 07:00 | 29.05 | 71.5 | 99700 | 100 | 3000 | 22.1278 | 78.8145 | 71.7411 | 0 | 7.2692 | FALSE | FALSE
2025-06-03 08:00 | 31.95 | 59 | 99710 | 100 | 3000 | 23.2284 | 72.3263 | 72.7442 | 0 | 7.2692 | FALSE | FALSE
2025-06-03 09:00 | 34.65 | 46.5 | 99700 | 100 | 3000 | 24.2435 | 64.5279 | 70.0461 | 0 | 7.2692 | FALSE | FALSE
2025-06-03 10:00 | 37.3 | 35.5 | 99675 | 100 | 3000 | 25.2288 | 56.7012 | 65.9302 | 0 | 7.2692 | FALSE | FALSE
2025-06-03 11:00 | 39.5 | 28.5 | 99640 | 100 | 3000 | 26.0294 | 51.2466 | 63.2709 | 0 | 7.2692 | FALSE | FALSE
2025-06-03 12:00 | 40.35 | 28.5 | 99585 | 100 | 3000 | 26.3095 | 51.5545 | 66.013 | 0 | 7.2692 | FALSE | FALSE
2025-06-03 13:00 | 39.3 | 37 | 99520 | 100 | 3000 | 25.8796 | 59.086 | 75.3157 | 0 | 7.2692 | FALSE | FALSE
2025-06-03 14:00 | 38.15 | 39.5 | 99470 | 100 | 3000 | 25.4798 | 60.7016 | 74.5684 | 0 | 7.2692 | FALSE | FALSE
2025-06-03 15:00 | 37.4 | 38 | 99440 | 100 | 3000 | 25.2425 | 58.9576 | 69.6555 | 0 | 7.2692 | FALSE | FALSE
2025-06-03 16:00 | 35.8 | 46.5 | 99440 | 100 | 3000 | 24.6387 | 65.281 | 74.6212 | 0 | 7.2692 | FALSE | FALSE
2025-06-03 17:00 | 33.9 | 58.5 | 99455 | 100 | 3000 | 23.9154 | 73.5444 | 80.8702 | 0 | 7.2692 | FALSE | FALSE
2025-06-03 18:00 | 32.2 | 69.5 | 99490 | 100 | 3000 | 23.2708 | 80.3547 | 84.9046 | 0 | 7.2692 | FALSE | FALSE
2025-06-03 19:00 | 30.95 | 77.5 | 99545 | 100 | 3000 | 22.7975 | 84.8519 | 86.775 | 0 | 7.2692 | FALSE | FALSE
2025-06-03 20:00 | 30.25 | 81.5 | 99610 | 100 | 3000 | 22.5336 | 86.8801 | 87.0324 | 0 | 7.2692 | FALSE | FALSE
2025-06-03 21:00 | 29.75 | 83.5 | 99660 | 100 | 3000 | 22.3474 | 87.6852 | 86.2984 | 0 | 7.2692 | FALSE | FALSE
2025-06-03 22:00 | 29.2 | 85.5 | 99660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-03 23:00 | 28.6 | 87.5 | 99635 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-04 | 28.15 | 87 | 99610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-04 01:00 | 27.8 | 85 | 99595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-04 02:00 | 27.35 | 83 | 99595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-04 03:00 | 26.8 | 82 | 99600 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-04 04:00 | 26.6 | 81.5 | 99590 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-04 05:00 | 26.6 | 81 | 99615 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-04 06:00 | 27.15 | 77.5 | 99675 | 100 | 3000 | 21.3982 | 81.1279 | 67.9337 | 0 | 7.2692 | FALSE | FALSE
2025-06-04 07:00 | 29.15 | 67.5 | 99725 | 100 | 3000 | 22.1765 | 76.1914 | 68.5353 | 0 | 7.2692 | FALSE | FALSE
2025-06-04 08:00 | 31.75 | 56 | 99755 | 100 | 3000 | 23.1692 | 69.9667 | 68.7304 | 0 | 7.2692 | FALSE | FALSE
2025-06-04 09:00 | 34.1 | 47 | 99750 | 100 | 3000 | 24.0486 | 64.5936 | 68.4539 | 0 | 7.2692 | FALSE | FALSE
2025-06-04 10:00 | 36 | 40 | 99725 | 100 | 3000 | 24.7517 | 59.9325 | 67.184 | 0 | 7.2692 | FALSE | FALSE
2025-06-04 11:00 | 37.15 | 35.5 | 99690 | 100 | 3000 | 25.1778 | 56.6335 | 65.4018 | 0 | 7.2692 | FALSE | FALSE
2025-06-04 12:00 | 37.5 | 34.5 | 99655 | 100 | 3000 | 25.3046 | 55.9135 | 65.2522 | 0 | 7.2692 | FALSE | FALSE
2025-06-04 13:00 | 37.1 | 36.5 | 99620 | 100 | 3000 | 25.153 | 57.4862 | 66.5642 | 0 | 7.2692 | FALSE | FALSE
2025-06-04 14:00 | 36.3 | 40 | 99585 | 100 | 3000 | 24.8544 | 60.0985 | 68.271 | 0 | 7.2692 | FALSE | FALSE
2025-06-04 15:00 | 35.45 | 42.5 | 99565 | 100 | 3000 | 24.5454 | 61.7387 | 68.2355 | 0 | 7.2692 | FALSE | FALSE
2025-06-04 16:00 | 34.4 | 45.5 | 99575 | 100 | 3000 | 24.1621 | 63.5898 | 67.8246 | 0 | 7.2692 | FALSE | FALSE
2025-06-04 17:00 | 33 | 53 | 99605 | 100 | 3000 | 23.6295 | 68.5773 | 70.7617 | 0 | 7.2692 | FALSE | FALSE
2025-06-04 18:00 | 31.5 | 62.5 | 99655 | 100 | 3000 | 23.0526 | 74.5482 | 74.36 | 0 | 7.2692 | FALSE | FALSE
2025-06-04 19:00 | 30.45 | 69 | 99725 | 100 | 3000 | 22.6494 | 78.3069 | 76.0108 | 0 | 7.2692 | FALSE | FALSE
2025-06-04 20:00 | 29.8 | 71 | 99785 | 100 | 3000 | 22.4059 | 79.1177 | 74.8526 | 0 | 7.2692 | FALSE | FALSE
2025-06-04 21:00 | 29.25 | 71 | 99830 | 100 | 3000 | 22.2034 | 78.6341 | 72.2503 | 0 | 7.2692 | FALSE | FALSE
2025-06-04 22:00 | 28.65 | 72 | 99850 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-04 23:00 | 27.95 | 74.5 | 99840 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-05 | 27.3 | 77 | 99810 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-05 01:00 | 26.7 | 79 | 99775 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-05 02:00 | 26.15 | 80.5 | 99760 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-05 03:00 | 25.65 | 81.5 | 99775 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-05 04:00 | 25.5 | 79 | 99795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-05 05:00 | 25.45 | 75.5 | 99835 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-05 06:00 | 26.05 | 70.5 | 99895 | 100 | 3000 | 20.9874 | 75.9192 | 57.1652 | 0 | 7.2692 | FALSE | FALSE
2025-06-05 07:00 | 28.2 | 60 | 99945 | 100 | 3000 | 21.839 | 70.5301 | 57.6047 | 0 | 7.2692 | FALSE | FALSE
2025-06-05 08:00 | 30.85 | 50 | 99985 | 100 | 3000 | 22.864 | 65.0654 | 58.8867 | 0 | 7.2692 | FALSE | FALSE
2025-06-05 09:00 | 33.3 | 42.5 | 100000 | 100 | 3000 | 23.7883 | 60.6379 | 60.2065 | 0 | 7.2692 | FALSE | FALSE
2025-06-05 10:00 | 35.55 | 36 | 99985 | 100 | 3000 | 24.6224 | 56.373 | 60.4996 | 0 | 7.2692 | FALSE | FALSE
2025-06-05 11:00 | 37.3 | 30.5 | 99955 | 100 | 3000 | 25.2682 | 52.3077 | 59.1181 | 0 | 7.2692 | FALSE | FALSE
2025-06-05 12:00 | 38.15 | 28.5 | 99925 | 100 | 3000 | 25.5753 | 50.7966 | 59.0269 | 0 | 7.2692 | FALSE | FALSE
2025-06-05 13:00 | 37.95 | 31.5 | 99870 | 100 | 3000 | 25.4819 | 53.418 | 62.6477 | 0 | 7.2692 | FALSE | FALSE
2025-06-05 14:00 | 37.1 | 37 | 99820 | 100 | 3000 | 25.1493 | 57.9039 | 67.2972 | 0 | 7.2692 | FALSE | FALSE
2025-06-05 15:00 | 35.95 | 41.5 | 99815 | 100 | 3000 | 24.7243 | 61.1572 | 68.9466 | 0 | 7.2692 | FALSE | FALSE
2025-06-05 16:00 | 34.6 | 48 | 99840 | 100 | 3000 | 24.2174 | 65.6912 | 71.6807 | 0 | 7.2692 | FALSE | FALSE
2025-06-05 17:00 | 32.9 | 59.5 | 99880 | 100 | 3000 | 23.563 | 73.4368 | 77.5639 | 0 | 7.2692 | FALSE | FALSE
2025-06-05 18:00 | 31.3 | 68.5 | 99930 | 100 | 3000 | 22.9574 | 78.7041 | 79.6067 | 0 | 7.2692 | FALSE | FALSE
2025-06-05 19:00 | 30.3 | 72 | 99990 | 100 | 3000 | 22.5848 | 80.2516 | 78.2544 | 0 | 7.2692 | FALSE | FALSE
2025-06-05 20:00 | 29.7 | 72 | 100055 | 100 | 3000 | 22.3663 | 79.6907 | 75.3685 | 0 | 7.2692 | FALSE | FALSE
2025-06-05 21:00 | 29.2 | 71.5 | 100115 | 100 | 3000 | 22.1837 | 78.9023 | 72.5269 | 0 | 7.2692 | FALSE | FALSE
2025-06-05 22:00 | 28.6 | 71.5 | 100150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-05 23:00 | 28.05 | 70 | 100150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-06 | 27.6 | 67.5 | 100135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-06 01:00 | 27 | 67 | 100105 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-06 02:00 | 26.2 | 69 | 100080 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-06 03:00 | 25.4 | 70 | 100075 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-06 04:00 | 24.95 | 70 | 100075 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-06 05:00 | 24.95 | 68 | 100100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-06 06:00 | 26.15 | 60.5 | 100155 | 100 | 3000 | 21.0442 | 69.787 | 49.5812 | 0 | 7.2692 | FALSE | FALSE
2025-06-06 07:00 | 29 | 48.5 | 100210 | 100 | 3000 | 22.1742 | 63.2025 | 50.3342 | 0 | 7.2692 | FALSE | FALSE
2025-06-06 08:00 | 31.9 | 41 | 100245 | 100 | 3000 | 23.2862 | 58.9294 | 53.479 | 0 | 7.2692 | FALSE | FALSE
2025-06-06 09:00 | 33.65 | 39.5 | 100260 | 100 | 3000 | 23.9292 | 58.4292 | 58.0849 | 0 | 7.2692 | FALSE | FALSE
2025-06-06 10:00 | 34.55 | 38.5 | 100255 | 100 | 3000 | 24.2554 | 57.9944 | 60.1284 | 0 | 7.2692 | FALSE | FALSE
2025-06-06 11:00 | 35.25 | 36 | 100240 | 100 | 3000 | 24.5173 | 56.2376 | 59.5154 | 0 | 7.2692 | FALSE | FALSE
2025-06-06 12:00 | 35.65 | 34 | 100205 | 100 | 3000 | 24.6704 | 54.731 | 58.346 | 0 | 7.2692 | FALSE | FALSE
2025-06-06 13:00 | 35.5 | 34.5 | 100165 | 100 | 3000 | 24.6146 | 55.0976 | 58.4632 | 0 | 7.2692 | FALSE | FALSE
2025-06-06 14:00 | 35.05 | 36.5 | 100130 | 100 | 3000 | 24.4438 | 56.5813 | 59.4132 | 0 | 7.2692 | FALSE | FALSE
2025-06-06 15:00 | 34.35 | 41 | 100110 | 100 | 3000 | 24.1703 | 59.923 | 62.38 | 0 | 7.2692 | FALSE | FALSE
2025-06-06 16:00 | 33.4 | 47 | 100125 | 100 | 3000 | 23.8015 | 64.1589 | 65.7591 | 0 | 7.2692 | FALSE | FALSE
2025-06-06 17:00 | 32.25 | 53.5 | 100145 | 100 | 3000 | 23.3601 | 68.4092 | 68.2754 | 0 | 7.2692 | FALSE | FALSE
2025-06-06 18:00 | 30.9 | 62 | 100170 | 100 | 3000 | 22.8383 | 73.6671 | 71.2516 | 0 | 7.2692 | FALSE | FALSE
2025-06-06 19:00 | 29.85 | 70 | 100215 | 100 | 3000 | 22.4277 | 78.4295 | 74.2251 | 0 | 7.2692 | FALSE | FALSE
2025-06-06 20:00 | 29.2 | 74.5 | 100275 | 100 | 3000 | 22.175 | 80.9176 | 75.3141 | 0 | 7.2692 | FALSE | FALSE
2025-06-06 21:00 | 28.6 | 77.5 | 100335 | 100 | 3000 | 21.9445 | 82.3611 | 75.0973 | 0 | 7.2692 | FALSE | FALSE
2025-06-06 22:00 | 27.95 | 80.5 | 100360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-06 23:00 | 27.25 | 83.5 | 100340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-07 | 26.35 | 86.5 | 100295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-07 01:00 | 25.4 | 90 | 100255 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-07 02:00 | 24.65 | 93.5 | 100230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-07 03:00 | 24.05 | 95.5 | 100235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-07 04:00 | 24 | 95 | 100265 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-07 05:00 | 24.1 | 94 | 100305 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-07 06:00 | 24.8 | 89.5 | 100350 | 100 | 3000 | 20.4684 | 86.3227 | 65.9359 | 0 | 7.2692 | FALSE | FALSE
2025-06-07 07:00 | 26.75 | 79 | 100385 | 100 | 3000 | 21.2426 | 81.6627 | 67.3591 | 0 | 7.2692 | FALSE | FALSE
2025-06-07 08:00 | 29.15 | 65.5 | 100400 | 100 | 3000 | 22.1827 | 74.7719 | 66.8098 | 0 | 7.2692 | FALSE | FALSE
2025-06-07 09:00 | 31.75 | 51.5 | 100390 | 100 | 3000 | 23.1881 | 66.5981 | 64.1304 | 0 | 7.2692 | FALSE | FALSE
2025-06-07 10:00 | 34.1 | 44.5 | 100365 | 100 | 3000 | 24.0627 | 62.5599 | 65.6569 | 0 | 7.2692 | FALSE | FALSE
2025-06-07 11:00 | 35.85 | 41.5 | 100320 | 100 | 3000 | 24.6902 | 61.0599 | 68.6961 | 0 | 7.2692 | FALSE | FALSE
2025-06-07 12:00 | 36.6 | 40.5 | 100255 | 100 | 3000 | 24.9535 | 60.6276 | 70.2388 | 0 | 7.2692 | FALSE | FALSE
2025-06-07 13:00 | 36.05 | 45.5 | 100185 | 100 | 3000 | 24.7311 | 64.5434 | 74.5585 | 0 | 7.2692 | FALSE | FALSE
2025-06-07 14:00 | 35.4 | 49 | 100125 | 100 | 3000 | 24.4867 | 67.0192 | 76.2732 | 0 | 7.2692 | FALSE | FALSE
2025-06-07 15:00 | 35.25 | 52 | 100080 | 100 | 3000 | 24.4163 | 69.3771 | 79.3149 | 0 | 7.2692 | FALSE | FALSE
2025-06-07 16:00 | 34.55 | 55 | 100080 | 100 | 3000 | 24.1593 | 71.2534 | 79.8623 | 0 | 7.2692 | FALSE | FALSE
2025-06-07 17:00 | 33.8 | 56.5 | 100095 | 100 | 3000 | 23.8924 | 71.8341 | 78.2858 | 0 | 7.2692 | FALSE | FALSE
2025-06-07 18:00 | 32.75 | 63.5 | 100120 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-07 19:00 | 31.4 | 72 | 100170 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-07 20:00 | 30.9 | 75 | 100210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-07 21:00 | 30.55 | 77 | 100250 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-07 22:00 | 30 | 81.5 | 100270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-07 23:00 | 29.45 | 85.5 | 100245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 | 29 | 88 | 100205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 01:00 | 28.55 | 90 | 100175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 02:00 | 28.15 | 92 | 100145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 03:00 | 27.65 | 94 | 100140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 04:00 | 27.7 | 94 | 100145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 05:00 | 28.05 | 93.5 | 100165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 06:00 | 28.65 | 90.5 | 100230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 07:00 | 30.4 | 80.5 | 100295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 08:00 | 32.55 | 65 | 100325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 09:00 | 34.65 | 49 | 100320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 10:00 | 36.75 | 38.5 | 100275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 11:00 | 38.5 | 30 | 100220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 12:00 | 38.05 | 37.5 | 100160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 13:00 | 36.25 | 53.5 | 100100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 14:00 | 35.1 | 58 | 100070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 15:00 | 34.55 | 58 | 100045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 16:00 | 33.95 | 58 | 100050 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 17:00 | 33.3 | 60 | 100075 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 18:00 | 32.45 | 64 | 100105 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 19:00 | 31.45 | 68.5 | 100155 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 20:00 | 31.1 | 71 | 100195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 21:00 | 30.7 | 74.5 | 100220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 22:00 | 30.15 | 77.5 | 100230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-08 23:00 | 29.65 | 79 | 100220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-09 | 29.2 | 81 | 100180 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-09 01:00 | 28.8 | 83 | 100140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-09 02:00 | 28.3 | 85 | 100135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-09 03:00 | 27.8 | 87 | 100140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-09 04:00 | 27.95 | 86.5 | 100145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-09 05:00 | 28.2 | 85.5 | 100170 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-09 06:00 | 28.9 | 80.5 | 100235 | 100 | 3000 | 22.0472 | 84.667 | 79.2669 | 0 | 7.2692 | FALSE | FALSE
2025-06-09 07:00 | 31.35 | 63.5 | 100300 | 100 | 3000 | 22.9953 | 75.092 | 74.8362 | 0 | 7.2692 | FALSE | FALSE
2025-06-09 08:00 | 34 | 46 | 100340 | 100 | 3000 | 24.0192 | 63.6932 | 67.0241 | 0 | 7.2692 | FALSE | FALSE
2025-06-09 09:00 | 35.95 | 37.5 | 100355 | 100 | 3000 | 24.7517 | 57.7573 | 63.9399 | 0 | 7.2692 | FALSE | FALSE
2025-06-09 10:00 | 37.95 | 32 | 100330 | 100 | 3000 | 25.4778 | 53.8265 | 63.4869 | 0 | 7.2692 | FALSE | FALSE
2025-06-09 11:00 | 39.85 | 26 | 100280 | 100 | 3000 | 26.1709 | 48.958 | 60.723 | 0 | 7.2692 | FALSE | FALSE
2025-06-09 12:00 | 41.05 | 21.5 | 100200 | 100 | 3000 | 26.6177 | 44.9264 | 57.05 | 0 | 7.2692 | FALSE | FALSE
2025-06-09 13:00 | 40.9 | 24.5 | 100110 | 100 | 3000 | 26.5341 | 47.8265 | 61.4969 | 0 | 7.2692 | FALSE | FALSE
2025-06-09 14:00 | 39.1 | 34 | 100045 | 100 | 3000 | 25.8437 | 56.1587 | 70.2947 | 0 | 7.2692 | FALSE | FALSE
2025-06-09 15:00 | 38.25 | 36 | 100000 | 100 | 3000 | 25.544 | 57.5677 | 70.133 | 0 | 7.2692 | FALSE | FALSE
2025-06-09 16:00 | 38.55 | 33.5 | 99980 | 100 | 3000 | 25.6661 | 55.4515 | 67.6037 | 0 | 7.2692 | FALSE | FALSE
2025-06-09 17:00 | 38.1 | 33.5 | 99990 | 100 | 3000 | 25.5155 | 55.2548 | 66.0369 | 0 | 7.2692 | FALSE | FALSE
2025-06-09 18:00 | 36.95 | 37 | 100005 | 100 | 3000 | 25.0984 | 57.8172 | 66.8034 | 0 | 7.2692 | FALSE | FALSE
2025-06-09 19:00 | 35.35 | 44 | 100030 | 100 | 3000 | 24.5015 | 62.8787 | 69.8399 | 0 | 7.2692 | FALSE | FALSE
2025-06-09 20:00 | 34.55 | 45 | 100075 | 100 | 3000 | 24.2177 | 63.2304 | 67.9373 | 0 | 7.2692 | FALSE | FALSE
2025-06-09 21:00 | 34.3 | 41 | 100120 | 100 | 3000 | 24.1526 | 59.8993 | 62.197 | 0 | 7.2692 | FALSE | FALSE
2025-06-09 22:00 | 33.75 | 39 | 100145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-09 23:00 | 33 | 40 | 100130 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-10 | 32.15 | 41 | 100065 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-10 01:00 | 31.25 | 41.5 | 100000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-10 02:00 | 30.35 | 43.5 | 99995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-10 03:00 | 29.75 | 46 | 100000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-10 04:00 | 29.4 | 49 | 100000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-10 05:00 | 29 | 52 | 100030 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-10 06:00 | 29.6 | 49.5 | 100075 | 100 | 3000 | 22.3988 | 64.1344 | 53.5426 | 0 | 7.2692 | FALSE | FALSE
2025-06-10 07:00 | 31.85 | 42.5 | 100125 | 100 | 3000 | 23.2616 | 60.0321 | 54.8847 | 0 | 7.2692 | FALSE | FALSE
2025-06-10 08:00 | 35 | 34 | 100150 | 100 | 3000 | 24.4413 | 54.5238 | 56.1318 | 0 | 7.2692 | FALSE | FALSE
2025-06-10 09:00 | 38.1 | 25.5 | 100130 | 100 | 3000 | 25.5838 | 48.0792 | 54.6023 | 0 | 7.2692 | FALSE | FALSE
2025-06-10 10:00 | 40.5 | 18.5 | 100100 | 100 | 3000 | 26.4673 | 41.9467 | 50.6157 | 0 | 7.2692 | FALSE | FALSE
2025-06-10 11:00 | 41.95 | 14.5 | 100070 | 100 | 3000 | 27.0003 | 38.0934 | 47.4893 | 0 | 7.2692 | FALSE | FALSE
2025-06-10 12:00 | 42.85 | 14 | 100005 | 100 | 3000 | 27.3058 | 37.6032 | 48.6899 | 0 | 7.2692 | FALSE | FALSE
2025-06-10 13:00 | 43.35 | 14 | 99925 | 100 | 3000 | 27.4703 | 37.6211 | 49.83 | 0 | 7.2692 | FALSE | FALSE
2025-06-10 14:00 | 42.95 | 14 | 99860 | 100 | 3000 | 27.3389 | 37.6154 | 48.8745 | 0 | 7.2692 | FALSE | FALSE
2025-06-10 15:00 | 41.75 | 16 | 99815 | 100 | 3000 | 26.9153 | 39.6064 | 49.5194 | 0 | 7.2692 | FALSE | FALSE
2025-06-10 16:00 | 40.55 | 17.5 | 99825 | 100 | 3000 | 26.4953 | 41.0084 | 49.0333 | 0 | 7.2692 | FALSE | FALSE
2025-06-10 17:00 | 39.15 | 20.5 | 99835 | 100 | 3000 | 25.9887 | 43.7197 | 50.0899 | 0 | 7.2692 | FALSE | FALSE
2025-06-10 18:00 | 37.05 | 30.5 | 99850 | 100 | 3000 | 25.1821 | 52.239 | 58.2739 | 0 | 7.2692 | FALSE | FALSE
2025-06-10 19:00 | 34.85 | 45 | 99880 | 100 | 3000 | 24.3221 | 63.4189 | 69.0688 | 0 | 7.2692 | FALSE | FALSE
2025-06-10 20:00 | 33.5 | 53 | 99910 | 100 | 3000 | 23.806 | 68.8949 | 72.9489 | 0 | 7.2692 | FALSE | FALSE
2025-06-10 21:00 | 32.95 | 51 | 99960 | 100 | 3000 | 23.6217 | 66.9843 | 68.4099 | 0 | 7.2692 | FALSE | FALSE
2025-06-10 22:00 | 32.25 | 48 | 99980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-10 23:00 | 31.5 | 47.5 | 99955 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-11 | 30.75 | 50 | 99910 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-11 01:00 | 30 | 51.5 | 99880 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-11 02:00 | 29.5 | 46.5 | 99865 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-11 03:00 | 28.85 | 39.5 | 99865 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-11 04:00 | 28.8 | 34.5 | 99860 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-11 05:00 | 29.2 | 31.5 | 99870 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-11 06:00 | 30 | 29 | 99930 | 100 | 3000 | 22.615 | 49.9918 | 34.7609 | 0 | 7.2692 | FALSE | FALSE
2025-06-11 07:00 | 31.85 | 25.5 | 100000 | 100 | 3000 | 23.3314 | 47.458 | 36.4255 | 0 | 7.2692 | FALSE | FALSE
2025-06-11 08:00 | 34.45 | 21.5 | 100060 | 100 | 3000 | 24.3159 | 44.3424 | 38.9011 | 0 | 7.2692 | FALSE | FALSE
2025-06-11 09:00 | 37.45 | 17 | 100080 | 100 | 3000 | 25.4262 | 40.4911 | 42.2754 | 0 | 7.2692 | FALSE | FALSE
2025-06-11 10:00 | 39.85 | 15 | 100060 | 100 | 3000 | 26.2823 | 38.5967 | 44.8325 | 0 | 7.2692 | FALSE | FALSE
2025-06-11 11:00 | 41.35 | 16 | 100025 | 100 | 3000 | 26.7814 | 39.573 | 48.6045 | 0 | 7.2692 | FALSE | FALSE
2025-06-11 12:00 | 42.25 | 16.5 | 99975 | 100 | 3000 | 27.0748 | 40.1298 | 51.6802 | 0 | 7.2692 | FALSE | FALSE
2025-06-11 13:00 | 42.65 | 15.5 | 99910 | 100 | 3000 | 27.2198 | 39.1433 | 50.8775 | 0 | 7.2692 | FALSE | FALSE
2025-06-11 14:00 | 42.35 | 15.5 | 99845 | 100 | 3000 | 27.1209 | 39.1314 | 50.1255 | 0 | 7.2692 | FALSE | FALSE
2025-06-11 15:00 | 41.4 | 16.5 | 99800 | 100 | 3000 | 26.7925 | 40.0851 | 49.502 | 0 | 7.2692 | FALSE | FALSE
2025-06-11 16:00 | 40.1 | 19 | 99790 | 100 | 3000 | 26.3271 | 42.4115 | 50.2754 | 0 | 7.2692 | FALSE | FALSE
2025-06-11 17:00 | 38.35 | 26.5 | 99805 | 100 | 3000 | 25.6608 | 49.0605 | 56.7193 | 0 | 7.2692 | FALSE | FALSE
2025-06-11 18:00 | 36.5 | 34.5 | 99820 | 100 | 3000 | 24.9626 | 55.4926 | 61.8138 | 0 | 7.2692 | FALSE | FALSE
2025-06-11 19:00 | 35.15 | 39.5 | 99845 | 100 | 3000 | 24.4603 | 59.0986 | 63.4336 | 0 | 7.2692 | FALSE | FALSE
2025-06-11 20:00 | 34.15 | 43 | 99885 | 100 | 3000 | 24.0884 | 61.4389 | 63.9595 | 0 | 7.2692 | FALSE | FALSE
2025-06-11 21:00 | 33.35 | 44 | 99920 | 100 | 3000 | 23.7987 | 61.8282 | 62.0913 | 0 | 7.2692 | FALSE | FALSE
2025-06-11 22:00 | 32.65 | 44.5 | 99920 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-11 23:00 | 31.75 | 45.5 | 99900 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-12 | 30.8 | 46 | 99870 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-12 01:00 | 30.05 | 47 | 99855 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-12 02:00 | 29.3 | 51.5 | 99855 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-12 03:00 | 28.45 | 60 | 99840 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-12 04:00 | 28.3 | 64.5 | 99835 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-12 05:00 | 28.3 | 64 | 99880 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-12 06:00 | 28.95 | 57 | 99950 | 100 | 3000 | 22.1315 | 68.9451 | 58.0015 | 0 | 7.2692 | FALSE | FALSE
2025-06-12 07:00 | 31.8 | 44 | 100005 | 100 | 3000 | 23.2371 | 61.1313 | 56.2803 | 0 | 7.2692 | FALSE | FALSE
2025-06-12 08:00 | 35.6 | 30 | 100030 | 100 | 3000 | 24.6788 | 51.4085 | 52.9958 | 0 | 7.2692 | FALSE | FALSE
2025-06-12 09:00 | 38.85 | 18.5 | 100030 | 100 | 3000 | 25.9038 | 41.8431 | 46.3155 | 0 | 7.2692 | FALSE | FALSE
2025-06-12 10:00 | 41.15 | 14 | 100015 | 100 | 3000 | 26.7371 | 37.6063 | 46.1556 | 0 | 7.2692 | FALSE | FALSE
2025-06-12 11:00 | 42.8 | 12.5 | 99975 | 100 | 3000 | 27.3094 | 36.0617 | 47.8163 | 0 | 7.2692 | FALSE | FALSE
2025-06-12 12:00 | 43.9 | 12 | 99910 | 100 | 3000 | 27.6795 | 35.5181 | 48.8472 | 0 | 7.2692 | FALSE | FALSE
2025-06-12 13:00 | 44.35 | 12 | 99845 | 100 | 3000 | 27.8264 | 35.5164 | 49.228 | 0 | 7.2692 | FALSE | FALSE
2025-06-12 14:00 | 44 | 13 | 99785 | 100 | 3000 | 27.6973 | 36.5901 | 49.4055 | 0 | 7.2692 | FALSE | FALSE
2025-06-12 15:00 | 42.4 | 17.5 | 99745 | 100 | 3000 | 27.1115 | 41.1759 | 53.7425 | 0 | 7.2692 | FALSE | FALSE
2025-06-12 16:00 | 39.9 | 27.5 | 99735 | 100 | 3000 | 26.1721 | 50.4329 | 63.0444 | 0 | 7.2692 | FALSE | FALSE
2025-06-12 17:00 | 37.65 | 36.5 | 99730 | 100 | 3000 | 25.3389 | 57.739 | 68.5823 | 0 | 7.2692 | FALSE | FALSE
2025-06-12 18:00 | 35.9 | 42.5 | 99745 | 100 | 3000 | 24.7003 | 61.9733 | 70.0161 | 0 | 7.2692 | FALSE | FALSE
2025-06-12 19:00 | 34.55 | 50 | 99780 | 100 | 3000 | 24.1883 | 67.2695 | 73.8507 | 0 | 7.2692 | FALSE | FALSE
2025-06-12 20:00 | 33.85 | 53 | 99815 | 100 | 3000 | 23.9284 | 69.1533 | 74.4187 | 0 | 7.2692 | FALSE | FALSE
2025-06-12 21:00 | 33.25 | 53 | 99835 | 100 | 3000 | 23.718 | 68.7273 | 71.8707 | 0 | 7.2692 | FALSE | FALSE
2025-06-12 22:00 | 32.4 | 56 | 99860 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-12 23:00 | 31.65 | 58 | 99865 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-13 | 31 | 59.5 | 99835 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-13 01:00 | 30.5 | 62 | 99815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-13 02:00 | 29.75 | 64 | 99815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-13 03:00 | 28.7 | 63 | 99805 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-13 04:00 | 28.6 | 57 | 99780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-13 05:00 | 28.95 | 53 | 99790 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-13 06:00 | 29.95 | 49 | 99855 | 100 | 3000 | 22.5321 | 63.9569 | 54.3621 | 0 | 7.2692 | FALSE | FALSE
2025-06-13 07:00 | 32.85 | 39 | 99910 | 100 | 3000 | 23.6427 | 57.782 | 54.581 | 0 | 7.2692 | FALSE | FALSE
2025-06-13 08:00 | 36.4 | 28 | 99920 | 100 | 3000 | 24.9743 | 49.9173 | 52.8465 | 0 | 7.2692 | FALSE | FALSE
2025-06-13 09:00 | 39.45 | 20.5 | 99925 | 100 | 3000 | 26.0911 | 43.746 | 50.931 | 0 | 7.2692 | FALSE | FALSE
2025-06-13 10:00 | 41.95 | 16 | 99925 | 100 | 3000 | 26.9818 | 39.6091 | 50.0471 | 0 | 7.2692 | FALSE | FALSE
2025-06-13 11:00 | 43.85 | 13.5 | 99895 | 100 | 3000 | 27.6409 | 37.111 | 50.0473 | 0 | 7.2692 | FALSE | FALSE
2025-06-13 12:00 | 44.95 | 12.5 | 99835 | 100 | 3000 | 28.0124 | 36.0635 | 50.5947 | 0 | 7.2692 | FALSE | FALSE
2025-06-13 13:00 | 44.85 | 13.5 | 99770 | 100 | 3000 | 27.9641 | 37.1584 | 52.3157 | 0 | 7.2692 | FALSE | FALSE
2025-06-13 14:00 | 42.65 | 20.5 | 99740 | 100 | 3000 | 27.1531 | 44.2824 | 59.6994 | 0 | 7.2692 | FALSE | FALSE
2025-06-13 15:00 | 40.4 | 27.5 | 99720 | 100 | 3000 | 26.3368 | 50.6025 | 64.6356 | 0 | 7.2692 | FALSE | FALSE
2025-06-13 16:00 | 38.95 | 34.5 | 99695 | 100 | 3000 | 25.7893 | 56.5749 | 70.3954 | 0 | 7.2692 | FALSE | FALSE
2025-06-13 17:00 | 36.9 | 46 | 99695 | 100 | 3000 | 25.0126 | 65.5892 | 78.5425 | 0 | 7.2692 | FALSE | FALSE
2025-06-13 18:00 | 34.85 | 57.5 | 99710 | 100 | 3000 | 24.2459 | 73.5558 | 84.0864 | 0 | 7.2692 | FALSE | FALSE
2025-06-13 19:00 | 33.3 | 68.5 | 99725 | 100 | 3000 | 23.6567 | 80.7186 | 89.3055 | 0 | 7.2692 | FALSE | FALSE
2025-06-13 20:00 | 32.35 | 76.5 | 99755 | 100 | 3000 | 23.2916 | 85.709 | 93.0548 | 0 | 7.2692 | FALSE | FALSE
2025-06-13 21:00 | 31.8 | 78 | 99800 | 100 | 3000 | 23.0946 | 86.1628 | 91.738 | 0 | 7.2692 | FALSE | FALSE
2025-06-13 22:00 | 31.3 | 77 | 99815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-13 23:00 | 30.65 | 77 | 99775 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-14 | 30.15 | 76 | 99725 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-14 01:00 | 29.55 | 76 | 99705 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-14 02:00 | 28.75 | 78 | 99700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-14 03:00 | 28.1 | 79 | 99700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-14 04:00 | 28.3 | 74 | 99705 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-14 05:00 | 28.7 | 68.5 | 99740 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-14 06:00 | 29.5 | 64 | 99795 | 100 | 3000 | 22.3171 | 74.0636 | 66.8661 | 0 | 7.2692 | FALSE | FALSE
2025-06-14 07:00 | 32.25 | 53 | 99830 | 100 | 3000 | 23.3621 | 68.0646 | 67.6684 | 0 | 7.2692 | FALSE | FALSE
2025-06-14 08:00 | 35.8 | 38.5 | 99850 | 100 | 3000 | 24.6929 | 58.5692 | 64.5508 | 0 | 7.2692 | FALSE | FALSE
2025-06-14 09:00 | 39 | 26 | 99860 | 100 | 3000 | 25.8859 | 48.7625 | 57.9856 | 0 | 7.2692 | FALSE | FALSE
2025-06-14 10:00 | 41.7 | 17 | 99845 | 100 | 3000 | 26.8865 | 40.5981 | 51.1199 | 0 | 7.2692 | FALSE | FALSE
2025-06-14 11:00 | 43.6 | 12 | 99805 | 100 | 3000 | 27.5812 | 35.5319 | 48.5194 | 0 | 7.2692 | FALSE | FALSE
2025-06-14 12:00 | 44.05 | 12 | 99755 | 100 | 3000 | 27.7288 | 35.5261 | 48.9105 | 0 | 7.2692 | FALSE | FALSE
2025-06-14 13:00 | 42.2 | 17.5 | 99710 | 100 | 3000 | 27.0458 | 41.1565 | 53.2159 | 0 | 7.2692 | FALSE | FALSE
2025-06-14 14:00 | 39.95 | 24.5 | 99670 | 100 | 3000 | 26.2197 | 47.6133 | 58.5037 | 0 | 7.2692 | FALSE | FALSE
2025-06-14 15:00 | 38.9 | 27 | 99630 | 100 | 3000 | 25.8429 | 49.6729 | 59.1049 | 0 | 7.2692 | FALSE | FALSE
2025-06-14 16:00 | 37.8 | 31 | 99600 | 100 | 3000 | 25.4351 | 52.9418 | 61.3639 | 0 | 7.2692 | FALSE | FALSE
2025-06-14 17:00 | 36.35 | 39 | 99570 | 100 | 3000 | 24.8787 | 59.2769 | 67.1462 | 0 | 7.2692 | FALSE | FALSE
2025-06-14 18:00 | 34.75 | 48.5 | 99565 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-14 19:00 | 33.35 | 56.5 | 99600 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-14 20:00 | 32.5 | 59.5 | 99625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-14 21:00 | 31.9 | 59 | 99615 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-14 22:00 | 31.15 | 58.5 | 99620 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-14 23:00 | 30.25 | 59 | 99625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 | 29.45 | 57.5 | 99580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 01:00 | 28.7 | 56 | 99555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 02:00 | 27.95 | 55.5 | 99545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 03:00 | 27.5 | 52 | 99530 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 04:00 | 28 | 46 | 99515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 05:00 | 28.55 | 39.5 | 99500 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 06:00 | 29.6 | 31.5 | 99510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 07:00 | 32.35 | 24 | 99540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 08:00 | 35.35 | 19 | 99565 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 09:00 | 37.85 | 15.5 | 99570 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 10:00 | 39.35 | 16 | 99545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 11:00 | 39.9 | 20 | 99495 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 12:00 | 40 | 23 | 99450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 13:00 | 39.7 | 25 | 99395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 14:00 | 39.4 | 26.5 | 99330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 15:00 | 38.85 | 28.5 | 99275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 16:00 | 37.55 | 33 | 99255 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 17:00 | 36.05 | 40 | 99260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 18:00 | 34.55 | 49 | 99265 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 19:00 | 33.25 | 56 | 99260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 20:00 | 32.45 | 59.5 | 99240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 21:00 | 31.75 | 60.5 | 99270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 22:00 | 30.9 | 66 | 99345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-15 23:00 | 30.1 | 72.5 | 99355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-16 | 29.25 | 73 | 99315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-16 01:00 | 28.4 | 73 | 99270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-16 02:00 | 27.8 | 73 | 99245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-16 03:00 | 27.6 | 69 | 99235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-16 04:00 | 27.8 | 60.5 | 99230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-16 05:00 | 27.95 | 54.5 | 99275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-16 06:00 | 28.95 | 49.5 | 99305 | 100 | 3000 | 22.1524 | 63.946 | 50.918 | 0 | 7.2692 | FALSE | FALSE
2025-06-16 07:00 | 31.4 | 41.5 | 99315 | 100 | 3000 | 23.0996 | 59.2118 | 52.0263 | 0 | 7.2692 | FALSE | FALSE
2025-06-16 08:00 | 34.3 | 34 | 99350 | 100 | 3000 | 24.1918 | 54.3834 | 53.5893 | 0 | 7.2692 | FALSE | FALSE
2025-06-16 09:00 | 37.1 | 28 | 99360 | 100 | 3000 | 25.2186 | 50.1217 | 54.8638 | 0 | 7.2692 | FALSE | FALSE
2025-06-16 10:00 | 39.65 | 23.5 | 99330 | 100 | 3000 | 26.1294 | 46.6296 | 55.9585 | 0 | 7.2692 | FALSE | FALSE
2025-06-16 11:00 | 41.7 | 22 | 99285 | 100 | 3000 | 26.8256 | 45.6252 | 59.4482 | 0 | 7.2692 | FALSE | FALSE
2025-06-16 12:00 | 43.1 | 24 | 99215 | 100 | 3000 | 27.2484 | 48.0615 | 67.0461 | 0 | 7.2692 | FALSE | FALSE
2025-06-16 13:00 | 43.45 | 27 | 99140 | 100 | 3000 | 27.3142 | 51.3448 | 73.4842 | 0 | 7.2692 | FALSE | FALSE
2025-06-16 14:00 | 43.3 | 26.5 | 99085 | 100 | 3000 | 27.275 | 50.7588 | 72.0843 | 0 | 7.2692 | FALSE | FALSE
2025-06-16 15:00 | 42.7 | 28 | 99055 | 100 | 3000 | 27.0669 | 52.0601 | 72.7453 | 0 | 7.2692 | FALSE | FALSE
2025-06-16 16:00 | 40.7 | 31.5 | 99060 | 100 | 3000 | 26.3894 | 54.6368 | 71.7757 | 0 | 7.2692 | FALSE | FALSE
2025-06-16 17:00 | 38.5 | 35 | 99075 | 100 | 3000 | 25.6354 | 56.8632 | 69.3353 | 0 | 7.2692 | FALSE | FALSE
2025-06-16 18:00 | 36.9 | 41.5 | 99095 | 100 | 3000 | 25.0465 | 61.7557 | 72.4029 | 0 | 7.2692 | FALSE | FALSE
2025-06-16 19:00 | 35.35 | 49.5 | 99120 | 100 | 3000 | 24.4653 | 67.4836 | 76.4248 | 0 | 7.2692 | FALSE | FALSE
2025-06-16 20:00 | 33.85 | 58.5 | 99145 | 100 | 3000 | 23.8978 | 73.5297 | 80.5691 | 0 | 7.2692 | FALSE | FALSE
2025-06-16 21:00 | 32.5 | 69 | 99195 | 100 | 3000 | 23.3773 | 80.3142 | 85.7811 | 0 | 7.2692 | FALSE | FALSE
2025-06-16 22:00 | 31.6 | 76.5 | 99235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-16 23:00 | 30.95 | 80.5 | 99220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-17 | 30.15 | 87 | 99200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-17 01:00 | 29.55 | 91.5 | 99210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-17 02:00 | 29.2 | 92 | 99225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-17 03:00 | 28.6 | 92 | 99245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-17 04:00 | 28.2 | 90.5 | 99240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-17 05:00 | 28.4 | 83 | 99225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-17 06:00 | 29.85 | 61.5 | 99255 | 100 | 3000 | 22.4544 | 72.6405 | 65.9346 | 0 | 7.2692 | FALSE | FALSE
2025-06-17 07:00 | 32.25 | 44.5 | 99310 | 100 | 3000 | 23.3993 | 61.7563 | 58.3526 | 0 | 7.2692 | FALSE | FALSE
2025-06-17 08:00 | 35.3 | 35.5 | 99340 | 100 | 3000 | 24.5379 | 55.9215 | 58.8326 | 0 | 7.2692 | FALSE | FALSE
2025-06-17 09:00 | 39.1 | 22.5 | 99330 | 100 | 3000 | 25.953 | 45.5988 | 52.8453 | 0 | 7.2692 | FALSE | FALSE
2025-06-17 10:00 | 42.1 | 16 | 99320 | 100 | 3000 | 27.0322 | 39.6612 | 50.2196 | 0 | 7.2692 | FALSE | FALSE
2025-06-17 11:00 | 42.4 | 22.5 | 99310 | 100 | 3000 | 27.046 | 46.2997 | 62.3444 | 0 | 7.2692 | FALSE | FALSE
2025-06-17 12:00 | 41.4 | 29 | 99285 | 100 | 3000 | 26.6432 | 52.485 | 70.1862 | 0 | 7.2692 | FALSE | FALSE
2025-06-17 13:00 | 41.05 | 30 | 99245 | 100 | 3000 | 26.5192 | 53.3207 | 70.6279 | 0 | 7.2692 | FALSE | FALSE
2025-06-17 14:00 | 40.7 | 31 | 99200 | 100 | 3000 | 26.3952 | 54.1409 | 71.0245 | 0 | 7.2692 | FALSE | FALSE
2025-06-17 15:00 | 39.9 | 33.5 | 99185 | 100 | 3000 | 26.1095 | 56.1531 | 72.1274 | 0 | 7.2692 | FALSE | FALSE
2025-06-17 16:00 | 38.75 | 38 | 99185 | 100 | 3000 | 25.6903 | 59.7181 | 74.6199 | 0 | 7.2692 | FALSE | FALSE
2025-06-17 17:00 | 37.45 | 43.5 | 99190 | 100 | 3000 | 25.2144 | 63.8343 | 77.2843 | 0 | 7.2692 | FALSE | FALSE
2025-06-17 18:00 | 36.1 | 51 | 99220 | 100 | 3000 | 24.7084 | 69.2906 | 81.518 | 0 | 7.2692 | FALSE | FALSE
2025-06-17 19:00 | 35.05 | 55 | 99270 | 100 | 3000 | 24.3285 | 71.739 | 81.8773 | 0 | 7.2692 | FALSE | FALSE
2025-06-17 20:00 | 34.1 | 56.5 | 99330 | 100 | 3000 | 23.9952 | 72.1477 | 79.4366 | 0 | 7.2692 | FALSE | FALSE
2025-06-17 21:00 | 33 | 59 | 99370 | 100 | 3000 | 23.6 | 73.1845 | 77.3482 | 0 | 7.2692 | FALSE | FALSE
2025-06-17 22:00 | 31.75 | 63.5 | 99380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-17 23:00 | 30.65 | 68.5 | 99365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-18 | 29.8 | 72 | 99325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-18 01:00 | 29.1 | 72 | 99290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-18 02:00 | 28.6 | 70 | 99295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-18 03:00 | 28.35 | 70 | 99325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-18 04:00 | 28.45 | 65.5 | 99345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-18 05:00 | 28.6 | 61.5 | 99400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-18 06:00 | 29.35 | 61.5 | 99470 | 100 | 3000 | 22.2686 | 72.283 | 63.7984 | 0 | 7.2692 | FALSE | FALSE
2025-06-18 07:00 | 31.4 | 56 | 99505 | 100 | 3000 | 23.0424 | 69.7565 | 67.1877 | 0 | 7.2692 | FALSE | FALSE
2025-06-18 08:00 | 34 | 48 | 99530 | 100 | 3000 | 24.0078 | 65.3435 | 69.1717 | 0 | 7.2692 | FALSE | FALSE
2025-06-18 09:00 | 36.55 | 38.5 | 99525 | 100 | 3000 | 24.9506 | 58.9538 | 67.2147 | 0 | 7.2692 | FALSE | FALSE
2025-06-18 10:00 | 38.95 | 29.5 | 99505 | 100 | 3000 | 25.8363 | 51.9942 | 62.9486 | 0 | 7.2692 | FALSE | FALSE
2025-06-18 11:00 | 41.1 | 23.5 | 99470 | 100 | 3000 | 26.6113 | 46.9507 | 60.2589 | 0 | 7.2692 | FALSE | FALSE
2025-06-18 12:00 | 42.7 | 19.5 | 99400 | 100 | 3000 | 27.1829 | 43.2902 | 57.9568 | 0 | 7.2692 | FALSE | FALSE
2025-06-18 13:00 | 43.05 | 21 | 99340 | 100 | 3000 | 27.2749 | 44.9179 | 61.5839 | 0 | 7.2692 | FALSE | FALSE
2025-06-18 14:00 | 41.55 | 33 | 99295 | 100 | 3000 | 26.6418 | 56.5287 | 77.2678 | 0 | 7.2692 | FALSE | FALSE
2025-06-18 15:00 | 39.65 | 40.5 | 99265 | 100 | 3000 | 25.9565 | 62.5992 | 81.7938 | 0 | 7.2692 | FALSE | FALSE
2025-06-18 16:00 | 38.2 | 41 | 99270 | 100 | 3000 | 25.4829 | 62.0959 | 76.8168 | 0 | 7.2692 | FALSE | FALSE
2025-06-18 17:00 | 36.7 | 46 | 99270 | 100 | 3000 | 24.9454 | 65.4853 | 77.6065 | 0 | 7.2692 | FALSE | FALSE
2025-06-18 18:00 | 35.05 | 55 | 99280 | 100 | 3000 | 24.3285 | 71.7381 | 81.8799 | 0 | 7.2692 | FALSE | FALSE
2025-06-18 19:00 | 33.4 | 66 | 99320 | 100 | 3000 | 23.7032 | 78.9321 | 86.9397 | 0 | 7.2692 | FALSE | FALSE
2025-06-18 20:00 | 32.65 | 70.5 | 99380 | 100 | 3000 | 23.4226 | 81.5821 | 88.1625 | 0 | 7.2692 | FALSE | FALSE
2025-06-18 21:00 | 32.2 | 72.5 | 99425 | 100 | 3000 | 23.2573 | 82.5913 | 88.0313 | 0 | 7.2692 | FALSE | FALSE
2025-06-18 22:00 | 31.35 | 79 | 99420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-18 23:00 | 30.6 | 84.5 | 99390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-19 | 29.9 | 88.5 | 99360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-19 01:00 | 29.15 | 94 | 99350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-19 02:00 | 28.7 | 98 | 99360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-19 03:00 | 28.6 | 98 | 99370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-19 04:00 | 28.55 | 97 | 99365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-19 05:00 | 28.3 | 97.5 | 99380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-19 06:00 | 28.65 | 94.5 | 99430 | 100 | 3000 | 21.9157 | 93.7763 | 90.2141 | 0 | 7.2692 | FALSE | FALSE
2025-06-19 07:00 | 30.2 | 85 | 99480 | 100 | 3000 | 22.5035 | 89.274 | 90.0612 | 0 | 7.2692 | FALSE | FALSE
2025-06-19 08:00 | 33.1 | 67 | 99500 | 100 | 3000 | 23.5952 | 79.3806 | 86.6261 | 0 | 7.2692 | FALSE | FALSE
2025-06-19 09:00 | 36.7 | 46.5 | 99500 | 100 | 3000 | 24.9419 | 65.8944 | 78.3242 | 0 | 7.2692 | FALSE | FALSE
2025-06-19 10:00 | 39.6 | 34 | 99485 | 100 | 3000 | 26.0071 | 56.4497 | 71.9098 | 0 | 7.2692 | FALSE | FALSE
2025-06-19 11:00 | 41.6 | 28 | 99445 | 100 | 3000 | 26.7194 | 51.5627 | 69.2465 | 0 | 7.2692 | FALSE | FALSE
2025-06-19 12:00 | 43 | 24 | 99390 | 100 | 3000 | 27.2169 | 48.0152 | 66.7989 | 0 | 7.2692 | FALSE | FALSE
2025-06-19 13:00 | 43.7 | 22 | 99335 | 100 | 3000 | 27.4665 | 46.1394 | 65.2708 | 0 | 7.2692 | FALSE | FALSE
2025-06-19 14:00 | 42.65 | 29 | 99280 | 100 | 3000 | 27.0377 | 53.0491 | 74.3817 | 0 | 7.2692 | FALSE | FALSE
2025-06-19 15:00 | 40.35 | 37 | 99245 | 100 | 3000 | 26.2164 | 59.7365 | 79.1827 | 0 | 7.2692 | FALSE | FALSE
2025-06-19 16:00 | 38 | 43 | 99235 | 100 | 3000 | 25.3998 | 63.7588 | 78.813 | 0 | 7.2692 | FALSE | FALSE
2025-06-19 17:00 | 35.8 | 53 | 99245 | 100 | 3000 | 24.5941 | 70.7199 | 82.7338 | 0 | 7.2692 | FALSE | FALSE
2025-06-19 18:00 | 34.1 | 62 | 99290 | 100 | 3000 | 23.9642 | 76.4985 | 85.767 | 0 | 7.2692 | FALSE | FALSE
2025-06-19 19:00 | 33 | 68 | 99345 | 100 | 3000 | 23.5555 | 80.0567 | 87.1915 | 0 | 7.2692 | FALSE | FALSE
2025-06-19 20:00 | 32.25 | 72 | 99405 | 100 | 3000 | 23.2769 | 82.2752 | 87.7549 | 0 | 7.2692 | FALSE | FALSE
2025-06-19 21:00 | 31.55 | 77.5 | 99470 | 100 | 3000 | 23.0089 | 85.5375 | 89.8555 | 0 | 7.2692 | FALSE | FALSE
2025-06-19 22:00 | 30.8 | 85 | 99490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-19 23:00 | 30 | 91.5 | 99470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-20 | 29.25 | 95.5 | 99430 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-20 01:00 | 28.65 | 97.5 | 99395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-20 02:00 | 28.25 | 98 | 99385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-20 03:00 | 27.9 | 98 | 99380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-20 04:00 | 28.35 | 95.5 | 99380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-20 05:00 | 28.65 | 94 | 99415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-20 06:00 | 28.8 | 90.5 | 99470 | 100 | 3000 | 21.9816 | 91.3063 | 87.5259 | 0 | 7.2692 | FALSE | FALSE
2025-06-20 07:00 | 30.15 | 80.5 | 99505 | 100 | 3000 | 22.5011 | 86.08 | 85.5404 | 0 | 7.2692 | FALSE | FALSE
2025-06-20 08:00 | 32.05 | 69 | 99530 | 100 | 3000 | 23.2205 | 79.8295 | 83.6572 | 0 | 7.2692 | FALSE | FALSE
2025-06-20 09:00 | 34.45 | 56 | 99530 | 100 | 3000 | 24.1185 | 72.0213 | 80.4617 | 0 | 7.2692 | FALSE | FALSE
2025-06-20 10:00 | 37.45 | 40 | 99500 | 100 | 3000 | 25.2431 | 60.7348 | 72.5985 | 0 | 7.2692 | FALSE | FALSE
2025-06-20 11:00 | 40.35 | 26 | 99460 | 100 | 3000 | 26.3366 | 49.1674 | 62.021 | 0 | 7.2692 | FALSE | FALSE
2025-06-20 12:00 | 42.5 | 18.5 | 99405 | 100 | 3000 | 27.1313 | 42.2328 | 55.6534 | 0 | 7.2692 | FALSE | FALSE
2025-06-20 13:00 | 42.8 | 20 | 99345 | 100 | 3000 | 27.2084 | 43.8279 | 59.1006 | 0 | 7.2692 | FALSE | FALSE
2025-06-20 14:00 | 40.7 | 32.5 | 99305 | 100 | 3000 | 26.3783 | 55.587 | 73.4381 | 0 | 7.2692 | FALSE | FALSE
2025-06-20 15:00 | 38.85 | 40 | 99285 | 100 | 3000 | 25.7042 | 61.6014 | 77.927 | 0 | 7.2692 | FALSE | FALSE
2025-06-20 16:00 | 37.95 | 41 | 99285 | 100 | 3000 | 25.4006 | 61.9371 | 75.8459 | 0 | 7.2692 | FALSE | FALSE
2025-06-20 17:00 | 36.35 | 47.5 | 99300 | 100 | 3000 | 24.8172 | 66.5148 | 78.1219 | 0 | 7.2692 | FALSE | FALSE
2025-06-20 18:00 | 34.25 | 60 | 99345 | 100 | 3000 | 24.0268 | 75.05 | 84.1755 | 0 | 7.2692 | FALSE | FALSE
2025-06-20 19:00 | 32.75 | 70.5 | 99395 | 100 | 3000 | 23.4572 | 81.6877 | 88.6647 | 0 | 7.2692 | FALSE | FALSE
2025-06-20 20:00 | 31.95 | 75.5 | 99435 | 100 | 3000 | 23.157 | 84.5336 | 89.8736 | 0 | 7.2692 | FALSE | FALSE
2025-06-20 21:00 | 31.3 | 78 | 99490 | 100 | 3000 | 22.9191 | 85.6108 | 89.0654 | 0 | 7.2692 | FALSE | FALSE
2025-06-20 22:00 | 30.7 | 78.5 | 99525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-20 23:00 | 30.05 | 80.5 | 99520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-21 | 29.35 | 84 | 99495 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-21 01:00 | 28.7 | 87 | 99470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-21 02:00 | 28.15 | 88 | 99460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-21 03:00 | 27.7 | 88 | 99470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-21 04:00 | 27.7 | 87.5 | 99460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-21 05:00 | 27.95 | 87.5 | 99470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-21 06:00 | 28.5 | 84.5 | 99545 | 100 | 3000 | 21.888 | 86.9733 | 80.6499 | 0 | 7.2692 | FALSE | FALSE
2025-06-21 07:00 | 29.9 | 77 | 99610 | 100 | 3000 | 22.4227 | 83.3743 | 80.9749 | 0 | 7.2692 | FALSE | FALSE
2025-06-21 08:00 | 31.7 | 69.5 | 99645 | 100 | 3000 | 23.0951 | 79.8414 | 82.4968 | 0 | 7.2692 | FALSE | FALSE
2025-06-21 09:00 | 33.5 | 62.5 | 99660 | 100 | 3000 | 23.7564 | 76.289 | 83.5995 | 0 | 7.2692 | FALSE | FALSE
2025-06-21 10:00 | 35.5 | 53.5 | 99645 | 100 | 3000 | 24.4906 | 70.8504 | 82.1368 | 0 | 7.2692 | FALSE | FALSE
2025-06-21 11:00 | 37.75 | 42.5 | 99615 | 100 | 3000 | 25.3223 | 63.1147 | 77.231 | 0 | 7.2692 | FALSE | FALSE
2025-06-21 12:00 | 39.65 | 33 | 99570 | 100 | 3000 | 26.0336 | 55.5289 | 70.598 | 0 | 7.2692 | FALSE | FALSE
2025-06-21 13:00 | 40.4 | 29 | 99515 | 100 | 3000 | 26.3204 | 52.0589 | 66.9443 | 0 | 7.2692 | FALSE | FALSE
2025-06-21 14:00 | 40.1 | 29 | 99470 | 100 | 3000 | 26.2223 | 51.9473 | 65.9439 | 0 | 7.2692 | FALSE | FALSE
2025-06-21 15:00 | 39.6 | 29.5 | 99435 | 100 | 3000 | 26.0525 | 52.2345 | 65.0606 | 0 | 7.2692 | FALSE | FALSE
2025-06-21 16:00 | 39.05 | 32.5 | 99420 | 100 | 3000 | 25.8412 | 54.8021 | 67.713 | 0 | 7.2692 | FALSE | FALSE
2025-06-21 17:00 | 37.6 | 40 | 99415 | 100 | 3000 | 25.2931 | 60.8284 | 73.1474 | 0 | 7.2692 | FALSE | FALSE
2025-06-21 18:00 | 35.3 | 52 | 99430 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-21 19:00 | 33.2 | 66 | 99475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-21 20:00 | 31.9 | 77.5 | 99535 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-21 21:00 | 31.3 | 82 | 99590 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-21 22:00 | 30.8 | 82.5 | 99615 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-21 23:00 | 30.1 | 85.5 | 99615 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 | 29.3 | 89 | 99580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 01:00 | 28.5 | 91 | 99540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 02:00 | 27.75 | 93 | 99520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 03:00 | 27.1 | 95.5 | 99500 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 04:00 | 27.4 | 95 | 99490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 05:00 | 27.85 | 93 | 99510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 06:00 | 28.35 | 88 | 99550 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 07:00 | 30.25 | 74 | 99595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 08:00 | 32.7 | 59.5 | 99630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 09:00 | 35 | 49.5 | 99640 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 10:00 | 37.2 | 40 | 99615 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 11:00 | 39.05 | 30.5 | 99575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 12:00 | 39.75 | 26 | 99535 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 13:00 | 39.6 | 27 | 99480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 14:00 | 39.1 | 30 | 99415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 15:00 | 38.2 | 34 | 99360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 16:00 | 37.1 | 38.5 | 99345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 17:00 | 35.65 | 45.5 | 99350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 18:00 | 34.1 | 52 | 99360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 19:00 | 32.8 | 58.5 | 99390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 20:00 | 31.85 | 66 | 99430 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 21:00 | 31.2 | 71 | 99460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 22:00 | 30.5 | 74.5 | 99460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-22 23:00 | 29.75 | 77.5 | 99425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-23 | 29.1 | 79.5 | 99390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-23 01:00 | 28.55 | 81 | 99355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-23 02:00 | 28 | 83.5 | 99330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-23 03:00 | 27.45 | 85.5 | 99335 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-23 04:00 | 28.05 | 85 | 99340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-23 05:00 | 28.65 | 85 | 99365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-23 06:00 | 29.15 | 81.5 | 99410 | 100 | 3000 | 22.1353 | 85.6824 | 81.2952 | 0 | 7.2692 | FALSE | FALSE
2025-06-23 07:00 | 31.1 | 71 | 99455 | 100 | 3000 | 22.8757 | 80.3609 | 81.0556 | 0 | 7.2692 | FALSE | FALSE
2025-06-23 08:00 | 33.55 | 59 | 99490 | 100 | 3000 | 23.7918 | 73.6325 | 79.8589 | 0 | 7.2692 | FALSE | FALSE
2025-06-23 09:00 | 36 | 45.5 | 99485 | 100 | 3000 | 24.7135 | 64.5715 | 74.1732 | 0 | 7.2692 | FALSE | FALSE
2025-06-23 10:00 | 37.9 | 33.5 | 99465 | 100 | 3000 | 25.448 | 55.2133 | 65.1945 | 0 | 7.2692 | FALSE | FALSE
2025-06-23 11:00 | 38.8 | 28.5 | 99450 | 100 | 3000 | 25.7953 | 51.0318 | 60.9645 | 0 | 7.2692 | FALSE | FALSE
2025-06-23 12:00 | 39.3 | 26 | 99415 | 100 | 3000 | 25.9871 | 48.8749 | 58.7725 | 0 | 7.2692 | FALSE | FALSE
2025-06-23 13:00 | 39.8 | 22.5 | 99350 | 100 | 3000 | 26.19 | 45.7166 | 54.8413 | 0 | 7.2692 | FALSE | FALSE
2025-06-23 14:00 | 39.8 | 21 | 99280 | 100 | 3000 | 26.2053 | 44.3082 | 52.4732 | 0 | 7.2692 | FALSE | FALSE
2025-06-23 15:00 | 39.05 | 24.5 | 99235 | 100 | 3000 | 25.9171 | 47.4415 | 55.6971 | 0 | 7.2692 | FALSE | FALSE
2025-06-23 16:00 | 37.65 | 31.5 | 99215 | 100 | 3000 | 25.3799 | 53.3634 | 61.4615 | 0 | 7.2692 | FALSE | FALSE
2025-06-23 17:00 | 36.1 | 37.5 | 99215 | 100 | 3000 | 24.8032 | 57.9202 | 64.183 | 0 | 7.2692 | FALSE | FALSE
2025-06-23 18:00 | 34.45 | 46.5 | 99240 | 100 | 3000 | 24.1735 | 64.4482 | 69.1346 | 0 | 7.2692 | FALSE | FALSE
2025-06-23 19:00 | 33 | 56 | 99275 | 100 | 3000 | 23.6146 | 70.9009 | 74.0138 | 0 | 7.2692 | FALSE | FALSE
2025-06-23 20:00 | 32.15 | 60 | 99305 | 100 | 3000 | 23.2951 | 73.2604 | 74.6034 | 0 | 7.2692 | FALSE | FALSE
2025-06-23 21:00 | 31.45 | 62.5 | 99340 | 100 | 3000 | 23.0344 | 74.5374 | 74.0667 | 0 | 7.2692 | FALSE | FALSE
2025-06-23 22:00 | 30.85 | 66 | 99365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-23 23:00 | 30.3 | 70 | 99355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-24 | 29.8 | 72 | 99315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-24 01:00 | 29.3 | 71 | 99265 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-24 02:00 | 28.65 | 70.5 | 99225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-24 03:00 | 28 | 71 | 99225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-24 04:00 | 28.1 | 66.5 | 99235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-24 05:00 | 28.35 | 62.5 | 99255 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-24 06:00 | 28.9 | 60 | 99295 | 100 | 3000 | 22.1041 | 71.0004 | 60.4445 | 0 | 7.2692 | FALSE | FALSE
2025-06-24 07:00 | 30.95 | 52.5 | 99320 | 100 | 3000 | 22.8914 | 66.972 | 61.6942 | 0 | 7.2692 | FALSE | FALSE
2025-06-24 08:00 | 33.6 | 44.5 | 99335 | 100 | 3000 | 23.8851 | 62.3919 | 63.4849 | 0 | 7.2692 | FALSE | FALSE
2025-06-24 09:00 | 36.15 | 36.5 | 99330 | 100 | 3000 | 24.8275 | 57.0889 | 63.09 | 0 | 7.2692 | FALSE | FALSE
2025-06-24 10:00 | 38.45 | 26 | 99310 | 100 | 3000 | 25.6994 | 48.6717 | 56.1514 | 0 | 7.2692 | FALSE | FALSE
2025-06-24 11:00 | 39.8 | 19.5 | 99280 | 100 | 3000 | 26.2205 | 42.8947 | 50.1187 | 0 | 7.2692 | FALSE | FALSE
2025-06-24 12:00 | 40.15 | 20 | 99230 | 100 | 3000 | 26.3339 | 43.4103 | 51.8313 | 0 | 7.2692 | FALSE | FALSE
2025-06-24 13:00 | 39.85 | 24.5 | 99175 | 100 | 3000 | 26.1864 | 47.6273 | 58.0554 | 0 | 7.2692 | FALSE | FALSE
2025-06-24 14:00 | 39.1 | 30 | 99125 | 100 | 3000 | 25.8816 | 52.5389 | 64.0749 | 0 | 7.2692 | FALSE | FALSE
2025-06-24 15:00 | 38.1 | 34.5 | 99075 | 100 | 3000 | 25.5065 | 56.2254 | 67.1993 | 0 | 7.2692 | FALSE | FALSE
2025-06-24 16:00 | 37.1 | 37.5 | 99065 | 100 | 3000 | 25.145 | 58.4013 | 67.769 | 0 | 7.2692 | FALSE | FALSE
2025-06-24 17:00 | 35.95 | 41 | 99090 | 100 | 3000 | 24.7273 | 60.8 | 68.1163 | 0 | 7.2692 | FALSE | FALSE
2025-06-24 18:00 | 34.45 | 48.5 | 99135 | 100 | 3000 | 24.1618 | 66.0581 | 71.4929 | 0 | 7.2692 | FALSE | FALSE
2025-06-24 19:00 | 33.25 | 56.5 | 99190 | 100 | 3000 | 23.6998 | 71.4823 | 75.6434 | 0 | 7.2692 | FALSE | FALSE
2025-06-24 20:00 | 32.45 | 61 | 99225 | 100 | 3000 | 23.3969 | 74.2587 | 77.0056 | 0 | 7.2692 | FALSE | FALSE
2025-06-24 21:00 | 31.65 | 62.5 | 99245 | 100 | 3000 | 23.106 | 74.7088 | 74.9549 | 0 | 7.2692 | FALSE | FALSE
2025-06-24 22:00 | 30.85 | 62 | 99240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-24 23:00 | 30.15 | 61.5 | 99195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-25 | 29.35 | 63.5 | 99145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-25 01:00 | 28.4 | 64.5 | 99130 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-25 02:00 | 27.7 | 63 | 99135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-25 03:00 | 27.35 | 61 | 99135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-25 04:00 | 27.7 | 54 | 99125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-25 05:00 | 28.15 | 46.5 | 99135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-25 06:00 | 28.8 | 41.5 | 99175 | 100 | 3000 | 22.117 | 58.5182 | 42.8824 | 0 | 7.2692 | FALSE | FALSE
2025-06-25 07:00 | 30.7 | 34.5 | 99215 | 100 | 3000 | 22.8636 | 53.9993 | 42.3503 | 0 | 7.2692 | FALSE | FALSE
2025-06-25 08:00 | 33.2 | 29 | 99240 | 100 | 3000 | 23.8187 | 50.2471 | 44.1435 | 0 | 7.2692 | FALSE | FALSE
2025-06-25 09:00 | 35.7 | 24.5 | 99240 | 100 | 3000 | 24.7505 | 46.9162 | 45.9618 | 0 | 7.2692 | FALSE | FALSE
2025-06-25 10:00 | 38 | 19.5 | 99210 | 100 | 3000 | 25.6003 | 42.7736 | 45.3568 | 0 | 7.2692 | FALSE | FALSE
2025-06-25 11:00 | 40 | 15.5 | 99175 | 100 | 3000 | 26.3298 | 39.1318 | 44.5659 | 0 | 7.2692 | FALSE | FALSE
2025-06-25 12:00 | 41.6 | 13.5 | 99125 | 100 | 3000 | 26.8962 | 37.1655 | 46.215 | 0 | 7.2692 | FALSE | FALSE
2025-06-25 13:00 | 42.4 | 14 | 99060 | 100 | 3000 | 27.1578 | 37.6642 | 47.331 | 0 | 7.2692 | FALSE | FALSE
2025-06-25 14:00 | 41.6 | 23 | 99010 | 100 | 3000 | 26.7808 | 46.6182 | 60.7558 | 0 | 7.2692 | FALSE | FALSE
2025-06-25 15:00 | 39.7 | 36 | 98975 | 100 | 3000 | 26.0186 | 58.423 | 75.1417 | 0 | 7.2692 | FALSE | FALSE
2025-06-25 16:00 | 37.85 | 44 | 98985 | 100 | 3000 | 25.3417 | 64.5674 | 79.5225 | 0 | 7.2692 | FALSE | FALSE
2025-06-25 17:00 | 36.25 | 50.5 | 99010 | 100 | 3000 | 24.7617 | 69.0063 | 81.4722 | 0 | 7.2692 | FALSE | FALSE
2025-06-25 18:00 | 34.5 | 57.5 | 99035 | 100 | 3000 | 24.1261 | 73.3085 | 82.3273 | 0 | 7.2692 | FALSE | FALSE
2025-06-25 19:00 | 32.9 | 68 | 99080 | 100 | 3000 | 23.5206 | 79.9787 | 86.6405 | 0 | 7.2692 | FALSE | FALSE
2025-06-25 20:00 | 31.85 | 78.5 | 99135 | 100 | 3000 | 23.1087 | 86.6528 | 92.3632 | 0 | 7.2692 | FALSE | FALSE
2025-06-25 21:00 | 31.15 | 83 | 99195 | 100 | 3000 | 22.8462 | 89.0588 | 93.1719 | 0 | 7.2692 | FALSE | FALSE
2025-06-25 22:00 | 30.7 | 85 | 99225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-25 23:00 | 30.15 | 87 | 99220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-26 | 29.45 | 89 | 99200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-26 01:00 | 28.8 | 92 | 99190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-26 02:00 | 28.15 | 94.5 | 99200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-26 03:00 | 27.65 | 94 | 99215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-26 04:00 | 27.95 | 93.5 | 99235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-26 05:00 | 28.35 | 93.5 | 99265 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-26 06:00 | 28.95 | 89.5 | 99320 | 100 | 3000 | 22.0389 | 90.8374 | 87.4239 | 0 | 7.2692 | FALSE | FALSE
2025-06-26 07:00 | 30.7 | 79 | 99380 | 100 | 3000 | 22.7028 | 85.6555 | 86.9211 | 0 | 7.2692 | FALSE | FALSE
2025-06-26 08:00 | 32.95 | 66 | 99395 | 100 | 3000 | 23.5482 | 78.4772 | 84.7855 | 0 | 7.2692 | FALSE | FALSE
2025-06-26 09:00 | 35.4 | 53.5 | 99380 | 100 | 3000 | 24.4566 | 70.7915 | 81.628 | 0 | 7.2692 | FALSE | FALSE
2025-06-26 10:00 | 38.05 | 41 | 99355 | 100 | 3000 | 25.4337 | 61.9939 | 76.2554 | 0 | 7.2692 | FALSE | FALSE
2025-06-26 11:00 | 40.45 | 31.5 | 99310 | 100 | 3000 | 26.3091 | 54.4997 | 70.9886 | 0 | 7.2692 | FALSE | FALSE
2025-06-26 12:00 | 41.7 | 28.5 | 99255 | 100 | 3000 | 26.7451 | 52.1176 | 70.3463 | 0 | 7.2692 | FALSE | FALSE
2025-06-26 13:00 | 40.7 | 35.5 | 99220 | 100 | 3000 | 26.3441 | 58.5036 | 78.1481 | 0 | 7.2692 | FALSE | FALSE
2025-06-26 14:00 | 39.25 | 40 | 99175 | 100 | 3000 | 25.8334 | 61.8699 | 79.4531 | 0 | 7.2692 | FALSE | FALSE
2025-06-26 15:00 | 38.55 | 40 | 99140 | 100 | 3000 | 25.6064 | 61.4239 | 76.7215 | 0 | 7.2692 | FALSE | FALSE
2025-06-26 16:00 | 37.5 | 41 | 99135 | 100 | 3000 | 25.2514 | 61.6737 | 74.0574 | 0 | 7.2692 | FALSE | FALSE
2025-06-26 17:00 | 36.1 | 46 | 99130 | 100 | 3000 | 24.7436 | 65.0884 | 75.1233 | 0 | 7.2692 | FALSE | FALSE
2025-06-26 18:00 | 34.6 | 56 | 99140 | 100 | 3000 | 24.1693 | 72.1817 | 81.0344 | 0 | 7.2692 | FALSE | FALSE
2025-06-26 19:00 | 33.45 | 64 | 99165 | 100 | 3000 | 23.7306 | 77.4493 | 84.9208 | 0 | 7.2692 | FALSE | FALSE
2025-06-26 20:00 | 32.75 | 69.5 | 99210 | 100 | 3000 | 23.4617 | 80.9486 | 87.5496 | 0 | 7.2692 | FALSE | FALSE
2025-06-26 21:00 | 32.25 | 72 | 99265 | 100 | 3000 | 23.2767 | 82.2885 | 87.7235 | 0 | 7.2692 | FALSE | FALSE
2025-06-26 22:00 | 31.7 | 75.5 | 99295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-26 23:00 | 31 | 80.5 | 99300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-27 | 30.2 | 85.5 | 99280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-27 01:00 | 29.5 | 89.5 | 99265 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-27 02:00 | 28.9 | 92.5 | 99270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-27 03:00 | 28.45 | 94 | 99280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-27 04:00 | 28.6 | 88.5 | 99275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-27 05:00 | 28.95 | 80.5 | 99275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-27 06:00 | 30.15 | 69 | 99300 | 100 | 3000 | 22.5399 | 78.0842 | 74.5096 | 0 | 7.2692 | FALSE | FALSE
2025-06-27 07:00 | 33 | 53 | 99315 | 100 | 3000 | 23.6293 | 68.6037 | 70.6957 | 0 | 7.2692 | FALSE | FALSE
2025-06-27 08:00 | 36.6 | 40 | 99320 | 100 | 3000 | 24.9565 | 60.2792 | 69.3283 | 0 | 7.2692 | FALSE | FALSE
2025-06-27 09:00 | 40.1 | 28 | 99305 | 100 | 3000 | 26.2328 | 51.0085 | 64.3327 | 0 | 7.2692 | FALSE | FALSE
2025-06-27 10:00 | 42.85 | 18.5 | 99270 | 100 | 3000 | 27.2452 | 42.2953 | 56.5371 | 0 | 7.2692 | FALSE | FALSE
2025-06-27 11:00 | 44.4 | 15 | 99220 | 100 | 3000 | 27.7963 | 38.7941 | 53.9712 | 0 | 7.2692 | FALSE | FALSE
2025-06-27 12:00 | 43.25 | 24 | 99170 | 100 | 3000 | 27.2956 | 48.1154 | 67.4897 | 0 | 7.2692 | FALSE | FALSE
2025-06-27 13:00 | 41.2 | 33.5 | 99125 | 100 | 3000 | 26.5254 | 56.8432 | 76.7644 | 0 | 7.2692 | FALSE | FALSE
2025-06-27 14:00 | 40.25 | 35 | 99075 | 100 | 3000 | 26.2062 | 57.7746 | 75.6646 | 0 | 7.2692 | FALSE | FALSE
2025-06-27 15:00 | 39.4 | 37.5 | 99030 | 100 | 3000 | 25.9065 | 59.65 | 76.2879 | 0 | 7.2692 | FALSE | FALSE
2025-06-27 16:00 | 38 | 41.5 | 99030 | 100 | 3000 | 25.4125 | 62.4364 | 76.666 | 0 | 7.2692 | FALSE | FALSE
2025-06-27 17:00 | 36.15 | 48.5 | 99065 | 100 | 3000 | 24.7427 | 67.236 | 78.5083 | 0 | 7.2692 | FALSE | FALSE
2025-06-27 18:00 | 34.75 | 55.5 | 99100 | 100 | 3000 | 24.2233 | 71.9083 | 81.0994 | 0 | 7.2692 | FALSE | FALSE
2025-06-27 19:00 | 33.85 | 59 | 99130 | 100 | 3000 | 23.895 | 73.9233 | 81.1364 | 0 | 7.2692 | FALSE | FALSE
2025-06-27 20:00 | 33.25 | 62 | 99165 | 100 | 3000 | 23.6719 | 75.7188 | 81.7584 | 0 | 7.2692 | FALSE | FALSE
2025-06-27 21:00 | 32.75 | 65.5 | 99215 | 100 | 3000 | 23.4809 | 77.9206 | 83.2446 | 0 | 7.2692 | FALSE | FALSE
2025-06-27 22:00 | 32.15 | 68 | 99235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-27 23:00 | 31.35 | 71.5 | 99230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-28 | 30.55 | 75.5 | 99210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-28 01:00 | 29.95 | 77.5 | 99170 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-28 02:00 | 29.4 | 79 | 99155 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-28 03:00 | 28.8 | 80.5 | 99165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-28 04:00 | 29.2 | 71.5 | 99175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-28 05:00 | 30.1 | 64.5 | 99195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-28 06:00 | 31 | 70 | 99225 | 100 | 3000 | 22.8435 | 79.5693 | 79.5246 | 0 | 7.2692 | FALSE | FALSE
2025-06-28 07:00 | 32.85 | 68 | 99240 | 100 | 3000 | 23.5036 | 79.9125 | 86.4331 | 0 | 7.2692 | FALSE | FALSE
2025-06-28 08:00 | 35.95 | 53.5 | 99245 | 100 | 3000 | 24.6408 | 71.2641 | 84.0223 | 0 | 7.2692 | FALSE | FALSE
2025-06-28 09:00 | 39.45 | 36.5 | 99235 | 100 | 3000 | 25.9329 | 58.7291 | 75.0452 | 0 | 7.2692 | FALSE | FALSE
2025-06-28 10:00 | 42.1 | 25.5 | 99210 | 100 | 3000 | 26.9107 | 49.2603 | 66.5665 | 0 | 7.2692 | FALSE | FALSE
2025-06-28 11:00 | 43.2 | 24.5 | 99175 | 100 | 3000 | 27.2727 | 48.6203 | 68.2314 | 0 | 7.2692 | FALSE | FALSE
2025-06-28 12:00 | 41.9 | 35 | 99125 | 100 | 3000 | 26.7253 | 58.7514 | 81.7831 | 0 | 7.2692 | FALSE | FALSE
2025-06-28 13:00 | 39.75 | 45 | 99090 | 100 | 3000 | 25.941 | 66.9255 | 88.8429 | 0 | 7.2692 | FALSE | FALSE
2025-06-28 14:00 | 38.5 | 49 | 99045 | 100 | 3000 | 25.5072 | 69.5641 | 89.2246 | 0 | 7.2692 | FALSE | FALSE
2025-06-28 15:00 | 37.65 | 52 | 99000 | 100 | 3000 | 25.2087 | 71.4945 | 89.5749 | 0 | 7.2692 | FALSE | FALSE
2025-06-28 16:00 | 37 | 53 | 98995 | 100 | 3000 | 24.99 | 71.7809 | 87.9932 | 0 | 7.2692 | FALSE | FALSE
2025-06-28 17:00 | 36.25 | 55.5 | 98985 | 100 | 3000 | 24.7255 | 73.2368 | 87.8217 | 0 | 7.2692 | FALSE | FALSE
2025-06-28 18:00 | 35 | 61.5 | 98980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-28 19:00 | 33.85 | 67.5 | 99010 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-28 20:00 | 33.1 | 71 | 99045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-28 21:00 | 32.35 | 74 | 99090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-28 22:00 | 31.45 | 78 | 99125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-28 23:00 | 30.5 | 83 | 99125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 | 29.6 | 88.5 | 99100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 01:00 | 28.85 | 93 | 99065 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 02:00 | 28.3 | 95.5 | 99050 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 03:00 | 27.8 | 96.5 | 99055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 04:00 | 28.15 | 90 | 99065 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 05:00 | 28.65 | 84 | 99090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 06:00 | 29.1 | 81.5 | 99120 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 07:00 | 30.75 | 73 | 99140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 08:00 | 33.05 | 61 | 99150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 09:00 | 35.15 | 49 | 99140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 10:00 | 36.75 | 42 | 99120 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 11:00 | 36.85 | 45 | 99090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 12:00 | 36.2 | 50 | 99055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 13:00 | 36.15 | 48.5 | 99020 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 14:00 | 36.15 | 45.5 | 98970 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 15:00 | 36.35 | 42.5 | 98920 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 16:00 | 35.9 | 44.5 | 98900 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 17:00 | 34.95 | 50 | 98890 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 18:00 | 33.9 | 56.5 | 98905 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 19:00 | 32.6 | 64.5 | 98955 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 20:00 | 31.7 | 69 | 99005 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 21:00 | 31.1 | 71 | 99045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 22:00 | 30.45 | 73.5 | 99055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-29 23:00 | 29.7 | 76 | 99035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-30 | 28.9 | 77.5 | 99005 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-30 01:00 | 28.2 | 78.5 | 98975 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-30 02:00 | 27.6 | 80.5 | 98945 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-30 03:00 | 27.15 | 82 | 98935 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-30 04:00 | 27.85 | 78.5 | 98950 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-30 05:00 | 28.7 | 73.5 | 99000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-30 06:00 | 29.2 | 68 | 99065 | 100 | 3000 | 22.1933 | 76.6333 | 69.1059 | 0 | 7.2692 | FALSE | FALSE
2025-06-30 07:00 | 31.05 | 57 | 99105 | 100 | 3000 | 22.911 | 70.2869 | 66.6418 | 0 | 7.2692 | FALSE | FALSE
2025-06-30 08:00 | 33.85 | 44.5 | 99135 | 100 | 3000 | 23.9738 | 62.5374 | 64.3983 | 0 | 7.2692 | FALSE | FALSE
2025-06-30 09:00 | 36.25 | 37 | 99145 | 100 | 3000 | 24.8584 | 57.5703 | 64.0513 | 0 | 7.2692 | FALSE | FALSE
2025-06-30 10:00 | 37.65 | 34.5 | 99145 | 100 | 3000 | 25.3551 | 56.0201 | 65.6364 | 0 | 7.2692 | FALSE | FALSE
2025-06-30 11:00 | 38.05 | 35.5 | 99140 | 100 | 3000 | 25.4811 | 57.092 | 68.4573 | 0 | 7.2692 | FALSE | FALSE
2025-06-30 12:00 | 38.1 | 37 | 99095 | 100 | 3000 | 25.4848 | 58.4635 | 70.7467 | 0 | 7.2692 | FALSE | FALSE
2025-06-30 13:00 | 38.1 | 38.5 | 99025 | 100 | 3000 | 25.4716 | 59.8132 | 72.8434 | 0 | 7.2692 | FALSE | FALSE
2025-06-30 14:00 | 37.85 | 41 | 98970 | 100 | 3000 | 25.3673 | 61.9014 | 75.368 | 0 | 7.2692 | FALSE | FALSE
2025-06-30 15:00 | 37.5 | 43.5 | 98930 | 100 | 3000 | 25.2306 | 63.8899 | 77.4122 | 0 | 7.2692 | FALSE | FALSE
2025-06-30 16:00 | 36.95 | 46.5 | 98925 | 100 | 3000 | 25.0244 | 66.1232 | 79.2001 | 0 | 7.2692 | FALSE | FALSE
2025-06-30 17:00 | 36 | 52 | 98940 | 100 | 3000 | 24.6675 | 70.0752 | 82.2748 | 0 | 7.2692 | FALSE | FALSE
2025-06-30 18:00 | 34.65 | 61.5 | 98960 | 100 | 3000 | 24.1528 | 76.6628 | 87.7015 | 0 | 7.2692 | FALSE | FALSE
2025-06-30 19:00 | 33.5 | 69.5 | 99010 | 100 | 3000 | 23.7185 | 81.7739 | 91.2339 | 0 | 7.2692 | FALSE | FALSE
2025-06-30 20:00 | 32.7 | 74 | 99065 | 100 | 3000 | 23.4226 | 84.3078 | 92.0725 | 0 | 7.2692 | FALSE | FALSE
2025-06-30 21:00 | 31.95 | 77.5 | 99095 | 100 | 3000 | 23.1477 | 86.0399 | 91.8541 | 0 | 7.2692 | FALSE | FALSE
2025-06-30 22:00 | 31.2 | 81.5 | 99100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-06-30 23:00 | 30.45 | 84.5 | 99100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-01 | 29.75 | 84 | 99090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-01 01:00 | 29 | 82 | 99070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-01 02:00 | 28.25 | 82 | 99060 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-01 03:00 | 27.6 | 84 | 99080 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-01 04:00 | 27.5 | 80.5 | 99100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-01 05:00 | 27.65 | 74 | 99125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-01 06:00 | 28.5 | 66.5 | 99180 | 100 | 3000 | 21.9357 | 75.092 | 64.589 | 0 | 7.2692 | FALSE | FALSE
2025-07-01 07:00 | 30.8 | 55 | 99235 | 100 | 3000 | 22.827 | 68.6834 | 63.5927 | 0 | 7.2692 | FALSE | FALSE
2025-07-01 08:00 | 33.6 | 44 | 99280 | 100 | 3000 | 23.8877 | 62.0068 | 62.8944 | 0 | 7.2692 | FALSE | FALSE
2025-07-01 09:00 | 36.2 | 35.5 | 99295 | 100 | 3000 | 24.8517 | 56.2677 | 61.9501 | 0 | 7.2692 | FALSE | FALSE
2025-07-01 10:00 | 38.5 | 29 | 99275 | 100 | 3000 | 25.6896 | 51.4061 | 60.686 | 0 | 7.2692 | FALSE | FALSE
2025-07-01 11:00 | 40.5 | 24.5 | 99235 | 100 | 3000 | 26.4024 | 47.7857 | 60.0194 | 0 | 7.2692 | FALSE | FALSE
2025-07-01 12:00 | 41.8 | 23 | 99175 | 100 | 3000 | 26.8458 | 46.6572 | 61.3967 | 0 | 7.2692 | FALSE | FALSE
2025-07-01 13:00 | 42.15 | 22 | 99105 | 100 | 3000 | 26.9719 | 45.744 | 60.6857 | 0 | 7.2692 | FALSE | FALSE
2025-07-01 14:00 | 41.75 | 21.5 | 99050 | 100 | 3000 | 26.8482 | 45.1544 | 58.6685 | 0 | 7.2692 | FALSE | FALSE
2025-07-01 15:00 | 41 | 24 | 99015 | 100 | 3000 | 26.5727 | 47.4488 | 60.6391 | 0 | 7.2692 | FALSE | FALSE
2025-07-01 16:00 | 40.1 | 27.5 | 99010 | 100 | 3000 | 26.2381 | 50.5557 | 63.4612 | 0 | 7.2692 | FALSE | FALSE
2025-07-01 17:00 | 38.5 | 34 | 99025 | 100 | 3000 | 25.6445 | 55.9604 | 67.8771 | 0 | 7.2692 | FALSE | FALSE
2025-07-01 18:00 | 36.3 | 46.5 | 99030 | 100 | 3000 | 24.8074 | 65.6551 | 76.5544 | 0 | 7.2692 | FALSE | FALSE
2025-07-01 19:00 | 34.5 | 58 | 99040 | 100 | 3000 | 24.1232 | 73.7083 | 82.9158 | 0 | 7.2692 | FALSE | FALSE
2025-07-01 20:00 | 33.35 | 65 | 99075 | 100 | 3000 | 23.6909 | 78.133 | 85.533 | 0 | 7.2692 | FALSE | FALSE
2025-07-01 21:00 | 32.35 | 72 | 99130 | 100 | 3000 | 23.3112 | 82.4091 | 88.1947 | 0 | 7.2692 | FALSE | FALSE
2025-07-01 22:00 | 31.35 | 81 | 99180 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-01 23:00 | 30.6 | 88 | 99190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-02 | 29.85 | 91 | 99170 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-02 01:00 | 29 | 92 | 99160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-02 02:00 | 28.25 | 92.5 | 99145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-02 03:00 | 27.65 | 92.5 | 99145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-02 04:00 | 27.8 | 88.5 | 99160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-02 05:00 | 28 | 84 | 99190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-02 06:00 | 28.5 | 78 | 99245 | 100 | 3000 | 21.9052 | 82.7057 | 74.8569 | 0 | 7.2692 | FALSE | FALSE
2025-07-02 07:00 | 30.7 | 66 | 99290 | 100 | 3000 | 22.7504 | 76.442 | 74.1478 | 0 | 7.2692 | FALSE | FALSE
2025-07-02 08:00 | 33.4 | 54.5 | 99315 | 100 | 3000 | 23.7627 | 70.0397 | 74.0796 | 0 | 7.2692 | FALSE | FALSE
2025-07-02 09:00 | 35.6 | 46 | 99325 | 100 | 3000 | 24.5738 | 64.7446 | 73.1524 | 0 | 7.2692 | FALSE | FALSE
2025-07-02 10:00 | 37.4 | 39.5 | 99310 | 100 | 3000 | 25.2303 | 60.2837 | 71.6724 | 0 | 7.2692 | FALSE | FALSE
2025-07-02 11:00 | 38.75 | 36 | 99260 | 100 | 3000 | 25.709 | 57.8841 | 71.7398 | 0 | 7.2692 | FALSE | FALSE
2025-07-02 12:00 | 39.5 | 36.5 | 99195 | 100 | 3000 | 25.9491 | 58.7608 | 75.2189 | 0 | 7.2692 | FALSE | FALSE
2025-07-02 13:00 | 39.5 | 39.5 | 99140 | 100 | 3000 | 25.9187 | 61.571 | 79.678 | 0 | 7.2692 | FALSE | FALSE
2025-07-02 14:00 | 39 | 41.5 | 99090 | 100 | 3000 | 25.7382 | 63.0956 | 80.6337 | 0 | 7.2692 | FALSE | FALSE
2025-07-02 15:00 | 38.25 | 44 | 99045 | 100 | 3000 | 25.4723 | 64.8468 | 81.1652 | 0 | 7.2692 | FALSE | FALSE
2025-07-02 16:00 | 37.15 | 48 | 99045 | 100 | 3000 | 25.0789 | 67.5634 | 82.0598 | 0 | 7.2692 | FALSE | FALSE
2025-07-02 17:00 | 35.6 | 55 | 99060 | 100 | 3000 | 24.5133 | 72.2285 | 84.2797 | 0 | 7.2692 | FALSE | FALSE
2025-07-02 18:00 | 33.95 | 65.5 | 99085 | 100 | 3000 | 23.8932 | 79.1262 | 88.9916 | 0 | 7.2692 | FALSE | FALSE
2025-07-02 19:00 | 32.8 | 73.5 | 99145 | 100 | 3000 | 23.4594 | 84.0373 | 92.0708 | 0 | 7.2692 | FALSE | FALSE
2025-07-02 20:00 | 32.15 | 77 | 99195 | 100 | 3000 | 23.2194 | 85.8972 | 92.4044 | 0 | 7.2692 | FALSE | FALSE
2025-07-02 21:00 | 31.75 | 78.5 | 99225 | 100 | 3000 | 23.0741 | 86.5249 | 91.8584 | 0 | 7.2692 | FALSE | FALSE
2025-07-02 22:00 | 31.45 | 80 | 99235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-02 23:00 | 31.15 | 82.5 | 99225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-03 | 30.75 | 85 | 99210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-03 01:00 | 30.25 | 86.5 | 99195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-03 02:00 | 29.75 | 87 | 99180 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-03 03:00 | 29.2 | 87 | 99165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-03 04:00 | 29 | 88.5 | 99185 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-03 05:00 | 29.05 | 90 | 99240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-03 06:00 | 29.5 | 86.5 | 99300 | 100 | 3000 | 22.2472 | 89.4788 | 87.6698 | 0 | 7.2692 | FALSE | FALSE
2025-07-03 07:00 | 31.1 | 75.5 | 99345 | 100 | 3000 | 22.8581 | 83.6031 | 85.5188 | 0 | 7.2692 | FALSE | FALSE
2025-07-03 08:00 | 33.3 | 61.5 | 99345 | 100 | 3000 | 23.692 | 75.3622 | 81.4775 | 0 | 7.2692 | FALSE | FALSE
2025-07-03 09:00 | 35.5 | 49.5 | 99315 | 100 | 3000 | 24.5166 | 67.5747 | 77.1043 | 0 | 7.2692 | FALSE | FALSE
2025-07-03 10:00 | 37.85 | 39 | 99285 | 100 | 3000 | 25.3846 | 60.0969 | 72.6757 | 0 | 7.2692 | FALSE | FALSE
2025-07-03 11:00 | 39.9 | 32 | 99235 | 100 | 3000 | 26.1252 | 54.7295 | 69.8418 | 0 | 7.2692 | FALSE | FALSE
2025-07-03 12:00 | 40.7 | 32.5 | 99175 | 100 | 3000 | 26.3782 | 55.5974 | 73.3977 | 0 | 7.2692 | FALSE | FALSE
2025-07-03 13:00 | 40.1 | 38 | 99130 | 100 | 3000 | 26.1259 | 60.5445 | 79.7317 | 0 | 7.2692 | FALSE | FALSE
2025-07-03 14:00 | 39.1 | 42 | 99095 | 100 | 3000 | 25.7655 | 63.6262 | 81.7614 | 0 | 7.2692 | FALSE | FALSE
2025-07-03 15:00 | 38.15 | 46 | 99060 | 100 | 3000 | 25.4221 | 66.5682 | 83.548 | 0 | 7.2692 | FALSE | FALSE
2025-07-03 16:00 | 36.7 | 53 | 99045 | 100 | 3000 | 24.8921 | 71.5091 | 86.6665 | 0 | 7.2692 | FALSE | FALSE
2025-07-03 17:00 | 35.2 | 60 | 99055 | 100 | 3000 | 24.3467 | 75.9755 | 88.5351 | 0 | 7.2692 | FALSE | FALSE
2025-07-03 18:00 | 33.85 | 68 | 99080 | 100 | 3000 | 23.8454 | 80.9821 | 91.3225 | 0 | 7.2692 | FALSE | FALSE
2025-07-03 19:00 | 32.65 | 77 | 99120 | 100 | 3000 | 23.3911 | 86.5052 | 95.0062 | 0 | 7.2692 | FALSE | FALSE
2025-07-03 20:00 | 32 | 83 | 99175 | 100 | 3000 | 23.1409 | 90.1476 | 97.7676 | 0 | 7.2692 | FALSE | FALSE
2025-07-03 21:00 | 31.7 | 86 | 99230 | 100 | 3000 | 23.0249 | 91.9421 | 99.1663 | 0 | 7.2692 | FALSE | FALSE
2025-07-03 22:00 | 31.5 | 87 | 99250 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-03 23:00 | 31.15 | 87.5 | 99235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-04 | 30.6 | 88 | 99200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-04 01:00 | 30.05 | 87.5 | 99175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-04 02:00 | 29.55 | 86.5 | 99175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-04 03:00 | 29.05 | 85.5 | 99200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-04 04:00 | 28.85 | 84 | 99240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-04 05:00 | 28.8 | 82 | 99290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-04 06:00 | 29.25 | 78 | 99340 | 100 | 3000 | 22.1822 | 83.4268 | 78.5969 | 0 | 7.2692 | FALSE | FALSE
2025-07-04 07:00 | 30.9 | 69 | 99380 | 100 | 3000 | 22.8116 | 78.746 | 78.0813 | 0 | 7.2692 | FALSE | FALSE
2025-07-04 08:00 | 33.1 | 57 | 99400 | 100 | 3000 | 23.6449 | 71.731 | 75.5887 | 0 | 7.2692 | FALSE | FALSE
2025-07-04 09:00 | 35.25 | 46 | 99405 | 100 | 3000 | 24.4539 | 64.5163 | 71.766 | 0 | 7.2692 | FALSE | FALSE
2025-07-04 10:00 | 37.3 | 37 | 99390 | 100 | 3000 | 25.2167 | 58.0361 | 67.906 | 0 | 7.2692 | FALSE | FALSE
2025-07-04 11:00 | 39.3 | 30 | 99335 | 100 | 3000 | 25.9481 | 52.5966 | 64.7981 | 0 | 7.2692 | FALSE | FALSE
2025-07-04 12:00 | 41.3 | 24 | 99260 | 100 | 3000 | 26.6709 | 47.5109 | 61.6135 | 0 | 7.2692 | FALSE | FALSE
2025-07-04 13:00 | 42.65 | 20 | 99185 | 100 | 3000 | 27.1601 | 43.8098 | 58.6336 | 0 | 7.2692 | FALSE | FALSE
2025-07-04 14:00 | 41.6 | 30 | 99145 | 100 | 3000 | 26.6946 | 53.5783 | 72.4627 | 0 | 7.2692 | FALSE | FALSE
2025-07-04 15:00 | 39.3 | 43 | 99125 | 100 | 3000 | 25.8195 | 64.696 | 84.0393 | 0 | 7.2692 | FALSE | FALSE
2025-07-04 16:00 | 37.8 | 48 | 99115 | 100 | 3000 | 25.2913 | 68.0717 | 84.8403 | 0 | 7.2692 | FALSE | FALSE
2025-07-04 17:00 | 36.45 | 53 | 99115 | 100 | 3000 | 24.8099 | 71.2839 | 85.5729 | 0 | 7.2692 | FALSE | FALSE
2025-07-04 18:00 | 35 | 59.5 | 99135 | 100 | 3000 | 24.2831 | 75.3679 | 87.0198 | 0 | 7.2692 | FALSE | FALSE
2025-07-04 19:00 | 33.7 | 69.5 | 99200 | 100 | 3000 | 23.7867 | 81.9777 | 92.2826 | 0 | 7.2692 | FALSE | FALSE
2025-07-04 20:00 | 32.85 | 76.5 | 99275 | 100 | 3000 | 23.4621 | 86.3569 | 95.5635 | 0 | 7.2692 | FALSE | FALSE
2025-07-04 21:00 | 32.45 | 78 | 99340 | 100 | 3000 | 23.3183 | 86.9901 | 95.0542 | 0 | 7.2692 | FALSE | FALSE
2025-07-04 22:00 | 32.1 | 78.5 | 99370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-04 23:00 | 31.6 | 80.5 | 99345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-05 | 31.05 | 84.5 | 99310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-05 01:00 | 30.55 | 88.5 | 99305 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-05 02:00 | 30.15 | 90.5 | 99305 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-05 03:00 | 29.8 | 91 | 99305 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-05 04:00 | 29.7 | 90.5 | 99305 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-05 05:00 | 29.65 | 90 | 99320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-05 06:00 | 30 | 86 | 99375 | 100 | 3000 | 22.4286 | 89.734 | 89.906 | 0 | 7.2692 | FALSE | FALSE
2025-07-05 07:00 | 31.5 | 75 | 99425 | 100 | 3000 | 23.0015 | 83.6676 | 87.0625 | 0 | 7.2692 | FALSE | FALSE
2025-07-05 08:00 | 33.55 | 61 | 99445 | 100 | 3000 | 23.7812 | 75.1904 | 82.0996 | 0 | 7.2692 | FALSE | FALSE
2025-07-05 09:00 | 35.6 | 49 | 99425 | 100 | 3000 | 24.5539 | 67.2233 | 76.93 | 0 | 7.2692 | FALSE | FALSE
2025-07-05 10:00 | 37.6 | 40.5 | 99385 | 100 | 3000 | 25.289 | 61.272 | 73.827 | 0 | 7.2692 | FALSE | FALSE
2025-07-05 11:00 | 39.3 | 35.5 | 99335 | 100 | 3000 | 25.8942 | 57.7071 | 73.0321 | 0 | 7.2692 | FALSE | FALSE
2025-07-05 12:00 | 40.1 | 34.5 | 99265 | 100 | 3000 | 26.1636 | 57.1998 | 74.4047 | 0 | 7.2692 | FALSE | FALSE
2025-07-05 13:00 | 39.9 | 36.5 | 99200 | 100 | 3000 | 26.078 | 58.9916 | 76.71 | 0 | 7.2692 | FALSE | FALSE
2025-07-05 14:00 | 39.4 | 37.5 | 99150 | 100 | 3000 | 25.9066 | 59.6401 | 76.3236 | 0 | 7.2692 | FALSE | FALSE
2025-07-05 15:00 | 38.35 | 42 | 99125 | 100 | 3000 | 25.5229 | 63.1068 | 78.7763 | 0 | 7.2692 | FALSE | FALSE
2025-07-05 16:00 | 36.4 | 52 | 99125 | 100 | 3000 | 24.8008 | 70.3901 | 84.0734 | 0 | 7.2692 | FALSE | FALSE
2025-07-05 17:00 | 34.45 | 62 | 99135 | 100 | 3000 | 24.0827 | 76.8516 | 87.3831 | 0 | 7.2692 | FALSE | FALSE
2025-07-05 18:00 | 32.9 | 73.5 | 99175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-05 19:00 | 31.95 | 82 | 99240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-05 20:00 | 31.7 | 81.5 | 99285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-05 21:00 | 31.7 | 75 | 99330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-05 22:00 | 31.7 | 68.5 | 99355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-05 23:00 | 31.5 | 66.5 | 99335 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 | 31.05 | 68 | 99300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 01:00 | 30.55 | 69 | 99265 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 02:00 | 30.25 | 68.5 | 99250 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 03:00 | 29.85 | 68.5 | 99260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 04:00 | 29.55 | 69 | 99255 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 05:00 | 29.45 | 68.5 | 99260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 06:00 | 29.8 | 66 | 99295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 07:00 | 31.3 | 59 | 99320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 08:00 | 33.3 | 51 | 99330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 09:00 | 35.3 | 45 | 99320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 10:00 | 37.15 | 40 | 99285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 11:00 | 38.35 | 38 | 99245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 12:00 | 38.5 | 39 | 99200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 13:00 | 37.95 | 41 | 99145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 14:00 | 37.1 | 44.5 | 99110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 15:00 | 36.05 | 50.5 | 99090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 16:00 | 34.9 | 55.5 | 99105 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 17:00 | 33.85 | 58.5 | 99140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 18:00 | 32.9 | 59.5 | 99180 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 19:00 | 32.1 | 60 | 99225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 20:00 | 31.65 | 62 | 99265 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 21:00 | 31.4 | 64 | 99325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 22:00 | 31.1 | 65.5 | 99350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-06 23:00 | 30.6 | 66.5 | 99325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-07 | 30 | 68.5 | 99290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-07 01:00 | 29.35 | 70.5 | 99255 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-07 02:00 | 28.65 | 71 | 99245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-07 03:00 | 28 | 71.5 | 99250 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-07 04:00 | 27.9 | 70.5 | 99235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-07 05:00 | 28.05 | 68.5 | 99240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-07 06:00 | 28.55 | 65 | 99300 | 100 | 3000 | 21.9586 | 74.1189 | 63.4832 | 0 | 7.2692 | FALSE | FALSE
2025-07-07 07:00 | 30.2 | 58 | 99370 | 100 | 3000 | 22.5955 | 70.4226 | 64.0765 | 0 | 7.2692 | FALSE | FALSE
2025-07-07 08:00 | 32.4 | 49.5 | 99390 | 100 | 3000 | 23.4314 | 65.5728 | 64.3965 | 0 | 7.2692 | FALSE | FALSE
2025-07-07 09:00 | 34.5 | 40.5 | 99365 | 100 | 3000 | 24.2259 | 59.6556 | 62.1513 | 0 | 7.2692 | FALSE | FALSE
2025-07-07 10:00 | 36.4 | 32.5 | 99335 | 100 | 3000 | 24.9423 | 53.7934 | 58.6888 | 0 | 7.2692 | FALSE | FALSE
2025-07-07 11:00 | 37.85 | 28 | 99310 | 100 | 3000 | 25.4772 | 50.3156 | 57.1901 | 0 | 7.2692 | FALSE | FALSE
2025-07-07 12:00 | 38.35 | 29.5 | 99280 | 100 | 3000 | 25.6345 | 51.8098 | 60.9302 | 0 | 7.2692 | FALSE | FALSE
2025-07-07 13:00 | 37.95 | 34.5 | 99230 | 100 | 3000 | 25.4562 | 56.1452 | 66.7145 | 0 | 7.2692 | FALSE | FALSE
2025-07-07 14:00 | 37.5 | 37 | 99195 | 100 | 3000 | 25.2841 | 58.1504 | 68.5801 | 0 | 7.2692 | FALSE | FALSE
2025-07-07 15:00 | 37 | 39.5 | 99175 | 100 | 3000 | 25.0957 | 60.0757 | 70.1277 | 0 | 7.2692 | FALSE | FALSE
2025-07-07 16:00 | 36.15 | 42.5 | 99165 | 100 | 3000 | 24.7852 | 62.1661 | 70.8322 | 0 | 7.2692 | FALSE | FALSE
2025-07-07 17:00 | 34.95 | 46.5 | 99170 | 100 | 3000 | 24.3471 | 64.7585 | 71.1171 | 0 | 7.2692 | FALSE | FALSE
2025-07-07 18:00 | 33.55 | 53 | 99210 | 100 | 3000 | 23.823 | 68.9934 | 72.9975 | 0 | 7.2692 | FALSE | FALSE
2025-07-07 19:00 | 32.55 | 58 | 99270 | 100 | 3000 | 23.4461 | 72.0781 | 74.2295 | 0 | 7.2692 | FALSE | FALSE
2025-07-07 20:00 | 31.9 | 62.5 | 99315 | 100 | 3000 | 23.1953 | 74.9087 | 76.1096 | 0 | 7.2692 | FALSE | FALSE
2025-07-07 21:00 | 31.4 | 66.5 | 99370 | 100 | 3000 | 23.0005 | 77.3992 | 77.9328 | 0 | 7.2692 | FALSE | FALSE
2025-07-07 22:00 | 30.95 | 68.5 | 99400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-07 23:00 | 30.4 | 69 | 99390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-08 | 29.75 | 69.5 | 99350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-08 01:00 | 29.05 | 70.5 | 99300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-08 02:00 | 28.5 | 71.5 | 99280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-08 03:00 | 28.05 | 73 | 99275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-08 04:00 | 28.1 | 72 | 99285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-08 05:00 | 28.25 | 69.5 | 99310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-08 06:00 | 28.55 | 66.5 | 99355 | 100 | 3000 | 21.9546 | 75.1105 | 64.8431 | 0 | 7.2692 | FALSE | FALSE
2025-07-08 07:00 | 30.1 | 59.5 | 99420 | 100 | 3000 | 22.5535 | 71.4024 | 65.1205 | 0 | 7.2692 | FALSE | FALSE
2025-07-08 08:00 | 32.25 | 51 | 99465 | 100 | 3000 | 23.3707 | 66.6034 | 65.433 | 0 | 7.2692 | FALSE | FALSE
2025-07-08 09:00 | 34.25 | 42 | 99475 | 100 | 3000 | 24.1291 | 60.7288 | 63.0494 | 0 | 7.2692 | FALSE | FALSE
2025-07-08 10:00 | 36 | 34 | 99455 | 100 | 3000 | 24.7927 | 54.9149 | 59.3431 | 0 | 7.2692 | FALSE | FALSE
2025-07-08 11:00 | 37.4 | 29.5 | 99420 | 100 | 3000 | 25.3105 | 51.5058 | 57.906 | 0 | 7.2692 | FALSE | FALSE
2025-07-08 12:00 | 38.1 | 28.5 | 99370 | 100 | 3000 | 25.5583 | 50.8265 | 58.7105 | 0 | 7.2692 | FALSE | FALSE
2025-07-08 13:00 | 38.15 | 28 | 99315 | 100 | 3000 | 25.5797 | 50.3969 | 58.1332 | 0 | 7.2692 | FALSE | FALSE
2025-07-08 14:00 | 37.95 | 26.5 | 99280 | 100 | 3000 | 25.524 | 49.0073 | 55.3479 | 0 | 7.2692 | FALSE | FALSE
2025-07-08 15:00 | 37.5 | 26.5 | 99255 | 100 | 3000 | 25.369 | 48.9094 | 53.9737 | 0 | 7.2692 | FALSE | FALSE
2025-07-08 16:00 | 36.75 | 28.5 | 99245 | 100 | 3000 | 25.0932 | 50.4794 | 54.4265 | 0 | 7.2692 | FALSE | FALSE
2025-07-08 17:00 | 35.8 | 31 | 99255 | 100 | 3000 | 24.743 | 52.3561 | 54.729 | 0 | 7.2692 | FALSE | FALSE
2025-07-08 18:00 | 34.8 | 32.5 | 99280 | 100 | 3000 | 24.3793 | 53.3207 | 53.3867 | 0 | 7.2692 | FALSE | FALSE
2025-07-08 19:00 | 33.75 | 35 | 99325 | 100 | 3000 | 23.9886 | 55.0207 | 52.9371 | 0 | 7.2692 | FALSE | FALSE
2025-07-08 20:00 | 32.6 | 40.5 | 99375 | 100 | 3000 | 23.5447 | 58.881 | 55.251 | 0 | 7.2692 | FALSE | FALSE
2025-07-08 21:00 | 31.55 | 46.5 | 99425 | 100 | 3000 | 23.1351 | 62.9142 | 57.8671 | 0 | 7.2692 | FALSE | FALSE
2025-07-08 22:00 | 30.7 | 50 | 99445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-08 23:00 | 29.95 | 52.5 | 99430 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-09 | 29.2 | 54.5 | 99405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-09 01:00 | 28.45 | 54.5 | 99375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-09 02:00 | 27.75 | 53 | 99345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-09 03:00 | 27.15 | 51.5 | 99330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-09 04:00 | 27.15 | 50 | 99330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-09 05:00 | 27.25 | 48.5 | 99345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-09 06:00 | 27.8 | 44.5 | 99400 | 100 | 3000 | 21.7221 | 60.2665 | 42.17 | 0 | 7.2692 | FALSE | FALSE
2025-07-09 07:00 | 29.85 | 37.5 | 99460 | 100 | 3000 | 22.5309 | 55.9563 | 42.6455 | 0 | 7.2692 | FALSE | FALSE
2025-07-09 08:00 | 32.45 | 31.5 | 99495 | 100 | 3000 | 23.5302 | 52.0314 | 44.7396 | 0 | 7.2692 | FALSE | FALSE
2025-07-09 09:00 | 34.8 | 27 | 99505 | 100 | 3000 | 24.4118 | 48.8445 | 46.5982 | 0 | 7.2692 | FALSE | FALSE
2025-07-09 10:00 | 36.75 | 23 | 99475 | 100 | 3000 | 25.1337 | 45.7313 | 46.9883 | 0 | 7.2692 | FALSE | FALSE
2025-07-09 11:00 | 37.95 | 21.5 | 99435 | 100 | 3000 | 25.5659 | 44.537 | 48.1897 | 0 | 7.2692 | FALSE | FALSE
2025-07-09 12:00 | 38.45 | 22.5 | 99410 | 100 | 3000 | 25.7304 | 45.4958 | 51.0329 | 0 | 7.2692 | FALSE | FALSE
2025-07-09 13:00 | 38.65 | 23 | 99365 | 100 | 3000 | 25.7946 | 45.983 | 52.3273 | 0 | 7.2692 | FALSE | FALSE
2025-07-09 14:00 | 38.55 | 23.5 | 99305 | 100 | 3000 | 25.7559 | 46.4259 | 52.7648 | 0 | 7.2692 | FALSE | FALSE
2025-07-09 15:00 | 38.1 | 25.5 | 99260 | 100 | 3000 | 25.584 | 48.1481 | 54.3554 | 0 | 7.2692 | FALSE | FALSE
2025-07-09 16:00 | 37.15 | 29 | 99240 | 100 | 3000 | 25.2282 | 51.0138 | 56.3669 | 0 | 7.2692 | FALSE | FALSE
2025-07-09 17:00 | 36 | 33 | 99235 | 100 | 3000 | 24.7995 | 54.093 | 57.9828 | 0 | 7.2692 | FALSE | FALSE
2025-07-09 18:00 | 34.8 | 38.5 | 99255 | 100 | 3000 | 24.3434 | 58.183 | 60.7802 | 0 | 7.2692 | FALSE | FALSE
2025-07-09 19:00 | 33.6 | 44.5 | 99300 | 100 | 3000 | 23.8851 | 62.395 | 63.4767 | 0 | 7.2692 | FALSE | FALSE
2025-07-09 20:00 | 32.65 | 48 | 99350 | 100 | 3000 | 23.5282 | 64.5832 | 63.739 | 0 | 7.2692 | FALSE | FALSE
2025-07-09 21:00 | 31.75 | 50 | 99395 | 100 | 3000 | 23.1939 | 65.5856 | 62.3345 | 0 | 7.2692 | FALSE | FALSE
2025-07-09 22:00 | 30.8 | 52.5 | 99410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-09 23:00 | 29.9 | 56 | 99395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-10 | 29.15 | 59.5 | 99365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-10 01:00 | 28.45 | 60 | 99345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-10 02:00 | 27.8 | 57 | 99325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-10 03:00 | 27.2 | 52.5 | 99315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-10 04:00 | 27.4 | 45.5 | 99320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-10 05:00 | 27.9 | 39.5 | 99330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-10 06:00 | 28.75 | 35.5 | 99355 | 100 | 3000 | 22.1137 | 54.4537 | 37.1318 | 0 | 7.2692 | FALSE | FALSE
2025-07-10 07:00 | 30.8 | 31 | 99395 | 100 | 3000 | 22.9139 | 51.4876 | 39.0847 | 0 | 7.2692 | FALSE | FALSE
2025-07-10 08:00 | 33.1 | 28.5 | 99440 | 100 | 3000 | 23.7842 | 49.8332 | 43.3093 | 0 | 7.2692 | FALSE | FALSE
2025-07-10 09:00 | 35.3 | 26 | 99475 | 100 | 3000 | 24.5976 | 48.0941 | 46.8027 | 0 | 7.2692 | FALSE | FALSE
2025-07-10 10:00 | 37.15 | 23.5 | 99485 | 100 | 3000 | 25.2706 | 46.2071 | 48.8102 | 0 | 7.2692 | FALSE | FALSE
2025-07-10 11:00 | 38.35 | 24 | 99465 | 100 | 3000 | 25.6828 | 46.8314 | 52.9681 | 0 | 7.2692 | FALSE | FALSE
2025-07-10 12:00 | 38.95 | 25 | 99425 | 100 | 3000 | 25.8785 | 47.865 | 56.2074 | 0 | 7.2692 | FALSE | FALSE
2025-07-10 13:00 | 39.35 | 23 | 99360 | 100 | 3000 | 26.0331 | 46.1023 | 54.3294 | 0 | 7.2692 | FALSE | FALSE
2025-07-10 14:00 | 39.55 | 20.5 | 99285 | 100 | 3000 | 26.1255 | 43.8063 | 51.0112 | 0 | 7.2692 | FALSE | FALSE
2025-07-10 15:00 | 39.1 | 21 | 99245 | 100 | 3000 | 25.9672 | 44.221 | 50.5414 | 0 | 7.2692 | FALSE | FALSE
2025-07-10 16:00 | 38.45 | 22.5 | 99260 | 100 | 3000 | 25.7304 | 45.5075 | 50.9897 | 0 | 7.2692 | FALSE | FALSE
2025-07-10 17:00 | 37.4 | 25.5 | 99270 | 100 | 3000 | 25.3423 | 48.01 | 52.2732 | 0 | 7.2692 | FALSE | FALSE
2025-07-10 18:00 | 35.75 | 32 | 99285 | 100 | 3000 | 24.7187 | 53.1743 | 55.8687 | 0 | 7.2692 | FALSE | FALSE
2025-07-10 19:00 | 34.15 | 42 | 99340 | 100 | 3000 | 24.0937 | 60.6933 | 62.6425 | 0 | 7.2692 | FALSE | FALSE
2025-07-10 20:00 | 32.85 | 53 | 99390 | 100 | 3000 | 23.5761 | 68.496 | 70.0816 | 0 | 7.2692 | FALSE | FALSE
2025-07-10 21:00 | 31.8 | 61 | 99435 | 100 | 3000 | 23.1661 | 73.7109 | 74.1143 | 0 | 7.2692 | FALSE | FALSE
2025-07-10 22:00 | 31 | 61.5 | 99470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-10 23:00 | 30.45 | 59 | 99465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-11 | 29.85 | 60.5 | 99425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-11 01:00 | 29.2 | 64 | 99375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-11 02:00 | 28.4 | 66.5 | 99345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-11 03:00 | 27.5 | 66 | 99345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-11 04:00 | 27.6 | 64 | 99365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-11 05:00 | 28.1 | 63.5 | 99395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-11 06:00 | 29.15 | 61 | 99435 | 100 | 3000 | 22.1953 | 71.8169 | 62.4617 | 0 | 7.2692 | FALSE | FALSE
2025-07-11 07:00 | 31.95 | 58 | 99475 | 100 | 3000 | 23.2325 | 71.6086 | 71.639 | 0 | 7.2692 | FALSE | FALSE
2025-07-11 08:00 | 35.3 | 50.5 | 99490 | 100 | 3000 | 24.4423 | 68.2365 | 77.5394 | 0 | 7.2692 | FALSE | FALSE
2025-07-11 09:00 | 38.3 | 36.5 | 99490 | 100 | 3000 | 25.5559 | 58.0854 | 70.8824 | 0 | 7.2692 | FALSE | FALSE
2025-07-11 10:00 | 40.75 | 25.5 | 99485 | 100 | 3000 | 26.4736 | 48.8033 | 62.4649 | 0 | 7.2692 | FALSE | FALSE
2025-07-11 11:00 | 42.45 | 19.5 | 99455 | 100 | 3000 | 27.1018 | 43.2416 | 57.2942 | 0 | 7.2692 | FALSE | FALSE
2025-07-11 12:00 | 42.5 | 23 | 99405 | 100 | 3000 | 27.0715 | 46.8304 | 63.5406 | 0 | 7.2692 | FALSE | FALSE
2025-07-11 13:00 | 40.55 | 31 | 99365 | 100 | 3000 | 26.347 | 54.0594 | 70.5613 | 0 | 7.2692 | FALSE | FALSE
2025-07-11 14:00 | 38.95 | 36.5 | 99330 | 100 | 3000 | 25.7701 | 58.4434 | 73.2234 | 0 | 7.2692 | FALSE | FALSE
2025-07-11 15:00 | 38.5 | 43 | 99305 | 100 | 3000 | 25.5628 | 64.0998 | 80.8446 | 0 | 7.2692 | FALSE | FALSE
2025-07-11 16:00 | 37.8 | 49 | 99315 | 100 | 3000 | 25.2831 | 68.9419 | 86.2611 | 0 | 7.2692 | FALSE | FALSE
2025-07-11 17:00 | 36.85 | 53.5 | 99340 | 100 | 3000 | 24.9378 | 72.0469 | 88.0678 | 0 | 7.2692 | FALSE | FALSE
2025-07-11 18:00 | 35.8 | 57.5 | 99380 | 100 | 3000 | 24.5634 | 74.4593 | 88.3652 | 0 | 7.2692 | FALSE | FALSE
2025-07-11 19:00 | 34.65 | 63 | 99445 | 100 | 3000 | 24.1446 | 77.824 | 89.5829 | 0 | 7.2692 | FALSE | FALSE
2025-07-11 20:00 | 33.6 | 70 | 99505 | 100 | 3000 | 23.7507 | 82.2265 | 92.4096 | 0 | 7.2692 | FALSE | FALSE
2025-07-11 21:00 | 32.9 | 74 | 99540 | 100 | 3000 | 23.4919 | 84.4949 | 93.2125 | 0 | 7.2692 | FALSE | FALSE
2025-07-11 22:00 | 32.5 | 75 | 99555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-11 23:00 | 31.75 | 79 | 99550 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-12 | 30.75 | 86.5 | 99520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-12 01:00 | 30 | 93 | 99490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-12 02:00 | 29.45 | 97 | 99480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-12 03:00 | 29 | 99 | 99485 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-12 04:00 | 29.7 | 88.5 | 99490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-12 05:00 | 30.5 | 76.5 | 99505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-12 06:00 | 31.2 | 70.5 | 99540 | 100 | 3000 | 22.9134 | 80.0902 | 81.059 | 0 | 7.2692 | FALSE | FALSE
2025-07-12 07:00 | 33 | 59.5 | 99585 | 100 | 3000 | 23.5977 | 73.5467 | 77.9482 | 0 | 7.2692 | FALSE | FALSE
2025-07-12 08:00 | 35.1 | 49.5 | 99615 | 100 | 3000 | 24.3805 | 67.2623 | 75.5038 | 0 | 7.2692 | FALSE | FALSE
2025-07-12 09:00 | 37.25 | 41 | 99625 | 100 | 3000 | 25.1683 | 61.4831 | 73.2269 | 0 | 7.2692 | FALSE | FALSE
2025-07-12 10:00 | 39.3 | 33 | 99630 | 100 | 3000 | 25.9189 | 55.3602 | 69.3888 | 0 | 7.2692 | FALSE | FALSE
2025-07-12 11:00 | 41.05 | 27.5 | 99610 | 100 | 3000 | 26.5485 | 50.8434 | 66.6896 | 0 | 7.2692 | FALSE | FALSE
2025-07-12 12:00 | 42.25 | 25 | 99560 | 100 | 3000 | 26.9652 | 48.7786 | 66.2918 | 0 | 7.2692 | FALSE | FALSE
2025-07-12 13:00 | 42.35 | 27 | 99505 | 100 | 3000 | 26.9707 | 50.8533 | 70.022 | 0 | 7.2692 | FALSE | FALSE
2025-07-12 14:00 | 41.25 | 33 | 99465 | 100 | 3000 | 26.5475 | 56.3508 | 76.2445 | 0 | 7.2692 | FALSE | FALSE
2025-07-12 15:00 | 40.2 | 36 | 99440 | 100 | 3000 | 26.1797 | 58.6725 | 77.136 | 0 | 7.2692 | FALSE | FALSE
2025-07-12 16:00 | 39.65 | 36 | 99450 | 100 | 3000 | 26.0029 | 58.3562 | 75.0998 | 0 | 7.2692 | FALSE | FALSE
2025-07-12 17:00 | 38.8 | 36.5 | 99485 | 100 | 3000 | 25.721 | 58.3495 | 72.7159 | 0 | 7.2692 | FALSE | FALSE
2025-07-12 18:00 | 37.9 | 39.5 | 99515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-12 19:00 | 36.95 | 44 | 99570 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-12 20:00 | 35.95 | 49 | 99640 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-12 21:00 | 35.6 | 50.5 | 99685 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-12 22:00 | 35.35 | 49 | 99690 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-12 23:00 | 34.75 | 49.5 | 99665 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 | 34.1 | 50.5 | 99625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 01:00 | 33.4 | 50.5 | 99595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 02:00 | 32.55 | 49.5 | 99590 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 03:00 | 31.8 | 48.5 | 99605 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 04:00 | 32.1 | 47 | 99620 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 05:00 | 32.65 | 47 | 99640 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 06:00 | 32.7 | 55 | 99695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 07:00 | 34 | 59 | 99750 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 08:00 | 36.7 | 45 | 99765 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 09:00 | 39.6 | 28 | 99750 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 10:00 | 42.25 | 19.5 | 99715 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 11:00 | 44.3 | 16 | 99660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 12:00 | 45.7 | 14 | 99600 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 13:00 | 46.4 | 12.5 | 99520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 14:00 | 45.8 | 16.5 | 99440 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 15:00 | 43.8 | 26 | 99405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 16:00 | 41.25 | 35.5 | 99410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 17:00 | 39 | 44.5 | 99415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 18:00 | 37.35 | 51 | 99430 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 19:00 | 36.45 | 53.5 | 99475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 20:00 | 36 | 53.5 | 99530 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 21:00 | 35.35 | 56.5 | 99570 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 22:00 | 35 | 55 | 99580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-13 23:00 | 34.9 | 48 | 99560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-14 | 34.55 | 43 | 99515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-14 01:00 | 34.1 | 39.5 | 99460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-14 02:00 | 33.45 | 39.5 | 99440 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-14 03:00 | 32.75 | 41.5 | 99465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-14 04:00 | 32.45 | 41.5 | 99480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-14 05:00 | 32.25 | 39.5 | 99485 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-14 06:00 | 32.85 | 36.5 | 99500 | 100 | 3000 | 23.6544 | 55.9109 | 51.6675 | 0 | 7.2692 | FALSE | FALSE
2025-07-14 07:00 | 35.4 | 31.5 | 99515 | 100 | 3000 | 24.5985 | 52.6428 | 54.1439 | 0 | 7.2692 | FALSE | FALSE
2025-07-14 08:00 | 38.6 | 28 | 99545 | 100 | 3000 | 25.7324 | 50.5072 | 59.6184 | 0 | 7.2692 | FALSE | FALSE
2025-07-14 09:00 | 41.2 | 23 | 99560 | 100 | 3000 | 26.6499 | 46.4778 | 59.7571 | 0 | 7.2692 | FALSE | FALSE
2025-07-14 10:00 | 43.45 | 17.5 | 99520 | 100 | 3000 | 27.453 | 41.3255 | 56.3849 | 0 | 7.2692 | FALSE | FALSE
2025-07-14 11:00 | 45.45 | 15 | 99460 | 100 | 3000 | 28.1297 | 38.8831 | 56.6117 | 0 | 7.2692 | FALSE | FALSE
2025-07-14 12:00 | 46.4 | 14 | 99390 | 100 | 3000 | 28.4452 | 37.8627 | 56.8321 | 0 | 7.2692 | FALSE | FALSE
2025-07-14 13:00 | 46.05 | 16 | 99320 | 100 | 3000 | 28.2993 | 40.0988 | 60.0803 | 0 | 7.2692 | FALSE | FALSE
2025-07-14 14:00 | 45.15 | 18.5 | 99265 | 100 | 3000 | 27.9758 | 42.7285 | 62.7064 | 0 | 7.2692 | FALSE | FALSE
2025-07-14 15:00 | 43.7 | 22 | 99235 | 100 | 3000 | 27.4665 | 46.1467 | 65.2368 | 0 | 7.2692 | FALSE | FALSE
2025-07-14 16:00 | 41.9 | 25.5 | 99245 | 100 | 3000 | 26.8466 | 49.189 | 65.9534 | 0 | 7.2692 | FALSE | FALSE
2025-07-14 17:00 | 40.35 | 29.5 | 99250 | 100 | 3000 | 26.2985 | 52.5398 | 67.4855 | 0 | 7.2692 | FALSE | FALSE
2025-07-14 18:00 | 38.5 | 39 | 99260 | 100 | 3000 | 25.5993 | 60.4757 | 75.1339 | 0 | 7.2692 | FALSE | FALSE
2025-07-14 19:00 | 37.2 | 46 | 99310 | 100 | 3000 | 25.1116 | 65.8368 | 79.6727 | 0 | 7.2692 | FALSE | FALSE
2025-07-14 20:00 | 36.75 | 46 | 99350 | 100 | 3000 | 24.9622 | 65.5133 | 77.833 | 0 | 7.2692 | FALSE | FALSE
2025-07-14 21:00 | 36.05 | 46 | 99380 | 100 | 3000 | 24.7269 | 65.0335 | 74.9862 | 0 | 7.2692 | FALSE | FALSE
2025-07-14 22:00 | 35.1 | 49.5 | 99405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-14 23:00 | 34.45 | 53 | 99395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-15 | 34.55 | 52 | 99355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-15 01:00 | 34.55 | 48.5 | 99315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-15 02:00 | 33.9 | 49 | 99305 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-15 03:00 | 33.45 | 51.5 | 99325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-15 04:00 | 32.65 | 56 | 99335 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-15 05:00 | 32.05 | 57 | 99345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-15 06:00 | 33.15 | 48.5 | 99375 | 100 | 3000 | 23.7047 | 65.242 | 66.2912 | 0 | 7.2692 | FALSE | FALSE
2025-07-15 07:00 | 35.6 | 38 | 99410 | 100 | 3000 | 24.6267 | 58.1008 | 63.074 | 0 | 7.2692 | FALSE | FALSE
2025-07-15 08:00 | 38.75 | 29.5 | 99435 | 100 | 3000 | 25.7693 | 51.9308 | 62.2753 | 0 | 7.2692 | FALSE | FALSE
2025-07-15 09:00 | 41.75 | 23 | 99430 | 100 | 3000 | 26.8295 | 46.6252 | 61.3313 | 0 | 7.2692 | FALSE | FALSE
2025-07-15 10:00 | 44 | 17.5 | 99400 | 100 | 3000 | 27.6295 | 41.416 | 57.776 | 0 | 7.2692 | FALSE | FALSE
2025-07-15 11:00 | 45.55 | 14.5 | 99345 | 100 | 3000 | 28.17 | 38.3443 | 55.8081 | 0 | 7.2692 | FALSE | FALSE
2025-07-15 12:00 | 46.55 | 13 | 99275 | 100 | 3000 | 28.5111 | 36.7372 | 55.0435 | 0 | 7.2692 | FALSE | FALSE
2025-07-15 13:00 | 45.4 | 19.5 | 99215 | 100 | 3000 | 28.0359 | 43.9018 | 65.3434 | 0 | 7.2692 | FALSE | FALSE
2025-07-15 14:00 | 43.45 | 27 | 99170 | 100 | 3000 | 27.3142 | 51.3425 | 73.4943 | 0 | 7.2692 | FALSE | FALSE
2025-07-15 15:00 | 43 | 26.5 | 99145 | 100 | 3000 | 27.1816 | 50.6299 | 71.1352 | 0 | 7.2692 | FALSE | FALSE
2025-07-15 16:00 | 42.1 | 26 | 99145 | 100 | 3000 | 26.9042 | 49.7706 | 67.397 | 0 | 7.2692 | FALSE | FALSE
2025-07-15 17:00 | 40.65 | 27 | 99140 | 100 | 3000 | 26.424 | 50.2512 | 64.457 | 0 | 7.2692 | FALSE | FALSE
2025-07-15 18:00 | 39 | 33 | 99170 | 100 | 3000 | 25.8197 | 55.2608 | 68.2065 | 0 | 7.2692 | FALSE | FALSE
2025-07-15 19:00 | 37.6 | 38.5 | 99245 | 100 | 3000 | 25.3054 | 59.5194 | 71.0324 | 0 | 7.2692 | FALSE | FALSE
2025-07-15 20:00 | 37.25 | 36.5 | 99310 | 100 | 3000 | 25.2038 | 57.5821 | 67.0197 | 0 | 7.2692 | FALSE | FALSE
2025-07-15 21:00 | 36.8 | 34.5 | 99350 | 100 | 3000 | 25.0658 | 55.6494 | 62.7276 | 0 | 7.2692 | FALSE | FALSE
2025-07-15 22:00 | 35.8 | 36.5 | 99365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-15 23:00 | 34.8 | 41 | 99370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-16 | 33.9 | 48 | 99350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-16 01:00 | 33.05 | 55.5 | 99315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-16 02:00 | 32.5 | 60.5 | 99310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-16 03:00 | 32.3 | 61.5 | 99350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-16 04:00 | 33.15 | 46.5 | 99395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-16 05:00 | 33.75 | 33.5 | 99435 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-16 06:00 | 34.7 | 32 | 99475 | 100 | 3000 | 24.3465 | 52.8739 | 52.4907 | 0 | 7.2692 | FALSE | FALSE
2025-07-16 07:00 | 37.15 | 26.5 | 99495 | 100 | 3000 | 25.2475 | 48.8174 | 52.9807 | 0 | 7.2692 | FALSE | FALSE
2025-07-16 08:00 | 39.35 | 23.5 | 99490 | 100 | 3000 | 26.0282 | 46.5572 | 55.1333 | 0 | 7.2692 | FALSE | FALSE
2025-07-16 09:00 | 41.5 | 21.5 | 99485 | 100 | 3000 | 26.7662 | 45.0696 | 58.0984 | 0 | 7.2692 | FALSE | FALSE
2025-07-16 10:00 | 43.6 | 18.5 | 99465 | 100 | 3000 | 27.4867 | 42.4059 | 58.6017 | 0 | 7.2692 | FALSE | FALSE
2025-07-16 11:00 | 45.15 | 16 | 99415 | 100 | 3000 | 28.0181 | 39.9568 | 57.8408 | 0 | 7.2692 | FALSE | FALSE
2025-07-16 12:00 | 45.95 | 15 | 99350 | 100 | 3000 | 28.2865 | 38.9506 | 57.7964 | 0 | 7.2692 | FALSE | FALSE
2025-07-16 13:00 | 44.45 | 20.5 | 99295 | 100 | 3000 | 27.7247 | 44.7441 | 64.6277 | 0 | 7.2692 | FALSE | FALSE
2025-07-16 14:00 | 41.95 | 28 | 99275 | 100 | 3000 | 26.8308 | 51.7197 | 70.3407 | 0 | 7.2692 | FALSE | FALSE
2025-07-16 15:00 | 40.3 | 31.5 | 99275 | 100 | 3000 | 26.2606 | 54.4333 | 70.4604 | 0 | 7.2692 | FALSE | FALSE
2025-07-16 16:00 | 38.85 | 36 | 99285 | 100 | 3000 | 25.742 | 57.9345 | 72.1121 | 0 | 7.2692 | FALSE | FALSE
2025-07-16 17:00 | 37.75 | 41.5 | 99295 | 100 | 3000 | 25.3303 | 62.2555 | 75.7617 | 0 | 7.2692 | FALSE | FALSE
2025-07-16 18:00 | 36.6 | 45.5 | 99310 | 100 | 3000 | 24.9157 | 64.9848 | 76.5545 | 0 | 7.2692 | FALSE | FALSE
2025-07-16 19:00 | 35.4 | 49 | 99355 | 100 | 3000 | 24.4859 | 67.0869 | 76.0762 | 0 | 7.2692 | FALSE | FALSE
2025-07-16 20:00 | 34.55 | 53 | 99425 | 100 | 3000 | 24.1703 | 69.7081 | 77.3314 | 0 | 7.2692 | FALSE | FALSE
2025-07-16 21:00 | 33.75 | 56.5 | 99480 | 100 | 3000 | 23.8744 | 71.8497 | 77.9175 | 0 | 7.2692 | FALSE | FALSE
2025-07-16 22:00 | 32.9 | 58.5 | 99490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-16 23:00 | 32.1 | 61 | 99460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-17 | 31.3 | 66.5 | 99415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-17 01:00 | 30.6 | 72 | 99390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-17 02:00 | 30.1 | 74.5 | 99390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-17 03:00 | 29.55 | 75.5 | 99400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-17 04:00 | 29.75 | 67 | 99415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-17 05:00 | 30.4 | 55.5 | 99435 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-17 06:00 | 31.4 | 48.5 | 99465 | 100 | 3000 | 23.0721 | 64.3006 | 59.3928 | 0 | 7.2692 | FALSE | FALSE
2025-07-17 07:00 | 34.15 | 37 | 99495 | 100 | 3000 | 24.1215 | 56.7112 | 56.7215 | 0 | 7.2692 | FALSE | FALSE
2025-07-17 08:00 | 38.1 | 25 | 99520 | 100 | 3000 | 25.5882 | 47.6797 | 53.7061 | 0 | 7.2692 | FALSE | FALSE
2025-07-17 09:00 | 41.6 | 18 | 99530 | 100 | 3000 | 26.8414 | 41.6071 | 52.4687 | 0 | 7.2692 | FALSE | FALSE
2025-07-17 10:00 | 42.95 | 18 | 99530 | 100 | 3000 | 27.2843 | 41.7748 | 55.9912 | 0 | 7.2692 | FALSE | FALSE
2025-07-17 11:00 | 42 | 23.5 | 99520 | 100 | 3000 | 26.9042 | 47.1877 | 62.951 | 0 | 7.2692 | FALSE | FALSE
2025-07-17 12:00 | 41.15 | 27 | 99475 | 100 | 3000 | 26.5867 | 50.3998 | 66.1529 | 0 | 7.2692 | FALSE | FALSE
2025-07-17 13:00 | 41.45 | 25 | 99410 | 100 | 3000 | 26.7077 | 48.5318 | 63.7754 | 0 | 7.2692 | FALSE | FALSE
2025-07-17 14:00 | 41.5 | 22.5 | 99360 | 100 | 3000 | 26.7542 | 46.0707 | 59.7363 | 0 | 7.2692 | FALSE | FALSE
2025-07-17 15:00 | 41.05 | 22.5 | 99320 | 100 | 3000 | 26.6065 | 45.9708 | 58.4206 | 0 | 7.2692 | FALSE | FALSE
2025-07-17 16:00 | 40.45 | 24 | 99310 | 100 | 3000 | 26.3914 | 47.2863 | 59.0929 | 0 | 7.2692 | FALSE | FALSE
2025-07-17 17:00 | 39.55 | 26 | 99310 | 100 | 3000 | 26.0709 | 48.95 | 59.5078 | 0 | 7.2692 | FALSE | FALSE
2025-07-17 18:00 | 38.15 | 31.5 | 99315 | 100 | 3000 | 25.5494 | 53.5368 | 63.1615 | 0 | 7.2692 | FALSE | FALSE
2025-07-17 19:00 | 36.55 | 39.5 | 99345 | 100 | 3000 | 24.9432 | 59.8233 | 68.4873 | 0 | 7.2692 | FALSE | FALSE
2025-07-17 20:00 | 35.55 | 43 | 99375 | 100 | 3000 | 24.5765 | 62.2239 | 69.2003 | 0 | 7.2692 | FALSE | FALSE
2025-07-17 21:00 | 34.9 | 43 | 99410 | 100 | 3000 | 24.3514 | 61.8655 | 66.7053 | 0 | 7.2692 | FALSE | FALSE
2025-07-17 22:00 | 33.9 | 46.5 | 99435 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-17 23:00 | 32.95 | 50.5 | 99440 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-18 | 32.4 | 52 | 99425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-18 01:00 | 32 | 56 | 99400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-18 02:00 | 31.55 | 55 | 99400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-18 03:00 | 31.05 | 48.5 | 99420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-18 04:00 | 31.25 | 43.5 | 99435 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-18 05:00 | 31.75 | 49 | 99460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-18 06:00 | 32.95 | 54 | 99500 | 100 | 3000 | 23.6069 | 69.3165 | 71.6356 | 0 | 7.2692 | FALSE | FALSE
2025-07-18 07:00 | 36 | 40 | 99535 | 100 | 3000 | 24.7516 | 59.9486 | 67.1344 | 0 | 7.2692 | FALSE | FALSE
2025-07-18 08:00 | 39.25 | 25.5 | 99570 | 100 | 3000 | 25.9751 | 48.386 | 57.907 | 0 | 7.2692 | FALSE | FALSE
2025-07-18 09:00 | 41.8 | 20.5 | 99580 | 100 | 3000 | 26.8767 | 44.1253 | 57.2783 | 0 | 7.2692 | FALSE | FALSE
2025-07-18 10:00 | 44.15 | 17 | 99550 | 100 | 3000 | 27.6849 | 40.8932 | 57.2739 | 0 | 7.2692 | FALSE | FALSE
2025-07-18 11:00 | 45.95 | 14 | 99500 | 100 | 3000 | 28.3045 | 37.811 | 55.803 | 0 | 7.2692 | FALSE | FALSE
2025-07-18 12:00 | 46.15 | 15.5 | 99435 | 100 | 3000 | 28.3395 | 39.5389 | 59.3477 | 0 | 7.2692 | FALSE | FALSE
2025-07-18 13:00 | 44.25 | 23 | 99380 | 100 | 3000 | 27.6228 | 47.3782 | 68.7741 | 0 | 7.2692 | FALSE | FALSE
2025-07-18 14:00 | 42.3 | 31 | 99340 | 100 | 3000 | 26.9019 | 54.9162 | 76.6154 | 0 | 7.2692 | FALSE | FALSE
2025-07-18 15:00 | 41.65 | 36 | 99325 | 100 | 3000 | 26.6356 | 59.5779 | 82.5464 | 0 | 7.2692 | FALSE | FALSE
2025-07-18 16:00 | 41.45 | 39 | 99335 | 100 | 3000 | 26.5367 | 62.4269 | 86.6266 | 0 | 7.2692 | FALSE | FALSE
2025-07-18 17:00 | 40.4 | 43 | 99335 | 100 | 3000 | 26.1656 | 65.53 | 88.6289 | 0 | 7.2692 | FALSE | FALSE
2025-07-18 18:00 | 38.9 | 47.5 | 99360 | 100 | 3000 | 25.6489 | 68.5139 | 88.933 | 0 | 7.2692 | FALSE | FALSE
2025-07-18 19:00 | 38.4 | 48 | 99400 | 100 | 3000 | 25.4851 | 68.5421 | 87.4955 | 0 | 7.2692 | FALSE | FALSE
2025-07-18 20:00 | 38.15 | 46 | 99410 | 100 | 3000 | 25.4226 | 66.5383 | 83.6485 | 0 | 7.2692 | FALSE | FALSE
2025-07-18 21:00 | 37.5 | 44 | 99405 | 100 | 3000 | 25.227 | 64.2892 | 78.2249 | 0 | 7.2692 | FALSE | FALSE
2025-07-18 22:00 | 36.85 | 42 | 99390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-18 23:00 | 36.05 | 44.5 | 99360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-19 | 35.05 | 49.5 | 99360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-19 01:00 | 34.4 | 51 | 99370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-19 02:00 | 33.9 | 49 | 99345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-19 03:00 | 33.25 | 47.5 | 99345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-19 04:00 | 32.8 | 56 | 99350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-19 05:00 | 32.6 | 64.5 | 99350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-19 06:00 | 33.4 | 58.5 | 99390 | 100 | 3000 | 23.7422 | 73.128 | 78.5956 | 0 | 7.2692 | FALSE | FALSE
2025-07-19 07:00 | 35.85 | 42.5 | 99435 | 100 | 3000 | 24.6829 | 61.9717 | 69.7423 | 0 | 7.2692 | FALSE | FALSE
2025-07-19 08:00 | 38.7 | 29 | 99455 | 100 | 3000 | 25.757 | 51.4561 | 61.3825 | 0 | 7.2692 | FALSE | FALSE
2025-07-19 09:00 | 41.15 | 23.5 | 99450 | 100 | 3000 | 26.6277 | 46.9649 | 60.4006 | 0 | 7.2692 | FALSE | FALSE
2025-07-19 10:00 | 43.3 | 20 | 99410 | 100 | 3000 | 27.369 | 43.927 | 60.5076 | 0 | 7.2692 | FALSE | FALSE
2025-07-19 11:00 | 44.2 | 20 | 99355 | 100 | 3000 | 27.6543 | 44.1368 | 62.9989 | 0 | 7.2692 | FALSE | FALSE
2025-07-19 12:00 | 43.7 | 23.5 | 99310 | 100 | 3000 | 27.444 | 47.731 | 68.0057 | 0 | 7.2692 | FALSE | FALSE
2025-07-19 13:00 | 43.65 | 24 | 99245 | 100 | 3000 | 27.4209 | 48.2482 | 68.7418 | 0 | 7.2692 | FALSE | FALSE
2025-07-19 14:00 | 43.7 | 24 | 99170 | 100 | 3000 | 27.4365 | 48.2715 | 68.8701 | 0 | 7.2692 | FALSE | FALSE
2025-07-19 15:00 | 42.9 | 25.5 | 99125 | 100 | 3000 | 27.1643 | 49.555 | 69.0496 | 0 | 7.2692 | FALSE | FALSE
2025-07-19 16:00 | 41.45 | 31.5 | 99100 | 100 | 3000 | 26.6286 | 55.0005 | 74.3968 | 0 | 7.2692 | FALSE | FALSE
2025-07-19 17:00 | 39.55 | 40 | 99095 | 100 | 3000 | 25.9295 | 62.076 | 80.6035 | 0 | 7.2692 | FALSE | FALSE
2025-07-19 18:00 | 37.9 | 47 | 99110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-19 19:00 | 36.65 | 54.5 | 99130 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-19 20:00 | 35.95 | 58 | 99165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-19 21:00 | 35.5 | 58.5 | 99185 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-19 22:00 | 34.75 | 61.5 | 99190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-19 23:00 | 33.7 | 72.5 | 99205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 | 32.85 | 83 | 99200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 01:00 | 32.35 | 86.5 | 99185 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 02:00 | 31.8 | 88.5 | 99160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 03:00 | 31.25 | 89 | 99135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 04:00 | 31.25 | 84.5 | 99110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 05:00 | 31.4 | 78.5 | 99095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 06:00 | 32.05 | 72.5 | 99115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 07:00 | 33.95 | 62.5 | 99160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 08:00 | 36.4 | 50.5 | 99205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 09:00 | 38.3 | 41 | 99220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 10:00 | 39.35 | 38.5 | 99200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 11:00 | 40.05 | 40.5 | 99145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 12:00 | 40.35 | 41.5 | 99080 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 13:00 | 40.1 | 43 | 99035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 14:00 | 39.65 | 47 | 98995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 15:00 | 39.35 | 48.5 | 98940 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 16:00 | 38.75 | 49.5 | 98955 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 17:00 | 38.2 | 49 | 98975 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 18:00 | 37.55 | 48.5 | 98980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 19:00 | 36.6 | 51.5 | 99030 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 20:00 | 35.8 | 55.5 | 99065 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 21:00 | 35 | 60.5 | 99095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 22:00 | 34.3 | 64 | 99105 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-20 23:00 | 33.65 | 67.5 | 99080 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-21 | 32.85 | 75 | 99070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-21 01:00 | 31.95 | 86 | 99070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-21 02:00 | 31.4 | 92 | 99090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-21 03:00 | 31.15 | 92.5 | 99140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-21 04:00 | 31.3 | 87 | 99175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-21 05:00 | 31.55 | 78 | 99190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-21 06:00 | 32.3 | 68 | 99195 | 100 | 3000 | 23.3122 | 79.3649 | 83.7472 | 0 | 7.2692 | FALSE | FALSE
2025-07-21 07:00 | 34.7 | 54.5 | 99215 | 100 | 3000 | 24.2125 | 71.0506 | 79.7159 | 0 | 7.2692 | FALSE | FALSE
2025-07-21 08:00 | 38.55 | 37.5 | 99230 | 100 | 3000 | 25.6293 | 59.1455 | 73.1625 | 0 | 7.2692 | FALSE | FALSE
2025-07-21 09:00 | 42.2 | 22 | 99225 | 100 | 3000 | 26.9881 | 45.7472 | 60.869 | 0 | 7.2692 | FALSE | FALSE
2025-07-21 10:00 | 44.65 | 15.5 | 99205 | 100 | 3000 | 27.8682 | 39.3614 | 55.5425 | 0 | 7.2692 | FALSE | FALSE
2025-07-21 11:00 | 46.4 | 13 | 99165 | 100 | 3000 | 28.4643 | 36.7338 | 54.6588 | 0 | 7.2692 | FALSE | FALSE
2025-07-21 12:00 | 47.5 | 11.5 | 99115 | 100 | 3000 | 28.8365 | 35.0568 | 53.8833 | 0 | 7.2692 | FALSE | FALSE
2025-07-21 13:00 | 47.45 | 12.5 | 99060 | 100 | 3000 | 28.8004 | 36.2371 | 55.9439 | 0 | 7.2692 | FALSE | FALSE
2025-07-21 14:00 | 44.4 | 24 | 99035 | 100 | 3000 | 27.6529 | 48.5379 | 70.9841 | 0 | 7.2692 | FALSE | FALSE
2025-07-21 15:00 | 41.95 | 33 | 99030 | 100 | 3000 | 26.7665 | 56.7747 | 78.6245 | 0 | 7.2692 | FALSE | FALSE
2025-07-21 16:00 | 41.45 | 37 | 99030 | 100 | 3000 | 26.5608 | 60.4654 | 83.3103 | 0 | 7.2692 | FALSE | FALSE
2025-07-21 17:00 | 40.45 | 44 | 99040 | 100 | 3000 | 26.1693 | 66.5584 | 90.2721 | 0 | 7.2692 | FALSE | FALSE
2025-07-21 18:00 | 39.4 | 48 | 99060 | 100 | 3000 | 25.8006 | 69.4399 | 91.7328 | 0 | 7.2692 | FALSE | FALSE
2025-07-21 19:00 | 38.25 | 51 | 99110 | 100 | 3000 | 25.4095 | 71.1415 | 90.9214 | 0 | 7.2692 | FALSE | FALSE
2025-07-21 20:00 | 37.6 | 51.5 | 99160 | 100 | 3000 | 25.1971 | 70.9941 | 88.7247 | 0 | 7.2692 | FALSE | FALSE
2025-07-21 21:00 | 37.2 | 49.5 | 99210 | 100 | 3000 | 25.0835 | 68.8946 | 84.3138 | 0 | 7.2692 | FALSE | FALSE
2025-07-21 22:00 | 36.8 | 48.5 | 99240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-21 23:00 | 36 | 54 | 99225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-22 | 34.9 | 60.5 | 99205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-22 01:00 | 34.05 | 62.5 | 99195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-22 02:00 | 33.45 | 63.5 | 99205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-22 03:00 | 33.1 | 62.5 | 99250 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-22 04:00 | 33.2 | 57.5 | 99280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-22 05:00 | 32.75 | 61 | 99300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-22 06:00 | 32.6 | 66.5 | 99350 | 100 | 3000 | 23.4241 | 78.5189 | 83.6332 | 0 | 7.2692 | FALSE | FALSE
2025-07-22 07:00 | 34.75 | 57.5 | 99390 | 100 | 3000 | 24.2116 | 73.4959 | 83.5504 | 0 | 7.2692 | FALSE | FALSE
2025-07-22 08:00 | 38.5 | 39 | 99400 | 100 | 3000 | 25.5994 | 60.4641 | 75.1743 | 0 | 7.2692 | FALSE | FALSE
2025-07-22 09:00 | 41.9 | 24 | 99390 | 100 | 3000 | 26.8656 | 47.6715 | 63.4595 | 0 | 7.2692 | FALSE | FALSE
2025-07-22 10:00 | 44.15 | 18.5 | 99350 | 100 | 3000 | 27.6618 | 42.5157 | 60.0371 | 0 | 7.2692 | FALSE | FALSE
2025-07-22 11:00 | 45.9 | 16 | 99295 | 100 | 3000 | 28.2528 | 40.0765 | 59.6914 | 0 | 7.2692 | FALSE | FALSE
2025-07-22 12:00 | 47.05 | 14.5 | 99230 | 100 | 3000 | 28.6364 | 38.5292 | 59.3925 | 0 | 7.2692 | FALSE | FALSE
2025-07-22 13:00 | 45.9 | 19 | 99165 | 100 | 3000 | 28.1982 | 43.4744 | 65.7187 | 0 | 7.2692 | FALSE | FALSE
2025-07-22 14:00 | 43.8 | 26.5 | 99130 | 100 | 3000 | 27.4295 | 50.9701 | 73.7222 | 0 | 7.2692 | FALSE | FALSE
2025-07-22 15:00 | 42.4 | 32 | 99110 | 100 | 3000 | 26.9193 | 56.0081 | 78.588 | 0 | 7.2692 | FALSE | FALSE
2025-07-22 16:00 | 41.4 | 38 | 99130 | 100 | 3000 | 26.5332 | 61.4154 | 84.7585 | 0 | 7.2692 | FALSE | FALSE
2025-07-22 17:00 | 40.25 | 44 | 99165 | 100 | 3000 | 26.1076 | 66.382 | 89.4713 | 0 | 7.2692 | FALSE | FALSE
2025-07-22 18:00 | 38.4 | 50.5 | 99175 | 100 | 3000 | 25.4619 | 70.8219 | 90.915 | 0 | 7.2692 | FALSE | FALSE
2025-07-22 19:00 | 37.05 | 55 | 99205 | 100 | 3000 | 24.9909 | 73.5412 | 90.8948 | 0 | 7.2692 | FALSE | FALSE
2025-07-22 20:00 | 36.25 | 57 | 99240 | 100 | 3000 | 24.715 | 74.4821 | 89.7857 | 0 | 7.2692 | FALSE | FALSE
2025-07-22 21:00 | 35.6 | 57.5 | 99265 | 100 | 3000 | 24.4968 | 74.2812 | 87.4114 | 0 | 7.2692 | FALSE | FALSE
2025-07-22 22:00 | 34.9 | 59.5 | 99260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-22 23:00 | 33.9 | 64.5 | 99225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-23 | 32.8 | 73 | 99210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-23 01:00 | 32.25 | 81 | 99200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-23 02:00 | 32.15 | 82 | 99170 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-23 03:00 | 31.85 | 80.5 | 99150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-23 04:00 | 31.65 | 77 | 99140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-23 05:00 | 31.4 | 74.5 | 99155 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-23 06:00 | 31.6 | 72 | 99210 | 100 | 3000 | 23.0489 | 81.6095 | 84.4713 | 0 | 7.2692 | FALSE | FALSE
2025-07-23 07:00 | 33 | 65.5 | 99260 | 100 | 3000 | 23.5678 | 78.1574 | 84.4494 | 0 | 7.2692 | FALSE | FALSE
2025-07-23 08:00 | 34.75 | 58.5 | 99280 | 100 | 3000 | 24.2053 | 74.3125 | 84.709 | 0 | 7.2692 | FALSE | FALSE
2025-07-23 09:00 | 36.4 | 52 | 99260 | 100 | 3000 | 24.801 | 70.3782 | 84.1097 | 0 | 7.2692 | FALSE | FALSE
2025-07-23 10:00 | 38.05 | 46.5 | 99220 | 100 | 3000 | 25.3855 | 66.9248 | 83.868 | 0 | 7.2692 | FALSE | FALSE
2025-07-23 11:00 | 39.3 | 44.5 | 99165 | 100 | 3000 | 25.8046 | 66.0872 | 86.243 | 0 | 7.2692 | FALSE | FALSE
2025-07-23 12:00 | 39.7 | 48 | 99095 | 100 | 3000 | 25.894 | 69.7083 | 93.0564 | 0 | 7.2692 | FALSE | FALSE
2025-07-23 13:00 | 39.6 | 51.5 | 99015 | 100 | 3000 | 25.8263 | 72.9097 | 97.6948 | 0 | 7.2692 | FALSE | FALSE
2025-07-23 14:00 | 39.45 | 50.5 | 98940 | 100 | 3000 | 25.7903 | 71.831 | 95.542 | 0 | 7.2692 | FALSE | FALSE
2025-07-23 15:00 | 39.05 | 50 | 98890 | 100 | 3000 | 25.6708 | 70.9898 | 93.017 | 0 | 7.2692 | FALSE | FALSE
2025-07-23 16:00 | 37.8 | 54 | 98890 | 100 | 3000 | 25.2393 | 73.4162 | 92.9166 | 0 | 7.2692 | FALSE | FALSE
2025-07-23 17:00 | 36.4 | 58 | 98895 | 100 | 3000 | 24.7561 | 75.5073 | 91.6555 | 0 | 7.2692 | FALSE | FALSE
2025-07-23 18:00 | 35.3 | 60.5 | 98895 | 100 | 3000 | 24.3765 | 76.4981 | 89.5679 | 0 | 7.2692 | FALSE | FALSE
2025-07-23 19:00 | 34.25 | 64.5 | 98930 | 100 | 3000 | 24.0001 | 78.66 | 89.2665 | 0 | 7.2692 | FALSE | FALSE
2025-07-23 20:00 | 33.45 | 70 | 98965 | 100 | 3000 | 23.6988 | 82.1098 | 91.5248 | 0 | 7.2692 | FALSE | FALSE
2025-07-23 21:00 | 32.85 | 75.5 | 98995 | 100 | 3000 | 23.4665 | 85.6254 | 94.4308 | 0 | 7.2692 | FALSE | FALSE
2025-07-23 22:00 | 32.4 | 79 | 99010 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-23 23:00 | 31.85 | 82 | 98995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-24 | 31.15 | 86.5 | 98965 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-24 01:00 | 30.5 | 90 | 98935 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-24 02:00 | 30 | 92 | 98910 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-24 03:00 | 29.6 | 94 | 98885 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-24 04:00 | 29.55 | 93.5 | 98885 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-24 05:00 | 29.5 | 92 | 98915 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-24 06:00 | 29.8 | 89 | 98950 | 100 | 3000 | 22.3465 | 91.5945 | 91.5274 | 0 | 7.2692 | FALSE | FALSE
2025-07-24 07:00 | 31.15 | 81.5 | 99000 | 100 | 3000 | 22.8518 | 88.0009 | 91.6501 | 0 | 7.2692 | FALSE | FALSE
2025-07-24 08:00 | 33 | 71.5 | 99030 | 100 | 3000 | 23.5376 | 82.7549 | 90.9117 | 0 | 7.2692 | FALSE | FALSE
2025-07-24 09:00 | 35 | 62 | 99030 | 100 | 3000 | 24.2672 | 77.4092 | 89.9742 | 0 | 7.2692 | FALSE | FALSE
2025-07-24 10:00 | 37.1 | 54.5 | 99005 | 100 | 3000 | 25.0106 | 73.1727 | 90.4133 | 0 | 7.2692 | FALSE | FALSE
2025-07-24 11:00 | 38.9 | 50 | 98945 | 100 | 3000 | 25.6239 | 70.8456 | 92.3662 | 0 | 7.2692 | FALSE | FALSE
2025-07-24 12:00 | 39.6 | 50 | 98870 | 100 | 3000 | 25.8416 | 71.5141 | 95.4693 | 0 | 7.2692 | FALSE | FALSE
2025-07-24 13:00 | 38.5 | 54.5 | 98805 | 100 | 3000 | 25.4555 | 74.5739 | 96.8075 | 0 | 7.2692 | FALSE | FALSE
2025-07-24 14:00 | 38.15 | 55.5 | 98745 | 100 | 3000 | 25.3365 | 75.1195 | 96.5283 | 0 | 7.2692 | FALSE | FALSE
2025-07-24 15:00 | 38.9 | 52 | 98695 | 100 | 3000 | 25.604 | 72.7044 | 95.1219 | 0 | 7.2692 | FALSE | FALSE
2025-07-24 16:00 | 38.4 | 52 | 98695 | 100 | 3000 | 25.4471 | 72.2202 | 92.8561 | 0 | 7.2692 | FALSE | FALSE
2025-07-24 17:00 | 37.65 | 53.5 | 98715 | 100 | 3000 | 25.1953 | 72.8445 | 91.5096 | 0 | 7.2692 | FALSE | FALSE
2025-07-24 18:00 | 36.7 | 56.5 | 98735 | 100 | 3000 | 24.8647 | 74.5377 | 91.0957 | 0 | 7.2692 | FALSE | FALSE
2025-07-24 19:00 | 35.5 | 63 | 98775 | 100 | 3000 | 24.4258 | 78.7727 | 93.5187 | 0 | 7.2692 | FALSE | FALSE
2025-07-24 20:00 | 34.8 | 69.5 | 98830 | 100 | 3000 | 24.1533 | 83.2795 | 97.7632 | 0 | 7.2692 | FALSE | FALSE
2025-07-24 21:00 | 34.85 | 70 | 98870 | 100 | 3000 | 24.1668 | 83.7393 | 98.6123 | 0 | 7.2692 | FALSE | FALSE
2025-07-24 22:00 | 35.2 | 64.5 | 98870 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-24 23:00 | 35.2 | 58 | 98860 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-25 | 34.7 | 56 | 98845 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-25 01:00 | 33.9 | 59.5 | 98815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-25 02:00 | 33.2 | 63 | 98805 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-25 03:00 | 33.05 | 58.5 | 98825 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-25 04:00 | 33.3 | 54 | 98855 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-25 05:00 | 33.1 | 58.5 | 98900 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-25 06:00 | 32.85 | 64.5 | 98960 | 100 | 3000 | 23.5202 | 77.2806 | 82.5783 | 0 | 7.2692 | FALSE | FALSE
2025-07-25 07:00 | 33.7 | 64 | 99000 | 100 | 3000 | 23.8162 | 77.7077 | 86.0723 | 0 | 7.2692 | FALSE | FALSE
2025-07-25 08:00 | 35.85 | 56.5 | 99015 | 100 | 3000 | 24.5863 | 73.7047 | 87.2581 | 0 | 7.2692 | FALSE | FALSE
2025-07-25 09:00 | 38.8 | 45 | 99020 | 100 | 3000 | 25.6404 | 66.169 | 84.8391 | 0 | 7.2692 | FALSE | FALSE
2025-07-25 10:00 | 41.8 | 34 | 98985 | 100 | 3000 | 26.7069 | 57.6963 | 79.7186 | 0 | 7.2692 | FALSE | FALSE
2025-07-25 11:00 | 44 | 28 | 98930 | 100 | 3000 | 27.4673 | 52.6806 | 77.0454 | 0 | 7.2692 | FALSE | FALSE
2025-07-25 12:00 | 45.5 | 24 | 98870 | 100 | 3000 | 27.9866 | 48.9867 | 74.3526 | 0 | 7.2692 | FALSE | FALSE
2025-07-25 13:00 | 46.55 | 21 | 98795 | 100 | 3000 | 28.3565 | 45.9822 | 71.5065 | 0 | 7.2692 | FALSE | FALSE
2025-07-25 14:00 | 47.3 | 18.5 | 98740 | 100 | 3000 | 28.6304 | 43.3061 | 68.3962 | 0 | 7.2692 | FALSE | FALSE
2025-07-25 15:00 | 47.55 | 16 | 98710 | 100 | 3000 | 28.7578 | 40.4129 | 63.6766 | 0 | 7.2692 | FALSE | FALSE
2025-07-25 16:00 | 46.65 | 16 | 98730 | 100 | 3000 | 28.4845 | 40.2411 | 61.3883 | 0 | 7.2692 | FALSE | FALSE
2025-07-25 17:00 | 45.65 | 17 | 98765 | 100 | 3000 | 28.1574 | 41.1951 | 60.8806 | 0 | 7.2692 | FALSE | FALSE
2025-07-25 18:00 | 43.85 | 23 | 98810 | 100 | 3000 | 27.4983 | 47.2865 | 67.3732 | 0 | 7.2692 | FALSE | FALSE
2025-07-25 19:00 | 40.95 | 33.5 | 98885 | 100 | 3000 | 26.4461 | 56.725 | 75.7879 | 0 | 7.2692 | FALSE | FALSE
2025-07-25 20:00 | 38.9 | 39.5 | 98950 | 100 | 3000 | 25.7248 | 61.2021 | 77.2976 | 0 | 7.2692 | FALSE | FALSE
2025-07-25 21:00 | 37.45 | 43.5 | 98995 | 100 | 3000 | 25.2141 | 63.8509 | 77.2301 | 0 | 7.2692 | FALSE | FALSE
2025-07-25 22:00 | 36.5 | 44.5 | 99000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-25 23:00 | 36.1 | 40 | 98980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-26 | 35.65 | 36.5 | 98965 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-26 01:00 | 35 | 36 | 98955 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-26 02:00 | 34.25 | 37 | 98985 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-26 03:00 | 33.6 | 39.5 | 99065 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-26 04:00 | 33 | 46.5 | 99125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-26 05:00 | 32.6 | 53.5 | 99160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-26 06:00 | 32.65 | 54.5 | 99210 | 100 | 3000 | 23.4978 | 69.5145 | 70.843 | 0 | 7.2692 | FALSE | FALSE
2025-07-26 07:00 | 33.8 | 57 | 99260 | 100 | 3000 | 23.8888 | 72.3016 | 78.6583 | 0 | 7.2692 | FALSE | FALSE
2025-07-26 08:00 | 36.9 | 49 | 99280 | 100 | 3000 | 24.9889 | 68.2143 | 82.3853 | 0 | 7.2692 | FALSE | FALSE
2025-07-26 09:00 | 40.15 | 33 | 99270 | 100 | 3000 | 26.1958 | 55.7957 | 72.2689 | 0 | 7.2692 | FALSE | FALSE
2025-07-26 10:00 | 42.25 | 25.5 | 99245 | 100 | 3000 | 26.9585 | 49.31 | 67.047 | 0 | 7.2692 | FALSE | FALSE
2025-07-26 11:00 | 44.05 | 21 | 99205 | 100 | 3000 | 27.5916 | 45.1819 | 64.3938 | 0 | 7.2692 | FALSE | FALSE
2025-07-26 12:00 | 45.5 | 17.5 | 99150 | 100 | 3000 | 28.1019 | 41.6991 | 61.6254 | 0 | 7.2692 | FALSE | FALSE
2025-07-26 13:00 | 46.05 | 17 | 99085 | 100 | 3000 | 28.281 | 41.2491 | 62.0384 | 0 | 7.2692 | FALSE | FALSE
2025-07-26 14:00 | 45.35 | 21 | 99030 | 100 | 3000 | 27.9943 | 45.5711 | 68.0857 | 0 | 7.2692 | FALSE | FALSE
2025-07-26 15:00 | 43.9 | 26.5 | 99010 | 100 | 3000 | 27.4601 | 51.0232 | 74.0069 | 0 | 7.2692 | FALSE | FALSE
2025-07-26 16:00 | 42.2 | 32 | 99040 | 100 | 3000 | 26.8572 | 55.9026 | 77.8522 | 0 | 7.2692 | FALSE | FALSE
2025-07-26 17:00 | 40.8 | 36 | 99070 | 100 | 3000 | 26.3698 | 59.0618 | 79.2619 | 0 | 7.2692 | FALSE | FALSE
2025-07-26 18:00 | 39.6 | 38.5 | 99090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-26 19:00 | 38.4 | 41.5 | 99140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-26 20:00 | 37.9 | 41 | 99195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-26 21:00 | 37.7 | 39 | 99230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-26 22:00 | 36.95 | 40.5 | 99245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-26 23:00 | 35.95 | 44 | 99230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 | 35 | 49 | 99180 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 01:00 | 34.1 | 54.5 | 99175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 02:00 | 33.35 | 59 | 99210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 03:00 | 32.6 | 63 | 99240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 04:00 | 31.65 | 65.5 | 99280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 05:00 | 31 | 63.5 | 99295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 06:00 | 31.85 | 52.5 | 99315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 07:00 | 34.75 | 35.5 | 99355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 08:00 | 38.25 | 25.5 | 99375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 09:00 | 40.5 | 24.5 | 99365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 10:00 | 42.2 | 23.5 | 99330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 11:00 | 44.1 | 20.5 | 99285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 12:00 | 45.6 | 17.5 | 99210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 13:00 | 45.85 | 18 | 99130 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 14:00 | 44.1 | 23.5 | 99105 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 15:00 | 41.8 | 30 | 99100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 16:00 | 40.6 | 32 | 99090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 17:00 | 39.9 | 33.5 | 99120 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 18:00 | 39.1 | 37 | 99165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 19:00 | 38.15 | 40 | 99210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 20:00 | 37.35 | 42 | 99240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 21:00 | 36.6 | 43.5 | 99260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 22:00 | 35.7 | 45.5 | 99290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-27 23:00 | 34.65 | 56 | 99285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-28 | 33.35 | 73 | 99255 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-28 01:00 | 32.5 | 80.5 | 99235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-28 02:00 | 32.05 | 82 | 99235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-28 03:00 | 31.5 | 80.5 | 99245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-28 04:00 | 31.3 | 71 | 99260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-28 05:00 | 31.25 | 61.5 | 99295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-28 06:00 | 31.95 | 51 | 99340 | 100 | 3000 | 23.2623 | 66.4404 | 64.1881 | 0 | 7.2692 | FALSE | FALSE
2025-07-28 07:00 | 35.05 | 34 | 99365 | 100 | 3000 | 24.459 | 54.6059 | 56.1039 | 0 | 7.2692 | FALSE | FALSE
2025-07-28 08:00 | 38.8 | 23 | 99385 | 100 | 3000 | 25.8459 | 46.0056 | 52.7613 | 0 | 7.2692 | FALSE | FALSE
2025-07-28 09:00 | 41.3 | 21 | 99400 | 100 | 3000 | 26.7064 | 44.5424 | 56.6715 | 0 | 7.2692 | FALSE | FALSE
2025-07-28 10:00 | 43.4 | 20 | 99385 | 100 | 3000 | 27.4009 | 43.9505 | 60.777 | 0 | 7.2692 | FALSE | FALSE
2025-07-28 11:00 | 45.35 | 17.5 | 99345 | 100 | 3000 | 28.0551 | 41.6561 | 61.2989 | 0 | 7.2692 | FALSE | FALSE
2025-07-28 12:00 | 46.85 | 15 | 99280 | 100 | 3000 | 28.5651 | 39.0791 | 59.9852 | 0 | 7.2692 | FALSE | FALSE
2025-07-28 13:00 | 47.1 | 14 | 99205 | 100 | 3000 | 28.6619 | 37.9535 | 58.4326 | 0 | 7.2692 | FALSE | FALSE
2025-07-28 14:00 | 44.2 | 24 | 99180 | 100 | 3000 | 27.5915 | 48.4522 | 70.4153 | 0 | 7.2692 | FALSE | FALSE
2025-07-28 15:00 | 40.7 | 37.5 | 99195 | 100 | 3000 | 26.3212 | 60.4461 | 81.2789 | 0 | 7.2692 | FALSE | FALSE
2025-07-28 16:00 | 39.25 | 42 | 99205 | 100 | 3000 | 25.8137 | 63.7237 | 82.3967 | 0 | 7.2692 | FALSE | FALSE
2025-07-28 17:00 | 38.65 | 44 | 99220 | 100 | 3000 | 25.6019 | 65.1247 | 82.8514 | 0 | 7.2692 | FALSE | FALSE
2025-07-28 18:00 | 38.85 | 40 | 99255 | 100 | 3000 | 25.7042 | 61.6039 | 77.9182 | 0 | 7.2692 | FALSE | FALSE
2025-07-28 19:00 | 38.8 | 34.5 | 99285 | 100 | 3000 | 25.7395 | 56.5354 | 69.7406 | 0 | 7.2692 | FALSE | FALSE
2025-07-28 20:00 | 37.5 | 40.5 | 99325 | 100 | 3000 | 25.2556 | 61.2179 | 73.4258 | 0 | 7.2692 | FALSE | FALSE
2025-07-28 21:00 | 36.1 | 51 | 99360 | 100 | 3000 | 24.7085 | 69.2783 | 81.5551 | 0 | 7.2692 | FALSE | FALSE
2025-07-28 22:00 | 35.25 | 57.5 | 99370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-28 23:00 | 34.6 | 62.5 | 99365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-29 | 34.2 | 65 | 99330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-29 01:00 | 33.85 | 64.5 | 99290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-29 02:00 | 33.2 | 64 | 99275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-29 03:00 | 32.45 | 64 | 99300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-29 04:00 | 32.05 | 60.5 | 99360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-29 05:00 | 31.75 | 58 | 99420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-29 06:00 | 32.1 | 55 | 99470 | 100 | 3000 | 23.2993 | 69.49 | 69.1018 | 0 | 7.2692 | FALSE | FALSE
2025-07-29 07:00 | 34.35 | 44 | 99500 | 100 | 3000 | 24.1531 | 62.3709 | 65.8214 | 0 | 7.2692 | FALSE | FALSE
2025-07-29 08:00 | 38.1 | 29.5 | 99520 | 100 | 3000 | 25.5497 | 51.7102 | 60.1888 | 0 | 7.2692 | FALSE | FALSE
2025-07-29 09:00 | 41.1 | 20 | 99525 | 100 | 3000 | 26.6518 | 43.517 | 54.4963 | 0 | 7.2692 | FALSE | FALSE
2025-07-29 10:00 | 43.2 | 17 | 99485 | 100 | 3000 | 27.3794 | 40.7724 | 54.8145 | 0 | 7.2692 | FALSE | FALSE
2025-07-29 11:00 | 45.3 | 15 | 99425 | 100 | 3000 | 28.0824 | 38.8687 | 56.2328 | 0 | 7.2692 | FALSE | FALSE
2025-07-29 12:00 | 46.85 | 13 | 99355 | 100 | 3000 | 28.6044 | 36.755 | 55.7629 | 0 | 7.2692 | FALSE | FALSE
2025-07-29 13:00 | 47.15 | 13.5 | 99300 | 100 | 3000 | 28.6873 | 37.3684 | 57.5115 | 0 | 7.2692 | FALSE | FALSE
2025-07-29 14:00 | 43.7 | 25.5 | 99290 | 100 | 3000 | 27.414 | 49.8534 | 71.6389 | 0 | 7.2692 | FALSE | FALSE
2025-07-29 15:00 | 40.1 | 38 | 99295 | 100 | 3000 | 26.1261 | 60.531 | 79.7821 | 0 | 7.2692 | FALSE | FALSE
2025-07-29 16:00 | 39.05 | 43 | 99300 | 100 | 3000 | 25.74 | 64.4962 | 83.0726 | 0 | 7.2692 | FALSE | FALSE
2025-07-29 17:00 | 37.8 | 48 | 99315 | 100 | 3000 | 25.2917 | 68.0544 | 84.8971 | 0 | 7.2692 | FALSE | FALSE
2025-07-29 18:00 | 36.45 | 55.5 | 99350 | 100 | 3000 | 24.7918 | 73.3901 | 88.8328 | 0 | 7.2692 | FALSE | FALSE
2025-07-29 19:00 | 35.5 | 61 | 99395 | 100 | 3000 | 24.4404 | 77.0656 | 91.2543 | 0 | 7.2692 | FALSE | FALSE
2025-07-29 20:00 | 34.9 | 61.5 | 99410 | 100 | 3000 | 24.2375 | 76.8685 | 89.0005 | 0 | 7.2692 | FALSE | FALSE
2025-07-29 21:00 | 34.25 | 62 | 99425 | 100 | 3000 | 24.0154 | 76.6305 | 86.5083 | 0 | 7.2692 | FALSE | FALSE
2025-07-29 22:00 | 33.65 | 62 | 99425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-29 23:00 | 33 | 62.5 | 99400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-30 | 32.25 | 63.5 | 99385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-30 01:00 | 31.45 | 64 | 99365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-30 02:00 | 30.7 | 64 | 99350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-30 03:00 | 30.15 | 62.5 | 99345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-30 04:00 | 30.8 | 56 | 99320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-30 05:00 | 31.35 | 52 | 99315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-30 06:00 | 31.5 | 52 | 99355 | 100 | 3000 | 23.0947 | 66.9165 | 63.4193 | 0 | 7.2692 | FALSE | FALSE
2025-07-30 07:00 | 33.25 | 48.5 | 99395 | 100 | 3000 | 23.7403 | 65.2983 | 66.6967 | 0 | 7.2692 | FALSE | FALSE
2025-07-30 08:00 | 35.75 | 46 | 99425 | 100 | 3000 | 24.625 | 64.8326 | 73.7834 | 0 | 7.2692 | FALSE | FALSE
2025-07-30 09:00 | 38.25 | 42 | 99445 | 100 | 3000 | 25.4906 | 63.013 | 78.4712 | 0 | 7.2692 | FALSE | FALSE
2025-07-30 10:00 | 40.45 | 32 | 99430 | 100 | 3000 | 26.3037 | 54.9713 | 71.8113 | 0 | 7.2692 | FALSE | FALSE
2025-07-30 11:00 | 41.55 | 25.5 | 99395 | 100 | 3000 | 26.734 | 49.0609 | 64.9119 | 0 | 7.2692 | FALSE | FALSE
2025-07-30 12:00 | 41.75 | 25.5 | 99345 | 100 | 3000 | 26.7985 | 49.1309 | 65.5181 | 0 | 7.2692 | FALSE | FALSE
2025-07-30 13:00 | 41.65 | 28.5 | 99270 | 100 | 3000 | 26.7291 | 52.0953 | 70.1856 | 0 | 7.2692 | FALSE | FALSE
2025-07-30 14:00 | 41.1 | 34 | 99205 | 100 | 3000 | 26.488 | 57.2725 | 77.2311 | 0 | 7.2692 | FALSE | FALSE
2025-07-30 15:00 | 40.2 | 39.5 | 99165 | 100 | 3000 | 26.1414 | 62.0393 | 82.4222 | 0 | 7.2692 | FALSE | FALSE
2025-07-30 16:00 | 39.3 | 43 | 99145 | 100 | 3000 | 25.8196 | 64.6943 | 84.0453 | 0 | 7.2692 | FALSE | FALSE
2025-07-30 17:00 | 38.25 | 46 | 99140 | 100 | 3000 | 25.4545 | 66.6389 | 83.9895 | 0 | 7.2692 | FALSE | FALSE
2025-07-30 18:00 | 36.95 | 52 | 99150 | 100 | 3000 | 24.9818 | 70.8581 | 86.5038 | 0 | 7.2692 | FALSE | FALSE
2025-07-30 19:00 | 35.9 | 59 | 99180 | 100 | 3000 | 24.5857 | 75.8265 | 90.6374 | 0 | 7.2692 | FALSE | FALSE
2025-07-30 20:00 | 35.15 | 63 | 99220 | 100 | 3000 | 24.3111 | 78.361 | 91.9369 | 0 | 7.2692 | FALSE | FALSE
2025-07-30 21:00 | 34.35 | 66.5 | 99250 | 100 | 3000 | 24.0227 | 80.3254 | 92.1352 | 0 | 7.2692 | FALSE | FALSE
2025-07-30 22:00 | 33.45 | 71 | 99250 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-30 23:00 | 32.7 | 73 | 99215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-31 | 32.15 | 71.5 | 99175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-31 01:00 | 31.65 | 71 | 99140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-31 02:00 | 31.2 | 72 | 99110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-31 03:00 | 30.95 | 70.5 | 99080 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-31 04:00 | 31.25 | 65 | 99040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-31 05:00 | 31.45 | 59 | 99045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-31 06:00 | 32.2 | 51.5 | 99085 | 100 | 3000 | 23.3503 | 66.9819 | 65.6851 | 0 | 7.2692 | FALSE | FALSE
2025-07-31 07:00 | 34.45 | 41.5 | 99120 | 100 | 3000 | 24.2024 | 60.4554 | 63.112 | 0 | 7.2692 | FALSE | FALSE
2025-07-31 08:00 | 36.45 | 36 | 99165 | 100 | 3000 | 24.9344 | 56.8057 | 63.4528 | 0 | 7.2692 | FALSE | FALSE
2025-07-31 09:00 | 37.9 | 33.5 | 99185 | 100 | 3000 | 25.4479 | 55.2362 | 65.1158 | 0 | 7.2692 | FALSE | FALSE
2025-07-31 10:00 | 39.45 | 31 | 99165 | 100 | 3000 | 25.9878 | 53.6003 | 66.7583 | 0 | 7.2692 | FALSE | FALSE
2025-07-31 11:00 | 41.55 | 26.5 | 99130 | 100 | 3000 | 26.7217 | 50.0753 | 66.4925 | 0 | 7.2692 | FALSE | FALSE
2025-07-31 12:00 | 43.75 | 21 | 99080 | 100 | 3000 | 27.4973 | 45.1115 | 63.4919 | 0 | 7.2692 | FALSE | FALSE
2025-07-31 13:00 | 44.65 | 19 | 99015 | 100 | 3000 | 27.8115 | 43.1837 | 62.2272 | 0 | 7.2692 | FALSE | FALSE
2025-07-31 14:00 | 44.65 | 20.5 | 98945 | 100 | 3000 | 27.787 | 44.823 | 65.0752 | 0 | 7.2692 | FALSE | FALSE
2025-07-31 15:00 | 44.2 | 26.5 | 98890 | 100 | 3000 | 27.5517 | 51.1664 | 74.9444 | 0 | 7.2692 | FALSE | FALSE
2025-07-31 16:00 | 42.95 | 30 | 98895 | 100 | 3000 | 27.1163 | 54.2612 | 77.0136 | 0 | 7.2692 | FALSE | FALSE
2025-07-31 17:00 | 41.65 | 30.5 | 98925 | 100 | 3000 | 26.704 | 54.1178 | 73.3897 | 0 | 7.2692 | FALSE | FALSE
2025-07-31 18:00 | 39.9 | 36.5 | 98950 | 100 | 3000 | 26.0778 | 59.0119 | 76.6342 | 0 | 7.2692 | FALSE | FALSE
2025-07-31 19:00 | 38 | 41 | 98985 | 100 | 3000 | 25.4168 | 61.9936 | 75.9556 | 0 | 7.2692 | FALSE | FALSE
2025-07-31 20:00 | 37.4 | 40 | 99025 | 100 | 3000 | 25.226 | 60.7461 | 72.2766 | 0 | 7.2692 | FALSE | FALSE
2025-07-31 21:00 | 37 | 38.5 | 99055 | 100 | 3000 | 25.1033 | 59.2196 | 68.7496 | 0 | 7.2692 | FALSE | FALSE
2025-07-31 22:00 | 36.3 | 37 | 99050 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-07-31 23:00 | 35.35 | 39 | 99040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-01 | 33.85 | 51 | 99030 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-01 01:00 | 33.5 | 66 | 99030 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-01 02:00 | 33.8 | 70 | 99050 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-01 03:00 | 33.45 | 59 | 99075 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-01 04:00 | 32.55 | 58.5 | 99095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-01 05:00 | 31.8 | 68 | 99125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-01 06:00 | 32.35 | 67 | 99170 | 100 | 3000 | 23.3342 | 78.6691 | 82.925 | 0 | 7.2692 | FALSE | FALSE
2025-08-01 07:00 | 34.25 | 58.5 | 99200 | 100 | 3000 | 24.0352 | 73.8721 | 82.4001 | 0 | 7.2692 | FALSE | FALSE
2025-08-01 08:00 | 37.4 | 46.5 | 99215 | 100 | 3000 | 25.1734 | 66.4289 | 81.147 | 0 | 7.2692 | FALSE | FALSE
2025-08-01 09:00 | 41 | 33.5 | 99235 | 100 | 3000 | 26.4623 | 56.7244 | 76.0777 | 0 | 7.2692 | FALSE | FALSE
2025-08-01 10:00 | 43.85 | 23.5 | 99240 | 100 | 3000 | 27.4908 | 47.7873 | 68.4383 | 0 | 7.2692 | FALSE | FALSE
2025-08-01 11:00 | 45.4 | 20.5 | 99220 | 100 | 3000 | 28.0184 | 45.0157 | 67.3156 | 0 | 7.2692 | FALSE | FALSE
2025-08-01 12:00 | 46.15 | 20 | 99180 | 100 | 3000 | 28.2557 | 44.6784 | 68.4483 | 0 | 7.2692 | FALSE | FALSE
2025-08-01 13:00 | 46.75 | 19 | 99140 | 100 | 3000 | 28.4558 | 43.7071 | 68.0711 | 0 | 7.2692 | FALSE | FALSE
2025-08-01 14:00 | 47 | 16.5 | 99120 | 100 | 3000 | 28.5811 | 40.8616 | 63.4843 | 0 | 7.2692 | FALSE | FALSE
2025-08-01 15:00 | 47.4 | 13 | 99085 | 100 | 3000 | 28.7746 | 36.8205 | 56.9302 | 0 | 7.2692 | FALSE | FALSE
2025-08-01 16:00 | 46.75 | 14 | 99100 | 100 | 3000 | 28.5541 | 37.9199 | 57.5589 | 0 | 7.2692 | FALSE | FALSE
2025-08-01 17:00 | 44.55 | 21.5 | 99145 | 100 | 3000 | 27.7396 | 45.8683 | 66.7606 | 0 | 7.2692 | FALSE | FALSE
2025-08-01 18:00 | 42.1 | 31.5 | 99180 | 100 | 3000 | 26.8328 | 55.3307 | 76.7036 | 0 | 7.2692 | FALSE | FALSE
2025-08-01 19:00 | 39.25 | 44.5 | 99240 | 100 | 3000 | 25.7889 | 66.0415 | 86.0572 | 0 | 7.2692 | FALSE | FALSE
2025-08-01 20:00 | 36.8 | 54.5 | 99285 | 100 | 3000 | 24.9137 | 72.8666 | 89.1249 | 0 | 7.2692 | FALSE | FALSE
2025-08-01 21:00 | 35.5 | 57 | 99290 | 100 | 3000 | 24.4669 | 73.7728 | 86.3452 | 0 | 7.2692 | FALSE | FALSE
2025-08-01 22:00 | 35.4 | 52.5 | 99275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-01 23:00 | 35.35 | 48.5 | 99260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-02 | 34.7 | 49.5 | 99245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-02 01:00 | 33.75 | 52.5 | 99240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-02 02:00 | 32.7 | 56.5 | 99290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-02 03:00 | 31.95 | 58 | 99365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-02 04:00 | 31.4 | 65 | 99400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-02 05:00 | 30.95 | 73.5 | 99420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-02 06:00 | 31.6 | 70.5 | 99460 | 100 | 3000 | 23.0554 | 80.4911 | 82.9939 | 0 | 7.2692 | FALSE | FALSE
2025-08-02 07:00 | 33.8 | 60 | 99515 | 100 | 3000 | 23.8729 | 74.6278 | 82.1392 | 0 | 7.2692 | FALSE | FALSE
2025-08-02 08:00 | 37 | 45.5 | 99545 | 100 | 3000 | 25.0495 | 65.2402 | 78.2488 | 0 | 7.2692 | FALSE | FALSE
2025-08-02 09:00 | 40.2 | 32 | 99545 | 100 | 3000 | 26.2229 | 54.8436 | 70.9764 | 0 | 7.2692 | FALSE | FALSE
2025-08-02 10:00 | 42.7 | 24 | 99530 | 100 | 3000 | 27.1219 | 47.907 | 65.9304 | 0 | 7.2692 | FALSE | FALSE
2025-08-02 11:00 | 44.65 | 19.5 | 99485 | 100 | 3000 | 27.8032 | 43.6949 | 63.3498 | 0 | 7.2692 | FALSE | FALSE
2025-08-02 12:00 | 45.95 | 17 | 99415 | 100 | 3000 | 28.25 | 41.2068 | 61.8963 | 0 | 7.2692 | FALSE | FALSE
2025-08-02 13:00 | 46.1 | 18.5 | 99355 | 100 | 3000 | 28.2685 | 42.945 | 65.3252 | 0 | 7.2692 | FALSE | FALSE
2025-08-02 14:00 | 45 | 23.5 | 99315 | 100 | 3000 | 27.8447 | 48.199 | 71.988 | 0 | 7.2692 | FALSE | FALSE
2025-08-02 15:00 | 43.5 | 28 | 99295 | 100 | 3000 | 27.3149 | 52.4102 | 75.4912 | 0 | 7.2692 | FALSE | FALSE
2025-08-02 16:00 | 41.8 | 35.5 | 99295 | 100 | 3000 | 26.6883 | 59.1766 | 82.2857 | 0 | 7.2692 | FALSE | FALSE
2025-08-02 17:00 | 40.15 | 44 | 99305 | 100 | 3000 | 26.0769 | 66.288 | 89.0955 | 0 | 7.2692 | FALSE | FALSE
2025-08-02 18:00 | 38.75 | 50 | 99340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-02 19:00 | 37.95 | 53.5 | 99385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-02 20:00 | 38.25 | 48.5 | 99420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-02 21:00 | 37.85 | 44.5 | 99435 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-02 22:00 | 36.45 | 48 | 99415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-02 23:00 | 35.25 | 51.5 | 99390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 | 34.3 | 55 | 99370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 01:00 | 33.7 | 60.5 | 99395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 02:00 | 33.25 | 65 | 99445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 03:00 | 32.75 | 65 | 99470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 04:00 | 32.75 | 56.5 | 99475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 05:00 | 32.95 | 49.5 | 99480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 06:00 | 34.1 | 39.5 | 99505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 07:00 | 36.35 | 27.5 | 99535 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 08:00 | 38.7 | 24.5 | 99560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 09:00 | 41.15 | 22 | 99565 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 10:00 | 43.25 | 20 | 99550 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 11:00 | 43.6 | 24.5 | 99520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 12:00 | 41.95 | 35.5 | 99480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 13:00 | 41.25 | 39 | 99435 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 14:00 | 41.4 | 36 | 99395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 15:00 | 40.95 | 34 | 99365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 16:00 | 40.45 | 34.5 | 99365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 17:00 | 39.9 | 35.5 | 99365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 18:00 | 39.4 | 36 | 99370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 19:00 | 39.1 | 37 | 99415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 20:00 | 38.75 | 38 | 99470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 21:00 | 37.75 | 43 | 99525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 22:00 | 36.55 | 47.5 | 99525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-03 23:00 | 35.85 | 48.5 | 99475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-04 | 35 | 51.5 | 99460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-04 01:00 | 34.1 | 55 | 99500 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-04 02:00 | 33.6 | 58 | 99555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-04 03:00 | 32.85 | 59 | 99590 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-04 04:00 | 31.9 | 62.5 | 99600 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-04 05:00 | 31.25 | 68 | 99620 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-04 06:00 | 32 | 60.5 | 99665 | 100 | 3000 | 23.2398 | 73.4791 | 74.5381 | 0 | 7.2692 | FALSE | FALSE
2025-08-04 07:00 | 34.25 | 46.5 | 99710 | 100 | 3000 | 24.1039 | 64.2886 | 68.4524 | 0 | 7.2692 | FALSE | FALSE
2025-08-04 08:00 | 36.8 | 35.5 | 99740 | 100 | 3000 | 25.0584 | 56.4779 | 64.1769 | 0 | 7.2692 | FALSE | FALSE
2025-08-04 09:00 | 39.1 | 28 | 99765 | 100 | 3000 | 25.9007 | 50.6416 | 61.2694 | 0 | 7.2692 | FALSE | FALSE
2025-08-04 10:00 | 40.9 | 24.5 | 99775 | 100 | 3000 | 26.5341 | 47.852 | 61.3923 | 0 | 7.2692 | FALSE | FALSE
2025-08-04 11:00 | 42.4 | 22 | 99750 | 100 | 3000 | 27.0526 | 45.7576 | 61.6188 | 0 | 7.2692 | FALSE | FALSE
2025-08-04 12:00 | 43.65 | 20 | 99700 | 100 | 3000 | 27.4804 | 43.9833 | 61.5796 | 0 | 7.2692 | FALSE | FALSE
2025-08-04 13:00 | 44.25 | 19 | 99630 | 100 | 3000 | 27.6856 | 43.0531 | 61.3476 | 0 | 7.2692 | FALSE | FALSE
2025-08-04 14:00 | 43.95 | 21 | 99565 | 100 | 3000 | 27.5602 | 45.129 | 64.2301 | 0 | 7.2692 | FALSE | FALSE
2025-08-04 15:00 | 42.7 | 26 | 99515 | 100 | 3000 | 27.0946 | 49.966 | 69.4205 | 0 | 7.2692 | FALSE | FALSE
2025-08-04 16:00 | 40.75 | 32 | 99505 | 100 | 3000 | 26.4002 | 55.1109 | 72.8824 | 0 | 7.2692 | FALSE | FALSE
2025-08-04 17:00 | 39.2 | 39 | 99515 | 100 | 3000 | 25.8275 | 60.8822 | 77.8893 | 0 | 7.2692 | FALSE | FALSE
2025-08-04 18:00 | 38.1 | 47.5 | 99515 | 100 | 3000 | 25.3934 | 67.8344 | 85.5474 | 0 | 7.2692 | FALSE | FALSE
2025-08-04 19:00 | 37.3 | 52.5 | 99550 | 100 | 3000 | 25.0925 | 71.568 | 88.8322 | 0 | 7.2692 | FALSE | FALSE
2025-08-04 20:00 | 37.05 | 52 | 99620 | 100 | 3000 | 25.0153 | 70.9042 | 87.0767 | 0 | 7.2692 | FALSE | FALSE
2025-08-04 21:00 | 36.55 | 51.5 | 99685 | 100 | 3000 | 24.855 | 70.0406 | 84.239 | 0 | 7.2692 | FALSE | FALSE
2025-08-04 22:00 | 35.45 | 54.5 | 99695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-04 23:00 | 34.4 | 57.5 | 99650 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-05 | 33.65 | 58.5 | 99600 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-05 01:00 | 32.95 | 60.5 | 99575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-05 02:00 | 32.95 | 59.5 | 99600 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-05 03:00 | 34.45 | 46 | 99635 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-05 04:00 | 35.4 | 35.5 | 99645 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-05 05:00 | 34.7 | 38 | 99680 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-05 06:00 | 34.4 | 40 | 99740 | 100 | 3000 | 24.1936 | 59.1784 | 61.2729 | 0 | 7.2692 | FALSE | FALSE
2025-08-05 07:00 | 35.2 | 38.5 | 99800 | 100 | 3000 | 24.484 | 58.3057 | 62.3581 | 0 | 7.2692 | FALSE | FALSE
2025-08-05 08:00 | 36.65 | 35.5 | 99835 | 100 | 3000 | 25.007 | 56.4067 | 63.6733 | 0 | 7.2692 | FALSE | FALSE
2025-08-05 09:00 | 38.45 | 32 | 99835 | 100 | 3000 | 25.6461 | 54.0612 | 65.0435 | 0 | 7.2692 | FALSE | FALSE
2025-08-05 10:00 | 40.3 | 28 | 99805 | 100 | 3000 | 26.2986 | 51.0401 | 65.1299 | 0 | 7.2692 | FALSE | FALSE
2025-08-05 11:00 | 41.9 | 25 | 99760 | 100 | 3000 | 26.853 | 48.6478 | 65.2735 | 0 | 7.2692 | FALSE | FALSE
2025-08-05 12:00 | 43.05 | 23 | 99710 | 100 | 3000 | 27.2468 | 46.9686 | 65.2793 | 0 | 7.2692 | FALSE | FALSE
2025-08-05 13:00 | 43.15 | 24.5 | 99650 | 100 | 3000 | 27.2572 | 48.5673 | 68.2355 | 0 | 7.2692 | FALSE | FALSE
2025-08-05 14:00 | 42.35 | 28 | 99600 | 100 | 3000 | 26.9575 | 51.8647 | 71.7653 | 0 | 7.2692 | FALSE | FALSE
2025-08-05 15:00 | 41.55 | 30 | 99570 | 100 | 3000 | 26.679 | 53.522 | 72.4281 | 0 | 7.2692 | FALSE | FALSE
2025-08-05 16:00 | 40.65 | 32.5 | 99565 | 100 | 3000 | 26.3625 | 55.5412 | 73.3424 | 0 | 7.2692 | FALSE | FALSE
2025-08-05 17:00 | 39.25 | 36.5 | 99555 | 100 | 3000 | 25.8682 | 58.5905 | 74.3986 | 0 | 7.2692 | FALSE | FALSE
2025-08-05 18:00 | 37.55 | 43 | 99555 | 100 | 3000 | 25.252 | 63.43 | 77.1044 | 0 | 7.2692 | FALSE | FALSE
2025-08-05 19:00 | 36.3 | 50 | 99585 | 100 | 3000 | 24.7828 | 68.572 | 81.2004 | 0 | 7.2692 | FALSE | FALSE
2025-08-05 20:00 | 35.8 | 52.5 | 99620 | 100 | 3000 | 24.5981 | 70.2697 | 82.2074 | 0 | 7.2692 | FALSE | FALSE
2025-08-05 21:00 | 35.8 | 47.5 | 99650 | 100 | 3000 | 24.6321 | 66.097 | 75.9379 | 0 | 7.2692 | FALSE | FALSE
2025-08-05 22:00 | 35.6 | 42.5 | 99645 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-05 23:00 | 34.95 | 42.5 | 99610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-06 | 34.3 | 43.5 | 99590 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-06 01:00 | 33.65 | 45 | 99585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-06 02:00 | 33 | 46.5 | 99585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-06 03:00 | 32.6 | 47.5 | 99620 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-06 04:00 | 32.75 | 49.5 | 99655 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-06 05:00 | 33.05 | 46.5 | 99670 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-06 06:00 | 33.8 | 37.5 | 99710 | 100 | 3000 | 23.9934 | 56.9655 | 56.1444 | 0 | 7.2692 | FALSE | FALSE
2025-08-06 07:00 | 35.4 | 32.5 | 99745 | 100 | 3000 | 24.5921 | 53.4487 | 55.4752 | 0 | 7.2692 | FALSE | FALSE
2025-08-06 08:00 | 37.2 | 31.5 | 99755 | 100 | 3000 | 25.226 | 53.1643 | 60.1139 | 0 | 7.2692 | FALSE | FALSE
2025-08-06 09:00 | 39.05 | 29.5 | 99760 | 100 | 3000 | 25.8698 | 52.009 | 63.3504 | 0 | 7.2692 | FALSE | FALSE
2025-08-06 10:00 | 40.85 | 26.5 | 99745 | 100 | 3000 | 26.4951 | 49.7866 | 64.4727 | 0 | 7.2692 | FALSE | FALSE
2025-08-06 11:00 | 42.35 | 23.5 | 99695 | 100 | 3000 | 27.0168 | 47.2755 | 64.0559 | 0 | 7.2692 | FALSE | FALSE
2025-08-06 12:00 | 43.5 | 21.5 | 99625 | 100 | 3000 | 27.4108 | 45.5341 | 63.8729 | 0 | 7.2692 | FALSE | FALSE
2025-08-06 13:00 | 44 | 21.5 | 99555 | 100 | 3000 | 27.5683 | 45.6775 | 65.2994 | 0 | 7.2692 | FALSE | FALSE
2025-08-06 14:00 | 43.4 | 25 | 99505 | 100 | 3000 | 27.3283 | 49.1926 | 69.8606 | 0 | 7.2692 | FALSE | FALSE
2025-08-06 15:00 | 42 | 29.5 | 99490 | 100 | 3000 | 26.8276 | 53.2364 | 73.0999 | 0 | 7.2692 | FALSE | FALSE
2025-08-06 16:00 | 40.9 | 30 | 99500 | 100 | 3000 | 26.4712 | 53.2346 | 70.2006 | 0 | 7.2692 | FALSE | FALSE
2025-08-06 17:00 | 39.65 | 32.5 | 99515 | 100 | 3000 | 26.0386 | 55.0638 | 69.8223 | 0 | 7.2692 | FALSE | FALSE
2025-08-06 18:00 | 37.9 | 41.5 | 99525 | 100 | 3000 | 25.3801 | 62.3309 | 76.4139 | 0 | 7.2692 | FALSE | FALSE
2025-08-06 19:00 | 36.6 | 48.5 | 99540 | 100 | 3000 | 24.8937 | 67.5303 | 80.5285 | 0 | 7.2692 | FALSE | FALSE
2025-08-06 20:00 | 36.15 | 49 | 99580 | 100 | 3000 | 24.7397 | 67.6127 | 79.2827 | 0 | 7.2692 | FALSE | FALSE
2025-08-06 21:00 | 36.3 | 44.5 | 99615 | 100 | 3000 | 24.8223 | 63.9097 | 74.1262 | 0 | 7.2692 | FALSE | FALSE
2025-08-06 22:00 | 36.05 | 41 | 99605 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-06 23:00 | 35.3 | 41.5 | 99585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-07 | 34.45 | 43 | 99575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-07 01:00 | 33.8 | 45 | 99575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-07 02:00 | 33.55 | 45.5 | 99590 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-07 03:00 | 33.25 | 47 | 99620 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-07 04:00 | 33.1 | 50 | 99640 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-07 05:00 | 33.2 | 54 | 99660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-07 06:00 | 34.05 | 50.5 | 99715 | 100 | 3000 | 24.0117 | 67.3332 | 72.3401 | 0 | 7.2692 | FALSE | FALSE
2025-08-07 07:00 | 35.85 | 36.5 | 99775 | 100 | 3000 | 24.7236 | 56.9263 | 62.1422 | 0 | 7.2692 | FALSE | FALSE
2025-08-07 08:00 | 37.7 | 28 | 99810 | 100 | 3000 | 25.4256 | 50.2359 | 56.8601 | 0 | 7.2692 | FALSE | FALSE
2025-08-07 09:00 | 39.5 | 26 | 99825 | 100 | 3000 | 26.0541 | 48.8963 | 59.5079 | 0 | 7.2692 | FALSE | FALSE
2025-08-07 10:00 | 41.15 | 24.5 | 99805 | 100 | 3000 | 26.616 | 47.9197 | 62.1584 | 0 | 7.2692 | FALSE | FALSE
2025-08-07 11:00 | 42.6 | 23 | 99740 | 100 | 3000 | 27.1035 | 46.834 | 63.9477 | 0 | 7.2692 | FALSE | FALSE
2025-08-07 12:00 | 43.65 | 21 | 99660 | 100 | 3000 | 27.4656 | 45.0435 | 63.4027 | 0 | 7.2692 | FALSE | FALSE
2025-08-07 13:00 | 43.7 | 22 | 99590 | 100 | 3000 | 27.4665 | 46.1207 | 65.3573 | 0 | 7.2692 | FALSE | FALSE
2025-08-07 14:00 | 42.75 | 25.5 | 99550 | 100 | 3000 | 27.1172 | 49.4672 | 68.7175 | 0 | 7.2692 | FALSE | FALSE
2025-08-07 15:00 | 41.35 | 28.5 | 99525 | 100 | 3000 | 26.6334 | 51.9508 | 69.2753 | 0 | 7.2692 | FALSE | FALSE
2025-08-07 16:00 | 39.85 | 33 | 99530 | 100 | 3000 | 26.0987 | 55.628 | 71.2895 | 0 | 7.2692 | FALSE | FALSE
2025-08-07 17:00 | 38.55 | 39 | 99555 | 100 | 3000 | 25.6159 | 60.481 | 75.4098 | 0 | 7.2692 | FALSE | FALSE
2025-08-07 18:00 | 37.75 | 41.5 | 99585 | 100 | 3000 | 25.3306 | 62.2311 | 75.8431 | 0 | 7.2692 | FALSE | FALSE
2025-08-07 19:00 | 37.3 | 40.5 | 99615 | 100 | 3000 | 25.189 | 61.0766 | 72.7383 | 0 | 7.2692 | FALSE | FALSE
2025-08-07 20:00 | 37 | 38.5 | 99630 | 100 | 3000 | 25.1037 | 59.1713 | 68.9059 | 0 | 7.2692 | FALSE | FALSE
2025-08-07 21:00 | 36.9 | 39 | 99630 | 100 | 3000 | 25.066 | 59.5519 | 69.2057 | 0 | 7.2692 | FALSE | FALSE
2025-08-07 22:00 | 36.2 | 49 | 99635 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-07 23:00 | 35 | 58.5 | 99640 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-08 | 34.15 | 61 | 99625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-08 01:00 | 33.6 | 62 | 99625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-08 02:00 | 33.2 | 61.5 | 99630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-08 03:00 | 32.8 | 61 | 99655 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-08 04:00 | 32.35 | 64 | 99685 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-08 05:00 | 32.1 | 66.5 | 99725 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-08 06:00 | 33.25 | 58.5 | 99785 | 100 | 3000 | 23.6903 | 72.9679 | 78.0133 | 0 | 7.2692 | FALSE | FALSE
2025-08-08 07:00 | 35.55 | 41 | 99825 | 100 | 3000 | 24.5898 | 60.5287 | 66.7956 | 0 | 7.2692 | FALSE | FALSE
2025-08-08 08:00 | 37.45 | 30.5 | 99845 | 100 | 3000 | 25.3197 | 52.3641 | 59.5783 | 0 | 7.2692 | FALSE | FALSE
2025-08-08 09:00 | 39.2 | 28.5 | 99850 | 100 | 3000 | 25.9294 | 51.1293 | 62.3657 | 0 | 7.2692 | FALSE | FALSE
2025-08-08 10:00 | 40.95 | 25.5 | 99845 | 100 | 3000 | 26.5391 | 48.8363 | 63.1943 | 0 | 7.2692 | FALSE | FALSE
2025-08-08 11:00 | 42.35 | 23 | 99810 | 100 | 3000 | 27.0234 | 46.7581 | 63.2279 | 0 | 7.2692 | FALSE | FALSE
2025-08-08 12:00 | 43.3 | 21.5 | 99750 | 100 | 3000 | 27.3474 | 45.4719 | 63.3367 | 0 | 7.2692 | FALSE | FALSE
2025-08-08 13:00 | 43 | 24 | 99705 | 100 | 3000 | 27.217 | 47.9918 | 66.9037 | 0 | 7.2692 | FALSE | FALSE
2025-08-08 14:00 | 41.85 | 28 | 99675 | 100 | 3000 | 26.7993 | 51.6473 | 70.1408 | 0 | 7.2692 | FALSE | FALSE
2025-08-08 15:00 | 40.85 | 30.5 | 99660 | 100 | 3000 | 26.4495 | 53.6871 | 70.8829 | 0 | 7.2692 | FALSE | FALSE
2025-08-08 16:00 | 39.7 | 33.5 | 99665 | 100 | 3000 | 26.0449 | 56.0153 | 71.5622 | 0 | 7.2692 | FALSE | FALSE
2025-08-08 17:00 | 38.3 | 38.5 | 99675 | 100 | 3000 | 25.5383 | 59.8726 | 73.782 | 0 | 7.2692 | FALSE | FALSE
2025-08-08 18:00 | 37.05 | 44.5 | 99705 | 100 | 3000 | 25.0741 | 64.3943 | 77.164 | 0 | 7.2692 | FALSE | FALSE
2025-08-08 19:00 | 36.7 | 44.5 | 99765 | 100 | 3000 | 24.9572 | 64.1559 | 75.7696 | 0 | 7.2692 | FALSE | FALSE
2025-08-08 20:00 | 36.85 | 41 | 99825 | 100 | 3000 | 25.0341 | 61.2335 | 71.7416 | 0 | 7.2692 | FALSE | FALSE
2025-08-08 21:00 | 36.65 | 41.5 | 99865 | 100 | 3000 | 24.9628 | 61.5448 | 71.6459 | 0 | 7.2692 | FALSE | FALSE
2025-08-08 22:00 | 36.15 | 48 | 99875 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-08 23:00 | 35.3 | 55 | 99850 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-09 | 34.65 | 58.5 | 99810 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-09 01:00 | 34.55 | 59.5 | 99780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-09 02:00 | 34.65 | 55.5 | 99775 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-09 03:00 | 34.15 | 54 | 99835 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-09 04:00 | 33.2 | 59.5 | 99930 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-09 05:00 | 32.55 | 63 | 99990 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-09 06:00 | 32.95 | 60 | 100045 | 100 | 3000 | 23.5783 | 73.8442 | 78.3768 | 0 | 7.2692 | FALSE | FALSE
2025-08-09 07:00 | 35.05 | 44.5 | 100100 | 100 | 3000 | 24.3947 | 63.1089 | 69.299 | 0 | 7.2692 | FALSE | FALSE
2025-08-09 08:00 | 37.05 | 31.5 | 100130 | 100 | 3000 | 25.1745 | 53.0836 | 59.7185 | 0 | 7.2692 | FALSE | FALSE
2025-08-09 09:00 | 38.4 | 30 | 100130 | 100 | 3000 | 25.647 | 52.2099 | 62.0617 | 0 | 7.2692 | FALSE | FALSE
2025-08-09 10:00 | 40 | 27.5 | 100105 | 100 | 3000 | 26.2052 | 50.437 | 63.4749 | 0 | 7.2692 | FALSE | FALSE
2025-08-09 11:00 | 41.45 | 25 | 100065 | 100 | 3000 | 26.7078 | 48.482 | 63.9835 | 0 | 7.2692 | FALSE | FALSE
2025-08-09 12:00 | 42.45 | 23.5 | 100005 | 100 | 3000 | 27.0489 | 47.2819 | 64.4577 | 0 | 7.2692 | FALSE | FALSE
2025-08-09 13:00 | 42.7 | 24 | 99940 | 100 | 3000 | 27.1219 | 47.8764 | 66.0656 | 0 | 7.2692 | FALSE | FALSE
2025-08-09 14:00 | 42.15 | 25.5 | 99890 | 100 | 3000 | 26.9268 | 49.2262 | 66.9434 | 0 | 7.2692 | FALSE | FALSE
2025-08-09 15:00 | 41.1 | 27.5 | 99865 | 100 | 3000 | 26.5648 | 50.8423 | 66.9309 | 0 | 7.2692 | FALSE | FALSE
2025-08-09 16:00 | 39.95 | 29.5 | 99850 | 100 | 3000 | 26.1679 | 52.3348 | 66.3414 | 0 | 7.2692 | FALSE | FALSE
2025-08-09 17:00 | 38.6 | 33 | 99825 | 100 | 3000 | 25.6872 | 55.0317 | 67.0072 | 0 | 7.2692 | FALSE | FALSE
2025-08-09 18:00 | 37 | 40 | 99830 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-09 19:00 | 35.9 | 46 | 99885 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-09 20:00 | 35.8 | 45 | 99945 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-09 21:00 | 35.75 | 41.5 | 99980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-09 22:00 | 35.3 | 40.5 | 99965 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-09 23:00 | 34.85 | 40 | 99935 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 | 34.25 | 42.5 | 99920 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 01:00 | 33.65 | 46.5 | 99920 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 02:00 | 32.9 | 54.5 | 99940 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 03:00 | 32.25 | 61 | 99960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 04:00 | 32.1 | 59 | 99950 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 05:00 | 32.1 | 58 | 99940 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 06:00 | 33.2 | 48 | 99960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 07:00 | 35.2 | 34.5 | 99985 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 08:00 | 36.95 | 31 | 100010 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 09:00 | 38.75 | 28.5 | 100025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 10:00 | 40.55 | 26 | 100010 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 11:00 | 42 | 24 | 99955 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 12:00 | 43.05 | 22 | 99885 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 13:00 | 43.3 | 22 | 99820 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 14:00 | 42.55 | 24 | 99770 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 15:00 | 41.35 | 27 | 99730 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 16:00 | 40.15 | 28.5 | 99715 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 17:00 | 39 | 30 | 99705 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 18:00 | 37.75 | 36.5 | 99710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 19:00 | 36.65 | 42 | 99755 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 20:00 | 36.2 | 42.5 | 99800 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 21:00 | 35.95 | 42 | 99830 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 22:00 | 35.45 | 42 | 99830 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-10 23:00 | 35 | 41 | 99795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-11 | 34.45 | 40.5 | 99760 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-11 01:00 | 33.95 | 41 | 99750 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-11 02:00 | 33.6 | 44.5 | 99760 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-11 03:00 | 33.4 | 51.5 | 99795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-11 04:00 | 33.9 | 44 | 99860 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-11 05:00 | 34.05 | 34 | 99930 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-11 06:00 | 34 | 35 | 99985 | 100 | 3000 | 24.0786 | 55.0362 | 53.936 | 0 | 7.2692 | FALSE | FALSE
2025-08-11 07:00 | 34.9 | 34.5 | 100025 | 100 | 3000 | 24.4028 | 54.9095 | 56.3844 | 0 | 7.2692 | FALSE | FALSE
2025-08-11 08:00 | 36.2 | 34 | 100060 | 100 | 3000 | 24.8624 | 54.9358 | 60.1844 | 0 | 7.2692 | FALSE | FALSE
2025-08-11 09:00 | 37.75 | 32.5 | 100065 | 100 | 3000 | 25.4058 | 54.216 | 63.4393 | 0 | 7.2692 | FALSE | FALSE
2025-08-11 10:00 | 39.45 | 29 | 100050 | 100 | 3000 | 26.0079 | 51.6638 | 63.9911 | 0 | 7.2692 | FALSE | FALSE
2025-08-11 11:00 | 41 | 26 | 100015 | 100 | 3000 | 26.5497 | 49.3274 | 64.2168 | 0 | 7.2692 | FALSE | FALSE
2025-08-11 12:00 | 42.15 | 24 | 99945 | 100 | 3000 | 26.9461 | 47.7044 | 64.3951 | 0 | 7.2692 | FALSE | FALSE
2025-08-11 13:00 | 42.35 | 25 | 99875 | 100 | 3000 | 26.9971 | 48.7887 | 66.7048 | 0 | 7.2692 | FALSE | FALSE
2025-08-11 14:00 | 41.55 | 28 | 99830 | 100 | 3000 | 26.7036 | 51.5129 | 69.2054 | 0 | 7.2692 | FALSE | FALSE
2025-08-11 15:00 | 40.55 | 30.5 | 99805 | 100 | 3000 | 26.3528 | 53.5422 | 69.9064 | 0 | 7.2692 | FALSE | FALSE
2025-08-11 16:00 | 39.3 | 34 | 99800 | 100 | 3000 | 25.9092 | 56.2756 | 70.9338 | 0 | 7.2692 | FALSE | FALSE
2025-08-11 17:00 | 37.8 | 40 | 99795 | 100 | 3000 | 25.36 | 60.9136 | 74.0194 | 0 | 7.2692 | FALSE | FALSE
2025-08-11 18:00 | 36.55 | 45.5 | 99780 | 100 | 3000 | 24.8995 | 64.9104 | 76.4775 | 0 | 7.2692 | FALSE | FALSE
2025-08-11 19:00 | 35.5 | 49 | 99790 | 100 | 3000 | 24.5204 | 67.1197 | 76.6055 | 0 | 7.2692 | FALSE | FALSE
2025-08-11 20:00 | 34.9 | 51 | 99825 | 100 | 3000 | 24.3029 | 68.3206 | 76.5353 | 0 | 7.2692 | FALSE | FALSE
2025-08-11 21:00 | 34.7 | 50 | 99870 | 100 | 3000 | 24.2402 | 67.3653 | 74.4997 | 0 | 7.2692 | FALSE | FALSE
2025-08-11 22:00 | 34.3 | 48 | 99875 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-11 23:00 | 33.7 | 46.5 | 99845 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-12 | 33 | 46.5 | 99815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-12 01:00 | 32.25 | 47.5 | 99795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-12 02:00 | 31.65 | 48.5 | 99800 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-12 03:00 | 31.25 | 49 | 99820 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-12 04:00 | 31.2 | 48.5 | 99860 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-12 05:00 | 31.25 | 47.5 | 99910 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-12 06:00 | 32.05 | 44 | 99955 | 100 | 3000 | 23.3287 | 61.2392 | 57.201 | 0 | 7.2692 | FALSE | FALSE
2025-08-12 07:00 | 34.3 | 36 | 99995 | 100 | 3000 | 24.1806 | 55.9235 | 56.1606 | 0 | 7.2692 | FALSE | FALSE
2025-08-12 08:00 | 36.5 | 30 | 100030 | 100 | 3000 | 24.995 | 51.6363 | 55.8675 | 0 | 7.2692 | FALSE | FALSE
2025-08-12 09:00 | 38.3 | 27.5 | 100050 | 100 | 3000 | 25.635 | 49.9299 | 58.0895 | 0 | 7.2692 | FALSE | FALSE
2025-08-12 10:00 | 40.15 | 25 | 100030 | 100 | 3000 | 26.281 | 48.1113 | 60.0008 | 0 | 7.2692 | FALSE | FALSE
2025-08-12 11:00 | 41.65 | 22.5 | 99975 | 100 | 3000 | 26.803 | 46.0605 | 60.3687 | 0 | 7.2692 | FALSE | FALSE
2025-08-12 12:00 | 42.55 | 21 | 99895 | 100 | 3000 | 27.1141 | 44.7615 | 60.3487 | 0 | 7.2692 | FALSE | FALSE
2025-08-12 13:00 | 42.5 | 22 | 99830 | 100 | 3000 | 27.0848 | 45.7768 | 61.9351 | 0 | 7.2692 | FALSE | FALSE
2025-08-12 14:00 | 41.95 | 22.5 | 99780 | 100 | 3000 | 26.9006 | 46.1488 | 61.181 | 0 | 7.2692 | FALSE | FALSE
2025-08-12 15:00 | 41.15 | 23.5 | 99735 | 100 | 3000 | 26.6276 | 46.9434 | 60.4903 | 0 | 7.2692 | FALSE | FALSE
2025-08-12 16:00 | 39.7 | 28 | 99715 | 100 | 3000 | 26.1008 | 50.8397 | 63.1718 | 0 | 7.2692 | FALSE | FALSE
2025-08-12 17:00 | 38 | 35 | 99705 | 100 | 3000 | 25.469 | 56.5752 | 67.7316 | 0 | 7.2692 | FALSE | FALSE
2025-08-12 18:00 | 36.35 | 44.5 | 99710 | 100 | 3000 | 24.8393 | 63.9335 | 74.3513 | 0 | 7.2692 | FALSE | FALSE
2025-08-12 19:00 | 35 | 55 | 99725 | 100 | 3000 | 24.3122 | 71.6563 | 81.7701 | 0 | 7.2692 | FALSE | FALSE
2025-08-12 20:00 | 34.2 | 63 | 99750 | 100 | 3000 | 23.9932 | 77.3448 | 87.5034 | 0 | 7.2692 | FALSE | FALSE
2025-08-12 21:00 | 33.7 | 67 | 99775 | 100 | 3000 | 23.8012 | 79.9755 | 89.6272 | 0 | 7.2692 | FALSE | FALSE
2025-08-12 22:00 | 33.15 | 69 | 99760 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-12 23:00 | 32.4 | 70.5 | 99735 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-13 | 31.75 | 71.5 | 99725 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-13 01:00 | 31.2 | 72 | 99695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-13 02:00 | 30.8 | 72 | 99675 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-13 03:00 | 30.5 | 71.5 | 99675 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-13 04:00 | 30.8 | 66.5 | 99655 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-13 05:00 | 31.1 | 60.5 | 99650 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-13 06:00 | 31.45 | 55.5 | 99685 | 100 | 3000 | 23.0627 | 69.4084 | 66.9197 | 0 | 7.2692 | FALSE | FALSE
2025-08-13 07:00 | 33.35 | 47.5 | 99720 | 100 | 3000 | 23.781 | 64.5542 | 66.0367 | 0 | 7.2692 | FALSE | FALSE
2025-08-13 08:00 | 36.2 | 38.5 | 99740 | 100 | 3000 | 24.8308 | 58.7659 | 65.9853 | 0 | 7.2692 | FALSE | FALSE
2025-08-13 09:00 | 38.95 | 30.5 | 99745 | 100 | 3000 | 25.827 | 52.8942 | 64.5031 | 0 | 7.2692 | FALSE | FALSE
2025-08-13 10:00 | 40.3 | 29 | 99740 | 100 | 3000 | 26.2878 | 52.0025 | 66.6839 | 0 | 7.2692 | FALSE | FALSE
2025-08-13 11:00 | 40.35 | 31.5 | 99720 | 100 | 3000 | 26.277 | 54.421 | 70.7693 | 0 | 7.2692 | FALSE | FALSE
2025-08-13 12:00 | 40.2 | 34 | 99665 | 100 | 3000 | 26.2015 | 56.744 | 74.1161 | 0 | 7.2692 | FALSE | FALSE
2025-08-13 13:00 | 40.05 | 36 | 99595 | 100 | 3000 | 26.1319 | 58.5726 | 76.6256 | 0 | 7.2692 | FALSE | FALSE
2025-08-13 14:00 | 39.7 | 37.5 | 99535 | 100 | 3000 | 26.0038 | 59.7886 | 77.5723 | 0 | 7.2692 | FALSE | FALSE
2025-08-13 15:00 | 39 | 40 | 99490 | 100 | 3000 | 25.7531 | 61.6807 | 78.5709 | 0 | 7.2692 | FALSE | FALSE
2025-08-13 16:00 | 38.1 | 40.5 | 99460 | 100 | 3000 | 25.4546 | 61.5686 | 75.7792 | 0 | 7.2692 | FALSE | FALSE
2025-08-13 17:00 | 37.05 | 41.5 | 99440 | 100 | 3000 | 25.0972 | 61.8151 | 73.077 | 0 | 7.2692 | FALSE | FALSE
2025-08-13 18:00 | 36 | 47 | 99445 | 100 | 3000 | 24.7031 | 65.8342 | 76.0741 | 0 | 7.2692 | FALSE | FALSE
2025-08-13 19:00 | 35.1 | 54.5 | 99475 | 100 | 3000 | 24.3489 | 71.3548 | 81.5469 | 0 | 7.2692 | FALSE | FALSE
2025-08-13 20:00 | 34.3 | 60 | 99500 | 100 | 3000 | 24.044 | 75.0818 | 84.4453 | 0 | 7.2692 | FALSE | FALSE
2025-08-13 21:00 | 33.5 | 63.5 | 99520 | 100 | 3000 | 23.751 | 77.0772 | 84.6845 | 0 | 7.2692 | FALSE | FALSE
2025-08-13 22:00 | 32.75 | 66 | 99520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-13 23:00 | 32.05 | 68 | 99505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-14 | 31.4 | 69 | 99485 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-14 01:00 | 30.75 | 68.5 | 99460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-14 02:00 | 30.15 | 67.5 | 99440 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-14 03:00 | 29.65 | 65.5 | 99420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-14 04:00 | 29.9 | 61 | 99405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-14 05:00 | 30.15 | 58.5 | 99425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-14 06:00 | 30.5 | 56 | 99465 | 100 | 3000 | 22.7132 | 69.1915 | 63.3886 | 0 | 7.2692 | FALSE | FALSE
2025-08-14 07:00 | 32.55 | 48 | 99495 | 100 | 3000 | 23.4923 | 64.5162 | 63.3763 | 0 | 7.2692 | FALSE | FALSE
2025-08-14 08:00 | 35.5 | 39.5 | 99530 | 100 | 3000 | 24.5821 | 59.2878 | 64.6404 | 0 | 7.2692 | FALSE | FALSE
2025-08-14 09:00 | 37.8 | 35 | 99560 | 100 | 3000 | 25.4017 | 56.4954 | 66.9803 | 0 | 7.2692 | FALSE | FALSE
2025-08-14 10:00 | 39.15 | 34 | 99555 | 100 | 3000 | 25.8598 | 56.2224 | 70.3281 | 0 | 7.2692 | FALSE | FALSE
2025-08-14 11:00 | 40.05 | 34 | 99505 | 100 | 3000 | 26.153 | 56.6782 | 73.5277 | 0 | 7.2692 | FALSE | FALSE
2025-08-14 12:00 | 40.4 | 34 | 99440 | 100 | 3000 | 26.2656 | 56.8683 | 74.768 | 0 | 7.2692 | FALSE | FALSE
2025-08-14 13:00 | 40.45 | 34.5 | 99380 | 100 | 3000 | 26.276 | 57.3813 | 75.7112 | 0 | 7.2692 | FALSE | FALSE
2025-08-14 14:00 | 40.25 | 36.5 | 99315 | 100 | 3000 | 26.1901 | 59.1904 | 78.0552 | 0 | 7.2692 | FALSE | FALSE
2025-08-14 15:00 | 39.6 | 38 | 99250 | 100 | 3000 | 25.9662 | 60.2205 | 77.8575 | 0 | 7.2692 | FALSE | FALSE
2025-08-14 16:00 | 38.95 | 37.5 | 99235 | 100 | 3000 | 25.7605 | 59.3707 | 74.6582 | 0 | 7.2692 | FALSE | FALSE
2025-08-14 17:00 | 38.15 | 40.5 | 99245 | 100 | 3000 | 25.4708 | 61.6176 | 75.9117 | 0 | 7.2692 | FALSE | FALSE
2025-08-14 18:00 | 37.1 | 47 | 99255 | 100 | 3000 | 25.0706 | 66.6381 | 80.5771 | 0 | 7.2692 | FALSE | FALSE
2025-08-14 19:00 | 36.05 | 54.5 | 99285 | 100 | 3000 | 24.667 | 72.1865 | 85.7357 | 0 | 7.2692 | FALSE | FALSE
2025-08-14 20:00 | 35.1 | 62.5 | 99325 | 100 | 3000 | 24.2978 | 77.8916 | 91.1255 | 0 | 7.2692 | FALSE | FALSE
2025-08-14 21:00 | 34.8 | 63.5 | 99350 | 100 | 3000 | 24.1916 | 78.3896 | 90.8694 | 0 | 7.2692 | FALSE | FALSE
2025-08-14 22:00 | 34.85 | 58 | 99340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-14 23:00 | 34.3 | 55.5 | 99315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-15 | 33.5 | 57 | 99300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-15 01:00 | 33.2 | 54 | 99290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-15 02:00 | 33.2 | 46.5 | 99295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-15 03:00 | 32.75 | 52.5 | 99340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-15 04:00 | 32.45 | 64.5 | 99385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-15 05:00 | 32.5 | 67.5 | 99415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-15 06:00 | 32.55 | 67.5 | 99455 | 100 | 3000 | 23.4021 | 79.2128 | 84.4855 | 0 | 7.2692 | FALSE | FALSE
2025-08-15 07:00 | 33.4 | 63.5 | 99490 | 100 | 3000 | 23.7165 | 76.9846 | 84.2038 | 0 | 7.2692 | FALSE | FALSE
2025-08-15 08:00 | 35.4 | 54.5 | 99500 | 100 | 3000 | 24.4502 | 71.6043 | 82.8853 | 0 | 7.2692 | FALSE | FALSE
2025-08-15 09:00 | 38.1 | 43.5 | 99500 | 100 | 3000 | 25.4285 | 64.2527 | 79.9875 | 0 | 7.2692 | FALSE | FALSE
2025-08-15 10:00 | 40.45 | 35.5 | 99475 | 100 | 3000 | 26.265 | 58.3362 | 77.3002 | 0 | 7.2692 | FALSE | FALSE
2025-08-15 11:00 | 41.7 | 32.5 | 99430 | 100 | 3000 | 26.6952 | 56.1017 | 77.0278 | 0 | 7.2692 | FALSE | FALSE
2025-08-15 12:00 | 42.15 | 31.5 | 99375 | 100 | 3000 | 26.8486 | 55.3421 | 76.9433 | 0 | 7.2692 | FALSE | FALSE
2025-08-15 13:00 | 42.45 | 30.5 | 99305 | 100 | 3000 | 26.9552 | 54.4866 | 76.2774 | 0 | 7.2692 | FALSE | FALSE
2025-08-15 14:00 | 42.55 | 30 | 99250 | 100 | 3000 | 26.9929 | 54.0296 | 75.7504 | 0 | 7.2692 | FALSE | FALSE
2025-08-15 15:00 | 42.3 | 29.5 | 99220 | 100 | 3000 | 26.9216 | 53.3987 | 74.0311 | 0 | 7.2692 | FALSE | FALSE
2025-08-15 16:00 | 42 | 27 | 99215 | 100 | 3000 | 26.8595 | 50.7371 | 68.797 | 0 | 7.2692 | FALSE | FALSE
2025-08-15 17:00 | 40.85 | 28.5 | 99225 | 100 | 3000 | 26.4721 | 51.7737 | 67.5366 | 0 | 7.2692 | FALSE | FALSE
2025-08-15 18:00 | 38.5 | 36.5 | 99240 | 100 | 3000 | 25.6219 | 58.2101 | 71.5429 | 0 | 7.2692 | FALSE | FALSE
2025-08-15 19:00 | 36.25 | 44 | 99270 | 100 | 3000 | 24.8087 | 63.4845 | 73.1892 | 0 | 7.2692 | FALSE | FALSE
2025-08-15 20:00 | 34.5 | 51.5 | 99300 | 100 | 3000 | 24.1618 | 68.4797 | 75.3068 | 0 | 7.2692 | FALSE | FALSE
2025-08-15 21:00 | 33.45 | 55.5 | 99310 | 100 | 3000 | 23.7751 | 70.8521 | 75.4236 | 0 | 7.2692 | FALSE | FALSE
2025-08-15 22:00 | 33.15 | 54 | 99300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-15 23:00 | 32.8 | 54 | 99300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-16 | 32.05 | 58 | 99320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-16 01:00 | 31.1 | 65 | 99325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-16 02:00 | 30.2 | 72 | 99325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-16 03:00 | 29.65 | 75 | 99355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-16 04:00 | 29.75 | 74.5 | 99395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-16 05:00 | 30.05 | 72.5 | 99425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-16 06:00 | 30.5 | 68.5 | 99465 | 100 | 3000 | 22.6691 | 78.0235 | 75.7072 | 0 | 7.2692 | FALSE | FALSE
2025-08-16 07:00 | 31.95 | 64 | 99510 | 100 | 3000 | 23.2068 | 76.0405 | 77.9519 | 0 | 7.2692 | FALSE | FALSE
2025-08-16 08:00 | 34.65 | 55.5 | 99540 | 100 | 3000 | 24.1898 | 71.7855 | 80.7642 | 0 | 7.2692 | FALSE | FALSE
2025-08-16 09:00 | 38 | 41 | 99540 | 100 | 3000 | 25.4174 | 61.9469 | 76.1129 | 0 | 7.2692 | FALSE | FALSE
2025-08-16 10:00 | 40.8 | 30 | 99510 | 100 | 3000 | 26.439 | 53.1902 | 69.866 | 0 | 7.2692 | FALSE | FALSE
2025-08-16 11:00 | 42.65 | 25 | 99460 | 100 | 3000 | 27.0924 | 48.9235 | 67.5015 | 0 | 7.2692 | FALSE | FALSE
2025-08-16 12:00 | 44 | 21.5 | 99385 | 100 | 3000 | 27.5683 | 45.6898 | 65.2412 | 0 | 7.2692 | FALSE | FALSE
2025-08-16 13:00 | 45 | 18.5 | 99295 | 100 | 3000 | 27.929 | 42.6935 | 62.3106 | 0 | 7.2692 | FALSE | FALSE
2025-08-16 14:00 | 45.65 | 16.5 | 99210 | 100 | 3000 | 28.1661 | 40.6039 | 60.035 | 0 | 7.2692 | FALSE | FALSE
2025-08-16 15:00 | 45.65 | 16 | 99155 | 100 | 3000 | 28.175 | 40.0474 | 59.009 | 0 | 7.2692 | FALSE | FALSE
2025-08-16 16:00 | 42.4 | 31 | 99195 | 100 | 3000 | 26.9328 | 54.9801 | 76.9182 | 0 | 7.2692 | FALSE | FALSE
2025-08-16 17:00 | 38.65 | 48 | 99250 | 100 | 3000 | 25.5646 | 68.767 | 88.5306 | 0 | 7.2692 | FALSE | FALSE
2025-08-16 18:00 | 37.55 | 51.5 | 99260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-16 19:00 | 37.15 | 52 | 99285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-16 20:00 | 37.1 | 48 | 99320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-16 21:00 | 37.25 | 42.5 | 99355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-16 22:00 | 36.8 | 43 | 99380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-16 23:00 | 35.5 | 49 | 99380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 | 34.7 | 50.5 | 99360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 01:00 | 34.3 | 46 | 99345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 02:00 | 33.75 | 41 | 99375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 03:00 | 32.95 | 45.5 | 99445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 04:00 | 32.65 | 49.5 | 99460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 05:00 | 32.25 | 52 | 99445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 06:00 | 32.1 | 56 | 99475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 07:00 | 33.95 | 50.5 | 99515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 08:00 | 37.05 | 38 | 99545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 09:00 | 39.9 | 27.5 | 99550 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 10:00 | 41.9 | 23.5 | 99520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 11:00 | 43.3 | 21 | 99470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 12:00 | 44.15 | 19.5 | 99395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 13:00 | 44.15 | 21 | 99325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 14:00 | 42.95 | 24.5 | 99280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 15:00 | 41.4 | 28.5 | 99255 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 16:00 | 39.85 | 33 | 99260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 17:00 | 38.25 | 39 | 99275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 18:00 | 36.65 | 46.5 | 99290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 19:00 | 35.45 | 52.5 | 99330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 20:00 | 35 | 55 | 99390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 21:00 | 34.6 | 56.5 | 99440 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 22:00 | 34 | 59.5 | 99470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-17 23:00 | 33.4 | 61 | 99505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-18 | 32.9 | 61 | 99525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-18 01:00 | 32.4 | 60.5 | 99515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-18 02:00 | 31.75 | 60.5 | 99510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-18 03:00 | 31.15 | 62 | 99515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-18 04:00 | 31.2 | 58.5 | 99515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-18 05:00 | 31.6 | 52.5 | 99540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-18 06:00 | 32.9 | 44 | 99590 | 100 | 3000 | 23.6371 | 61.6457 | 60.3109 | 0 | 7.2692 | FALSE | FALSE
2025-08-18 07:00 | 35.3 | 34 | 99620 | 100 | 3000 | 24.5474 | 54.6641 | 57.0108 | 0 | 7.2692 | FALSE | FALSE
2025-08-18 08:00 | 37.65 | 29 | 99640 | 100 | 3000 | 25.4003 | 51.12 | 58.0662 | 0 | 7.2692 | FALSE | FALSE
2025-08-18 09:00 | 39.8 | 25.5 | 99660 | 100 | 3000 | 26.1594 | 48.5206 | 59.6062 | 0 | 7.2692 | FALSE | FALSE
2025-08-18 10:00 | 41.55 | 23.5 | 99660 | 100 | 3000 | 26.7583 | 47.0535 | 61.6542 | 0 | 7.2692 | FALSE | FALSE
2025-08-18 11:00 | 42.9 | 22 | 99625 | 100 | 3000 | 27.213 | 45.8957 | 63.0302 | 0 | 7.2692 | FALSE | FALSE
2025-08-18 12:00 | 43.6 | 21 | 99565 | 100 | 3000 | 27.4498 | 45.0375 | 63.2275 | 0 | 7.2692 | FALSE | FALSE
2025-08-18 13:00 | 43.4 | 23 | 99500 | 100 | 3000 | 27.3574 | 47.0917 | 66.2564 | 0 | 7.2692 | FALSE | FALSE
2025-08-18 14:00 | 42.35 | 27.5 | 99445 | 100 | 3000 | 26.964 | 51.3672 | 70.8591 | 0 | 7.2692 | FALSE | FALSE
2025-08-18 15:00 | 40.8 | 31.5 | 99410 | 100 | 3000 | 26.4218 | 54.6567 | 72.2311 | 0 | 7.2692 | FALSE | FALSE
2025-08-18 16:00 | 39.5 | 34.5 | 99405 | 100 | 3000 | 25.9694 | 56.8736 | 72.2813 | 0 | 7.2692 | FALSE | FALSE
2025-08-18 17:00 | 38.4 | 38 | 99400 | 100 | 3000 | 25.5755 | 59.5008 | 73.3673 | 0 | 7.2692 | FALSE | FALSE
2025-08-18 18:00 | 37.35 | 41.5 | 99400 | 100 | 3000 | 25.1976 | 61.9992 | 74.2306 | 0 | 7.2692 | FALSE | FALSE
2025-08-18 19:00 | 36.75 | 43 | 99430 | 100 | 3000 | 24.9849 | 62.9287 | 73.9001 | 0 | 7.2692 | FALSE | FALSE
2025-08-18 20:00 | 36.25 | 43.5 | 99490 | 100 | 3000 | 24.8124 | 63.0425 | 72.6008 | 0 | 7.2692 | FALSE | FALSE
2025-08-18 21:00 | 35.55 | 45 | 99545 | 100 | 3000 | 24.5635 | 63.8654 | 71.755 | 0 | 7.2692 | FALSE | FALSE
2025-08-18 22:00 | 34.75 | 48 | 99560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-18 23:00 | 34.05 | 51.5 | 99565 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-19 | 33.6 | 53 | 99580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-19 01:00 | 33.15 | 54 | 99570 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-19 02:00 | 32.8 | 55.5 | 99545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-19 03:00 | 32.75 | 56 | 99560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-19 04:00 | 33.5 | 51 | 99580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-19 05:00 | 33.95 | 47 | 99600 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-19 06:00 | 34 | 47.5 | 99650 | 100 | 3000 | 24.0106 | 64.9382 | 68.6158 | 0 | 7.2692 | FALSE | FALSE
2025-08-19 07:00 | 35.15 | 45 | 99690 | 100 | 3000 | 24.4259 | 63.6114 | 70.2055 | 0 | 7.2692 | FALSE | FALSE
2025-08-19 08:00 | 36.85 | 40.5 | 99710 | 100 | 3000 | 25.0378 | 60.8122 | 71.044 | 0 | 7.2692 | FALSE | FALSE
2025-08-19 09:00 | 38.55 | 36 | 99715 | 100 | 3000 | 25.6434 | 57.7433 | 71.1424 | 0 | 7.2692 | FALSE | FALSE
2025-08-19 10:00 | 40.15 | 32 | 99690 | 100 | 3000 | 26.2068 | 54.8087 | 70.8468 | 0 | 7.2692 | FALSE | FALSE
2025-08-19 11:00 | 41.55 | 28.5 | 99630 | 100 | 3000 | 26.6974 | 52.0255 | 69.9696 | 0 | 7.2692 | FALSE | FALSE
2025-08-19 12:00 | 42.5 | 26 | 99545 | 100 | 3000 | 27.0314 | 49.8878 | 68.7943 | 0 | 7.2692 | FALSE | FALSE
2025-08-19 13:00 | 42.35 | 27.5 | 99470 | 100 | 3000 | 26.964 | 51.3653 | 70.8672 | 0 | 7.2692 | FALSE | FALSE
2025-08-19 14:00 | 41.25 | 33 | 99405 | 100 | 3000 | 26.5475 | 56.3556 | 76.2255 | 0 | 7.2692 | FALSE | FALSE
2025-08-19 15:00 | 39.9 | 39 | 99355 | 100 | 3000 | 26.0519 | 61.3458 | 80.5483 | 0 | 7.2692 | FALSE | FALSE
2025-08-19 16:00 | 38.05 | 47.5 | 99365 | 100 | 3000 | 25.377 | 67.8068 | 85.2912 | 0 | 7.2692 | FALSE | FALSE
2025-08-19 17:00 | 36.2 | 56.5 | 99370 | 100 | 3000 | 24.7025 | 74.0005 | 88.9591 | 0 | 7.2692 | FALSE | FALSE
2025-08-19 18:00 | 34.9 | 63.5 | 99365 | 100 | 3000 | 24.225 | 78.4924 | 91.3575 | 0 | 7.2692 | FALSE | FALSE
2025-08-19 19:00 | 34.05 | 68.5 | 99390 | 100 | 3000 | 23.9107 | 81.5663 | 92.9608 | 0 | 7.2692 | FALSE | FALSE
2025-08-19 20:00 | 33.7 | 70.5 | 99430 | 100 | 3000 | 23.7817 | 82.7354 | 93.4531 | 0 | 7.2692 | FALSE | FALSE
2025-08-19 21:00 | 33.6 | 70.5 | 99490 | 100 | 3000 | 23.748 | 82.6163 | 92.9609 | 0 | 7.2692 | FALSE | FALSE
2025-08-19 22:00 | 33.45 | 69.5 | 99515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-19 23:00 | 33.05 | 68.5 | 99505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-20 | 32.5 | 69.5 | 99485 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-20 01:00 | 31.95 | 71.5 | 99445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-20 02:00 | 31.5 | 71 | 99410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-20 03:00 | 31.35 | 68.5 | 99395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-20 04:00 | 31.95 | 63 | 99375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-20 05:00 | 32.4 | 59 | 99375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-20 06:00 | 33.05 | 57 | 99410 | 100 | 3000 | 23.6274 | 71.6914 | 75.3707 | 0 | 7.2692 | FALSE | FALSE
2025-08-20 07:00 | 34.3 | 54 | 99440 | 100 | 3000 | 24.0784 | 70.314 | 77.4311 | 0 | 7.2692 | FALSE | FALSE
2025-08-20 08:00 | 36.15 | 46.5 | 99460 | 100 | 3000 | 24.7573 | 65.5149 | 76.0544 | 0 | 7.2692 | FALSE | FALSE
2025-08-20 09:00 | 38.5 | 37 | 99485 | 100 | 3000 | 25.6176 | 58.6434 | 72.332 | 0 | 7.2692 | FALSE | FALSE
2025-08-20 10:00 | 40.4 | 32.5 | 99470 | 100 | 3000 | 26.2821 | 55.4246 | 72.4327 | 0 | 7.2692 | FALSE | FALSE
2025-08-20 11:00 | 42.05 | 29 | 99410 | 100 | 3000 | 26.8497 | 52.761 | 72.4013 | 0 | 7.2692 | FALSE | FALSE
2025-08-20 12:00 | 43.25 | 26 | 99325 | 100 | 3000 | 27.2669 | 50.1964 | 71.1132 | 0 | 7.2692 | FALSE | FALSE
2025-08-20 13:00 | 43.8 | 24.5 | 99230 | 100 | 3000 | 27.46 | 48.8344 | 70.1124 | 0 | 7.2692 | FALSE | FALSE
2025-08-20 14:00 | 43.8 | 23.5 | 99160 | 100 | 3000 | 27.4752 | 47.7761 | 68.2589 | 0 | 7.2692 | FALSE | FALSE
2025-08-20 15:00 | 42.7 | 29.5 | 99135 | 100 | 3000 | 27.0463 | 53.5991 | 75.3669 | 0 | 7.2692 | FALSE | FALSE
2025-08-20 16:00 | 40.7 | 37.5 | 99170 | 100 | 3000 | 26.3212 | 60.4482 | 81.2711 | 0 | 7.2692 | FALSE | FALSE
2025-08-20 17:00 | 39.1 | 41 | 99210 | 100 | 3000 | 25.7754 | 62.6927 | 80.3384 | 0 | 7.2692 | FALSE | FALSE
2025-08-20 18:00 | 38 | 44.5 | 99235 | 100 | 3000 | 25.3868 | 65.0984 | 80.8955 | 0 | 7.2692 | FALSE | FALSE
2025-08-20 19:00 | 37.5 | 46 | 99300 | 100 | 3000 | 25.2105 | 66.0569 | 80.9105 | 0 | 7.2692 | FALSE | FALSE
2025-08-20 20:00 | 37.4 | 45 | 99390 | 100 | 3000 | 25.1858 | 65.0989 | 79.1707 | 0 | 7.2692 | FALSE | FALSE
2025-08-20 21:00 | 36.65 | 44 | 99450 | 100 | 3000 | 24.9438 | 63.7218 | 74.8271 | 0 | 7.2692 | FALSE | FALSE
2025-08-20 22:00 | 35.15 | 47 | 99475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-20 23:00 | 33.9 | 51 | 99470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-21 | 33.3 | 52.5 | 99450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-21 01:00 | 33.25 | 51 | 99425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-21 02:00 | 33.45 | 48 | 99435 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-21 03:00 | 33.1 | 48 | 99470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-21 04:00 | 32.7 | 49 | 99545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-21 05:00 | 32.5 | 49 | 99660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-21 06:00 | 32.4 | 49.5 | 99745 | 100 | 3000 | 23.4316 | 65.5405 | 64.4746 | 0 | 7.2692 | FALSE | FALSE
2025-08-21 07:00 | 33.35 | 48.5 | 99805 | 100 | 3000 | 23.776 | 65.3201 | 67.1931 | 0 | 7.2692 | FALSE | FALSE
2025-08-21 08:00 | 35.2 | 44 | 99845 | 100 | 3000 | 24.4496 | 62.8085 | 69.2061 | 0 | 7.2692 | FALSE | FALSE
2025-08-21 09:00 | 37.1 | 38 | 99835 | 100 | 3000 | 25.1415 | 58.7713 | 68.6563 | 0 | 7.2692 | FALSE | FALSE
2025-08-21 10:00 | 38.8 | 32 | 99785 | 100 | 3000 | 25.763 | 54.2073 | 66.2226 | 0 | 7.2692 | FALSE | FALSE
2025-08-21 11:00 | 40.2 | 27.5 | 99730 | 100 | 3000 | 26.2711 | 50.5333 | 63.9992 | 0 | 7.2692 | FALSE | FALSE
2025-08-21 12:00 | 41.35 | 25 | 99655 | 100 | 3000 | 26.6753 | 48.4824 | 63.5461 | 0 | 7.2692 | FALSE | FALSE
2025-08-21 13:00 | 42.2 | 23 | 99570 | 100 | 3000 | 26.9751 | 46.7346 | 62.7052 | 0 | 7.2692 | FALSE | FALSE
2025-08-21 14:00 | 42.4 | 23 | 99490 | 100 | 3000 | 27.0394 | 46.7959 | 63.2717 | 0 | 7.2692 | FALSE | FALSE
2025-08-21 15:00 | 42.05 | 25 | 99445 | 100 | 3000 | 26.9011 | 48.7207 | 65.6354 | 0 | 7.2692 | FALSE | FALSE
2025-08-21 16:00 | 39.85 | 34 | 99480 | 100 | 3000 | 26.0883 | 56.5769 | 72.8026 | 0 | 7.2692 | FALSE | FALSE
2025-08-21 17:00 | 37.15 | 45 | 99520 | 100 | 3000 | 25.1033 | 64.9129 | 78.1871 | 0 | 7.2692 | FALSE | FALSE
2025-08-21 18:00 | 35.7 | 53.5 | 99550 | 100 | 3000 | 24.5577 | 71.0255 | 82.9952 | 0 | 7.2692 | FALSE | FALSE
2025-08-21 19:00 | 34.75 | 60.5 | 99610 | 100 | 3000 | 24.1936 | 75.8955 | 87.1586 | 0 | 7.2692 | FALSE | FALSE
2025-08-21 20:00 | 34.4 | 61.5 | 99685 | 100 | 3000 | 24.0696 | 76.3537 | 86.7016 | 0 | 7.2692 | FALSE | FALSE
2025-08-21 21:00 | 34.2 | 62 | 99755 | 100 | 3000 | 23.9989 | 76.552 | 86.3531 | 0 | 7.2692 | FALSE | FALSE
2025-08-21 22:00 | 33.9 | 64.5 | 99795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-21 23:00 | 33.4 | 66.5 | 99800 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-22 | 32.9 | 67 | 99780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-22 01:00 | 32.5 | 66.5 | 99750 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-22 02:00 | 32.15 | 66 | 99725 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-22 03:00 | 31.85 | 66 | 99730 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-22 04:00 | 32.15 | 58.5 | 99775 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-22 05:00 | 32.3 | 52 | 99820 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-22 06:00 | 32.15 | 53.5 | 99850 | 100 | 3000 | 23.324 | 68.3718 | 67.792 | 0 | 7.2692 | FALSE | FALSE
2025-08-22 07:00 | 33.05 | 51.5 | 99880 | 100 | 3000 | 23.6547 | 67.4375 | 69.3625 | 0 | 7.2692 | FALSE | FALSE
2025-08-22 08:00 | 34.75 | 46 | 99895 | 100 | 3000 | 24.2814 | 64.1678 | 69.89 | 0 | 7.2692 | FALSE | FALSE
2025-08-22 09:00 | 36.7 | 40 | 99890 | 100 | 3000 | 24.9908 | 60.2846 | 69.8584 | 0 | 7.2692 | FALSE | FALSE
2025-08-22 10:00 | 38.6 | 34.5 | 99850 | 100 | 3000 | 25.6736 | 56.3938 | 69.1924 | 0 | 7.2692 | FALSE | FALSE
2025-08-22 11:00 | 40.05 | 30.5 | 99785 | 100 | 3000 | 26.1902 | 53.3291 | 68.2058 | 0 | 7.2692 | FALSE | FALSE
2025-08-22 12:00 | 40.4 | 30 | 99720 | 100 | 3000 | 26.3096 | 53.0032 | 68.5839 | 0 | 7.2692 | FALSE | FALSE
2025-08-22 13:00 | 39.85 | 32.5 | 99655 | 100 | 3000 | 26.104 | 55.1456 | 70.5619 | 0 | 7.2692 | FALSE | FALSE
2025-08-22 14:00 | 39.15 | 36.5 | 99595 | 100 | 3000 | 25.8357 | 58.5316 | 74.0401 | 0 | 7.2692 | FALSE | FALSE
2025-08-22 15:00 | 38.3 | 43 | 99550 | 100 | 3000 | 25.4982 | 63.9388 | 80.1087 | 0 | 7.2692 | FALSE | FALSE
2025-08-22 16:00 | 37.4 | 48 | 99530 | 100 | 3000 | 25.1616 | 67.7166 | 83.2538 | 0 | 7.2692 | FALSE | FALSE
2025-08-22 17:00 | 36.45 | 52.5 | 99520 | 100 | 3000 | 24.8143 | 70.8228 | 85.0411 | 0 | 7.2692 | FALSE | FALSE
2025-08-22 18:00 | 35.5 | 59 | 99520 | 100 | 3000 | 24.454 | 75.4034 | 88.8504 | 0 | 7.2692 | FALSE | FALSE
2025-08-22 19:00 | 34.9 | 63.5 | 99550 | 100 | 3000 | 24.2253 | 78.4755 | 91.4048 | 0 | 7.2692 | FALSE | FALSE
2025-08-22 20:00 | 34.45 | 66 | 99600 | 100 | 3000 | 24.0598 | 80.0028 | 92.1398 | 0 | 7.2692 | FALSE | FALSE
2025-08-22 21:00 | 34 | 68 | 99645 | 100 | 3000 | 23.8971 | 81.0936 | 92.2075 | 0 | 7.2692 | FALSE | FALSE
2025-08-22 22:00 | 33.5 | 70 | 99655 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-22 23:00 | 32.8 | 73 | 99635 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-23 | 32.1 | 76 | 99605 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-23 01:00 | 31.5 | 78 | 99575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-23 02:00 | 30.95 | 80 | 99560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-23 03:00 | 30.65 | 81 | 99555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-23 04:00 | 30.9 | 77 | 99545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-23 05:00 | 31.2 | 71 | 99550 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-23 06:00 | 31.55 | 66.5 | 99585 | 100 | 3000 | 23.0542 | 77.5136 | 78.6853 | 0 | 7.2692 | FALSE | FALSE
2025-08-23 07:00 | 33 | 58 | 99630 | 100 | 3000 | 23.6051 | 72.3967 | 76.3051 | 0 | 7.2692 | FALSE | FALSE
2025-08-23 08:00 | 35.4 | 46.5 | 99660 | 100 | 3000 | 24.5024 | 65.0002 | 73.0546 | 0 | 7.2692 | FALSE | FALSE
2025-08-23 09:00 | 37.85 | 36 | 99675 | 100 | 3000 | 25.4102 | 57.3976 | 68.593 | 0 | 7.2692 | FALSE | FALSE
2025-08-23 10:00 | 39.6 | 30 | 99665 | 100 | 3000 | 26.0475 | 52.685 | 65.892 | 0 | 7.2692 | FALSE | FALSE
2025-08-23 11:00 | 40.35 | 29 | 99630 | 100 | 3000 | 26.3041 | 52.0305 | 66.8148 | 0 | 7.2692 | FALSE | FALSE
2025-08-23 12:00 | 40.55 | 29 | 99575 | 100 | 3000 | 26.3693 | 52.113 | 67.4575 | 0 | 7.2692 | FALSE | FALSE
2025-08-23 13:00 | 40.3 | 31 | 99505 | 100 | 3000 | 26.2661 | 53.9362 | 69.7488 | 0 | 7.2692 | FALSE | FALSE
2025-08-23 14:00 | 39.65 | 34.5 | 99430 | 100 | 3000 | 26.0182 | 56.9489 | 72.8287 | 0 | 7.2692 | FALSE | FALSE
2025-08-23 15:00 | 38.95 | 38 | 99380 | 100 | 3000 | 25.7559 | 59.8185 | 75.4309 | 0 | 7.2692 | FALSE | FALSE
2025-08-23 16:00 | 37.9 | 41.5 | 99355 | 100 | 3000 | 25.3799 | 62.3452 | 76.3659 | 0 | 7.2692 | FALSE | FALSE
2025-08-23 17:00 | 36.4 | 48 | 99345 | 100 | 3000 | 24.8304 | 66.9718 | 78.9875 | 0 | 7.2692 | FALSE | FALSE
2025-08-23 18:00 | 35 | 55.5 | 99360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-23 19:00 | 34.1 | 60.5 | 99400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-23 20:00 | 33.55 | 65 | 99455 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-23 21:00 | 33.1 | 68.5 | 99495 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-23 22:00 | 32.55 | 72 | 99510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-23 23:00 | 31.9 | 75 | 99490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 | 31.4 | 77 | 99475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 01:00 | 30.95 | 77.5 | 99470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 02:00 | 30.55 | 76.5 | 99460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 03:00 | 30.35 | 75 | 99460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 04:00 | 30.85 | 71 | 99450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 05:00 | 31.35 | 68.5 | 99455 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 06:00 | 31.55 | 68.5 | 99505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 07:00 | 32.65 | 66 | 99575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 08:00 | 34.35 | 60.5 | 99630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 09:00 | 36.15 | 52.5 | 99665 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 10:00 | 37.95 | 43.5 | 99670 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 11:00 | 39.1 | 37.5 | 99650 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 12:00 | 39.45 | 36 | 99625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 13:00 | 39.35 | 37.5 | 99585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 14:00 | 38.9 | 40 | 99525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 15:00 | 38.4 | 41 | 99480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 16:00 | 37.5 | 44 | 99490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 17:00 | 36.2 | 51 | 99505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 18:00 | 34.95 | 59 | 99520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 19:00 | 34.05 | 65 | 99570 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 20:00 | 33.5 | 68 | 99615 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 21:00 | 32.8 | 70 | 99640 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 22:00 | 32.05 | 71 | 99635 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-24 23:00 | 31.3 | 72 | 99625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-25 | 30.45 | 74 | 99610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-25 01:00 | 29.6 | 74.5 | 99585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-25 02:00 | 28.8 | 73 | 99580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-25 03:00 | 28.65 | 68.5 | 99580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-25 04:00 | 29.8 | 60.5 | 99560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-25 05:00 | 30.55 | 55 | 99560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-25 06:00 | 31 | 51 | 99595 | 100 | 3000 | 22.9155 | 65.8955 | 60.4218 | 0 | 7.2692 | FALSE | FALSE
2025-08-25 07:00 | 32.8 | 43.5 | 99640 | 100 | 3000 | 23.6034 | 61.215 | 59.3866 | 0 | 7.2692 | FALSE | FALSE
2025-08-25 08:00 | 35.15 | 35 | 99685 | 100 | 3000 | 24.4882 | 55.4291 | 57.775 | 0 | 7.2692 | FALSE | FALSE
2025-08-25 09:00 | 37.55 | 27 | 99700 | 100 | 3000 | 25.3821 | 49.325 | 54.9533 | 0 | 7.2692 | FALSE | FALSE
2025-08-25 10:00 | 39.95 | 20 | 99695 | 100 | 3000 | 26.266 | 43.3515 | 51.4338 | 0 | 7.2692 | FALSE | FALSE
2025-08-25 11:00 | 41.65 | 16 | 99650 | 100 | 3000 | 26.8821 | 39.6134 | 49.2207 | 0 | 7.2692 | FALSE | FALSE
2025-08-25 12:00 | 42.05 | 16.5 | 99585 | 100 | 3000 | 27.0091 | 40.1427 | 51.0528 | 0 | 7.2692 | FALSE | FALSE
2025-08-25 13:00 | 41.5 | 19.5 | 99530 | 100 | 3000 | 26.7902 | 43.0833 | 54.7453 | 0 | 7.2692 | FALSE | FALSE
2025-08-25 14:00 | 40.85 | 23 | 99475 | 100 | 3000 | 26.5347 | 46.4018 | 58.7071 | 0 | 7.2692 | FALSE | FALSE
2025-08-25 15:00 | 40.25 | 26 | 99435 | 100 | 3000 | 26.3036 | 49.1395 | 61.7036 | 0 | 7.2692 | FALSE | FALSE
2025-08-25 16:00 | 39.75 | 24.5 | 99455 | 100 | 3000 | 26.1529 | 47.5819 | 57.8415 | 0 | 7.2692 | FALSE | FALSE
2025-08-25 17:00 | 38.6 | 26.5 | 99495 | 100 | 3000 | 25.7459 | 49.1472 | 57.3971 | 0 | 7.2692 | FALSE | FALSE
2025-08-25 18:00 | 36.55 | 39.5 | 99515 | 100 | 3000 | 24.9433 | 59.8089 | 68.5327 | 0 | 7.2692 | FALSE | FALSE
2025-08-25 19:00 | 35 | 51 | 99530 | 100 | 3000 | 24.3368 | 68.4202 | 76.8861 | 0 | 7.2692 | FALSE | FALSE
2025-08-25 20:00 | 33.9 | 55 | 99545 | 100 | 3000 | 23.9346 | 70.786 | 76.874 | 0 | 7.2692 | FALSE | FALSE
2025-08-25 21:00 | 32.7 | 55.5 | 99580 | 100 | 3000 | 23.5112 | 70.2727 | 72.2333 | 0 | 7.2692 | FALSE | FALSE
2025-08-25 22:00 | 31.65 | 53.5 | 99595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-25 23:00 | 30.8 | 49.5 | 99580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-26 | 30.05 | 45 | 99565 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-26 01:00 | 29.3 | 42.5 | 99555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-26 02:00 | 28.5 | 41.5 | 99540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-26 03:00 | 27.95 | 39.5 | 99520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-26 04:00 | 28.4 | 39 | 99525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-26 05:00 | 28.9 | 40 | 99575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-26 06:00 | 29.5 | 37 | 99635 | 100 | 3000 | 22.3986 | 55.537 | 41.0355 | 0 | 7.2692 | FALSE | FALSE
2025-08-26 07:00 | 31.65 | 30.5 | 99690 | 100 | 3000 | 23.2362 | 51.1704 | 41.2098 | 0 | 7.2692 | FALSE | FALSE
2025-08-26 08:00 | 34.55 | 25 | 99735 | 100 | 3000 | 24.3328 | 47.1845 | 43.437 | 0 | 7.2692 | FALSE | FALSE
2025-08-26 09:00 | 37.35 | 21 | 99760 | 100 | 3000 | 25.3599 | 44.0218 | 45.9348 | 0 | 7.2692 | FALSE | FALSE
2025-08-26 10:00 | 39.7 | 18 | 99760 | 100 | 3000 | 26.2011 | 41.4401 | 47.6463 | 0 | 7.2692 | FALSE | FALSE
2025-08-26 11:00 | 41.4 | 15.5 | 99715 | 100 | 3000 | 26.8043 | 39.1038 | 47.7806 | 0 | 7.2692 | FALSE | FALSE
2025-08-26 12:00 | 42.6 | 13.5 | 99640 | 100 | 3000 | 27.2301 | 37.1138 | 47.405 | 0 | 7.2692 | FALSE | FALSE
2025-08-26 13:00 | 43.2 | 14 | 99565 | 100 | 3000 | 27.4215 | 37.642 | 49.3582 | 0 | 7.2692 | FALSE | FALSE
2025-08-26 14:00 | 43.2 | 14.5 | 99500 | 100 | 3000 | 27.4146 | 38.1671 | 50.2532 | 0 | 7.2692 | FALSE | FALSE
2025-08-26 15:00 | 42.65 | 14 | 99475 | 100 | 3000 | 27.2402 | 37.6374 | 48.0481 | 0 | 7.2692 | FALSE | FALSE
2025-08-26 16:00 | 41.85 | 15 | 99485 | 100 | 3000 | 26.9613 | 38.6345 | 47.93 | 0 | 7.2692 | FALSE | FALSE
2025-08-26 17:00 | 40.6 | 19 | 99495 | 100 | 3000 | 26.496 | 42.4831 | 51.5032 | 0 | 7.2692 | FALSE | FALSE
2025-08-26 18:00 | 38.5 | 27.5 | 99520 | 100 | 3000 | 25.703 | 50.0267 | 58.5632 | 0 | 7.2692 | FALSE | FALSE
2025-08-26 19:00 | 36.65 | 35 | 99565 | 100 | 3000 | 25.0106 | 56.0007 | 62.9334 | 0 | 7.2692 | FALSE | FALSE
2025-08-26 20:00 | 35.6 | 36.5 | 99600 | 100 | 3000 | 24.6365 | 56.8398 | 61.2135 | 0 | 7.2692 | FALSE | FALSE
2025-08-26 21:00 | 35 | 35 | 99620 | 100 | 3000 | 24.4352 | 55.3837 | 57.2454 | 0 | 7.2692 | FALSE | FALSE
2025-08-26 22:00 | 34.5 | 34.5 | 99620 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-26 23:00 | 33.45 | 47.5 | 99600 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-27 | 32.3 | 64 | 99575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-27 01:00 | 31.45 | 68.5 | 99545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-27 02:00 | 30.7 | 70.5 | 99530 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-27 03:00 | 30.05 | 74 | 99540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-27 04:00 | 29.95 | 75.5 | 99540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-27 05:00 | 30 | 75.5 | 99550 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-27 06:00 | 30.15 | 75.5 | 99595 | 100 | 3000 | 22.5182 | 82.5889 | 80.7989 | 0 | 7.2692 | FALSE | FALSE
2025-08-27 07:00 | 31.75 | 70.5 | 99650 | 100 | 3000 | 23.1086 | 80.6234 | 83.7704 | 0 | 7.2692 | FALSE | FALSE
2025-08-27 08:00 | 34.65 | 59.5 | 99690 | 100 | 3000 | 24.166 | 74.9886 | 85.5317 | 0 | 7.2692 | FALSE | FALSE
2025-08-27 09:00 | 38.05 | 44 | 99700 | 100 | 3000 | 25.408 | 64.6479 | 80.5379 | 0 | 7.2692 | FALSE | FALSE
2025-08-27 10:00 | 40.95 | 29.5 | 99690 | 100 | 3000 | 26.4931 | 52.7534 | 69.6236 | 0 | 7.2692 | FALSE | FALSE
2025-08-27 11:00 | 42.8 | 21.5 | 99640 | 100 | 3000 | 27.1879 | 45.3526 | 61.8594 | 0 | 7.2692 | FALSE | FALSE
2025-08-27 12:00 | 44.05 | 17.5 | 99555 | 100 | 3000 | 27.6453 | 41.4129 | 57.9597 | 0 | 7.2692 | FALSE | FALSE
2025-08-27 13:00 | 45 | 15 | 99470 | 100 | 3000 | 27.9875 | 38.8338 | 55.517 | 0 | 7.2692 | FALSE | FALSE
2025-08-27 14:00 | 45.15 | 16 | 99405 | 100 | 3000 | 28.0181 | 39.9575 | 57.8373 | 0 | 7.2692 | FALSE | FALSE
2025-08-27 15:00 | 44.05 | 20.5 | 99385 | 100 | 3000 | 27.5993 | 44.6337 | 63.5231 | 0 | 7.2692 | FALSE | FALSE
2025-08-27 16:00 | 41.85 | 31.5 | 99410 | 100 | 3000 | 26.7548 | 55.1812 | 75.8981 | 0 | 7.2692 | FALSE | FALSE
2025-08-27 17:00 | 39.9 | 41.5 | 99430 | 100 | 3000 | 26.0256 | 63.7068 | 84.3406 | 0 | 7.2692 | FALSE | FALSE
2025-08-27 18:00 | 39.05 | 42.5 | 99465 | 100 | 3000 | 25.7451 | 64.0211 | 82.3962 | 0 | 7.2692 | FALSE | FALSE
2025-08-27 19:00 | 38.6 | 40.5 | 99535 | 100 | 3000 | 25.6185 | 61.8771 | 77.7458 | 0 | 7.2692 | FALSE | FALSE
2025-08-27 20:00 | 37.4 | 43 | 99600 | 100 | 3000 | 25.2023 | 63.3278 | 76.5196 | 0 | 7.2692 | FALSE | FALSE
2025-08-27 21:00 | 35.7 | 49.5 | 99650 | 100 | 3000 | 24.5847 | 67.6914 | 78.0332 | 0 | 7.2692 | FALSE | FALSE
2025-08-27 22:00 | 34.25 | 55.5 | 99670 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-27 23:00 | 33.25 | 60.5 | 99650 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-28 | 32.75 | 62 | 99610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-28 01:00 | 32.35 | 60 | 99575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-28 02:00 | 31.85 | 55.5 | 99565 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-28 03:00 | 31.25 | 49.5 | 99580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-28 04:00 | 32.7 | 40 | 99630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-28 05:00 | 33.8 | 34 | 99710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-28 06:00 | 33.2 | 35 | 99785 | 100 | 3000 | 23.7892 | 54.8304 | 51.2012 | 0 | 7.2692 | FALSE | FALSE
2025-08-28 07:00 | 33.7 | 41.5 | 99835 | 100 | 3000 | 23.9366 | 60.0512 | 60.4987 | 0 | 7.2692 | FALSE | FALSE
2025-08-28 08:00 | 35.4 | 45.5 | 99860 | 100 | 3000 | 24.509 | 64.1587 | 71.862 | 0 | 7.2692 | FALSE | FALSE
2025-08-28 09:00 | 38.05 | 39 | 99865 | 100 | 3000 | 25.4515 | 60.1624 | 73.5964 | 0 | 7.2692 | FALSE | FALSE
2025-08-28 10:00 | 40.6 | 30.5 | 99835 | 100 | 3000 | 26.369 | 53.5619 | 70.0857 | 0 | 7.2692 | FALSE | FALSE
2025-08-28 11:00 | 42.6 | 24 | 99780 | 100 | 3000 | 27.0901 | 47.8564 | 65.7082 | 0 | 7.2692 | FALSE | FALSE
2025-08-28 12:00 | 44.1 | 19.5 | 99715 | 100 | 3000 | 27.6304 | 43.5512 | 61.9058 | 0 | 7.2692 | FALSE | FALSE
2025-08-28 13:00 | 44.75 | 18 | 99625 | 100 | 3000 | 27.859 | 42.071 | 60.7845 | 0 | 7.2692 | FALSE | FALSE
2025-08-28 14:00 | 43.6 | 24 | 99540 | 100 | 3000 | 27.4054 | 48.2088 | 68.688 | 0 | 7.2692 | FALSE | FALSE
2025-08-28 15:00 | 41.5 | 32.5 | 99505 | 100 | 3000 | 26.6325 | 55.9875 | 76.3379 | 0 | 7.2692 | FALSE | FALSE
2025-08-28 16:00 | 40.05 | 35.5 | 99525 | 100 | 3000 | 26.1371 | 58.1028 | 75.838 | 0 | 7.2692 | FALSE | FALSE
2025-08-28 17:00 | 39.1 | 37 | 99550 | 100 | 3000 | 25.8145 | 58.9695 | 74.5781 | 0 | 7.2692 | FALSE | FALSE
2025-08-28 18:00 | 38.1 | 41 | 99555 | 100 | 3000 | 25.4503 | 62.0086 | 76.5075 | 0 | 7.2692 | FALSE | FALSE
2025-08-28 19:00 | 37.05 | 45 | 99590 | 100 | 3000 | 25.0701 | 64.8378 | 77.7994 | 0 | 7.2692 | FALSE | FALSE
2025-08-28 20:00 | 36.25 | 46 | 99650 | 100 | 3000 | 24.7948 | 65.1439 | 75.8704 | 0 | 7.2692 | FALSE | FALSE
2025-08-28 21:00 | 35.45 | 46 | 99700 | 100 | 3000 | 24.5228 | 64.6163 | 72.6445 | 0 | 7.2692 | FALSE | FALSE
2025-08-28 22:00 | 34.65 | 45.5 | 99710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-28 23:00 | 34 | 45 | 99675 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-29 | 33.3 | 47 | 99645 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-29 01:00 | 32.45 | 51.5 | 99630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-29 02:00 | 31.7 | 55.5 | 99625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-29 03:00 | 30.9 | 57.5 | 99650 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-29 04:00 | 30.5 | 55 | 99685 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-29 05:00 | 30.4 | 51 | 99740 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-29 06:00 | 30.65 | 48.5 | 99800 | 100 | 3000 | 22.7952 | 63.9172 | 56.5507 | 0 | 7.2692 | FALSE | FALSE
2025-08-29 07:00 | 32.5 | 43.5 | 99830 | 100 | 3000 | 23.4948 | 61.0671 | 58.3074 | 0 | 7.2692 | FALSE | FALSE
2025-08-29 08:00 | 35.95 | 34.5 | 99835 | 100 | 3000 | 24.7719 | 55.285 | 59.9209 | 0 | 7.2692 | FALSE | FALSE
2025-08-29 09:00 | 39 | 28 | 99830 | 100 | 3000 | 25.8672 | 50.6053 | 60.9702 | 0 | 7.2692 | FALSE | FALSE
2025-08-29 10:00 | 40.85 | 25 | 99800 | 100 | 3000 | 26.5121 | 48.3228 | 62.0606 | 0 | 7.2692 | FALSE | FALSE
2025-08-29 11:00 | 42.4 | 21.5 | 99735 | 100 | 3000 | 27.0591 | 45.2494 | 60.7433 | 0 | 7.2692 | FALSE | FALSE
2025-08-29 12:00 | 43.5 | 19 | 99660 | 100 | 3000 | 27.4473 | 42.9004 | 59.3173 | 0 | 7.2692 | FALSE | FALSE
2025-08-29 13:00 | 43.35 | 21 | 99590 | 100 | 3000 | 27.3705 | 44.9727 | 62.5218 | 0 | 7.2692 | FALSE | FALSE
2025-08-29 14:00 | 42.4 | 24 | 99535 | 100 | 3000 | 27.0262 | 47.8118 | 65.0199 | 0 | 7.2692 | FALSE | FALSE
2025-08-29 15:00 | 41.2 | 27 | 99510 | 100 | 3000 | 26.6029 | 50.4151 | 66.3237 | 0 | 7.2692 | FALSE | FALSE
2025-08-29 16:00 | 39.7 | 33 | 99515 | 100 | 3000 | 26.0499 | 55.5571 | 70.7572 | 0 | 7.2692 | FALSE | FALSE
2025-08-29 17:00 | 37.8 | 44.5 | 99510 | 100 | 3000 | 25.3217 | 64.9315 | 80.1561 | 0 | 7.2692 | FALSE | FALSE
2025-08-29 18:00 | 35.7 | 57.5 | 99515 | 100 | 3000 | 24.5305 | 74.3527 | 87.9385 | 0 | 7.2692 | FALSE | FALSE
2025-08-29 19:00 | 34.5 | 64.5 | 99565 | 100 | 3000 | 24.0854 | 78.8607 | 90.6375 | 0 | 7.2692 | FALSE | FALSE
2025-08-29 20:00 | 34.1 | 66 | 99650 | 100 | 3000 | 23.9421 | 79.6246 | 90.4311 | 0 | 7.2692 | FALSE | FALSE
2025-08-29 21:00 | 33.9 | 61.5 | 99700 | 100 | 3000 | 23.8993 | 75.8781 | 84.3554 | 0 | 7.2692 | FALSE | FALSE
2025-08-29 22:00 | 33.55 | 58 | 99700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-29 23:00 | 32.7 | 60.5 | 99695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-30 | 31.7 | 66.5 | 99680 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-30 01:00 | 31.15 | 74 | 99670 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-30 02:00 | 30.85 | 84 | 99680 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-30 03:00 | 30.45 | 93 | 99700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-30 04:00 | 30.2 | 86.5 | 99720 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-30 05:00 | 29.8 | 75.5 | 99765 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-30 06:00 | 30.05 | 69.5 | 99830 | 100 | 3000 | 22.5022 | 78.2945 | 74.6209 | 0 | 7.2692 | FALSE | FALSE
2025-08-30 07:00 | 32.2 | 57 | 99875 | 100 | 3000 | 23.3266 | 71.0115 | 71.7544 | 0 | 7.2692 | FALSE | FALSE
2025-08-30 08:00 | 35.9 | 38.5 | 99890 | 100 | 3000 | 24.7275 | 58.612 | 64.9263 | 0 | 7.2692 | FALSE | FALSE
2025-08-30 09:00 | 39.65 | 23 | 99885 | 100 | 3000 | 26.1342 | 46.1178 | 55.35 | 0 | 7.2692 | FALSE | FALSE
2025-08-30 10:00 | 41.85 | 18.5 | 99865 | 100 | 3000 | 26.9178 | 42.1105 | 54.0847 | 0 | 7.2692 | FALSE | FALSE
2025-08-30 11:00 | 43.15 | 18.5 | 99830 | 100 | 3000 | 27.3419 | 42.3029 | 57.5224 | 0 | 7.2692 | FALSE | FALSE
2025-08-30 12:00 | 44.25 | 17.5 | 99775 | 100 | 3000 | 27.7089 | 41.4295 | 58.5584 | 0 | 7.2692 | FALSE | FALSE
2025-08-30 13:00 | 43.6 | 22.5 | 99710 | 100 | 3000 | 27.4277 | 46.6112 | 66.0167 | 0 | 7.2692 | FALSE | FALSE
2025-08-30 14:00 | 41.3 | 32.5 | 99680 | 100 | 3000 | 26.5696 | 55.8671 | 75.6812 | 0 | 7.2692 | FALSE | FALSE
2025-08-30 15:00 | 39.45 | 41 | 99665 | 100 | 3000 | 25.8882 | 62.8955 | 81.863 | 0 | 7.2692 | FALSE | FALSE
2025-08-30 16:00 | 38.05 | 49.5 | 99660 | 100 | 3000 | 25.36 | 69.57 | 88.131 | 0 | 7.2692 | FALSE | FALSE
2025-08-30 17:00 | 36.7 | 58.5 | 99680 | 100 | 3000 | 24.8514 | 76.1676 | 93.9221 | 0 | 7.2692 | FALSE | FALSE
2025-08-30 18:00 | 35.7 | 64.5 | 99705 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-30 19:00 | 35 | 67 | 99750 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-30 20:00 | 34.35 | 69.5 | 99800 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-30 21:00 | 33.85 | 69.5 | 99840 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-30 22:00 | 33.45 | 67 | 99835 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-30 23:00 | 33 | 65.5 | 99790 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 | 32.4 | 67.5 | 99750 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 01:00 | 31.6 | 74.5 | 99715 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 02:00 | 31.05 | 81 | 99710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 03:00 | 30.7 | 83.5 | 99720 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 04:00 | 30.45 | 72.5 | 99735 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 05:00 | 30.15 | 56.5 | 99790 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 06:00 | 30.25 | 52.5 | 99835 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 07:00 | 32 | 50 | 99870 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 08:00 | 35.45 | 37 | 99910 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 09:00 | 38.55 | 25.5 | 99915 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 10:00 | 40.6 | 23 | 99895 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 11:00 | 42.3 | 21 | 99845 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 12:00 | 43.7 | 18.5 | 99775 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 13:00 | 44.75 | 16.5 | 99695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 14:00 | 44.75 | 17 | 99610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 15:00 | 43.15 | 22.5 | 99555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 16:00 | 40.5 | 32.5 | 99555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 17:00 | 38.2 | 41.5 | 99565 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 18:00 | 36.8 | 47 | 99580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 19:00 | 36.1 | 48.5 | 99620 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 20:00 | 35.7 | 45.5 | 99645 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 21:00 | 34.95 | 43 | 99660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 22:00 | 34.1 | 44 | 99635 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-08-31 23:00 | 33.1 | 49 | 99595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-01 | 31.8 | 63.5 | 99575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-01 01:00 | 30.85 | 80.5 | 99555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-01 02:00 | 30.3 | 88.5 | 99540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-01 03:00 | 29.85 | 89 | 99540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-01 04:00 | 29.25 | 82 | 99555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-01 05:00 | 28.65 | 73 | 99570 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-01 06:00 | 29.1 | 62.5 | 99595 | 100 | 3000 | 22.1723 | 72.7847 | 63.6659 | 0 | 7.2692 | FALSE | FALSE
2025-09-01 07:00 | 31.6 | 46.5 | 99610 | 100 | 3000 | 23.1535 | 62.92 | 58.0968 | 0 | 7.2692 | FALSE | FALSE
2025-09-01 08:00 | 35.45 | 33.5 | 99615 | 100 | 3000 | 24.6034 | 54.3005 | 56.8807 | 0 | 7.2692 | FALSE | FALSE
2025-09-01 09:00 | 38.95 | 26 | 99605 | 100 | 3000 | 25.8691 | 48.7698 | 57.7582 | 0 | 7.2692 | FALSE | FALSE
2025-09-01 10:00 | 41.45 | 20 | 99565 | 100 | 3000 | 26.7677 | 43.5683 | 55.4632 | 0 | 7.2692 | FALSE | FALSE
2025-09-01 11:00 | 43.25 | 15.5 | 99510 | 100 | 3000 | 27.4168 | 39.2115 | 52.2088 | 0 | 7.2692 | FALSE | FALSE
2025-09-01 12:00 | 43.05 | 19.5 | 99460 | 100 | 3000 | 27.2958 | 43.3514 | 58.9324 | 0 | 7.2692 | FALSE | FALSE
2025-09-01 13:00 | 41 | 29.5 | 99410 | 100 | 3000 | 26.5091 | 52.7965 | 69.7035 | 0 | 7.2692 | FALSE | FALSE
2025-09-01 14:00 | 39.3 | 38 | 99350 | 100 | 3000 | 25.8695 | 60.0293 | 76.747 | 0 | 7.2692 | FALSE | FALSE
2025-09-01 15:00 | 38.1 | 45.5 | 99315 | 100 | 3000 | 25.4107 | 66.06 | 82.7181 | 0 | 7.2692 | FALSE | FALSE
2025-09-01 16:00 | 37 | 50 | 99325 | 100 | 3000 | 25.0142 | 69.1551 | 84.1435 | 0 | 7.2692 | FALSE | FALSE
2025-09-01 17:00 | 35.55 | 57 | 99350 | 100 | 3000 | 24.4837 | 73.8133 | 86.5898 | 0 | 7.2692 | FALSE | FALSE
2025-09-01 18:00 | 33.95 | 69 | 99390 | 100 | 3000 | 23.8742 | 81.848 | 93.0243 | 0 | 7.2692 | FALSE | FALSE
2025-09-01 19:00 | 33 | 77.5 | 99440 | 100 | 3000 | 23.5084 | 87.2869 | 97.4642 | 0 | 7.2692 | FALSE | FALSE
2025-09-01 20:00 | 32.45 | 82 | 99480 | 100 | 3000 | 23.2999 | 89.9685 | 99.2614 | 0 | 7.2692 | FALSE | FALSE
2025-09-01 21:00 | 31.9 | 86 | 99500 | 100 | 3000 | 23.0941 | 92.1889 | 100.3386 | 0 | 7.2692 | FALSE | FALSE
2025-09-01 22:00 | 31.2 | 90 | 99490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-01 23:00 | 30.45 | 94 | 99460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-02 | 29.8 | 97 | 99420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-02 01:00 | 29.3 | 98.5 | 99390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-02 02:00 | 28.85 | 99 | 99390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-02 03:00 | 28.45 | 99 | 99410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-02 04:00 | 28.75 | 96 | 99430 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-02 05:00 | 29.1 | 92.5 | 99465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-02 06:00 | 29.25 | 90.5 | 99515 | 100 | 3000 | 22.1449 | 91.8625 | 89.9927 | 0 | 7.2692 | FALSE | FALSE
2025-09-02 07:00 | 30.45 | 84.5 | 99550 | 100 | 3000 | 22.5943 | 89.2233 | 90.9422 | 0 | 7.2692 | FALSE | FALSE
2025-09-02 08:00 | 32.55 | 76.5 | 99580 | 100 | 3000 | 23.3601 | 85.9644 | 94.0603 | 0 | 7.2692 | FALSE | FALSE
2025-09-02 09:00 | 34.75 | 67.5 | 99585 | 100 | 3000 | 24.1508 | 81.5392 | 95.3719 | 0 | 7.2692 | FALSE | FALSE
2025-09-02 10:00 | 36.75 | 57 | 99550 | 100 | 3000 | 24.8788 | 74.9432 | 92.1958 | 0 | 7.2692 | FALSE | FALSE
2025-09-02 11:00 | 38.55 | 47.5 | 99500 | 100 | 3000 | 25.5379 | 68.2062 | 87.4684 | 0 | 7.2692 | FALSE | FALSE
2025-09-02 12:00 | 39.65 | 43 | 99435 | 100 | 3000 | 25.931 | 64.9343 | 85.5653 | 0 | 7.2692 | FALSE | FALSE
2025-09-02 13:00 | 39.25 | 45.5 | 99370 | 100 | 3000 | 25.7792 | 66.9587 | 87.5504 | 0 | 7.2692 | FALSE | FALSE
2025-09-02 14:00 | 38.55 | 46 | 99320 | 100 | 3000 | 25.5514 | 66.859 | 85.301 | 0 | 7.2692 | FALSE | FALSE
2025-09-02 15:00 | 38 | 46.5 | 99290 | 100 | 3000 | 25.3694 | 66.8799 | 83.6778 | 0 | 7.2692 | FALSE | FALSE
2025-09-02 16:00 | 37.1 | 48.5 | 99310 | 100 | 3000 | 25.0588 | 67.936 | 82.5852 | 0 | 7.2692 | FALSE | FALSE
2025-09-02 17:00 | 35.8 | 53.5 | 99360 | 100 | 3000 | 24.5909 | 71.1266 | 83.388 | 0 | 7.2692 | FALSE | FALSE
2025-09-02 18:00 | 34.25 | 64.5 | 99400 | 100 | 3000 | 24.0009 | 78.6167 | 89.3828 | 0 | 7.2692 | FALSE | FALSE
2025-09-02 19:00 | 33.45 | 71 | 99470 | 100 | 3000 | 23.6944 | 82.8357 | 92.7485 | 0 | 7.2692 | FALSE | FALSE
2025-09-02 20:00 | 33.25 | 72.5 | 99560 | 100 | 3000 | 23.6188 | 83.754 | 93.3944 | 0 | 7.2692 | FALSE | FALSE
2025-09-02 21:00 | 33 | 75 | 99620 | 100 | 3000 | 23.5212 | 85.3661 | 94.8238 | 0 | 7.2692 | FALSE | FALSE
2025-09-02 22:00 | 32.45 | 79.5 | 99625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-02 23:00 | 31.7 | 84.5 | 99605 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-03 | 30.9 | 88.5 | 99575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-03 01:00 | 30.05 | 92 | 99535 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-03 02:00 | 29.35 | 95 | 99525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-03 03:00 | 28.9 | 95.5 | 99545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-03 04:00 | 28.65 | 93 | 99575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-03 05:00 | 28.45 | 90.5 | 99605 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-03 06:00 | 28.8 | 86 | 99650 | 100 | 3000 | 21.9944 | 88.2907 | 83.5646 | 0 | 7.2692 | FALSE | FALSE
2025-09-03 07:00 | 30.7 | 72.5 | 99700 | 100 | 3000 | 22.7271 | 81.017 | 80.6355 | 0 | 7.2692 | FALSE | FALSE
2025-09-03 08:00 | 34.1 | 50.5 | 99720 | 100 | 3000 | 24.0291 | 67.3665 | 72.5497 | 0 | 7.2692 | FALSE | FALSE
2025-09-03 09:00 | 37.55 | 29.5 | 99720 | 100 | 3000 | 25.362 | 51.5255 | 58.4708 | 0 | 7.2692 | FALSE | FALSE
2025-09-03 10:00 | 39.8 | 19.5 | 99715 | 100 | 3000 | 26.2202 | 42.8619 | 50.2502 | 0 | 7.2692 | FALSE | FALSE
2025-09-03 11:00 | 41.1 | 17.5 | 99680 | 100 | 3000 | 26.6805 | 41.0573 | 50.3881 | 0 | 7.2692 | FALSE | FALSE
2025-09-03 12:00 | 42 | 16.5 | 99620 | 100 | 3000 | 26.9925 | 40.1365 | 50.9393 | 0 | 7.2692 | FALSE | FALSE
2025-09-03 13:00 | 42.45 | 16 | 99550 | 100 | 3000 | 27.1477 | 39.6671 | 51.1572 | 0 | 7.2692 | FALSE | FALSE
2025-09-03 14:00 | 42.1 | 16 | 99500 | 100 | 3000 | 27.032 | 39.6483 | 50.2782 | 0 | 7.2692 | FALSE | FALSE
2025-09-03 15:00 | 40.6 | 23 | 99490 | 100 | 3000 | 26.452 | 46.3442 | 57.9832 | 0 | 7.2692 | FALSE | FALSE
2025-09-03 16:00 | 39 | 32.5 | 99510 | 100 | 3000 | 25.8246 | 54.7731 | 67.5666 | 0 | 7.2692 | FALSE | FALSE
2025-09-03 17:00 | 37.55 | 40 | 99525 | 100 | 3000 | 25.2766 | 60.7902 | 72.9871 | 0 | 7.2692 | FALSE | FALSE
2025-09-03 18:00 | 36.15 | 47.5 | 99550 | 100 | 3000 | 24.7503 | 66.3504 | 77.3585 | 0 | 7.2692 | FALSE | FALSE
2025-09-03 19:00 | 35.55 | 50.5 | 99620 | 100 | 3000 | 24.5273 | 68.4118 | 78.6358 | 0 | 7.2692 | FALSE | FALSE
2025-09-03 20:00 | 35.35 | 51 | 99700 | 100 | 3000 | 24.4563 | 68.6663 | 78.4208 | 0 | 7.2692 | FALSE | FALSE
2025-09-03 21:00 | 34.85 | 53 | 99735 | 100 | 3000 | 24.2734 | 69.9114 | 78.7072 | 0 | 7.2692 | FALSE | FALSE
2025-09-03 22:00 | 33.85 | 56 | 99710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-03 23:00 | 32.9 | 57.5 | 99660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-04 | 32.1 | 60 | 99620 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-04 01:00 | 31.3 | 63.5 | 99595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-04 02:00 | 30.55 | 67.5 | 99580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-04 03:00 | 29.95 | 70.5 | 99580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-04 04:00 | 29.65 | 70.5 | 99595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-04 05:00 | 29.4 | 71 | 99650 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-04 06:00 | 29.9 | 64.5 | 99735 | 100 | 3000 | 22.4635 | 74.7093 | 69.1218 | 0 | 7.2692 | FALSE | FALSE
2025-09-04 07:00 | 32 | 51.5 | 99815 | 100 | 3000 | 23.2785 | 66.7964 | 65.0266 | 0 | 7.2692 | FALSE | FALSE
2025-09-04 08:00 | 34.65 | 43.5 | 99870 | 100 | 3000 | 24.2613 | 62.0969 | 66.4668 | 0 | 7.2692 | FALSE | FALSE
2025-09-04 09:00 | 37.15 | 37.5 | 99885 | 100 | 3000 | 25.1624 | 58.3574 | 68.1758 | 0 | 7.2692 | FALSE | FALSE
2025-09-04 10:00 | 39.45 | 31 | 99875 | 100 | 3000 | 25.9881 | 53.5437 | 66.9695 | 0 | 7.2692 | FALSE | FALSE
2025-09-04 11:00 | 41.65 | 24 | 99830 | 100 | 3000 | 26.7847 | 47.5658 | 62.8467 | 0 | 7.2692 | FALSE | FALSE
2025-09-04 12:00 | 43.6 | 17.5 | 99735 | 100 | 3000 | 27.5012 | 41.3318 | 56.8478 | 0 | 7.2692 | FALSE | FALSE
2025-09-04 13:00 | 44.35 | 15 | 99645 | 100 | 3000 | 27.7799 | 38.7603 | 53.9975 | 0 | 7.2692 | FALSE | FALSE
2025-09-04 14:00 | 43.85 | 16 | 99600 | 100 | 3000 | 27.6039 | 39.7852 | 54.6475 | 0 | 7.2692 | FALSE | FALSE
2025-09-04 15:00 | 42.75 | 20 | 99605 | 100 | 3000 | 27.1922 | 43.799 | 59.0485 | 0 | 7.2692 | FALSE | FALSE
2025-09-04 16:00 | 41.8 | 23 | 99625 | 100 | 3000 | 26.8457 | 46.6236 | 61.5412 | 0 | 7.2692 | FALSE | FALSE
2025-09-04 17:00 | 41.65 | 21.5 | 99640 | 100 | 3000 | 26.8153 | 45.0893 | 58.5736 | 0 | 7.2692 | FALSE | FALSE
2025-09-04 18:00 | 40.15 | 26 | 99695 | 100 | 3000 | 26.2705 | 49.0898 | 61.4734 | 0 | 7.2692 | FALSE | FALSE
2025-09-04 19:00 | 37.15 | 39 | 99765 | 100 | 3000 | 25.1506 | 59.6725 | 70.1768 | 0 | 7.2692 | FALSE | FALSE
2025-09-04 20:00 | 35 | 48.5 | 99835 | 100 | 3000 | 24.3526 | 66.359 | 73.9243 | 0 | 7.2692 | FALSE | FALSE
2025-09-04 21:00 | 33.75 | 52.5 | 99875 | 100 | 3000 | 23.8962 | 68.6846 | 73.4318 | 0 | 7.2692 | FALSE | FALSE
2025-09-04 22:00 | 33 | 55 | 99860 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-04 23:00 | 32.4 | 57 | 99845 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-05 | 31.9 | 58.5 | 99835 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-05 01:00 | 31.6 | 58 | 99835 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-05 02:00 | 31.55 | 54.5 | 99850 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-05 03:00 | 32.1 | 46.5 | 99860 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-05 04:00 | 33.05 | 41 | 99895 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-05 05:00 | 33.3 | 41 | 99950 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-05 06:00 | 33.3 | 41 | 100005 | 100 | 3000 | 23.7958 | 59.478 | 58.4907 | 0 | 7.2692 | FALSE | FALSE
2025-09-05 07:00 | 34.4 | 38.5 | 100080 | 100 | 3000 | 24.2022 | 57.9494 | 59.5479 | 0 | 7.2692 | FALSE | FALSE
2025-09-05 08:00 | 36.3 | 34 | 100140 | 100 | 3000 | 24.8971 | 54.9655 | 60.548 | 0 | 7.2692 | FALSE | FALSE
2025-09-05 09:00 | 38.3 | 29.5 | 100165 | 100 | 3000 | 25.6176 | 51.7226 | 61.0207 | 0 | 7.2692 | FALSE | FALSE
2025-09-05 10:00 | 40.2 | 25.5 | 100145 | 100 | 3000 | 26.2923 | 48.5928 | 60.977 | 0 | 7.2692 | FALSE | FALSE
2025-09-05 11:00 | 41.85 | 22.5 | 100085 | 100 | 3000 | 26.8681 | 46.1011 | 60.9873 | 0 | 7.2692 | FALSE | FALSE
2025-09-05 12:00 | 42.95 | 20 | 100000 | 100 | 3000 | 27.2565 | 43.8106 | 59.7334 | 0 | 7.2692 | FALSE | FALSE
2025-09-05 13:00 | 43.2 | 20.5 | 99910 | 100 | 3000 | 27.3297 | 44.3909 | 61.3 | 0 | 7.2692 | FALSE | FALSE
2025-09-05 14:00 | 42.35 | 26 | 99850 | 100 | 3000 | 26.984 | 49.8087 | 68.4178 | 0 | 7.2692 | FALSE | FALSE
2025-09-05 15:00 | 40.85 | 30.5 | 99820 | 100 | 3000 | 26.4496 | 53.6745 | 70.9328 | 0 | 7.2692 | FALSE | FALSE
2025-09-05 16:00 | 39.3 | 34 | 99840 | 100 | 3000 | 25.9093 | 56.2723 | 70.9457 | 0 | 7.2692 | FALSE | FALSE
2025-09-05 17:00 | 38 | 39.5 | 99870 | 100 | 3000 | 25.4306 | 60.5798 | 74.1089 | 0 | 7.2692 | FALSE | FALSE
2025-09-05 18:00 | 36.95 | 43 | 99890 | 100 | 3000 | 25.0525 | 63.0145 | 74.8142 | 0 | 7.2692 | FALSE | FALSE
2025-09-05 19:00 | 36.3 | 45.5 | 99945 | 100 | 3000 | 24.8155 | 64.7286 | 75.5067 | 0 | 7.2692 | FALSE | FALSE
2025-09-05 20:00 | 36.05 | 47 | 100015 | 100 | 3000 | 24.7206 | 65.8191 | 76.4293 | 0 | 7.2692 | FALSE | FALSE
2025-09-05 21:00 | 35.75 | 46.5 | 100050 | 100 | 3000 | 24.6223 | 65.1948 | 74.576 | 0 | 7.2692 | FALSE | FALSE
2025-09-05 22:00 | 35.3 | 46.5 | 100045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-05 23:00 | 34.75 | 47.5 | 100025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-06 | 33.9 | 49.5 | 100000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-06 01:00 | 32.8 | 53 | 99980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-06 02:00 | 32 | 56.5 | 99970 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-06 03:00 | 31.3 | 59 | 99980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-06 04:00 | 31 | 57.5 | 100020 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-06 05:00 | 30.55 | 56.5 | 100080 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-06 06:00 | 30.35 | 56 | 100140 | 100 | 3000 | 22.6581 | 69.0374 | 62.8942 | 0 | 7.2692 | FALSE | FALSE
2025-09-06 07:00 | 32.35 | 45.5 | 100185 | 100 | 3000 | 23.4315 | 62.4722 | 60.0136 | 0 | 7.2692 | FALSE | FALSE
2025-09-06 08:00 | 35.25 | 34 | 100215 | 100 | 3000 | 24.5297 | 54.5977 | 56.9922 | 0 | 7.2692 | FALSE | FALSE
2025-09-06 09:00 | 37.65 | 29 | 100225 | 100 | 3000 | 25.4003 | 51.0728 | 58.2293 | 0 | 7.2692 | FALSE | FALSE
2025-09-06 10:00 | 39.75 | 25 | 100200 | 100 | 3000 | 26.1477 | 47.9949 | 58.8412 | 0 | 7.2692 | FALSE | FALSE
2025-09-06 11:00 | 41.35 | 22 | 100150 | 100 | 3000 | 26.7108 | 45.4829 | 58.7184 | 0 | 7.2692 | FALSE | FALSE
2025-09-06 12:00 | 42.2 | 21 | 100070 | 100 | 3000 | 27.0008 | 44.6721 | 59.4156 | 0 | 7.2692 | FALSE | FALSE
2025-09-06 13:00 | 42.25 | 21 | 99980 | 100 | 3000 | 27.017 | 44.6895 | 59.5276 | 0 | 7.2692 | FALSE | FALSE
2025-09-06 14:00 | 41.7 | 21.5 | 99920 | 100 | 3000 | 26.8316 | 45.0791 | 58.8054 | 0 | 7.2692 | FALSE | FALSE
2025-09-06 15:00 | 41.2 | 22 | 99900 | 100 | 3000 | 26.6615 | 45.4694 | 58.2091 | 0 | 7.2692 | FALSE | FALSE
2025-09-06 16:00 | 40.45 | 24.5 | 99905 | 100 | 3000 | 26.3858 | 47.7214 | 60.0754 | 0 | 7.2692 | FALSE | FALSE
2025-09-06 17:00 | 38.5 | 34 | 99900 | 100 | 3000 | 25.6449 | 55.8892 | 68.1289 | 0 | 7.2692 | FALSE | FALSE
2025-09-06 18:00 | 36 | 50.5 | 99910 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-06 19:00 | 34.35 | 65 | 99935 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-06 20:00 | 33.5 | 73 | 99955 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-06 21:00 | 32.75 | 79.5 | 99975 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-06 22:00 | 32.2 | 83 | 99970 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-06 23:00 | 31.7 | 82 | 99955 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 | 31.35 | 80.5 | 99950 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 01:00 | 30.7 | 82 | 99945 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 02:00 | 29.65 | 85.5 | 99920 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 03:00 | 29 | 86.5 | 99900 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 04:00 | 29 | 84.5 | 99890 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 05:00 | 29.15 | 82 | 99885 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 06:00 | 29.6 | 76 | 99910 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 07:00 | 31.6 | 63 | 99950 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 08:00 | 34.45 | 50 | 99985 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 09:00 | 37.15 | 40.5 | 99995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 10:00 | 39.45 | 31.5 | 99980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 11:00 | 40.7 | 25.5 | 99940 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 12:00 | 40.85 | 25 | 99885 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 13:00 | 40.55 | 26.5 | 99825 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 14:00 | 40 | 29.5 | 99765 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 15:00 | 39 | 36 | 99725 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 16:00 | 37.8 | 42 | 99720 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 17:00 | 36.55 | 47.5 | 99725 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 18:00 | 35.35 | 53.5 | 99735 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 19:00 | 34.55 | 57 | 99765 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 20:00 | 33.95 | 61.5 | 99795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 21:00 | 33.15 | 69 | 99790 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 22:00 | 32.35 | 73 | 99750 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-07 23:00 | 31.7 | 74 | 99730 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-08 | 31 | 77 | 99725 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-08 01:00 | 30.4 | 81 | 99715 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-08 02:00 | 29.95 | 85 | 99700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-08 03:00 | 29.45 | 87.5 | 99685 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-08 04:00 | 29.3 | 87.5 | 99670 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-08 05:00 | 29.2 | 88.5 | 99670 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-08 06:00 | 29.4 | 88 | 99695 | 100 | 3000 | 22.2069 | 90.3388 | 88.5776 | 0 | 7.2692 | FALSE | FALSE
2025-09-08 07:00 | 31.05 | 80 | 99735 | 100 | 3000 | 22.8236 | 86.7352 | 89.798 | 0 | 7.2692 | FALSE | FALSE
2025-09-08 08:00 | 33.3 | 69.5 | 99775 | 100 | 3000 | 23.6516 | 81.4836 | 90.4161 | 0 | 7.2692 | FALSE | FALSE
2025-09-08 09:00 | 35.15 | 61.5 | 99775 | 100 | 3000 | 24.3217 | 77.0861 | 90.2852 | 0 | 7.2692 | FALSE | FALSE
2025-09-08 10:00 | 36.8 | 55 | 99740 | 100 | 3000 | 24.9107 | 73.2563 | 89.8976 | 0 | 7.2692 | FALSE | FALSE
2025-09-08 11:00 | 38.3 | 49.5 | 99700 | 100 | 3000 | 25.4402 | 69.7843 | 89.2374 | 0 | 7.2692 | FALSE | FALSE
2025-09-08 12:00 | 39.4 | 46 | 99650 | 100 | 3000 | 25.822 | 67.5242 | 88.9991 | 0 | 7.2692 | FALSE | FALSE
2025-09-08 13:00 | 39.65 | 46.5 | 99585 | 100 | 3000 | 25.8951 | 68.2109 | 90.7832 | 0 | 7.2692 | FALSE | FALSE
2025-09-08 14:00 | 39.3 | 47.5 | 99520 | 100 | 3000 | 25.7753 | 68.8463 | 90.7111 | 0 | 7.2692 | FALSE | FALSE
2025-09-08 15:00 | 38.65 | 48 | 99485 | 100 | 3000 | 25.5651 | 68.7468 | 88.5997 | 0 | 7.2692 | FALSE | FALSE
2025-09-08 16:00 | 37.55 | 51.5 | 99490 | 100 | 3000 | 25.1815 | 70.9206 | 88.596 | 0 | 7.2692 | FALSE | FALSE
2025-09-08 17:00 | 35.8 | 61.5 | 99505 | 100 | 3000 | 24.5361 | 77.7811 | 93.3342 | 0 | 7.2692 | FALSE | FALSE
2025-09-08 18:00 | 33.95 | 74.5 | 99540 | 100 | 3000 | 23.8437 | 86.152 | 99.2357 | 0 | 7.2692 | FALSE | FALSE
2025-09-08 19:00 | 33 | 81 | 99600 | 100 | 3000 | 23.4912 | 89.9352 | 101.2408 | 0 | 7.2692 | FALSE | FALSE
2025-09-08 20:00 | 32.6 | 83 | 99670 | 100 | 3000 | 23.3465 | 90.9005 | 101.1716 | 0 | 7.2692 | FALSE | FALSE
2025-09-08 21:00 | 32.2 | 84.5 | 99720 | 100 | 3000 | 23.2037 | 91.4712 | 100.5263 | 0 | 7.2692 | FALSE | FALSE
2025-09-08 22:00 | 31.75 | 86.5 | 99720 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-08 23:00 | 31.15 | 89.5 | 99690 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-09 | 30.5 | 92.5 | 99665 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-09 01:00 | 29.9 | 95.5 | 99650 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-09 02:00 | 29.4 | 98 | 99655 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-09 03:00 | 28.9 | 99.5 | 99675 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-09 04:00 | 29 | 100 | 99700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-09 05:00 | 29.3 | 100 | 99730 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-09 06:00 | 29.45 | 96 | 99775 | 100 | 3000 | 22.2003 | 95.8251 | 96.1303 | 0 | 7.2692 | FALSE | FALSE
2025-09-09 07:00 | 31.05 | 79.5 | 99840 | 100 | 3000 | 22.8256 | 86.3671 | 89.327 | 0 | 7.2692 | FALSE | FALSE
2025-09-09 08:00 | 34.2 | 59.5 | 99870 | 100 | 3000 | 24.0133 | 74.56 | 83.4941 | 0 | 7.2692 | FALSE | FALSE
2025-09-09 09:00 | 37.8 | 43.5 | 99870 | 100 | 3000 | 25.3306 | 64.0134 | 78.881 | 0 | 7.2692 | FALSE | FALSE
2025-09-09 10:00 | 40.75 | 31.5 | 99860 | 100 | 3000 | 26.4061 | 54.5973 | 72.1976 | 0 | 7.2692 | FALSE | FALSE
2025-09-09 11:00 | 42.7 | 26 | 99825 | 100 | 3000 | 27.0947 | 49.9426 | 69.5228 | 0 | 7.2692 | FALSE | FALSE
2025-09-09 12:00 | 44 | 23 | 99755 | 100 | 3000 | 27.5453 | 47.2666 | 68.1477 | 0 | 7.2692 | FALSE | FALSE
2025-09-09 13:00 | 44.8 | 20.5 | 99680 | 100 | 3000 | 27.8335 | 44.8114 | 65.7595 | 0 | 7.2692 | FALSE | FALSE
2025-09-09 14:00 | 45.05 | 18.5 | 99625 | 100 | 3000 | 27.9445 | 42.6811 | 62.5622 | 0 | 7.2692 | FALSE | FALSE
2025-09-09 15:00 | 44.85 | 17.5 | 99605 | 100 | 3000 | 27.8986 | 41.5445 | 60.0735 | 0 | 7.2692 | FALSE | FALSE
2025-09-09 16:00 | 42.5 | 31.5 | 99630 | 100 | 3000 | 26.9575 | 55.5112 | 78.2647 | 0 | 7.2692 | FALSE | FALSE
2025-09-09 17:00 | 39 | 52 | 99660 | 100 | 3000 | 25.6374 | 72.7187 | 95.8674 | 0 | 7.2692 | FALSE | FALSE
2025-09-09 18:00 | 36.95 | 60.5 | 99705 | 100 | 3000 | 24.9164 | 78.1521 | 97.6986 | 0 | 7.2692 | FALSE | FALSE
2025-09-09 19:00 | 36.1 | 60 | 99765 | 100 | 3000 | 24.6454 | 76.8147 | 92.9857 | 0 | 7.2692 | FALSE | FALSE
2025-09-09 20:00 | 35.7 | 53.5 | 99830 | 100 | 3000 | 24.558 | 71.0007 | 83.0683 | 0 | 7.2692 | FALSE | FALSE
2025-09-09 21:00 | 34.65 | 52 | 99875 | 100 | 3000 | 24.2111 | 68.9397 | 76.6826 | 0 | 7.2692 | FALSE | FALSE
2025-09-09 22:00 | 33.05 | 56.5 | 99865 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-09 23:00 | 31.85 | 59 | 99830 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-10 | 31.15 | 58.5 | 99795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-10 01:00 | 30.55 | 59 | 99785 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-10 02:00 | 29.95 | 62.5 | 99810 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-10 03:00 | 29.3 | 66.5 | 99850 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-10 04:00 | 29.45 | 61 | 99890 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-10 05:00 | 30.15 | 51.5 | 99930 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-10 06:00 | 30.65 | 48.5 | 99975 | 100 | 3000 | 22.7952 | 63.9009 | 56.5855 | 0 | 7.2692 | FALSE | FALSE
2025-09-10 07:00 | 31.85 | 45 | 100030 | 100 | 3000 | 23.2513 | 61.8885 | 57.5415 | 0 | 7.2692 | FALSE | FALSE
2025-09-10 08:00 | 33.9 | 39 | 100075 | 100 | 3000 | 24.0213 | 58.1502 | 58.3523 | 0 | 7.2692 | FALSE | FALSE
2025-09-10 09:00 | 36.3 | 32.5 | 100080 | 100 | 3000 | 24.9076 | 53.6987 | 58.5518 | 0 | 7.2692 | FALSE | FALSE
2025-09-10 10:00 | 38.75 | 26 | 100045 | 100 | 3000 | 25.8013 | 48.6856 | 57.2761 | 0 | 7.2692 | FALSE | FALSE
2025-09-10 11:00 | 40.65 | 21 | 99990 | 100 | 3000 | 26.4905 | 44.3842 | 55.0437 | 0 | 7.2692 | FALSE | FALSE
2025-09-10 12:00 | 41.8 | 18.5 | 99915 | 100 | 3000 | 26.9012 | 42.1005 | 53.969 | 0 | 7.2692 | FALSE | FALSE
2025-09-10 13:00 | 42.05 | 19 | 99840 | 100 | 3000 | 26.9773 | 42.6421 | 55.4695 | 0 | 7.2692 | FALSE | FALSE
2025-09-10 14:00 | 40.95 | 25 | 99795 | 100 | 3000 | 26.5448 | 48.3522 | 62.3647 | 0 | 7.2692 | FALSE | FALSE
2025-09-10 15:00 | 39 | 34 | 99780 | 100 | 3000 | 25.8106 | 56.1322 | 69.8619 | 0 | 7.2692 | FALSE | FALSE
2025-09-10 16:00 | 37.4 | 41.5 | 99780 | 100 | 3000 | 25.2146 | 61.9976 | 74.5304 | 0 | 7.2692 | FALSE | FALSE
2025-09-10 17:00 | 35.95 | 49.5 | 99770 | 100 | 3000 | 24.6692 | 67.8666 | 79.1217 | 0 | 7.2692 | FALSE | FALSE
2025-09-10 18:00 | 34.95 | 54 | 99770 | 100 | 3000 | 24.3014 | 70.7985 | 80.3558 | 0 | 7.2692 | FALSE | FALSE
2025-09-10 19:00 | 34.7 | 51.5 | 99815 | 100 | 3000 | 24.2312 | 68.5793 | 76.2836 | 0 | 7.2692 | FALSE | FALSE
2025-09-10 20:00 | 34.25 | 47.5 | 99870 | 100 | 3000 | 24.0984 | 65.0698 | 69.674 | 0 | 7.2692 | FALSE | FALSE
2025-09-10 21:00 | 33.7 | 45.5 | 99890 | 100 | 3000 | 23.9156 | 63.1758 | 65.1583 | 0 | 7.2692 | FALSE | FALSE
2025-09-10 22:00 | 33.2 | 47 | 99870 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-10 23:00 | 32.5 | 54.5 | 99835 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-11 | 31.65 | 61 | 99800 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-11 01:00 | 30.75 | 64.5 | 99765 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-11 02:00 | 30.1 | 67.5 | 99765 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-11 03:00 | 29.8 | 63.5 | 99805 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-11 04:00 | 30.3 | 53 | 99835 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-11 05:00 | 30.8 | 45 | 99865 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-11 06:00 | 31 | 42 | 99920 | 100 | 3000 | 22.949 | 59.3877 | 51.2415 | 0 | 7.2692 | FALSE | FALSE
2025-09-11 07:00 | 32.3 | 40 | 99975 | 100 | 3000 | 23.4374 | 58.3453 | 53.7603 | 0 | 7.2692 | FALSE | FALSE
2025-09-11 08:00 | 34.5 | 36.5 | 100015 | 100 | 3000 | 24.2491 | 56.3904 | 57.4632 | 0 | 7.2692 | FALSE | FALSE
2025-09-11 09:00 | 36.8 | 31.5 | 100040 | 100 | 3000 | 25.0882 | 53.0096 | 58.8662 | 0 | 7.2692 | FALSE | FALSE
2025-09-11 10:00 | 38.8 | 27 | 100030 | 100 | 3000 | 25.8091 | 49.6137 | 58.9101 | 0 | 7.2692 | FALSE | FALSE
2025-09-11 11:00 | 40.45 | 23.5 | 99975 | 100 | 3000 | 26.3967 | 46.7549 | 58.4974 | 0 | 7.2692 | FALSE | FALSE
2025-09-11 12:00 | 41.55 | 21.5 | 99910 | 100 | 3000 | 26.7825 | 45.0483 | 58.3758 | 0 | 7.2692 | FALSE | FALSE
2025-09-11 13:00 | 41.75 | 23 | 99840 | 100 | 3000 | 26.8295 | 46.5944 | 61.4628 | 0 | 7.2692 | FALSE | FALSE
2025-09-11 14:00 | 41.15 | 27.5 | 99785 | 100 | 3000 | 26.5809 | 50.8671 | 67.0672 | 0 | 7.2692 | FALSE | FALSE
2025-09-11 15:00 | 39.95 | 32.5 | 99760 | 100 | 3000 | 26.1366 | 55.1843 | 70.9432 | 0 | 7.2692 | FALSE | FALSE
2025-09-11 16:00 | 38.5 | 36.5 | 99760 | 100 | 3000 | 25.6223 | 58.1673 | 71.6926 | 0 | 7.2692 | FALSE | FALSE
2025-09-11 17:00 | 37.3 | 40 | 99760 | 100 | 3000 | 25.1931 | 60.6274 | 72.0987 | 0 | 7.2692 | FALSE | FALSE
2025-09-11 18:00 | 36.15 | 47 | 99775 | 100 | 3000 | 24.7541 | 65.9092 | 76.778 | 0 | 7.2692 | FALSE | FALSE
2025-09-11 19:00 | 35.15 | 54 | 99820 | 100 | 3000 | 24.3694 | 70.9571 | 81.2495 | 0 | 7.2692 | FALSE | FALSE
2025-09-11 20:00 | 34.85 | 54.5 | 99865 | 100 | 3000 | 24.2644 | 71.1141 | 80.5395 | 0 | 7.2692 | FALSE | FALSE
2025-09-11 21:00 | 34.2 | 56 | 99890 | 100 | 3000 | 24.0331 | 71.783 | 79.4371 | 0 | 7.2692 | FALSE | FALSE
2025-09-11 22:00 | 32.95 | 61.5 | 99865 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-11 23:00 | 32.4 | 63.5 | 99830 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-12 | 32.2 | 63.5 | 99805 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-12 01:00 | 31.65 | 65 | 99785 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-12 02:00 | 31.3 | 65.5 | 99800 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-12 03:00 | 31.25 | 66 | 99840 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-12 04:00 | 31.75 | 58.5 | 99880 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-12 05:00 | 32 | 51 | 99930 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-12 06:00 | 31.85 | 55 | 100000 | 100 | 3000 | 23.2096 | 69.2744 | 68.1559 | 0 | 7.2692 | FALSE | FALSE
2025-09-12 07:00 | 32.55 | 57 | 100070 | 100 | 3000 | 23.4514 | 71.251 | 73.3246 | 0 | 7.2692 | FALSE | FALSE
2025-09-12 08:00 | 33.9 | 52 | 100120 | 100 | 3000 | 23.9515 | 68.376 | 73.5496 | 0 | 7.2692 | FALSE | FALSE
2025-09-12 09:00 | 35.4 | 44 | 100140 | 100 | 3000 | 24.5188 | 62.8982 | 70.064 | 0 | 7.2692 | FALSE | FALSE
2025-09-12 10:00 | 36.8 | 38 | 100140 | 100 | 3000 | 25.0399 | 58.5964 | 67.6348 | 0 | 7.2692 | FALSE | FALSE
2025-09-12 11:00 | 38.15 | 34 | 100100 | 100 | 3000 | 25.528 | 55.7157 | 66.9548 | 0 | 7.2692 | FALSE | FALSE
2025-09-12 12:00 | 39.45 | 30 | 100020 | 100 | 3000 | 25.998 | 52.5991 | 65.499 | 0 | 7.2692 | FALSE | FALSE
2025-09-12 13:00 | 40.5 | 27 | 99945 | 100 | 3000 | 26.3751 | 50.1383 | 64.2296 | 0 | 7.2692 | FALSE | FALSE
2025-09-12 14:00 | 40.5 | 28.5 | 99885 | 100 | 3000 | 26.3586 | 51.5875 | 66.5951 | 0 | 7.2692 | FALSE | FALSE
2025-09-12 15:00 | 39.35 | 34.5 | 99860 | 100 | 3000 | 25.9207 | 56.7605 | 71.8774 | 0 | 7.2692 | FALSE | FALSE
2025-09-12 16:00 | 37.55 | 44 | 99865 | 100 | 3000 | 25.2441 | 64.2843 | 78.5553 | 0 | 7.2692 | FALSE | FALSE
2025-09-12 17:00 | 36.3 | 50.5 | 99865 | 100 | 3000 | 24.7795 | 68.9709 | 81.9155 | 0 | 7.2692 | FALSE | FALSE
2025-09-12 18:00 | 35.85 | 53 | 99875 | 100 | 3000 | 24.6117 | 70.7057 | 83.1193 | 0 | 7.2692 | FALSE | FALSE
2025-09-12 19:00 | 35.25 | 54 | 99915 | 100 | 3000 | 24.4034 | 71.031 | 81.7153 | 0 | 7.2692 | FALSE | FALSE
2025-09-12 20:00 | 34.2 | 55.5 | 99975 | 100 | 3000 | 24.036 | 71.3788 | 78.8756 | 0 | 7.2692 | FALSE | FALSE
2025-09-12 21:00 | 33.05 | 60.5 | 100040 | 100 | 3000 | 23.6108 | 74.3113 | 79.3815 | 0 | 7.2692 | FALSE | FALSE
2025-09-12 22:00 | 32.3 | 63.5 | 100055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-12 23:00 | 31.9 | 63 | 100030 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-13 | 31.4 | 63 | 100020 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-13 01:00 | 30.8 | 65 | 100010 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-13 02:00 | 30.2 | 68.5 | 100005 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-13 03:00 | 29.6 | 73 | 100025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-13 04:00 | 29.75 | 73 | 100050 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-13 05:00 | 30.1 | 71 | 100090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-13 06:00 | 30.35 | 70 | 100150 | 100 | 3000 | 22.61 | 78.8797 | 76.5917 | 0 | 7.2692 | FALSE | FALSE
2025-09-13 07:00 | 31.65 | 63 | 100205 | 100 | 3000 | 23.1048 | 74.9848 | 75.677 | 0 | 7.2692 | FALSE | FALSE
2025-09-13 08:00 | 33.45 | 53.5 | 100250 | 100 | 3000 | 23.7862 | 69.2166 | 73.3821 | 0 | 7.2692 | FALSE | FALSE
2025-09-13 09:00 | 34.95 | 48 | 100260 | 100 | 3000 | 24.3388 | 65.8817 | 73.2164 | 0 | 7.2692 | FALSE | FALSE
2025-09-13 10:00 | 36.45 | 43.5 | 100230 | 100 | 3000 | 24.8808 | 63.1019 | 73.5868 | 0 | 7.2692 | FALSE | FALSE
2025-09-13 11:00 | 37.8 | 39.5 | 100180 | 100 | 3000 | 25.3645 | 60.4377 | 73.4333 | 0 | 7.2692 | FALSE | FALSE
2025-09-13 12:00 | 38.95 | 36.5 | 100100 | 100 | 3000 | 25.7707 | 58.3804 | 73.4489 | 0 | 7.2692 | FALSE | FALSE
2025-09-13 13:00 | 40.1 | 33.5 | 100010 | 100 | 3000 | 26.1749 | 56.1878 | 73.0899 | 0 | 7.2692 | FALSE | FALSE
2025-09-13 14:00 | 40.65 | 32 | 99945 | 100 | 3000 | 26.3684 | 55.0271 | 72.6691 | 0 | 7.2692 | FALSE | FALSE
2025-09-13 15:00 | 40.15 | 33 | 99905 | 100 | 3000 | 26.1963 | 55.745 | 72.4626 | 0 | 7.2692 | FALSE | FALSE
2025-09-13 16:00 | 39.2 | 35.5 | 99915 | 100 | 3000 | 25.862 | 57.6069 | 72.8391 | 0 | 7.2692 | FALSE | FALSE
2025-09-13 17:00 | 37.75 | 39 | 99955 | 100 | 3000 | 25.3519 | 59.9847 | 72.4862 | 0 | 7.2692 | FALSE | FALSE
2025-09-13 18:00 | 35.9 | 44 | 99990 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-13 19:00 | 33.95 | 51.5 | 100045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-13 20:00 | 32.3 | 58.5 | 100110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-13 21:00 | 31.3 | 63 | 100140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-13 22:00 | 30.7 | 65.5 | 100130 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-13 23:00 | 30.3 | 66.5 | 100120 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 | 29.9 | 67.5 | 100115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 01:00 | 29.45 | 69 | 100125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 02:00 | 29.1 | 70.5 | 100145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 03:00 | 28.9 | 72 | 100165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 04:00 | 28.85 | 71.5 | 100190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 05:00 | 28.8 | 70.5 | 100230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 06:00 | 28.9 | 70.5 | 100290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 07:00 | 29.95 | 67 | 100360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 08:00 | 31.9 | 58 | 100420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 09:00 | 33.85 | 49 | 100430 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 10:00 | 35.45 | 44 | 100405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 11:00 | 36.85 | 40.5 | 100345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 12:00 | 38.15 | 37.5 | 100250 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 13:00 | 38.95 | 35 | 100175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 14:00 | 38.85 | 35 | 100115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 15:00 | 38 | 39.5 | 100080 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 16:00 | 36.9 | 46 | 100095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 17:00 | 36.05 | 49 | 100110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 18:00 | 35.65 | 45.5 | 100135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 19:00 | 34.95 | 43 | 100185 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 20:00 | 33.7 | 45.5 | 100240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 21:00 | 32.6 | 49 | 100280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 22:00 | 31.75 | 52.5 | 100285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-14 23:00 | 31.05 | 55.5 | 100285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-15 | 30.35 | 58.5 | 100270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-15 01:00 | 29.7 | 60.5 | 100235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-15 02:00 | 29.15 | 61.5 | 100230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-15 03:00 | 28.7 | 62.5 | 100245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-15 04:00 | 29.6 | 58.5 | 100250 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-15 05:00 | 30.6 | 52 | 100270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-15 06:00 | 30.35 | 52 | 100310 | 100 | 3000 | 22.6717 | 66.2037 | 58.9716 | 0 | 7.2692 | FALSE | FALSE
2025-09-15 07:00 | 30.7 | 53 | 100365 | 100 | 3000 | 22.7979 | 67.0935 | 61.3945 | 0 | 7.2692 | FALSE | FALSE
2025-09-15 08:00 | 32 | 49.5 | 100420 | 100 | 3000 | 23.2872 | 65.2577 | 63.0201 | 0 | 7.2692 | FALSE | FALSE
2025-09-15 09:00 | 33.6 | 44.5 | 100435 | 100 | 3000 | 23.8856 | 62.2945 | 63.7422 | 0 | 7.2692 | FALSE | FALSE
2025-09-15 10:00 | 35.1 | 40 | 100415 | 100 | 3000 | 24.44 | 59.4353 | 64.0135 | 0 | 7.2692 | FALSE | FALSE
2025-09-15 11:00 | 36.45 | 36.5 | 100345 | 100 | 3000 | 24.9312 | 57.1327 | 64.4271 | 0 | 7.2692 | FALSE | FALSE
2025-09-15 12:00 | 37.6 | 34 | 100240 | 100 | 3000 | 25.3427 | 55.4674 | 65.0697 | 0 | 7.2692 | FALSE | FALSE
2025-09-15 13:00 | 38.2 | 33 | 100150 | 100 | 3000 | 25.5535 | 54.8354 | 65.7156 | 0 | 7.2692 | FALSE | FALSE
2025-09-15 14:00 | 37.35 | 38.5 | 100095 | 100 | 3000 | 25.2221 | 59.3147 | 70.3349 | 0 | 7.2692 | FALSE | FALSE
2025-09-15 15:00 | 36.05 | 44.5 | 100080 | 100 | 3000 | 24.738 | 63.7117 | 73.2511 | 0 | 7.2692 | FALSE | FALSE
2025-09-15 16:00 | 35.25 | 48.5 | 100080 | 100 | 3000 | 24.4386 | 66.5076 | 75.0202 | 0 | 7.2692 | FALSE | FALSE
2025-09-15 17:00 | 34.15 | 54 | 100080 | 100 | 3000 | 24.0273 | 70.1411 | 76.9344 | 0 | 7.2692 | FALSE | FALSE
2025-09-15 18:00 | 33.4 | 58 | 100100 | 100 | 3000 | 23.7455 | 72.6763 | 78.2009 | 0 | 7.2692 | FALSE | FALSE
2025-09-15 19:00 | 33.05 | 62 | 100155 | 100 | 3000 | 23.6036 | 75.4477 | 81.0589 | 0 | 7.2692 | FALSE | FALSE
2025-09-15 20:00 | 32.65 | 65.5 | 100225 | 100 | 3000 | 23.4473 | 77.7311 | 82.9973 | 0 | 7.2692 | FALSE | FALSE
2025-09-15 21:00 | 32.3 | 69 | 100265 | 100 | 3000 | 23.309 | 80.0105 | 85.0416 | 0 | 7.2692 | FALSE | FALSE
2025-09-15 22:00 | 31.85 | 73 | 100255 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-15 23:00 | 31.4 | 76 | 100225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-16 | 30.95 | 78 | 100195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-16 01:00 | 30.45 | 80 | 100160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-16 02:00 | 29.95 | 81.5 | 100135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-16 03:00 | 29.55 | 82.5 | 100135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-16 04:00 | 29.55 | 82.5 | 100145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-16 05:00 | 29.65 | 82 | 100175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-16 06:00 | 29.95 | 80 | 100220 | 100 | 3000 | 22.4316 | 85.4423 | 84.1751 | 0 | 7.2692 | FALSE | FALSE
2025-09-16 07:00 | 31.25 | 74 | 100255 | 100 | 3000 | 22.9183 | 82.5961 | 84.9698 | 0 | 7.2692 | FALSE | FALSE
2025-09-16 08:00 | 33 | 66.5 | 100285 | 100 | 3000 | 23.5643 | 78.8249 | 85.7773 | 0 | 7.2692 | FALSE | FALSE
2025-09-16 09:00 | 34.75 | 57.5 | 100290 | 100 | 3000 | 24.2128 | 73.4146 | 83.7761 | 0 | 7.2692 | FALSE | FALSE
2025-09-16 10:00 | 36.55 | 47.5 | 100245 | 100 | 3000 | 24.8853 | 66.5776 | 79.2079 | 0 | 7.2692 | FALSE | FALSE
2025-09-16 11:00 | 38.1 | 40.5 | 100170 | 100 | 3000 | 25.4553 | 61.5092 | 75.9812 | 0 | 7.2692 | FALSE | FALSE
2025-09-16 12:00 | 39.05 | 38.5 | 100085 | 100 | 3000 | 25.7844 | 60.2805 | 76.7488 | 0 | 7.2692 | FALSE | FALSE
2025-09-16 13:00 | 38.9 | 42 | 100010 | 100 | 3000 | 25.7024 | 63.409 | 81.229 | 0 | 7.2692 | FALSE | FALSE
2025-09-16 14:00 | 38.2 | 43.5 | 99960 | 100 | 3000 | 25.4617 | 64.284 | 80.5241 | 0 | 7.2692 | FALSE | FALSE
2025-09-16 15:00 | 37.35 | 45.5 | 99935 | 100 | 3000 | 25.166 | 65.4546 | 79.7921 | 0 | 7.2692 | FALSE | FALSE
2025-09-16 16:00 | 36.05 | 52.5 | 99950 | 100 | 3000 | 24.6821 | 70.4471 | 83.3916 | 0 | 7.2692 | FALSE | FALSE
2025-09-16 17:00 | 34.5 | 63 | 99970 | 100 | 3000 | 24.095 | 77.6241 | 88.9942 | 0 | 7.2692 | FALSE | FALSE
2025-09-16 18:00 | 33.2 | 73.5 | 99990 | 100 | 3000 | 23.5975 | 84.4225 | 94.3281 | 0 | 7.2692 | FALSE | FALSE
2025-09-16 19:00 | 32.7 | 77.5 | 100030 | 100 | 3000 | 23.4075 | 86.8569 | 96.0109 | 0 | 7.2692 | FALSE | FALSE
2025-09-16 20:00 | 32.5 | 78.5 | 100075 | 100 | 3000 | 23.3345 | 87.3563 | 96.0128 | 0 | 7.2692 | FALSE | FALSE
2025-09-16 21:00 | 32.15 | 80.5 | 100110 | 100 | 3000 | 23.2053 | 88.4037 | 96.2278 | 0 | 7.2692 | FALSE | FALSE
2025-09-16 22:00 | 31.8 | 83 | 100100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-16 23:00 | 31.3 | 86 | 100070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-17 | 30.7 | 89 | 100055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-17 01:00 | 30.1 | 91.5 | 100040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-17 02:00 | 29.55 | 94.5 | 100040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-17 03:00 | 29.05 | 96.5 | 100060 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-17 04:00 | 29.25 | 95.5 | 100085 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-17 05:00 | 29.45 | 95 | 100115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-17 06:00 | 29.45 | 94.5 | 100160 | 100 | 3000 | 22.2055 | 94.7691 | 94.8482 | 0 | 7.2692 | FALSE | FALSE
2025-09-17 07:00 | 30.75 | 87 | 100225 | 100 | 3000 | 22.6922 | 91.2999 | 95.1154 | 0 | 7.2692 | FALSE | FALSE
2025-09-17 08:00 | 32.9 | 73 | 100280 | 100 | 3000 | 23.4981 | 83.6657 | 92.3119 | 0 | 7.2692 | FALSE | FALSE
2025-09-17 09:00 | 35.1 | 58.5 | 100290 | 100 | 3000 | 24.3248 | 74.5436 | 86.5806 | 0 | 7.2692 | FALSE | FALSE
2025-09-17 10:00 | 37.15 | 47 | 100265 | 100 | 3000 | 25.0884 | 66.5883 | 81.0644 | 0 | 7.2692 | FALSE | FALSE
2025-09-17 11:00 | 38.7 | 39.5 | 100205 | 100 | 3000 | 25.6611 | 60.9734 | 76.8925 | 0 | 7.2692 | FALSE | FALSE
2025-09-17 12:00 | 39.5 | 37.5 | 100110 | 100 | 3000 | 25.94 | 59.621 | 76.9878 | 0 | 7.2692 | FALSE | FALSE
2025-09-17 13:00 | 39.5 | 37.5 | 100035 | 100 | 3000 | 25.9399 | 59.6271 | 76.9654 | 0 | 7.2692 | FALSE | FALSE
2025-09-17 14:00 | 38.9 | 35.5 | 99985 | 100 | 3000 | 25.7636 | 57.4447 | 71.7675 | 0 | 7.2692 | FALSE | FALSE
2025-09-17 15:00 | 37.65 | 40 | 99965 | 100 | 3000 | 25.3103 | 60.8114 | 73.4922 | 0 | 7.2692 | FALSE | FALSE
2025-09-17 16:00 | 36.25 | 51 | 99970 | 100 | 3000 | 24.7594 | 69.3449 | 82.3664 | 0 | 7.2692 | FALSE | FALSE
2025-09-17 17:00 | 34.95 | 60 | 99960 | 100 | 3000 | 24.2645 | 75.6514 | 87.5928 | 0 | 7.2692 | FALSE | FALSE
2025-09-17 18:00 | 33.6 | 69.5 | 99975 | 100 | 3000 | 23.7542 | 81.7943 | 91.9677 | 0 | 7.2692 | FALSE | FALSE
2025-09-17 19:00 | 32.75 | 77.5 | 100030 | 100 | 3000 | 23.4246 | 86.9188 | 96.2759 | 0 | 7.2692 | FALSE | FALSE
2025-09-17 20:00 | 32.3 | 81 | 100085 | 100 | 3000 | 23.2545 | 88.9689 | 97.5478 | 0 | 7.2692 | FALSE | FALSE
2025-09-17 21:00 | 31.7 | 84.5 | 100120 | 100 | 3000 | 23.0329 | 90.7616 | 97.8575 | 0 | 7.2692 | FALSE | FALSE
2025-09-17 22:00 | 31.05 | 88 | 100115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-17 23:00 | 30.4 | 90.5 | 100095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-18 | 29.7 | 93 | 100075 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-18 01:00 | 29.05 | 95 | 100040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-18 02:00 | 28.45 | 96.5 | 100020 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-18 03:00 | 28.1 | 96.5 | 100025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-18 04:00 | 28.1 | 96.5 | 100045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-18 05:00 | 28 | 97 | 100070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-18 06:00 | 28.1 | 95 | 100110 | 100 | 3000 | 21.7139 | 93.3308 | 87.7105 | 0 | 7.2692 | FALSE | FALSE
2025-09-18 07:00 | 29.75 | 85.5 | 100180 | 100 | 3000 | 22.3416 | 89.0077 | 88.2565 | 0 | 7.2692 | FALSE | FALSE
2025-09-18 08:00 | 32.4 | 70.5 | 100235 | 100 | 3000 | 23.3371 | 81.2369 | 87.1123 | 0 | 7.2692 | FALSE | FALSE
2025-09-18 09:00 | 34.95 | 55 | 100245 | 100 | 3000 | 24.2959 | 71.5679 | 81.6788 | 0 | 7.2692 | FALSE | FALSE
2025-09-18 10:00 | 37.35 | 40.5 | 100205 | 100 | 3000 | 25.2063 | 61.0559 | 73.0931 | 0 | 7.2692 | FALSE | FALSE
2025-09-18 11:00 | 39.3 | 31.5 | 100135 | 100 | 3000 | 25.9338 | 53.9262 | 67.2901 | 0 | 7.2692 | FALSE | FALSE
2025-09-18 12:00 | 40.35 | 29 | 100065 | 100 | 3000 | 26.3043 | 51.9964 | 66.9482 | 0 | 7.2692 | FALSE | FALSE
2025-09-18 13:00 | 40.35 | 28.5 | 100000 | 100 | 3000 | 26.3097 | 51.5221 | 66.1402 | 0 | 7.2692 | FALSE | FALSE
2025-09-18 14:00 | 39.5 | 30 | 99945 | 100 | 3000 | 26.0146 | 52.6242 | 65.6429 | 0 | 7.2692 | FALSE | FALSE
2025-09-18 15:00 | 38.2 | 36.5 | 99910 | 100 | 3000 | 25.523 | 57.9993 | 70.6365 | 0 | 7.2692 | FALSE | FALSE
2025-09-18 16:00 | 36.8 | 42 | 99915 | 100 | 3000 | 25.0097 | 62.0578 | 72.9024 | 0 | 7.2692 | FALSE | FALSE
2025-09-18 17:00 | 35.1 | 47.5 | 99945 | 100 | 3000 | 24.3933 | 65.6007 | 73.141 | 0 | 7.2692 | FALSE | FALSE
2025-09-18 18:00 | 33.5 | 57 | 99980 | 100 | 3000 | 23.7854 | 71.9935 | 77.4938 | 0 | 7.2692 | FALSE | FALSE
2025-09-18 19:00 | 32.55 | 65.5 | 100025 | 100 | 3000 | 23.4121 | 77.655 | 82.4753 | 0 | 7.2692 | FALSE | FALSE
2025-09-18 20:00 | 31.8 | 72 | 100070 | 100 | 3000 | 23.1204 | 81.7353 | 85.6519 | 0 | 7.2692 | FALSE | FALSE
2025-09-18 21:00 | 30.9 | 78 | 100085 | 100 | 3000 | 22.7786 | 85.101 | 87.1222 | 0 | 7.2692 | FALSE | FALSE
2025-09-18 22:00 | 29.9 | 83.5 | 100070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-18 23:00 | 29 | 86.5 | 100040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-19 | 28.25 | 87.5 | 100010 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-19 01:00 | 27.5 | 90 | 99985 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-19 02:00 | 26.75 | 93.5 | 99965 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-19 03:00 | 26 | 95.5 | 99960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-19 04:00 | 26.1 | 94 | 99980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-19 05:00 | 26.6 | 90 | 100020 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-19 06:00 | 27.1 | 82.5 | 100075 | 100 | 3000 | 21.3688 | 84.2111 | 71.9123 | 0 | 7.2692 | FALSE | FALSE
2025-09-19 07:00 | 29.2 | 69 | 100150 | 100 | 3000 | 22.191 | 77.2054 | 70.2279 | 0 | 7.2692 | FALSE | FALSE
2025-09-19 08:00 | 32.2 | 56 | 100205 | 100 | 3000 | 23.3312 | 70.2356 | 70.7576 | 0 | 7.2692 | FALSE | FALSE
2025-09-19 09:00 | 34.6 | 47 | 100220 | 100 | 3000 | 24.2235 | 64.8538 | 70.5744 | 0 | 7.2692 | FALSE | FALSE
2025-09-19 10:00 | 36.35 | 41 | 100215 | 100 | 3000 | 24.8648 | 60.9199 | 69.9318 | 0 | 7.2692 | FALSE | FALSE
2025-09-19 11:00 | 37.45 | 38.5 | 100170 | 100 | 3000 | 25.2558 | 59.3616 | 70.7289 | 0 | 7.2692 | FALSE | FALSE
2025-09-19 12:00 | 37.9 | 39.5 | 100085 | 100 | 3000 | 25.3977 | 60.5035 | 73.7879 | 0 | 7.2692 | FALSE | FALSE
2025-09-19 13:00 | 38 | 42 | 100000 | 100 | 3000 | 25.4093 | 62.8012 | 77.6383 | 0 | 7.2692 | FALSE | FALSE
2025-09-19 14:00 | 38 | 41 | 99925 | 100 | 3000 | 25.4178 | 61.9146 | 76.2221 | 0 | 7.2692 | FALSE | FALSE
2025-09-19 15:00 | 37.55 | 39.5 | 99895 | 100 | 3000 | 25.281 | 60.3188 | 72.4028 | 0 | 7.2692 | FALSE | FALSE
2025-09-19 16:00 | 36.25 | 45.5 | 99915 | 100 | 3000 | 24.7986 | 64.698 | 75.2962 | 0 | 7.2692 | FALSE | FALSE
2025-09-19 17:00 | 34.55 | 56.5 | 99930 | 100 | 3000 | 24.1502 | 72.4695 | 81.5971 | 0 | 7.2692 | FALSE | FALSE
2025-09-19 18:00 | 33.2 | 65 | 99945 | 100 | 3000 | 23.6404 | 77.9056 | 85.0187 | 0 | 7.2692 | FALSE | FALSE
2025-09-19 19:00 | 32.55 | 69 | 99995 | 100 | 3000 | 23.3959 | 80.2902 | 86.2079 | 0 | 7.2692 | FALSE | FALSE
2025-09-19 20:00 | 32.25 | 70 | 100045 | 100 | 3000 | 23.2868 | 80.7256 | 85.7994 | 0 | 7.2692 | FALSE | FALSE
2025-09-19 21:00 | 31.8 | 72 | 100055 | 100 | 3000 | 23.1204 | 81.7367 | 85.6486 | 0 | 7.2692 | FALSE | FALSE
2025-09-19 22:00 | 31.2 | 75.5 | 100030 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-19 23:00 | 30.6 | 77.5 | 99990 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-20 | 30.1 | 77 | 99940 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-20 01:00 | 29.8 | 76 | 99900 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-20 02:00 | 29.55 | 75.5 | 99885 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-20 03:00 | 29.1 | 75 | 99885 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-20 04:00 | 29 | 71.5 | 99905 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-20 05:00 | 29.1 | 69 | 99950 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-20 06:00 | 29.3 | 69.5 | 100015 | 100 | 3000 | 22.2265 | 77.6396 | 71.1314 | 0 | 7.2692 | FALSE | FALSE
2025-09-20 07:00 | 30.4 | 68.5 | 100100 | 100 | 3000 | 22.6333 | 77.8749 | 75.3615 | 0 | 7.2692 | FALSE | FALSE
2025-09-20 08:00 | 32.35 | 64.5 | 100160 | 100 | 3000 | 23.3467 | 76.7072 | 80.4915 | 0 | 7.2692 | FALSE | FALSE
2025-09-20 09:00 | 35.05 | 53 | 100165 | 100 | 3000 | 24.3421 | 70.03 | 79.6855 | 0 | 7.2692 | FALSE | FALSE
2025-09-20 10:00 | 37.5 | 39.5 | 100140 | 100 | 3000 | 25.2644 | 60.2701 | 72.2812 | 0 | 7.2692 | FALSE | FALSE
2025-09-20 11:00 | 39.15 | 30 | 100090 | 100 | 3000 | 25.8984 | 52.4806 | 64.524 | 0 | 7.2692 | FALSE | FALSE
2025-09-20 12:00 | 40.5 | 23.5 | 100015 | 100 | 3000 | 26.4132 | 46.7635 | 58.657 | 0 | 7.2692 | FALSE | FALSE
2025-09-20 13:00 | 41.4 | 20 | 99930 | 100 | 3000 | 26.751 | 43.5333 | 55.4427 | 0 | 7.2692 | FALSE | FALSE
2025-09-20 14:00 | 41.35 | 20 | 99860 | 100 | 3000 | 26.7345 | 43.5306 | 55.2839 | 0 | 7.2692 | FALSE | FALSE
2025-09-20 15:00 | 39.5 | 33 | 99830 | 100 | 3000 | 25.9847 | 55.4371 | 70.149 | 0 | 7.2692 | FALSE | FALSE
2025-09-20 16:00 | 37.35 | 48 | 99845 | 100 | 3000 | 25.1457 | 67.6501 | 83.1292 | 0 | 7.2692 | FALSE | FALSE
2025-09-20 17:00 | 36.3 | 55 | 99860 | 100 | 3000 | 24.7471 | 72.7818 | 87.6507 | 0 | 7.2692 | FALSE | FALSE
2025-09-20 18:00 | 36.25 | 53.5 | 99895 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-20 19:00 | 35.55 | 50.5 | 99960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-20 20:00 | 33.8 | 55.5 | 100020 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-20 21:00 | 32.65 | 60 | 100055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-20 22:00 | 31.9 | 62 | 100050 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-20 23:00 | 31.3 | 62 | 100020 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 | 30.65 | 63 | 99995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 01:00 | 30.1 | 63 | 99995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 02:00 | 29.95 | 62 | 99995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 03:00 | 30 | 61.5 | 99995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 04:00 | 29.95 | 61 | 100015 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 05:00 | 29.7 | 61.5 | 100050 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 06:00 | 29.5 | 61.5 | 100095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 07:00 | 30.6 | 57.5 | 100175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 08:00 | 32.85 | 50 | 100255 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 09:00 | 34.9 | 43 | 100275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 10:00 | 36.7 | 37.5 | 100245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 11:00 | 38.55 | 32.5 | 100190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 12:00 | 40 | 29 | 100125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 13:00 | 40.4 | 29.5 | 100050 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 14:00 | 39.75 | 33 | 99975 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 15:00 | 38.65 | 37 | 99940 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 16:00 | 37.4 | 40.5 | 99955 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 17:00 | 35.85 | 44.5 | 99965 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 18:00 | 34.45 | 53 | 99990 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 19:00 | 33.6 | 61.5 | 100035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 20:00 | 33.25 | 64.5 | 100080 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 21:00 | 32.9 | 64 | 100125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 22:00 | 32.35 | 60.5 | 100130 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-21 23:00 | 31.8 | 57.5 | 100115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-22 | 31.1 | 59.5 | 100110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-22 01:00 | 30.35 | 67 | 100105 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-22 02:00 | 29.7 | 72.5 | 100100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-22 03:00 | 29.05 | 72 | 100105 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-22 04:00 | 28.9 | 68.5 | 100115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-22 05:00 | 28.95 | 67 | 100135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-22 06:00 | 29.2 | 67 | 100180 | 100 | 3000 | 22.1969 | 75.847 | 68.3843 | 0 | 7.2692 | FALSE | FALSE
2025-09-22 07:00 | 31 | 59.5 | 100250 | 100 | 3000 | 22.884 | 71.9419 | 69.1934 | 0 | 7.2692 | FALSE | FALSE
2025-09-22 08:00 | 33.8 | 47 | 100330 | 100 | 3000 | 23.9433 | 64.3671 | 67.3953 | 0 | 7.2692 | FALSE | FALSE
2025-09-22 09:00 | 36.4 | 37.5 | 100370 | 100 | 3000 | 24.9069 | 57.9589 | 65.5721 | 0 | 7.2692 | FALSE | FALSE
2025-09-22 10:00 | 38.4 | 32 | 100355 | 100 | 3000 | 25.6295 | 53.9992 | 65.0224 | 0 | 7.2692 | FALSE | FALSE
2025-09-22 11:00 | 39.65 | 29 | 100315 | 100 | 3000 | 26.0742 | 51.7144 | 64.7238 | 0 | 7.2692 | FALSE | FALSE
2025-09-22 12:00 | 39.75 | 30.5 | 100260 | 100 | 3000 | 26.0921 | 53.1673 | 67.3369 | 0 | 7.2692 | FALSE | FALSE
2025-09-22 13:00 | 38.95 | 33.5 | 100205 | 100 | 3000 | 25.799 | 55.6144 | 69.0724 | 0 | 7.2692 | FALSE | FALSE
2025-09-22 14:00 | 38.2 | 36.5 | 100170 | 100 | 3000 | 25.5231 | 57.9779 | 70.7105 | 0 | 7.2692 | FALSE | FALSE
2025-09-22 15:00 | 37.4 | 40.5 | 100150 | 100 | 3000 | 25.2229 | 61.0898 | 73.2701 | 0 | 7.2692 | FALSE | FALSE
2025-09-22 16:00 | 36.35 | 45 | 100155 | 100 | 3000 | 24.8361 | 64.3195 | 75.1177 | 0 | 7.2692 | FALSE | FALSE
2025-09-22 17:00 | 34.9 | 53.5 | 100165 | 100 | 3000 | 24.288 | 70.3175 | 79.634 | 0 | 7.2692 | FALSE | FALSE
2025-09-22 18:00 | 33.45 | 66 | 100180 | 100 | 3000 | 23.7217 | 78.9029 | 87.3863 | 0 | 7.2692 | FALSE | FALSE
2025-09-22 19:00 | 32.55 | 76 | 100225 | 100 | 3000 | 23.3636 | 85.5278 | 93.6819 | 0 | 7.2692 | FALSE | FALSE
2025-09-22 20:00 | 31.95 | 80.5 | 100265 | 100 | 3000 | 23.1366 | 88.1374 | 95.1892 | 0 | 7.2692 | FALSE | FALSE
2025-09-22 21:00 | 31.35 | 84 | 100295 | 100 | 3000 | 22.9139 | 89.9254 | 95.4806 | 0 | 7.2692 | FALSE | FALSE
2025-09-22 22:00 | 30.75 | 86.5 | 100295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-22 23:00 | 30.1 | 88 | 100280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-23 | 29.45 | 90 | 100265 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-23 01:00 | 28.9 | 93 | 100230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-23 02:00 | 28.4 | 96.5 | 100205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-23 03:00 | 28.05 | 99 | 100205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-23 04:00 | 28.2 | 95 | 100235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-23 05:00 | 28.15 | 93 | 100275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-23 06:00 | 28.05 | 96 | 100320 | 100 | 3000 | 21.6933 | 93.8959 | 88.3227 | 0 | 7.2692 | FALSE | FALSE
2025-09-23 07:00 | 29.3 | 89 | 100395 | 100 | 3000 | 22.1686 | 90.8242 | 89.0767 | 0 | 7.2692 | FALSE | FALSE
2025-09-23 08:00 | 31.1 | 76 | 100460 | 100 | 3000 | 22.8576 | 83.8549 | 86.2499 | 0 | 7.2692 | FALSE | FALSE
2025-09-23 09:00 | 32.8 | 65 | 100485 | 100 | 3000 | 23.5024 | 77.4711 | 83.2322 | 0 | 7.2692 | FALSE | FALSE
2025-09-23 10:00 | 34.65 | 55 | 100465 | 100 | 3000 | 24.1939 | 71.3003 | 80.4007 | 0 | 7.2692 | FALSE | FALSE
2025-09-23 11:00 | 36.3 | 47 | 100415 | 100 | 3000 | 24.8053 | 65.9586 | 77.5669 | 0 | 7.2692 | FALSE | FALSE
2025-09-23 12:00 | 37.25 | 44.5 | 100340 | 100 | 3000 | 25.1413 | 64.4761 | 78.1487 | 0 | 7.2692 | FALSE | FALSE
2025-09-23 13:00 | 37.5 | 44.5 | 100245 | 100 | 3000 | 25.224 | 64.6572 | 79.139 | 0 | 7.2692 | FALSE | FALSE
2025-09-23 14:00 | 37.3 | 43 | 100165 | 100 | 3000 | 25.1696 | 63.2148 | 76.2782 | 0 | 7.2692 | FALSE | FALSE
2025-09-23 15:00 | 36.45 | 45.5 | 100105 | 100 | 3000 | 24.8662 | 64.815 | 76.158 | 0 | 7.2692 | FALSE | FALSE
2025-09-23 16:00 | 35.2 | 51.5 | 100090 | 100 | 3000 | 24.4025 | 68.9282 | 78.4907 | 0 | 7.2692 | FALSE | FALSE
2025-09-23 17:00 | 33.8 | 58 | 100095 | 100 | 3000 | 23.8844 | 73.0089 | 79.9995 | 0 | 7.2692 | FALSE | FALSE
2025-09-23 18:00 | 32.4 | 66.5 | 100100 | 100 | 3000 | 23.3551 | 78.2559 | 82.8423 | 0 | 7.2692 | FALSE | FALSE
2025-09-23 19:00 | 31.6 | 74.5 | 100145 | 100 | 3000 | 23.0398 | 83.3439 | 87.2186 | 0 | 7.2692 | FALSE | FALSE
2025-09-23 20:00 | 31.25 | 80 | 100205 | 100 | 3000 | 22.8947 | 86.9259 | 90.9501 | 0 | 7.2692 | FALSE | FALSE
2025-09-23 21:00 | 30.75 | 84 | 100240 | 100 | 3000 | 22.7033 | 89.1735 | 92.2178 | 0 | 7.2692 | FALSE | FALSE
2025-09-23 22:00 | 30.25 | 87 | 100240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-23 23:00 | 29.8 | 89.5 | 100195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-24 | 29.15 | 93 | 100125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-24 01:00 | 28.6 | 95.5 | 100065 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-24 02:00 | 28.25 | 95.5 | 100030 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-24 03:00 | 27.95 | 94.5 | 100010 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-24 04:00 | 27.95 | 95.5 | 100040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-24 05:00 | 27.9 | 96.5 | 100090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-24 06:00 | 27.8 | 95 | 100115 | 100 | 3000 | 21.6032 | 92.9539 | 86.0525 | 0 | 7.2692 | FALSE | FALSE
2025-09-24 07:00 | 29.3 | 87 | 100175 | 100 | 3000 | 22.1744 | 89.4927 | 87.2205 | 0 | 7.2692 | FALSE | FALSE
2025-09-24 08:00 | 32.65 | 70.5 | 100230 | 100 | 3000 | 23.4239 | 81.5022 | 88.3571 | 0 | 7.2692 | FALSE | FALSE
2025-09-24 09:00 | 35.5 | 55.5 | 100240 | 100 | 3000 | 24.4783 | 72.4491 | 84.7518 | 0 | 7.2692 | FALSE | FALSE
2025-09-24 10:00 | 36.75 | 47.5 | 100220 | 100 | 3000 | 24.9519 | 66.7267 | 80.0378 | 0 | 7.2692 | FALSE | FALSE
2025-09-24 11:00 | 37.4 | 42.5 | 100165 | 100 | 3000 | 25.2069 | 62.8415 | 75.9972 | 0 | 7.2692 | FALSE | FALSE
2025-09-24 12:00 | 37.95 | 36 | 100075 | 100 | 3000 | 25.4439 | 57.4132 | 69.0669 | 0 | 7.2692 | FALSE | FALSE
2025-09-24 13:00 | 37.75 | 33 | 99980 | 100 | 3000 | 25.4016 | 54.666 | 64.1179 | 0 | 7.2692 | FALSE | FALSE
2025-09-24 14:00 | 36.8 | 35.5 | 99920 | 100 | 3000 | 25.0584 | 56.463 | 64.2254 | 0 | 7.2692 | FALSE | FALSE
2025-09-24 15:00 | 35.75 | 38.5 | 99895 | 100 | 3000 | 24.6756 | 58.5425 | 64.38 | 0 | 7.2692 | FALSE | FALSE
2025-09-24 16:00 | 34.45 | 44 | 99900 | 100 | 3000 | 24.1884 | 62.3891 | 66.3047 | 0 | 7.2692 | FALSE | FALSE
2025-09-24 17:00 | 33.1 | 51 | 99910 | 100 | 3000 | 23.6749 | 67.0834 | 69.0173 | 0 | 7.2692 | FALSE | FALSE
2025-09-24 18:00 | 32.2 | 55 | 99915 | 100 | 3000 | 23.3354 | 69.5167 | 69.6239 | 0 | 7.2692 | FALSE | FALSE
2025-09-24 19:00 | 31.65 | 56.5 | 99930 | 100 | 3000 | 23.1312 | 70.2495 | 68.8628 | 0 | 7.2692 | FALSE | FALSE
2025-09-24 20:00 | 31.2 | 58.5 | 99950 | 100 | 3000 | 22.9603 | 71.3914 | 68.9886 | 0 | 7.2692 | FALSE | FALSE
2025-09-24 21:00 | 30.75 | 61 | 99965 | 100 | 3000 | 22.7873 | 72.8607 | 69.5416 | 0 | 7.2692 | FALSE | FALSE
2025-09-24 22:00 | 30.2 | 63 | 99960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-24 23:00 | 29.55 | 65.5 | 99925 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-25 | 29 | 68.5 | 99880 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-25 01:00 | 28.65 | 72 | 99860 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-25 02:00 | 28.4 | 75 | 99845 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-25 03:00 | 28.2 | 76.5 | 99845 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-25 04:00 | 28.2 | 72 | 99885 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-25 05:00 | 28.1 | 68 | 99935 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-25 06:00 | 28.1 | 68 | 99995 | 100 | 3000 | 21.7811 | 75.7147 | 64.2641 | 0 | 7.2692 | FALSE | FALSE
2025-09-25 07:00 | 29.4 | 63.5 | 100065 | 100 | 3000 | 22.2816 | 73.6244 | 66.0021 | 0 | 7.2692 | FALSE | FALSE
2025-09-25 08:00 | 31.35 | 59.5 | 100130 | 100 | 3000 | 23.0109 | 72.2063 | 70.7059 | 0 | 7.2692 | FALSE | FALSE
2025-09-25 09:00 | 32.9 | 57 | 100150 | 100 | 3000 | 23.5753 | 71.5081 | 74.8791 | 0 | 7.2692 | FALSE | FALSE
2025-09-25 10:00 | 34.3 | 51.5 | 100115 | 100 | 3000 | 24.0934 | 68.2636 | 74.6586 | 0 | 7.2692 | FALSE | FALSE
2025-09-25 11:00 | 35.8 | 43 | 100055 | 100 | 3000 | 24.6628 | 62.3074 | 70.3457 | 0 | 7.2692 | FALSE | FALSE
2025-09-25 12:00 | 37.4 | 33.5 | 99965 | 100 | 3000 | 25.2787 | 54.9687 | 63.6064 | 0 | 7.2692 | FALSE | FALSE
2025-09-25 13:00 | 38.45 | 28 | 99875 | 100 | 3000 | 25.6816 | 50.4373 | 59.239 | 0 | 7.2692 | FALSE | FALSE
2025-09-25 14:00 | 37.45 | 37.5 | 99830 | 100 | 3000 | 25.2636 | 58.512 | 69.2614 | 0 | 7.2692 | FALSE | FALSE
2025-09-25 15:00 | 35.65 | 48.5 | 99835 | 100 | 3000 | 24.5747 | 66.8082 | 76.6201 | 0 | 7.2692 | FALSE | FALSE
2025-09-25 16:00 | 34.7 | 51 | 99885 | 100 | 3000 | 24.2342 | 68.17 | 75.7022 | 0 | 7.2692 | FALSE | FALSE
2025-09-25 17:00 | 33.6 | 55.5 | 99930 | 100 | 3000 | 23.828 | 70.9106 | 76.2246 | 0 | 7.2692 | FALSE | FALSE
2025-09-25 18:00 | 32.7 | 60.5 | 99960 | 100 | 3000 | 23.488 | 74.0223 | 77.7669 | 0 | 7.2692 | FALSE | FALSE
2025-09-25 19:00 | 32.25 | 64.5 | 100005 | 100 | 3000 | 23.3113 | 76.6311 | 79.9872 | 0 | 7.2692 | FALSE | FALSE
2025-09-25 20:00 | 31.75 | 68 | 100065 | 100 | 3000 | 23.1196 | 78.7507 | 81.2843 | 0 | 7.2692 | FALSE | FALSE
2025-09-25 21:00 | 31.2 | 71.5 | 100110 | 100 | 3000 | 22.9102 | 80.7565 | 82.1828 | 0 | 7.2692 | FALSE | FALSE
2025-09-25 22:00 | 30.55 | 74.5 | 100110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-25 23:00 | 29.95 | 77 | 100095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-26 | 29.4 | 79.5 | 100085 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-26 01:00 | 28.7 | 82.5 | 100075 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-26 02:00 | 27.85 | 85.5 | 100070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-26 03:00 | 27.1 | 86.5 | 100080 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-26 04:00 | 26.95 | 82.5 | 100115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-26 05:00 | 26.85 | 80 | 100180 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-26 06:00 | 26.9 | 80 | 100250 | 100 | 3000 | 21.2979 | 82.4338 | 68.8875 | 0 | 7.2692 | FALSE | FALSE
2025-09-26 07:00 | 28.4 | 73.5 | 100310 | 100 | 3000 | 21.8804 | 79.5359 | 70.5679 | 0 | 7.2692 | FALSE | FALSE
2025-09-26 08:00 | 30.8 | 62 | 100370 | 100 | 3000 | 22.8021 | 73.5722 | 70.8443 | 0 | 7.2692 | FALSE | FALSE
2025-09-26 09:00 | 32.9 | 53 | 100400 | 100 | 3000 | 23.5946 | 68.4377 | 70.5207 | 0 | 7.2692 | FALSE | FALSE
2025-09-26 10:00 | 34.65 | 47.5 | 100380 | 100 | 3000 | 24.2381 | 65.2731 | 71.4169 | 0 | 7.2692 | FALSE | FALSE
2025-09-26 11:00 | 36.35 | 41.5 | 100320 | 100 | 3000 | 24.8613 | 61.3353 | 70.6119 | 0 | 7.2692 | FALSE | FALSE
2025-09-26 12:00 | 37.8 | 36 | 100220 | 100 | 3000 | 25.3937 | 57.3285 | 68.5654 | 0 | 7.2692 | FALSE | FALSE
2025-09-26 13:00 | 38.15 | 37.5 | 100135 | 100 | 3000 | 25.4978 | 58.8522 | 71.9339 | 0 | 7.2692 | FALSE | FALSE
2025-09-26 14:00 | 37.3 | 44 | 100090 | 100 | 3000 | 25.1616 | 64.0949 | 77.6082 | 0 | 7.2692 | FALSE | FALSE
2025-09-26 15:00 | 36.15 | 48.5 | 100095 | 100 | 3000 | 24.7439 | 67.1461 | 78.7807 | 0 | 7.2692 | FALSE | FALSE
2025-09-26 16:00 | 35.1 | 53 | 100130 | 100 | 3000 | 24.3591 | 70.0727 | 79.8948 | 0 | 7.2692 | FALSE | FALSE
2025-09-26 17:00 | 33.85 | 59 | 100160 | 100 | 3000 | 23.8963 | 73.8294 | 81.3835 | 0 | 7.2692 | FALSE | FALSE
2025-09-26 18:00 | 32.8 | 64.5 | 100200 | 100 | 3000 | 23.5044 | 77.1185 | 82.6253 | 0 | 7.2692 | FALSE | FALSE
2025-09-26 19:00 | 32.4 | 67 | 100260 | 100 | 3000 | 23.3531 | 78.6153 | 83.4095 | 0 | 7.2692 | FALSE | FALSE
2025-09-26 20:00 | 32.25 | 66.5 | 100320 | 100 | 3000 | 23.3028 | 78.0924 | 82.1727 | 0 | 7.2692 | FALSE | FALSE
2025-09-26 21:00 | 31.85 | 67 | 100340 | 100 | 3000 | 23.1595 | 78.0843 | 80.788 | 0 | 7.2692 | FALSE | FALSE
2025-09-26 22:00 | 31.1 | 69 | 100340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-26 23:00 | 30.45 | 69.5 | 100320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-27 | 29.95 | 69 | 100295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-27 01:00 | 29.45 | 69.5 | 100285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-27 02:00 | 28.85 | 72 | 100275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-27 03:00 | 28.2 | 76 | 100280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-27 04:00 | 28.4 | 74 | 100305 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-27 05:00 | 28.65 | 69 | 100355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-27 06:00 | 28.75 | 64 | 100420 | 100 | 3000 | 22.037 | 73.4787 | 63.6559 | 0 | 7.2692 | FALSE | FALSE
2025-09-27 07:00 | 30.5 | 55 | 100495 | 100 | 3000 | 22.7171 | 68.387 | 62.5982 | 0 | 7.2692 | FALSE | FALSE
2025-09-27 08:00 | 32.65 | 47.5 | 100570 | 100 | 3000 | 23.531 | 64.0945 | 63.4593 | 0 | 7.2692 | FALSE | FALSE
2025-09-27 09:00 | 34.55 | 42 | 100600 | 100 | 3000 | 24.2353 | 60.7757 | 64.4513 | 0 | 7.2692 | FALSE | FALSE
2025-09-27 10:00 | 36.85 | 35.5 | 100585 | 100 | 3000 | 25.0758 | 56.4289 | 64.5817 | 0 | 7.2692 | FALSE | FALSE
2025-09-27 11:00 | 38.8 | 29.5 | 100525 | 100 | 3000 | 25.7862 | 51.8611 | 62.7552 | 0 | 7.2692 | FALSE | FALSE
2025-09-27 12:00 | 40.2 | 25.5 | 100430 | 100 | 3000 | 26.2923 | 48.5708 | 61.064 | 0 | 7.2692 | FALSE | FALSE
2025-09-27 13:00 | 41 | 23 | 100345 | 100 | 3000 | 26.584 | 46.3709 | 59.4179 | 0 | 7.2692 | FALSE | FALSE
2025-09-27 14:00 | 40.4 | 27.5 | 100290 | 100 | 3000 | 26.3369 | 50.5582 | 64.8106 | 0 | 7.2692 | FALSE | FALSE
2025-09-27 15:00 | 38.6 | 36.5 | 100275 | 100 | 3000 | 25.6558 | 58.1778 | 72.2088 | 0 | 7.2692 | FALSE | FALSE
2025-09-27 16:00 | 36.95 | 42.5 | 100305 | 100 | 3000 | 25.0567 | 62.547 | 74.2604 | 0 | 7.2692 | FALSE | FALSE
2025-09-27 17:00 | 35.35 | 52 | 100335 | 100 | 3000 | 24.4506 | 69.4323 | 79.8128 | 0 | 7.2692 | FALSE | FALSE
2025-09-27 18:00 | 34.05 | 60.5 | 100360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-27 19:00 | 33.6 | 61 | 100420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-27 20:00 | 33.35 | 59 | 100485 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-27 21:00 | 32.8 | 58.5 | 100510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-27 22:00 | 32 | 59 | 100500 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-27 23:00 | 31.25 | 60 | 100480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 | 30.5 | 62.5 | 100460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 01:00 | 29.65 | 65.5 | 100440 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 02:00 | 28.9 | 69.5 | 100430 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 03:00 | 28.3 | 75.5 | 100420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 04:00 | 28.05 | 78.5 | 100435 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 05:00 | 27.8 | 78 | 100490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 06:00 | 27.95 | 67 | 100540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 07:00 | 29.7 | 50 | 100585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 08:00 | 32.05 | 45.5 | 100625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 09:00 | 34.3 | 44 | 100630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 10:00 | 36.55 | 37 | 100610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 11:00 | 38.35 | 30 | 100555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 12:00 | 39.25 | 28 | 100460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 13:00 | 39.15 | 29.5 | 100380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 14:00 | 38.7 | 28.5 | 100325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 15:00 | 37.7 | 31.5 | 100295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 16:00 | 35.95 | 43 | 100300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 17:00 | 34.15 | 57 | 100310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 18:00 | 32.9 | 66 | 100315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 19:00 | 32.2 | 68.5 | 100330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 20:00 | 31.4 | 71 | 100355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 21:00 | 30.5 | 74.5 | 100355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 22:00 | 29.8 | 77.5 | 100325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-28 23:00 | 29.25 | 82.5 | 100300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-29 | 28.5 | 88.5 | 100275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-29 01:00 | 27.45 | 92 | 100245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-29 02:00 | 26.55 | 94.5 | 100215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-29 03:00 | 26.2 | 96.5 | 100195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-29 04:00 | 26.45 | 96.5 | 100205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-29 05:00 | 26.7 | 95.5 | 100235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-29 06:00 | 27.2 | 93.5 | 100250 | 100 | 3000 | 21.3831 | 91.2598 | 81.5501 | 0 | 7.2692 | FALSE | FALSE
2025-09-29 07:00 | 29.15 | 85 | 100265 | 100 | 3000 | 22.1259 | 87.958 | 84.6263 | 0 | 7.2692 | FALSE | FALSE
2025-09-29 08:00 | 32.5 | 68.5 | 100300 | 100 | 3000 | 23.3812 | 79.835 | 85.4992 | 0 | 7.2692 | FALSE | FALSE
2025-09-29 09:00 | 35.8 | 49 | 100310 | 100 | 3000 | 24.6227 | 67.2904 | 77.9989 | 0 | 7.2692 | FALSE | FALSE
2025-09-29 10:00 | 37.55 | 37.5 | 100290 | 100 | 3000 | 25.2975 | 58.5246 | 69.7571 | 0 | 7.2692 | FALSE | FALSE
2025-09-29 11:00 | 37.9 | 36.5 | 100260 | 100 | 3000 | 25.4231 | 57.8186 | 69.6401 | 0 | 7.2692 | FALSE | FALSE
2025-09-29 12:00 | 37.7 | 39 | 100195 | 100 | 3000 | 25.3354 | 59.9367 | 72.3645 | 0 | 7.2692 | FALSE | FALSE
2025-09-29 13:00 | 37.25 | 43 | 100105 | 100 | 3000 | 25.1529 | 63.1875 | 76.0628 | 0 | 7.2692 | FALSE | FALSE
2025-09-29 14:00 | 36.65 | 46.5 | 100030 | 100 | 3000 | 24.9258 | 65.8131 | 78.261 | 0 | 7.2692 | FALSE | FALSE
2025-09-29 15:00 | 35.8 | 50.5 | 100000 | 100 | 3000 | 24.6122 | 68.5685 | 79.8023 | 0 | 7.2692 | FALSE | FALSE
2025-09-29 16:00 | 34.7 | 56 | 100005 | 100 | 3000 | 24.2045 | 72.188 | 81.6969 | 0 | 7.2692 | FALSE | FALSE
2025-09-29 17:00 | 33.3 | 65 | 100000 | 100 | 3000 | 23.675 | 77.9982 | 85.5111 | 0 | 7.2692 | FALSE | FALSE
2025-09-29 18:00 | 32.1 | 72.5 | 99995 | 100 | 3000 | 23.2232 | 82.4294 | 87.6552 | 0 | 7.2692 | FALSE | FALSE
2025-09-29 19:00 | 31.4 | 75.5 | 100010 | 100 | 3000 | 22.9651 | 83.8651 | 87.1838 | 0 | 7.2692 | FALSE | FALSE
2025-09-29 20:00 | 30.85 | 77.5 | 100030 | 100 | 3000 | 22.7626 | 84.6946 | 86.3625 | 0 | 7.2692 | FALSE | FALSE
2025-09-29 21:00 | 30.25 | 80 | 100055 | 100 | 3000 | 22.5394 | 85.7895 | 85.6925 | 0 | 7.2692 | FALSE | FALSE
2025-09-29 22:00 | 29.55 | 83.5 | 100045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-29 23:00 | 28.85 | 87 | 100025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-30 | 28.15 | 90.5 | 100005 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-30 01:00 | 27.4 | 93 | 99970 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-30 02:00 | 26.8 | 94.5 | 99940 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-30 03:00 | 26.45 | 95.5 | 99920 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-30 04:00 | 26.35 | 94.5 | 99935 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-30 05:00 | 26.2 | 94 | 99965 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-30 06:00 | 26.3 | 93.5 | 99995 | 100 | 3000 | 21.0424 | 90.2684 | 76.6945 | 0 | 7.2692 | FALSE | FALSE
2025-09-30 07:00 | 28.1 | 84.5 | 100025 | 100 | 3000 | 21.7402 | 86.4983 | 78.6661 | 0 | 7.2692 | FALSE | FALSE
2025-09-30 08:00 | 30.65 | 74 | 100075 | 100 | 3000 | 22.7041 | 81.9942 | 81.9338 | 0 | 7.2692 | FALSE | FALSE
2025-09-30 09:00 | 32.7 | 64.5 | 100090 | 100 | 3000 | 23.4693 | 77.0354 | 82.1267 | 0 | 7.2692 | FALSE | FALSE
2025-09-30 10:00 | 34.9 | 51.5 | 100030 | 100 | 3000 | 24.3 | 68.7079 | 77.1903 | 0 | 7.2692 | FALSE | FALSE
2025-09-30 11:00 | 37.25 | 39 | 99945 | 100 | 3000 | 25.1844 | 59.7109 | 70.601 | 0 | 7.2692 | FALSE | FALSE
2025-09-30 12:00 | 38.8 | 32.5 | 99860 | 100 | 3000 | 25.7584 | 54.6587 | 66.9786 | 0 | 7.2692 | FALSE | FALSE
2025-09-30 13:00 | 39.05 | 30 | 99790 | 100 | 3000 | 25.8651 | 52.4676 | 64.1048 | 0 | 7.2692 | FALSE | FALSE
2025-09-30 14:00 | 38.35 | 29.5 | 99745 | 100 | 3000 | 25.6345 | 51.7725 | 61.0632 | 0 | 7.2692 | FALSE | FALSE
2025-09-30 15:00 | 37.3 | 36 | 99720 | 100 | 3000 | 25.2248 | 57.1346 | 66.628 | 0 | 7.2692 | FALSE | FALSE
2025-09-30 16:00 | 35.85 | 46 | 99710 | 100 | 3000 | 24.6593 | 64.873 | 74.2618 | 0 | 7.2692 | FALSE | FALSE
2025-09-30 17:00 | 33.95 | 58.5 | 99735 | 100 | 3000 | 23.933 | 73.562 | 81.1646 | 0 | 7.2692 | FALSE | FALSE
2025-09-30 18:00 | 32.7 | 68.5 | 99785 | 100 | 3000 | 23.45 | 80.0868 | 86.3621 | 0 | 7.2692 | FALSE | FALSE
2025-09-30 19:00 | 32.05 | 73.5 | 99825 | 100 | 3000 | 23.2012 | 83.1314 | 88.4038 | 0 | 7.2692 | FALSE | FALSE
2025-09-30 20:00 | 31.25 | 79 | 99850 | 100 | 3000 | 22.8981 | 86.2396 | 89.8792 | 0 | 7.2692 | FALSE | FALSE
2025-09-30 21:00 | 30.4 | 84 | 99870 | 100 | 3000 | 22.5788 | 88.7805 | 90.2618 | 0 | 7.2692 | FALSE | FALSE
2025-09-30 22:00 | 29.6 | 88 | 99865 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-09-30 23:00 | 29.05 | 90.5 | 99825 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-01 | 28.55 | 92.5 | 99775 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-01 01:00 | 27.65 | 95.5 | 99750 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-01 02:00 | 26.9 | 98 | 99745 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-01 03:00 | 26.85 | 99.5 | 99725 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-01 04:00 | 26.9 | 100 | 99715 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-01 05:00 | 27.05 | 100 | 99745 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-01 06:00 | 27.5 | 100 | 99805 | 100 | 3000 | 21.48 | 95.8071 | 88.506 | 0 | 7.2692 | FALSE | FALSE
2025-10-01 07:00 | 27.95 | 98.5 | 99860 | 100 | 3000 | 21.6497 | 95.4325 | 89.8042 | 0 | 7.2692 | FALSE | FALSE
2025-10-01 08:00 | 28.95 | 93 | 99910 | 100 | 3000 | 22.0295 | 93.1194 | 90.6491 | 0 | 7.2692 | FALSE | FALSE
2025-10-01 09:00 | 31.35 | 81 | 99935 | 100 | 3000 | 22.9253 | 87.7935 | 92.4175 | 0 | 7.2692 | FALSE | FALSE
2025-10-01 10:00 | 34.3 | 64.5 | 99915 | 100 | 3000 | 24.0187 | 78.6209 | 89.7529 | 0 | 7.2692 | FALSE | FALSE
2025-10-01 11:00 | 36.6 | 50.5 | 99860 | 100 | 3000 | 24.8792 | 69.2123 | 83.211 | 0 | 7.2692 | FALSE | FALSE
2025-10-01 12:00 | 37.8 | 44.5 | 99805 | 100 | 3000 | 25.3221 | 64.9063 | 80.2394 | 0 | 7.2692 | FALSE | FALSE
2025-10-01 13:00 | 37.6 | 46.5 | 99765 | 100 | 3000 | 25.2398 | 66.532 | 82.1355 | 0 | 7.2692 | FALSE | FALSE
2025-10-01 14:00 | 36.7 | 51 | 99710 | 100 | 3000 | 24.9083 | 69.7356 | 84.2539 | 0 | 7.2692 | FALSE | FALSE
2025-10-01 15:00 | 36.1 | 53.5 | 99675 | 100 | 3000 | 24.6913 | 71.3547 | 84.8027 | 0 | 7.2692 | FALSE | FALSE
2025-10-01 16:00 | 35.4 | 56.5 | 99675 | 100 | 3000 | 24.4374 | 73.2352 | 85.377 | 0 | 7.2692 | FALSE | FALSE
2025-10-01 17:00 | 34 | 63 | 99685 | 100 | 3000 | 23.9251 | 77.1544 | 86.5342 | 0 | 7.2692 | FALSE | FALSE
2025-10-01 18:00 | 32.6 | 69.5 | 99720 | 100 | 3000 | 23.4105 | 80.7439 | 86.9249 | 0 | 7.2692 | FALSE | FALSE
2025-10-01 19:00 | 31.8 | 73.5 | 99770 | 100 | 3000 | 23.1137 | 82.8648 | 87.1276 | 0 | 7.2692 | FALSE | FALSE
2025-10-01 20:00 | 31.3 | 77.5 | 99810 | 100 | 3000 | 22.9216 | 85.2191 | 88.6341 | 0 | 7.2692 | FALSE | FALSE
2025-10-01 21:00 | 30.55 | 80.5 | 99865 | 100 | 3000 | 22.6446 | 86.498 | 87.6944 | 0 | 7.2692 | FALSE | FALSE
2025-10-01 22:00 | 29.85 | 82 | 99890 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-01 23:00 | 29.25 | 85 | 99875 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-02 | 28.75 | 88 | 99870 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-02 01:00 | 28.4 | 89.5 | 99860 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-02 02:00 | 28 | 90.5 | 99860 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-02 03:00 | 27.65 | 92 | 99860 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-02 04:00 | 27.7 | 92 | 99880 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-02 05:00 | 27.45 | 92.5 | 99945 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-02 06:00 | 26.9 | 95.5 | 100015 | 100 | 3000 | 21.2659 | 92.1914 | 81.5221 | 0 | 7.2692 | FALSE | FALSE
2025-10-02 07:00 | 28.1 | 90.5 | 100085 | 100 | 3000 | 21.7252 | 90.4037 | 83.8489 | 0 | 7.2692 | FALSE | FALSE
2025-10-02 08:00 | 30.4 | 78 | 100155 | 100 | 3000 | 22.6002 | 84.5444 | 84.5686 | 0 | 7.2692 | FALSE | FALSE
2025-10-02 09:00 | 32.3 | 67 | 100210 | 100 | 3000 | 23.318 | 78.5233 | 82.9167 | 0 | 7.2692 | FALSE | FALSE
2025-10-02 10:00 | 34.1 | 56.5 | 100225 | 100 | 3000 | 23.9963 | 72.0666 | 79.6534 | 0 | 7.2692 | FALSE | FALSE
2025-10-02 11:00 | 35.7 | 47 | 100195 | 100 | 3000 | 24.602 | 65.5649 | 75.0387 | 0 | 7.2692 | FALSE | FALSE
2025-10-02 12:00 | 36.6 | 43.5 | 100135 | 100 | 3000 | 24.9313 | 63.2035 | 74.1557 | 0 | 7.2692 | FALSE | FALSE
2025-10-02 13:00 | 36.9 | 41 | 100070 | 100 | 3000 | 25.0511 | 61.2414 | 72.0001 | 0 | 7.2692 | FALSE | FALSE
2025-10-02 14:00 | 36.9 | 35.5 | 100025 | 100 | 3000 | 25.0927 | 56.497 | 64.6073 | 0 | 7.2692 | FALSE | FALSE
2025-10-02 15:00 | 36.3 | 39 | 99995 | 100 | 3000 | 24.8618 | 59.2161 | 67.0735 | 0 | 7.2692 | FALSE | FALSE
2025-10-02 16:00 | 35.1 | 46 | 99990 | 100 | 3000 | 24.4026 | 64.3722 | 71.3124 | 0 | 7.2692 | FALSE | FALSE
2025-10-02 17:00 | 33.5 | 53 | 100000 | 100 | 3000 | 23.8061 | 68.8868 | 72.97 | 0 | 7.2692 | FALSE | FALSE
2025-10-02 18:00 | 32.2 | 63.5 | 100060 | 100 | 3000 | 23.2981 | 75.8366 | 78.7069 | 0 | 7.2692 | FALSE | FALSE
2025-10-02 19:00 | 31.55 | 70.5 | 100150 | 100 | 3000 | 23.0385 | 80.3759 | 82.8969 | 0 | 7.2692 | FALSE | FALSE
2025-10-02 20:00 | 31 | 75 | 100205 | 100 | 3000 | 22.8256 | 83.0555 | 84.6972 | 0 | 7.2692 | FALSE | FALSE
2025-10-02 21:00 | 30.4 | 77.5 | 100245 | 100 | 3000 | 22.6021 | 84.1848 | 84.1055 | 0 | 7.2692 | FALSE | FALSE
2025-10-02 22:00 | 29.75 | 80 | 100260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-02 23:00 | 29.15 | 83 | 100250 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-03 | 28.65 | 85 | 100245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-03 01:00 | 28.3 | 86 | 100235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-03 02:00 | 28.1 | 86 | 100225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-03 03:00 | 27.9 | 87 | 100245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-03 04:00 | 27.5 | 89.5 | 100270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-03 05:00 | 26.8 | 93 | 100305 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-03 06:00 | 26.2 | 96.5 | 100385 | 100 | 3000 | 20.999 | 91.9588 | 78.5824 | 0 | 7.2692 | FALSE | FALSE
2025-10-03 07:00 | 27.25 | 92 | 100485 | 100 | 3000 | 21.4053 | 90.3433 | 80.6189 | 0 | 7.2692 | FALSE | FALSE
2025-10-03 08:00 | 29.9 | 77 | 100560 | 100 | 3000 | 22.4237 | 83.2818 | 81.1592 | 0 | 7.2692 | FALSE | FALSE
2025-10-03 09:00 | 32.4 | 62.5 | 100620 | 100 | 3000 | 23.3738 | 75.2117 | 78.6941 | 0 | 7.2692 | FALSE | FALSE
2025-10-03 10:00 | 34.7 | 48.5 | 100635 | 100 | 3000 | 24.2497 | 66.0885 | 72.8869 | 0 | 7.2692 | FALSE | FALSE
2025-10-03 11:00 | 36.8 | 35 | 100575 | 100 | 3000 | 25.0624 | 55.9781 | 63.7301 | 0 | 7.2692 | FALSE | FALSE
2025-10-03 12:00 | 38.2 | 28 | 100505 | 100 | 3000 | 25.5966 | 50.3159 | 58.6291 | 0 | 7.2692 | FALSE | FALSE
2025-10-03 13:00 | 38.35 | 31 | 100455 | 100 | 3000 | 25.6214 | 53.069 | 63.4371 | 0 | 7.2692 | FALSE | FALSE
2025-10-03 14:00 | 37.55 | 36 | 100415 | 100 | 3000 | 25.3097 | 57.1933 | 67.7181 | 0 | 7.2692 | FALSE | FALSE
2025-10-03 15:00 | 36.55 | 37 | 100405 | 100 | 3000 | 24.9619 | 57.5986 | 65.464 | 0 | 7.2692 | FALSE | FALSE
2025-10-03 16:00 | 35.05 | 45.5 | 100410 | 100 | 3000 | 24.3887 | 63.8971 | 70.6044 | 0 | 7.2692 | FALSE | FALSE
2025-10-03 17:00 | 33.15 | 60 | 100405 | 100 | 3000 | 23.6486 | 73.9802 | 79.3704 | 0 | 7.2692 | FALSE | FALSE
2025-10-03 18:00 | 31.8 | 69.5 | 100430 | 100 | 3000 | 23.1314 | 79.8656 | 83.154 | 0 | 7.2692 | FALSE | FALSE
2025-10-03 19:00 | 31.1 | 73 | 100480 | 100 | 3000 | 22.8692 | 81.6995 | 83.2671 | 0 | 7.2692 | FALSE | FALSE
2025-10-03 20:00 | 30.4 | 77 | 100520 | 100 | 3000 | 22.6042 | 83.8072 | 83.6791 | 0 | 7.2692 | FALSE | FALSE
2025-10-03 21:00 | 29.6 | 80.5 | 100545 | 100 | 3000 | 22.3036 | 85.3743 | 82.9026 | 0 | 7.2692 | FALSE | FALSE
2025-10-03 22:00 | 29 | 82 | 100535 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-03 23:00 | 28.45 | 85 | 100510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-04 | 27.95 | 88.5 | 100500 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-04 01:00 | 27.4 | 91.5 | 100490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-04 02:00 | 26.65 | 93.5 | 100485 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-04 03:00 | 25.95 | 95 | 100505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-04 04:00 | 25.7 | 95.5 | 100540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-04 05:00 | 25.65 | 95 | 100585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-04 06:00 | 25.65 | 94.5 | 100640 | 100 | 3000 | 20.7917 | 90.1083 | 74.1266 | 0 | 7.2692 | FALSE | FALSE
2025-10-04 07:00 | 27.2 | 88 | 100690 | 100 | 3000 | 21.3953 | 87.7317 | 77.0773 | 0 | 7.2692 | FALSE | FALSE
2025-10-04 08:00 | 30 | 76.5 | 100725 | 100 | 3000 | 22.4617 | 83.022 | 81.2214 | 0 | 7.2692 | FALSE | FALSE
2025-10-04 09:00 | 32.45 | 65 | 100740 | 100 | 3000 | 23.3802 | 77.1192 | 81.6262 | 0 | 7.2692 | FALSE | FALSE
2025-10-04 10:00 | 34.45 | 53 | 100705 | 100 | 3000 | 24.1372 | 69.5176 | 77.2142 | 0 | 7.2692 | FALSE | FALSE
2025-10-04 11:00 | 35.95 | 43.5 | 100630 | 100 | 3000 | 24.7112 | 62.7638 | 71.7194 | 0 | 7.2692 | FALSE | FALSE
2025-10-04 12:00 | 36.65 | 39 | 100555 | 100 | 3000 | 24.9816 | 59.3449 | 68.5228 | 0 | 7.2692 | FALSE | FALSE
2025-10-04 13:00 | 36.75 | 37.5 | 100495 | 100 | 3000 | 25.0267 | 58.1124 | 66.8792 | 0 | 7.2692 | FALSE | FALSE
2025-10-04 14:00 | 36.4 | 39.5 | 100435 | 100 | 3000 | 24.8927 | 59.6537 | 68.2168 | 0 | 7.2692 | FALSE | FALSE
2025-10-04 15:00 | 35.65 | 43 | 100400 | 100 | 3000 | 24.6116 | 62.192 | 69.8514 | 0 | 7.2692 | FALSE | FALSE
2025-10-04 16:00 | 34.7 | 45.5 | 100400 | 100 | 3000 | 24.2673 | 63.6903 | 69.2114 | 0 | 7.2692 | FALSE | FALSE
2025-10-04 17:00 | 33.35 | 53 | 100390 | 100 | 3000 | 23.7537 | 68.7465 | 72.4233 | 0 | 7.2692 | FALSE | FALSE
2025-10-04 18:00 | 31.95 | 64 | 100415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-04 19:00 | 31.1 | 71.5 | 100465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-04 20:00 | 30.5 | 75.5 | 100490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-04 21:00 | 29.85 | 79 | 100495 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-04 22:00 | 29.2 | 83.5 | 100480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-04 23:00 | 28.7 | 87 | 100460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 | 28.25 | 88.5 | 100440 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 01:00 | 27.65 | 90 | 100410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 02:00 | 27.05 | 91.5 | 100395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 03:00 | 26.8 | 91.5 | 100385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 04:00 | 26.85 | 91 | 100375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 05:00 | 26.7 | 91.5 | 100390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 06:00 | 26.85 | 89.5 | 100435 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 07:00 | 28.5 | 80.5 | 100505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 08:00 | 30.95 | 67.5 | 100560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 09:00 | 32.7 | 60 | 100580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 10:00 | 33.95 | 55.5 | 100570 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 11:00 | 35.1 | 49 | 100525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 12:00 | 35.8 | 43 | 100460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 13:00 | 36 | 38 | 100395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 14:00 | 35.6 | 38 | 100330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 15:00 | 34.65 | 44.5 | 100295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 16:00 | 33.45 | 53.5 | 100280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 17:00 | 32.25 | 60 | 100275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 18:00 | 31.35 | 63.5 | 100295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 19:00 | 30.7 | 67 | 100345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 20:00 | 30 | 71 | 100390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 21:00 | 29.25 | 75 | 100390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 22:00 | 28.5 | 79 | 100380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-05 23:00 | 27.7 | 82.5 | 100375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-06 | 26.9 | 85.5 | 100380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-06 01:00 | 26.15 | 88.5 | 100385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-06 02:00 | 25.5 | 91 | 100380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-06 03:00 | 25.1 | 91.5 | 100370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-06 04:00 | 25.05 | 91.5 | 100370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-06 05:00 | 24.85 | 93 | 100400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-06 06:00 | 24.8 | 93 | 100450 | 100 | 3000 | 20.4635 | 88.3692 | 68.5415 | 0 | 7.2692 | FALSE | FALSE
2025-10-06 07:00 | 26.45 | 83.5 | 100505 | 100 | 3000 | 21.1188 | 84.19 | 69.5608 | 0 | 7.2692 | FALSE | FALSE
2025-10-06 08:00 | 29.75 | 65.5 | 100565 | 100 | 3000 | 22.4055 | 75.2065 | 69.5542 | 0 | 7.2692 | FALSE | FALSE
2025-10-06 09:00 | 33 | 52.5 | 100600 | 100 | 3000 | 23.6326 | 68.1047 | 70.4323 | 0 | 7.2692 | FALSE | FALSE
2025-10-06 10:00 | 35.65 | 43 | 100565 | 100 | 3000 | 24.6117 | 62.1778 | 69.8938 | 0 | 7.2692 | FALSE | FALSE
2025-10-06 11:00 | 38.1 | 29.5 | 100480 | 100 | 3000 | 25.5498 | 51.6331 | 60.4608 | 0 | 7.2692 | FALSE | FALSE
2025-10-06 12:00 | 39.7 | 20.5 | 100380 | 100 | 3000 | 26.1758 | 43.7412 | 51.7485 | 0 | 7.2692 | FALSE | FALSE
2025-10-06 13:00 | 39.1 | 29 | 100305 | 100 | 3000 | 25.8913 | 51.5219 | 62.9263 | 0 | 7.2692 | FALSE | FALSE
2025-10-06 14:00 | 37 | 42.5 | 100275 | 100 | 3000 | 25.0735 | 62.5804 | 74.449 | 0 | 7.2692 | FALSE | FALSE
2025-10-06 15:00 | 35.5 | 49 | 100280 | 100 | 3000 | 24.5209 | 67.0767 | 76.7314 | 0 | 7.2692 | FALSE | FALSE
2025-10-06 16:00 | 34.35 | 57 | 100320 | 100 | 3000 | 24.0794 | 72.664 | 81.3802 | 0 | 7.2692 | FALSE | FALSE
2025-10-06 17:00 | 32.85 | 65 | 100360 | 100 | 3000 | 23.5196 | 77.5302 | 83.442 | 0 | 7.2692 | FALSE | FALSE
2025-10-06 18:00 | 31.8 | 71 | 100400 | 100 | 3000 | 23.1251 | 80.9699 | 84.6944 | 0 | 7.2692 | FALSE | FALSE
2025-10-06 19:00 | 31.25 | 75 | 100455 | 100 | 3000 | 22.9147 | 83.2982 | 86.014 | 0 | 7.2692 | FALSE | FALSE
2025-10-06 20:00 | 30.75 | 77 | 100500 | 100 | 3000 | 22.7294 | 84.1845 | 85.4577 | 0 | 7.2692 | FALSE | FALSE
2025-10-06 21:00 | 30.2 | 78.5 | 100510 | 100 | 3000 | 22.5271 | 84.6437 | 84.0951 | 0 | 7.2692 | FALSE | FALSE
2025-10-06 22:00 | 29.7 | 79.5 | 100490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-06 23:00 | 29.05 | 82 | 100470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-07 | 28.25 | 86 | 100460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-07 01:00 | 27.5 | 90 | 100440 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-07 02:00 | 26.75 | 93.5 | 100420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-07 03:00 | 26.1 | 95 | 100430 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-07 04:00 | 25.45 | 94.5 | 100450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-07 05:00 | 24.8 | 94 | 100475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-07 06:00 | 24.75 | 90.5 | 100520 | 100 | 3000 | 20.4474 | 86.8465 | 66.4462 | 0 | 7.2692 | FALSE | FALSE
2025-10-07 07:00 | 26.7 | 76.5 | 100580 | 100 | 3000 | 21.2284 | 80.0363 | 65.102 | 0 | 7.2692 | FALSE | FALSE
2025-10-07 08:00 | 30.2 | 57 | 100655 | 100 | 3000 | 22.5994 | 69.6001 | 63.3473 | 0 | 7.2692 | FALSE | FALSE
2025-10-07 09:00 | 33.75 | 38.5 | 100695 | 100 | 3000 | 23.9703 | 57.6465 | 57.3754 | 0 | 7.2692 | FALSE | FALSE
2025-10-07 10:00 | 36.6 | 25.5 | 100670 | 100 | 3000 | 25.0621 | 47.7607 | 50.2849 | 0 | 7.2692 | FALSE | FALSE
2025-10-07 11:00 | 38.3 | 19.5 | 100610 | 100 | 3000 | 25.7037 | 42.6801 | 46.5443 | 0 | 7.2692 | FALSE | FALSE
2025-10-07 12:00 | 39.3 | 16 | 100535 | 100 | 3000 | 26.0822 | 39.5077 | 44.4342 | 0 | 7.2692 | FALSE | FALSE
2025-10-07 13:00 | 39.15 | 20 | 100470 | 100 | 3000 | 25.9929 | 43.2093 | 49.5143 | 0 | 7.2692 | FALSE | FALSE
2025-10-07 14:00 | 37.85 | 28 | 100420 | 100 | 3000 | 25.477 | 50.2267 | 57.5019 | 0 | 7.2692 | FALSE | FALSE
2025-10-07 15:00 | 36.35 | 35.5 | 100405 | 100 | 3000 | 24.9039 | 56.2352 | 62.7689 | 0 | 7.2692 | FALSE | FALSE
2025-10-07 16:00 | 34.75 | 44.5 | 100415 | 100 | 3000 | 24.2906 | 62.9106 | 68.2011 | 0 | 7.2692 | FALSE | FALSE
2025-10-07 17:00 | 33 | 56 | 100435 | 100 | 3000 | 23.6156 | 70.7949 | 74.2788 | 0 | 7.2692 | FALSE | FALSE
2025-10-07 18:00 | 31.8 | 64.5 | 100470 | 100 | 3000 | 23.1524 | 76.1881 | 77.9832 | 0 | 7.2692 | FALSE | FALSE
2025-10-07 19:00 | 31.1 | 67 | 100515 | 100 | 3000 | 22.8921 | 77.385 | 77.2646 | 0 | 7.2692 | FALSE | FALSE
2025-10-07 20:00 | 30.25 | 70.5 | 100555 | 100 | 3000 | 22.5723 | 79.1005 | 76.6767 | 0 | 7.2692 | FALSE | FALSE
2025-10-07 21:00 | 29.2 | 76 | 100565 | 100 | 3000 | 22.1709 | 81.904 | 76.7429 | 0 | 7.2692 | FALSE | FALSE
2025-10-07 22:00 | 28.25 | 80 | 100560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-07 23:00 | 27.35 | 83 | 100550 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-08 | 26.55 | 85.5 | 100540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-08 01:00 | 25.9 | 87 | 100515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-08 02:00 | 25.05 | 89.5 | 100485 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-08 03:00 | 24.4 | 91.5 | 100495 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-08 04:00 | 24.35 | 90.5 | 100510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-08 05:00 | 24.25 | 89 | 100530 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-08 06:00 | 24.65 | 84.5 | 100585 | 100 | 3000 | 20.4162 | 83.2342 | 61.5214 | 0 | 7.2692 | FALSE | FALSE
2025-10-08 07:00 | 26.6 | 73.5 | 100675 | 100 | 3000 | 21.1957 | 78.0747 | 62.1939 | 0 | 7.2692 | FALSE | FALSE
2025-10-08 08:00 | 29.45 | 59 | 100760 | 100 | 3000 | 22.314 | 70.5147 | 62.1129 | 0 | 7.2692 | FALSE | FALSE
2025-10-08 09:00 | 32.2 | 44.5 | 100780 | 100 | 3000 | 23.3814 | 61.6018 | 58.4843 | 0 | 7.2692 | FALSE | FALSE
2025-10-08 10:00 | 34.45 | 35.5 | 100750 | 100 | 3000 | 24.237 | 55.5085 | 56.2546 | 0 | 7.2692 | FALSE | FALSE
2025-10-08 11:00 | 36.45 | 29 | 100670 | 100 | 3000 | 24.9845 | 50.7186 | 54.5401 | 0 | 7.2692 | FALSE | FALSE
2025-10-08 12:00 | 37.8 | 24 | 100565 | 100 | 3000 | 25.4926 | 46.6527 | 51.6828 | 0 | 7.2692 | FALSE | FALSE
2025-10-08 13:00 | 37.65 | 28.5 | 100490 | 100 | 3000 | 25.4043 | 50.6098 | 57.5985 | 0 | 7.2692 | FALSE | FALSE
2025-10-08 14:00 | 36.75 | 34 | 100435 | 100 | 3000 | 25.0526 | 55.1098 | 62.1743 | 0 | 7.2692 | FALSE | FALSE
2025-10-08 15:00 | 35.85 | 36.5 | 100430 | 100 | 3000 | 24.7238 | 56.871 | 62.3119 | 0 | 7.2692 | FALSE | FALSE
2025-10-08 16:00 | 34.35 | 46 | 100470 | 100 | 3000 | 24.1422 | 63.8815 | 68.4403 | 0 | 7.2692 | FALSE | FALSE
2025-10-08 17:00 | 32.5 | 57.5 | 100490 | 100 | 3000 | 23.4317 | 71.5512 | 73.7402 | 0 | 7.2692 | FALSE | FALSE
2025-10-08 18:00 | 31.1 | 67 | 100510 | 100 | 3000 | 22.8921 | 77.3855 | 77.2636 | 0 | 7.2692 | FALSE | FALSE
2025-10-08 19:00 | 30.2 | 74 | 100575 | 100 | 3000 | 22.5424 | 81.4976 | 79.8046 | 0 | 7.2692 | FALSE | FALSE
2025-10-08 20:00 | 29.4 | 78 | 100650 | 100 | 3000 | 22.2384 | 83.4493 | 79.5931 | 0 | 7.2692 | FALSE | FALSE
2025-10-08 21:00 | 28.75 | 79.5 | 100680 | 100 | 3000 | 21.995 | 83.803 | 77.6917 | 0 | 7.2692 | FALSE | FALSE
2025-10-08 22:00 | 28.3 | 78 | 100675 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-08 23:00 | 27.85 | 76.5 | 100670 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-09 | 27.15 | 80 | 100680 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-09 01:00 | 26.35 | 85 | 100680 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-09 02:00 | 25.7 | 86 | 100655 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-09 03:00 | 25.05 | 88 | 100665 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-09 04:00 | 24.65 | 89.5 | 100705 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-09 05:00 | 24.5 | 88.5 | 100735 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-09 06:00 | 24.65 | 83.5 | 100825 | 100 | 3000 | 20.4176 | 82.6228 | 60.8107 | 0 | 7.2692 | FALSE | FALSE
2025-10-09 07:00 | 26.1 | 68.5 | 100955 | 100 | 3000 | 21.0106 | 74.6121 | 55.9341 | 0 | 7.2692 | FALSE | FALSE
2025-10-09 08:00 | 28.6 | 55 | 101020 | 100 | 3000 | 22.0043 | 67.3209 | 54.9244 | 0 | 7.2692 | FALSE | FALSE
2025-10-09 09:00 | 31.3 | 48.5 | 101030 | 100 | 3000 | 23.0357 | 64.1079 | 59.3267 | 0 | 7.2692 | FALSE | FALSE
2025-10-09 10:00 | 33.85 | 40 | 101015 | 100 | 3000 | 23.9983 | 58.835 | 59.572 | 0 | 7.2692 | FALSE | FALSE
2025-10-09 11:00 | 35.8 | 31.5 | 100960 | 100 | 3000 | 24.7395 | 52.6319 | 55.8185 | 0 | 7.2692 | FALSE | FALSE
2025-10-09 12:00 | 37.15 | 26 | 100880 | 100 | 3000 | 25.2509 | 48.271 | 52.667 | 0 | 7.2692 | FALSE | FALSE
2025-10-09 13:00 | 37.95 | 22.5 | 100800 | 100 | 3000 | 25.5568 | 45.3216 | 50.0218 | 0 | 7.2692 | FALSE | FALSE
2025-10-09 14:00 | 37.9 | 24 | 100740 | 100 | 3000 | 25.5271 | 46.6549 | 52.0226 | 0 | 7.2692 | FALSE | FALSE
2025-10-09 15:00 | 36.55 | 32.5 | 100715 | 100 | 3000 | 24.9944 | 53.7292 | 59.5582 | 0 | 7.2692 | FALSE | FALSE
2025-10-09 16:00 | 34.9 | 38.5 | 100730 | 100 | 3000 | 24.379 | 58.098 | 61.5062 | 0 | 7.2692 | FALSE | FALSE
2025-10-09 17:00 | 33.35 | 44.5 | 100750 | 100 | 3000 | 23.7965 | 62.1414 | 62.8545 | 0 | 7.2692 | FALSE | FALSE
2025-10-09 18:00 | 31.9 | 52.5 | 100765 | 100 | 3000 | 23.2386 | 67.3898 | 65.884 | 0 | 7.2692 | FALSE | FALSE
2025-10-09 19:00 | 30.9 | 57.5 | 100795 | 100 | 3000 | 22.8553 | 70.388 | 66.8507 | 0 | 7.2692 | FALSE | FALSE
2025-10-09 20:00 | 29.9 | 62 | 100810 | 100 | 3000 | 22.4721 | 72.873 | 66.9298 | 0 | 7.2692 | FALSE | FALSE
2025-10-09 21:00 | 29 | 64 | 100795 | 100 | 3000 | 22.1311 | 73.6133 | 64.8271 | 0 | 7.2692 | FALSE | FALSE
2025-10-09 22:00 | 28.25 | 64 | 100790 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-09 23:00 | 27.55 | 67 | 100805 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-10 | 26.9 | 72 | 100800 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-10 01:00 | 26.45 | 74 | 100770 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-10 02:00 | 26.1 | 75 | 100740 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-10 03:00 | 25.5 | 78.5 | 100730 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-10 04:00 | 25.05 | 81.5 | 100735 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-10 05:00 | 24.65 | 85 | 100775 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-10 06:00 | 24.55 | 87 | 100845 | 100 | 3000 | 20.3734 | 84.5864 | 62.9091 | 0 | 7.2692 | FALSE | FALSE
2025-10-10 07:00 | 26.05 | 79 | 100905 | 100 | 3000 | 20.9728 | 81.0315 | 64.0763 | 0 | 7.2692 | FALSE | FALSE
2025-10-10 08:00 | 29.15 | 61.5 | 100945 | 100 | 3000 | 22.1944 | 72.0098 | 63.1997 | 0 | 7.2692 | FALSE | FALSE
2025-10-10 09:00 | 32.45 | 44 | 100965 | 100 | 3000 | 23.4746 | 61.3201 | 58.9209 | 0 | 7.2692 | FALSE | FALSE
2025-10-10 10:00 | 34.75 | 33 | 100940 | 100 | 3000 | 24.3583 | 53.5712 | 54.2513 | 0 | 7.2692 | FALSE | FALSE
2025-10-10 11:00 | 36.2 | 26.5 | 100875 | 100 | 3000 | 24.914 | 48.5289 | 50.4894 | 0 | 7.2692 | FALSE | FALSE
2025-10-10 12:00 | 37.2 | 22 | 100800 | 100 | 3000 | 25.2988 | 44.8018 | 47.2177 | 0 | 7.2692 | FALSE | FALSE
2025-10-10 13:00 | 37.7 | 19.5 | 100735 | 100 | 3000 | 25.494 | 42.6432 | 45.0026 | 0 | 7.2692 | FALSE | FALSE
2025-10-10 14:00 | 37.55 | 19.5 | 100680 | 100 | 3000 | 25.4413 | 42.6424 | 44.594 | 0 | 7.2692 | FALSE | FALSE
2025-10-10 15:00 | 36.6 | 23.5 | 100635 | 100 | 3000 | 25.0764 | 46.0521 | 47.5605 | 0 | 7.2692 | FALSE | FALSE
2025-10-10 16:00 | 34.9 | 31.5 | 100630 | 100 | 3000 | 24.4207 | 52.421 | 52.8045 | 0 | 7.2692 | FALSE | FALSE
2025-10-10 17:00 | 32.95 | 42.5 | 100625 | 100 | 3000 | 23.6625 | 60.4298 | 59.0466 | 0 | 7.2692 | FALSE | FALSE
2025-10-10 18:00 | 31.65 | 53 | 100615 | 100 | 3000 | 23.1458 | 67.6202 | 65.3457 | 0 | 7.2692 | FALSE | FALSE
2025-10-10 19:00 | 31 | 59 | 100645 | 100 | 3000 | 22.8862 | 71.5458 | 68.7684 | 0 | 7.2692 | FALSE | FALSE
2025-10-10 20:00 | 30.4 | 61.5 | 100675 | 100 | 3000 | 22.6579 | 72.893 | 68.6288 | 0 | 7.2692 | FALSE | FALSE
2025-10-10 21:00 | 29.75 | 63 | 100675 | 100 | 3000 | 22.4134 | 73.4712 | 67.1964 | 0 | 7.2692 | FALSE | FALSE
2025-10-10 22:00 | 29.25 | 65 | 100660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-10 23:00 | 28.55 | 68.5 | 100630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-11 | 27.45 | 74 | 100605 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-11 01:00 | 26.45 | 79.5 | 100595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-11 02:00 | 25.75 | 83 | 100575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-11 03:00 | 25.25 | 84.5 | 100580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-11 04:00 | 25.1 | 84 | 100615 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-11 05:00 | 25 | 83.5 | 100655 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-11 06:00 | 25.05 | 82.5 | 100710 | 100 | 3000 | 20.5766 | 82.3625 | 61.9705 | 0 | 7.2692 | FALSE | FALSE
2025-10-11 07:00 | 26.6 | 75.5 | 100765 | 100 | 3000 | 21.1919 | 79.314 | 63.8411 | 0 | 7.2692 | FALSE | FALSE
2025-10-11 08:00 | 29.15 | 65 | 100805 | 100 | 3000 | 22.1843 | 74.3941 | 66.4205 | 0 | 7.2692 | FALSE | FALSE
2025-10-11 09:00 | 31.2 | 54.5 | 100850 | 100 | 3000 | 22.9761 | 68.4164 | 65.0797 | 0 | 7.2692 | FALSE | FALSE
2025-10-11 10:00 | 32.95 | 41.5 | 100855 | 100 | 3000 | 23.6672 | 59.6448 | 57.9719 | 0 | 7.2692 | FALSE | FALSE
2025-10-11 11:00 | 34.65 | 29.5 | 100785 | 100 | 3000 | 24.3427 | 50.7346 | 49.5657 | 0 | 7.2692 | FALSE | FALSE
2025-10-11 12:00 | 35.8 | 24 | 100705 | 100 | 3000 | 24.7886 | 46.3894 | 45.9727 | 0 | 7.2692 | FALSE | FALSE
2025-10-11 13:00 | 35.75 | 29 | 100635 | 100 | 3000 | 24.7382 | 50.5604 | 52.3312 | 0 | 7.2692 | FALSE | FALSE
2025-10-11 14:00 | 34.4 | 42 | 100590 | 100 | 3000 | 24.1825 | 60.7035 | 63.883 | 0 | 7.2692 | FALSE | FALSE
2025-10-11 15:00 | 33.65 | 46.5 | 100570 | 100 | 3000 | 23.893 | 63.8695 | 66.2779 | 0 | 7.2692 | FALSE | FALSE
2025-10-11 16:00 | 33.05 | 49.5 | 100565 | 100 | 3000 | 23.6648 | 65.8436 | 67.2825 | 0 | 7.2692 | FALSE | FALSE
2025-10-11 17:00 | 31.65 | 56.5 | 100565 | 100 | 3000 | 23.1316 | 70.1906 | 68.9973 | 0 | 7.2692 | FALSE | FALSE
2025-10-11 18:00 | 30.85 | 59.5 | 100575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-11 19:00 | 30.45 | 62 | 100615 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-11 20:00 | 29.95 | 61.5 | 100660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-11 21:00 | 29.35 | 61 | 100695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-11 22:00 | 28.8 | 63 | 100690 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-11 23:00 | 28.25 | 65 | 100660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 | 27.5 | 67.5 | 100645 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 01:00 | 26.8 | 70.5 | 100630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 02:00 | 26.3 | 73.5 | 100615 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 03:00 | 25.95 | 75 | 100630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 04:00 | 25.85 | 75 | 100660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 05:00 | 25.75 | 75 | 100695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 06:00 | 25.9 | 73 | 100755 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 07:00 | 27.55 | 63 | 100825 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 08:00 | 30.15 | 45 | 100865 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 09:00 | 32.6 | 32 | 100890 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 10:00 | 34.7 | 28.5 | 100880 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 11:00 | 36.05 | 27 | 100795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 12:00 | 36.9 | 24.5 | 100710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 13:00 | 37.3 | 23 | 100645 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 14:00 | 37.7 | 22.5 | 100570 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 15:00 | 36.3 | 30.5 | 100570 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 16:00 | 34.1 | 38 | 100615 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 17:00 | 33.6 | 36.5 | 100625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 18:00 | 33.45 | 36 | 100655 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 19:00 | 32.75 | 41 | 100715 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 20:00 | 31.75 | 51 | 100765 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 21:00 | 31.35 | 53 | 100800 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 22:00 | 31.1 | 54 | 100805 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-12 23:00 | 30.9 | 54 | 100780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-13 | 30.8 | 46 | 100760 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-13 01:00 | 30.55 | 41.5 | 100730 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-13 02:00 | 30 | 42 | 100715 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-13 03:00 | 29.4 | 48 | 100745 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-13 04:00 | 29.2 | 53 | 100800 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-13 05:00 | 29.25 | 49.5 | 100850 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-13 06:00 | 29.45 | 44.5 | 100895 | 100 | 3000 | 22.357 | 60.5641 | 48.3321 | 0 | 7.2692 | FALSE | FALSE
2025-10-13 07:00 | 30.3 | 41.5 | 100945 | 100 | 3000 | 22.6883 | 58.7241 | 48.4459 | 0 | 7.2692 | FALSE | FALSE
2025-10-13 08:00 | 32 | 36.5 | 100990 | 100 | 3000 | 23.3418 | 55.5537 | 49.1158 | 0 | 7.2692 | FALSE | FALSE
2025-10-13 09:00 | 33.45 | 33 | 101030 | 100 | 3000 | 23.8898 | 53.2349 | 49.9975 | 0 | 7.2692 | FALSE | FALSE
2025-10-13 10:00 | 34.35 | 32 | 101030 | 100 | 3000 | 24.2207 | 52.6564 | 51.7357 | 0 | 7.2692 | FALSE | FALSE
2025-10-13 11:00 | 35.25 | 29.5 | 100970 | 100 | 3000 | 24.5574 | 50.8391 | 51.4906 | 0 | 7.2692 | FALSE | FALSE
2025-10-13 12:00 | 36.05 | 27 | 100890 | 100 | 3000 | 24.8575 | 48.9233 | 50.7031 | 0 | 7.2692 | FALSE | FALSE
2025-10-13 13:00 | 36.35 | 26 | 100820 | 100 | 3000 | 24.9704 | 48.1347 | 50.2564 | 0 | 7.2692 | FALSE | FALSE
2025-10-13 14:00 | 36.35 | 26 | 100765 | 100 | 3000 | 24.9704 | 48.1392 | 50.2418 | 0 | 7.2692 | FALSE | FALSE
2025-10-13 15:00 | 35.8 | 27 | 100725 | 100 | 3000 | 24.769 | 48.8935 | 49.9042 | 0 | 7.2692 | FALSE | FALSE
2025-10-13 16:00 | 34.9 | 29.5 | 100715 | 100 | 3000 | 24.4325 | 50.7888 | 50.3292 | 0 | 7.2692 | FALSE | FALSE
2025-10-13 17:00 | 33.65 | 38 | 100735 | 100 | 3000 | 23.937 | 57.2154 | 56.4453 | 0 | 7.2692 | FALSE | FALSE
2025-10-13 18:00 | 32.25 | 48.5 | 100770 | 100 | 3000 | 23.3823 | 64.6158 | 63.0149 | 0 | 7.2692 | FALSE | FALSE
2025-10-13 19:00 | 31.4 | 54 | 100805 | 100 | 3000 | 23.051 | 68.1807 | 65.3896 | 0 | 7.2692 | FALSE | FALSE
2025-10-13 20:00 | 30.6 | 58.5 | 100835 | 100 | 3000 | 22.7418 | 70.8968 | 66.5696 | 0 | 7.2692 | FALSE | FALSE
2025-10-13 21:00 | 30.05 | 59 | 100845 | 100 | 3000 | 22.5373 | 70.8852 | 64.6943 | 0 | 7.2692 | FALSE | FALSE
2025-10-13 22:00 | 29.85 | 58 | 100825 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-13 23:00 | 29.5 | 60.5 | 100795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-14 | 28.75 | 63 | 100760 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-14 01:00 | 27.95 | 64 | 100735 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-14 02:00 | 27.4 | 64 | 100730 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-14 03:00 | 26.6 | 63 | 100735 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-14 04:00 | 25.95 | 62.5 | 100735 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-14 05:00 | 25.75 | 63.5 | 100760 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-14 06:00 | 25.55 | 64.5 | 100805 | 100 | 3000 | 20.801 | 71.8824 | 50.3783 | 0 | 7.2692 | FALSE | FALSE
2025-10-14 07:00 | 27 | 60 | 100845 | 100 | 3000 | 21.3773 | 69.8076 | 52.7564 | 0 | 7.2692 | FALSE | FALSE
2025-10-14 08:00 | 29.8 | 54 | 100890 | 100 | 3000 | 22.4602 | 67.2601 | 58.8199 | 0 | 7.2692 | FALSE | FALSE
2025-10-14 09:00 | 32.1 | 51 | 100920 | 100 | 3000 | 23.3173 | 66.3825 | 65.1384 | 0 | 7.2692 | FALSE | FALSE
2025-10-14 10:00 | 33.95 | 43.5 | 100900 | 100 | 3000 | 24.0153 | 61.6456 | 64.0299 | 0 | 7.2692 | FALSE | FALSE
2025-10-14 11:00 | 35.35 | 34 | 100830 | 100 | 3000 | 24.565 | 54.5783 | 57.4867 | 0 | 7.2692 | FALSE | FALSE
2025-10-14 12:00 | 35.4 | 33 | 100770 | 100 | 3000 | 24.5889 | 53.7751 | 56.3715 | 0 | 7.2692 | FALSE | FALSE
2025-10-14 13:00 | 34.75 | 38 | 100720 | 100 | 3000 | 24.3291 | 57.6321 | 60.3496 | 0 | 7.2692 | FALSE | FALSE
2025-10-14 14:00 | 34.45 | 40.5 | 100660 | 100 | 3000 | 24.2087 | 59.5207 | 62.2826 | 0 | 7.2692 | FALSE | FALSE
2025-10-14 15:00 | 34.3 | 39 | 100610 | 100 | 3000 | 24.1639 | 58.2625 | 59.9185 | 0 | 7.2692 | FALSE | FALSE
2025-10-14 16:00 | 33.8 | 39.5 | 100595 | 100 | 3000 | 23.983 | 58.4588 | 58.7042 | 0 | 7.2692 | FALSE | FALSE
2025-10-14 17:00 | 32.7 | 46 | 100595 | 100 | 3000 | 23.5559 | 62.9816 | 62.0013 | 0 | 7.2692 | FALSE | FALSE
2025-10-14 18:00 | 31.75 | 53.5 | 100600 | 100 | 3000 | 23.18 | 68.0501 | 66.2831 | 0 | 7.2692 | FALSE | FALSE
2025-10-14 19:00 | 31.1 | 59.5 | 100615 | 100 | 3000 | 22.9206 | 71.9792 | 69.7068 | 0 | 7.2692 | FALSE | FALSE
2025-10-14 20:00 | 30.55 | 63.5 | 100630 | 100 | 3000 | 22.7058 | 74.4213 | 71.2601 | 0 | 7.2692 | FALSE | FALSE
2025-10-14 21:00 | 29.85 | 65 | 100645 | 100 | 3000 | 22.444 | 74.9302 | 69.5473 | 0 | 7.2692 | FALSE | FALSE
2025-10-14 22:00 | 29.3 | 66 | 100640 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-14 23:00 | 28.85 | 69.5 | 100610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-15 | 28.2 | 74 | 100580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-15 01:00 | 27.65 | 77.5 | 100550 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-15 02:00 | 27.2 | 80.5 | 100520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-15 03:00 | 26.75 | 80.5 | 100520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-15 04:00 | 26.5 | 79 | 100540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-15 05:00 | 26.3 | 79 | 100565 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-15 06:00 | 26.05 | 79 | 100610 | 100 | 3000 | 20.9727 | 81.0618 | 64.0344 | 0 | 7.2692 | FALSE | FALSE
2025-10-15 07:00 | 27.3 | 74 | 100665 | 100 | 3000 | 21.4634 | 78.9237 | 65.863 | 0 | 7.2692 | FALSE | FALSE
2025-10-15 08:00 | 29.75 | 66.5 | 100710 | 100 | 3000 | 22.4024 | 75.8822 | 70.5311 | 0 | 7.2692 | FALSE | FALSE
2025-10-15 09:00 | 31.6 | 63.5 | 100745 | 100 | 3000 | 23.0854 | 75.258 | 76.079 | 0 | 7.2692 | FALSE | FALSE
2025-10-15 10:00 | 33.15 | 58.5 | 100720 | 100 | 3000 | 23.6564 | 72.8004 | 77.7802 | 0 | 7.2692 | FALSE | FALSE
2025-10-15 11:00 | 34.8 | 48.5 | 100640 | 100 | 3000 | 24.2843 | 66.1542 | 73.3002 | 0 | 7.2692 | FALSE | FALSE
2025-10-15 12:00 | 35.65 | 43 | 100575 | 100 | 3000 | 24.6117 | 62.1769 | 69.8964 | 0 | 7.2692 | FALSE | FALSE
2025-10-15 13:00 | 35.3 | 45 | 100520 | 100 | 3000 | 24.4783 | 63.6288 | 71.01 | 0 | 7.2692 | FALSE | FALSE
2025-10-15 14:00 | 34.85 | 45 | 100470 | 100 | 3000 | 24.3225 | 63.3674 | 69.2154 | 0 | 7.2692 | FALSE | FALSE
2025-10-15 15:00 | 34.25 | 45 | 100455 | 100 | 3000 | 24.1128 | 63.0298 | 66.8543 | 0 | 7.2692 | FALSE | FALSE
2025-10-15 16:00 | 32.9 | 53 | 100460 | 100 | 3000 | 23.5946 | 68.4322 | 70.5343 | 0 | 7.2692 | FALSE | FALSE
2025-10-15 17:00 | 31.45 | 65 | 100455 | 100 | 3000 | 23.0254 | 76.2509 | 76.8641 | 0 | 7.2692 | FALSE | FALSE
2025-10-15 18:00 | 30.55 | 72 | 100470 | 100 | 3000 | 22.6757 | 80.4435 | 79.5676 | 0 | 7.2692 | FALSE | FALSE
2025-10-15 19:00 | 30.05 | 75 | 100525 | 100 | 3000 | 22.4846 | 82.0507 | 80.0074 | 0 | 7.2692 | FALSE | FALSE
2025-10-15 20:00 | 29.45 | 79.5 | 100575 | 100 | 3000 | 22.2521 | 84.5293 | 81.2155 | 0 | 7.2692 | FALSE | FALSE
2025-10-15 21:00 | 28.7 | 84 | 100605 | 100 | 3000 | 21.9642 | 86.7535 | 81.435 | 0 | 7.2692 | FALSE | FALSE
2025-10-15 22:00 | 28.05 | 87 | 100610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-15 23:00 | 27.4 | 89.5 | 100595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-16 | 26.55 | 93 | 100580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-16 01:00 | 25.8 | 96 | 100555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-16 02:00 | 25.2 | 97.5 | 100535 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-16 03:00 | 24.9 | 97.5 | 100545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-16 04:00 | 25.15 | 93.5 | 100580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-16 05:00 | 25.5 | 83 | 100640 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-16 06:00 | 25.7 | 72.5 | 100715 | 100 | 3000 | 20.8472 | 76.8301 | 57.2978 | 0 | 7.2692 | FALSE | FALSE
2025-10-16 07:00 | 26.9 | 64 | 100775 | 100 | 3000 | 21.3304 | 72.2933 | 55.6856 | 0 | 7.2692 | FALSE | FALSE
2025-10-16 08:00 | 29 | 55.5 | 100845 | 100 | 3000 | 22.1548 | 67.8731 | 56.9754 | 0 | 7.2692 | FALSE | FALSE
2025-10-16 09:00 | 30.9 | 48.5 | 100900 | 100 | 3000 | 22.8881 | 63.9297 | 57.7397 | 0 | 7.2692 | FALSE | FALSE
2025-10-16 10:00 | 32.65 | 41.5 | 100885 | 100 | 3000 | 23.5585 | 59.5226 | 56.8802 | 0 | 7.2692 | FALSE | FALSE
2025-10-16 11:00 | 34.1 | 36 | 100805 | 100 | 3000 | 24.1091 | 55.788 | 55.6667 | 0 | 7.2692 | FALSE | FALSE
2025-10-16 12:00 | 35.1 | 32.5 | 100720 | 100 | 3000 | 24.4858 | 53.2811 | 54.7314 | 0 | 7.2692 | FALSE | FALSE
2025-10-16 13:00 | 35.8 | 30 | 100655 | 100 | 3000 | 24.7493 | 51.4047 | 53.7932 | 0 | 7.2692 | FALSE | FALSE
2025-10-16 14:00 | 36 | 29 | 100595 | 100 | 3000 | 24.8265 | 50.6191 | 53.1043 | 0 | 7.2692 | FALSE | FALSE
2025-10-16 15:00 | 34.75 | 37.5 | 100575 | 100 | 3000 | 24.332 | 57.2404 | 59.7007 | 0 | 7.2692 | FALSE | FALSE
2025-10-16 16:00 | 33 | 48.5 | 100590 | 100 | 3000 | 23.6518 | 65.0465 | 65.9669 | 0 | 7.2692 | FALSE | FALSE
2025-10-16 17:00 | 31.95 | 53.5 | 100615 | 100 | 3000 | 23.2524 | 68.1741 | 67.121 | 0 | 7.2692 | FALSE | FALSE
2025-10-16 18:00 | 31.35 | 57.5 | 100660 | 100 | 3000 | 23.0191 | 70.7051 | 68.761 | 0 | 7.2692 | FALSE | FALSE
2025-10-16 19:00 | 30.9 | 60 | 100725 | 100 | 3000 | 22.8461 | 72.1839 | 69.3552 | 0 | 7.2692 | FALSE | FALSE
2025-10-16 20:00 | 30.15 | 63 | 100785 | 100 | 3000 | 22.5611 | 73.752 | 69.0013 | 0 | 7.2692 | FALSE | FALSE
2025-10-16 21:00 | 29.3 | 65 | 100815 | 100 | 3000 | 22.2403 | 74.5022 | 67.0957 | 0 | 7.2692 | FALSE | FALSE
2025-10-16 22:00 | 28.85 | 65 | 100815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-16 23:00 | 28.45 | 66 | 100800 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-17 | 27.8 | 68 | 100795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-17 01:00 | 27.2 | 68 | 100785 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-17 02:00 | 26.65 | 67 | 100780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-17 03:00 | 26.05 | 69 | 100805 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-17 04:00 | 25.85 | 71 | 100835 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-17 05:00 | 25.85 | 69.5 | 100880 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-17 06:00 | 25.95 | 60.5 | 100950 | 100 | 3000 | 20.9655 | 69.6164 | 48.878 | 0 | 7.2692 | FALSE | FALSE
2025-10-17 07:00 | 27.3 | 47.5 | 101025 | 100 | 3000 | 21.5201 | 61.9272 | 43.2702 | 0 | 7.2692 | FALSE | FALSE
2025-10-17 08:00 | 29.45 | 39 | 101075 | 100 | 3000 | 22.3731 | 56.77 | 43.0715 | 0 | 7.2692 | FALSE | FALSE
2025-10-17 09:00 | 31.3 | 34.5 | 101105 | 100 | 3000 | 23.0889 | 53.9249 | 44.6746 | 0 | 7.2692 | FALSE | FALSE
2025-10-17 10:00 | 32.8 | 31.5 | 101100 | 100 | 3000 | 23.6589 | 51.9467 | 46.1995 | 0 | 7.2692 | FALSE | FALSE
2025-10-17 11:00 | 34.05 | 29 | 101035 | 100 | 3000 | 24.1285 | 50.2108 | 47.1581 | 0 | 7.2692 | FALSE | FALSE
2025-10-17 12:00 | 34.95 | 27 | 100935 | 100 | 3000 | 24.4651 | 48.7456 | 47.4024 | 0 | 7.2692 | FALSE | FALSE
2025-10-17 13:00 | 35.6 | 25.5 | 100840 | 100 | 3000 | 24.7074 | 47.6058 | 47.387 | 0 | 7.2692 | FALSE | FALSE
2025-10-17 14:00 | 36 | 24.5 | 100770 | 100 | 3000 | 24.8566 | 46.8235 | 47.2211 | 0 | 7.2692 | FALSE | FALSE
2025-10-17 15:00 | 34.9 | 30.5 | 100755 | 100 | 3000 | 24.4265 | 51.598 | 51.5884 | 0 | 7.2692 | FALSE | FALSE
2025-10-17 16:00 | 32.95 | 40 | 100775 | 100 | 3000 | 23.6743 | 58.5048 | 56.2606 | 0 | 7.2692 | FALSE | FALSE
2025-10-17 17:00 | 31.55 | 47 | 100790 | 100 | 3000 | 23.1334 | 63.1554 | 58.6797 | 0 | 7.2692 | FALSE | FALSE
2025-10-17 18:00 | 30.7 | 53 | 100835 | 100 | 3000 | 22.798 | 67.0496 | 61.4884 | 0 | 7.2692 | FALSE | FALSE
2025-10-17 19:00 | 30.2 | 56 | 100905 | 100 | 3000 | 22.6028 | 68.8757 | 62.4163 | 0 | 7.2692 | FALSE | FALSE
2025-10-17 20:00 | 29.55 | 58 | 100955 | 100 | 3000 | 22.3545 | 69.8712 | 61.6256 | 0 | 7.2692 | FALSE | FALSE
2025-10-17 21:00 | 28.85 | 60.5 | 100990 | 100 | 3000 | 22.0844 | 71.1418 | 60.9917 | 0 | 7.2692 | FALSE | FALSE
2025-10-17 22:00 | 28.25 | 62.5 | 101000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-17 23:00 | 27.5 | 64.5 | 100970 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-18 | 26.55 | 67.5 | 100935 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-18 01:00 | 25.75 | 70 | 100905 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-18 02:00 | 25.1 | 72.5 | 100895 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-18 03:00 | 24.6 | 72.5 | 100930 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-18 04:00 | 24.45 | 70 | 100960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-18 05:00 | 24.35 | 69 | 100985 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-18 06:00 | 24.7 | 63 | 101035 | 100 | 3000 | 20.4649 | 70.5735 | 45.7346 | 0 | 7.2692 | FALSE | FALSE
2025-10-18 07:00 | 26.45 | 47.5 | 101075 | 100 | 3000 | 21.1858 | 61.7158 | 40.1985 | 0 | 7.2692 | FALSE | FALSE
2025-10-18 08:00 | 29 | 33.5 | 101095 | 100 | 3000 | 22.2154 | 52.9568 | 36.3424 | 0 | 7.2692 | FALSE | FALSE
2025-10-18 09:00 | 31.5 | 28.5 | 101115 | 100 | 3000 | 23.187 | 49.5642 | 38.9068 | 0 | 7.2692 | FALSE | FALSE
2025-10-18 10:00 | 33.45 | 27 | 101090 | 100 | 3000 | 23.9195 | 48.5646 | 42.9833 | 0 | 7.2692 | FALSE | FALSE
2025-10-18 11:00 | 34.7 | 25.5 | 100995 | 100 | 3000 | 24.3836 | 47.4953 | 44.802 | 0 | 7.2692 | FALSE | FALSE
2025-10-18 12:00 | 35.6 | 24 | 100890 | 100 | 3000 | 24.7169 | 46.3563 | 45.4517 | 0 | 7.2692 | FALSE | FALSE
2025-10-18 13:00 | 36.15 | 23 | 100785 | 100 | 3000 | 24.9201 | 45.5732 | 45.6586 | 0 | 7.2692 | FALSE | FALSE
2025-10-18 14:00 | 35.25 | 29.5 | 100705 | 100 | 3000 | 24.5575 | 50.8612 | 51.4236 | 0 | 7.2692 | FALSE | FALSE
2025-10-18 15:00 | 33.65 | 38.5 | 100680 | 100 | 3000 | 23.9344 | 57.611 | 57.0165 | 0 | 7.2692 | FALSE | FALSE
2025-10-18 16:00 | 32.6 | 43 | 100675 | 100 | 3000 | 23.5335 | 60.6564 | 58.3147 | 0 | 7.2692 | FALSE | FALSE
2025-10-18 17:00 | 31.5 | 48.5 | 100660 | 100 | 3000 | 23.1091 | 64.24 | 60.0331 | 0 | 7.2692 | FALSE | FALSE
2025-10-18 18:00 | 30.65 | 54.5 | 100665 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-18 19:00 | 30.1 | 59 | 100715 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-18 20:00 | 29.35 | 63 | 100760 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-18 21:00 | 28.6 | 65.5 | 100780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-18 22:00 | 28 | 65.5 | 100785 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-18 23:00 | 27.35 | 66.5 | 100770 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 | 26.6 | 69.5 | 100755 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 01:00 | 25.85 | 72.5 | 100725 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 02:00 | 25.3 | 75 | 100700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 03:00 | 24.8 | 74.5 | 100715 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 04:00 | 24.5 | 72 | 100725 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 05:00 | 24.2 | 71.5 | 100740 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 06:00 | 24 | 71 | 100795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 07:00 | 25.25 | 64.5 | 100855 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 08:00 | 28.05 | 54 | 100880 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 09:00 | 30.8 | 47 | 100905 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 10:00 | 32.65 | 42 | 100905 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 11:00 | 33.8 | 38.5 | 100830 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 12:00 | 34 | 42.5 | 100755 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 13:00 | 33.65 | 46.5 | 100695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 14:00 | 33.2 | 46 | 100620 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 15:00 | 32.5 | 51 | 100565 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 16:00 | 31.55 | 59 | 100545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 17:00 | 30.65 | 62.5 | 100545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 18:00 | 30.15 | 63.5 | 100565 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 19:00 | 29.75 | 65 | 100595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 20:00 | 29.1 | 68 | 100635 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 21:00 | 28.4 | 71.5 | 100665 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 22:00 | 27.8 | 74 | 100665 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-19 23:00 | 27.2 | 76.5 | 100660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-20 | 26.5 | 79.5 | 100645 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-20 01:00 | 25.65 | 82.5 | 100595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-20 02:00 | 24.9 | 85.5 | 100550 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-20 03:00 | 24.45 | 86 | 100555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-20 04:00 | 24.25 | 85.5 | 100570 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-20 05:00 | 23.85 | 88.5 | 100595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-20 06:00 | 23.65 | 91 | 100655 | 100 | 3000 | 20.0111 | 86.1444 | 61.3146 | 0 | 7.2692 | FALSE | FALSE
2025-10-20 07:00 | 25.25 | 84 | 100715 | 100 | 3000 | 20.6529 | 83.419 | 64.0763 | 0 | 7.2692 | FALSE | FALSE
2025-10-20 08:00 | 28.1 | 69 | 100765 | 100 | 3000 | 21.779 | 76.2935 | 65.2733 | 0 | 7.2692 | FALSE | FALSE
2025-10-20 09:00 | 30.4 | 59.5 | 100805 | 100 | 3000 | 22.6648 | 71.4717 | 66.6874 | 0 | 7.2692 | FALSE | FALSE
2025-10-20 10:00 | 32.35 | 51.5 | 100800 | 100 | 3000 | 23.4052 | 66.9157 | 66.6754 | 0 | 7.2692 | FALSE | FALSE
2025-10-20 11:00 | 34.2 | 38 | 100745 | 100 | 3000 | 24.1339 | 57.4157 | 58.3944 | 0 | 7.2692 | FALSE | FALSE
2025-10-20 12:00 | 35.05 | 28.5 | 100695 | 100 | 3000 | 24.4922 | 50.0043 | 49.5344 | 0 | 7.2692 | FALSE | FALSE
2025-10-20 13:00 | 35 | 27 | 100650 | 100 | 3000 | 24.4832 | 48.7763 | 47.4807 | 0 | 7.2692 | FALSE | FALSE
2025-10-20 14:00 | 34.35 | 33.5 | 100610 | 100 | 3000 | 24.2124 | 53.8905 | 53.4553 | 0 | 7.2692 | FALSE | FALSE
2025-10-20 15:00 | 33.6 | 38 | 100590 | 100 | 3000 | 23.919 | 57.2105 | 56.2352 | 0 | 7.2692 | FALSE | FALSE
2025-10-20 16:00 | 32.55 | 43.5 | 100585 | 100 | 3000 | 23.5131 | 61.0209 | 58.6613 | 0 | 7.2692 | FALSE | FALSE
2025-10-20 17:00 | 31.05 | 55 | 100600 | 100 | 3000 | 22.9193 | 68.708 | 64.9122 | 0 | 7.2692 | FALSE | FALSE
2025-10-20 18:00 | 30.25 | 58.5 | 100625 | 100 | 3000 | 22.6129 | 70.6861 | 65.0229 | 0 | 7.2692 | FALSE | FALSE
2025-10-20 19:00 | 29.7 | 56 | 100670 | 100 | 3000 | 22.4166 | 68.609 | 60.2914 | 0 | 7.2692 | FALSE | FALSE
2025-10-20 20:00 | 28.7 | 59 | 100720 | 100 | 3000 | 22.0317 | 70.0743 | 58.9352 | 0 | 7.2692 | FALSE | FALSE
2025-10-20 21:00 | 28.15 | 62 | 100765 | 100 | 3000 | 21.8152 | 71.7359 | 59.31 | 0 | 7.2692 | FALSE | FALSE
2025-10-20 22:00 | 27.85 | 62.5 | 100780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-20 23:00 | 27.3 | 64.5 | 100770 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-21 | 26.85 | 65.5 | 100760 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-21 01:00 | 26.2 | 67.5 | 100740 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-21 02:00 | 25.5 | 70.5 | 100725 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-21 03:00 | 24.8 | 77.5 | 100735 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-21 04:00 | 24.35 | 83.5 | 100750 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-21 05:00 | 24.05 | 85 | 100785 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-21 06:00 | 23.85 | 86 | 100855 | 100 | 3000 | 20.0966 | 83.4396 | 58.7799 | 0 | 7.2692 | FALSE | FALSE
2025-10-21 07:00 | 25.25 | 79.5 | 100915 | 100 | 3000 | 20.6597 | 80.7094 | 60.6708 | 0 | 7.2692 | FALSE | FALSE
2025-10-21 08:00 | 28.2 | 64 | 100960 | 100 | 3000 | 21.8293 | 73.0624 | 61.3349 | 0 | 7.2692 | FALSE | FALSE
2025-10-21 09:00 | 31.2 | 45.5 | 100985 | 100 | 3000 | 23.0102 | 61.8919 | 55.8184 | 0 | 7.2692 | FALSE | FALSE
2025-10-21 10:00 | 33.7 | 29.5 | 100985 | 100 | 3000 | 23.9986 | 50.555 | 46.6653 | 0 | 7.2692 | FALSE | FALSE
2025-10-21 11:00 | 35.4 | 20.5 | 100945 | 100 | 3000 | 24.6668 | 43.4464 | 40.3743 | 0 | 7.2692 | FALSE | FALSE
2025-10-21 12:00 | 36.25 | 18 | 100875 | 100 | 3000 | 24.9897 | 41.34 | 41.2732 | 0 | 7.2692 | FALSE | FALSE
2025-10-21 13:00 | 35.95 | 23.5 | 100810 | 100 | 3000 | 24.8454 | 45.9756 | 45.767 | 0 | 7.2692 | FALSE | FALSE
2025-10-21 14:00 | 34.8 | 32 | 100775 | 100 | 3000 | 24.382 | 52.7892 | 53.1372 | 0 | 7.2692 | FALSE | FALSE
2025-10-21 15:00 | 33.6 | 39 | 100775 | 100 | 3000 | 23.9139 | 57.9746 | 57.4436 | 0 | 7.2692 | FALSE | FALSE
2025-10-21 16:00 | 32.25 | 45.5 | 100770 | 100 | 3000 | 23.3953 | 62.3727 | 59.7591 | 0 | 7.2692 | FALSE | FALSE
2025-10-21 17:00 | 30.9 | 54.5 | 100770 | 100 | 3000 | 22.8662 | 68.2421 | 63.8128 | 0 | 7.2692 | FALSE | FALSE
2025-10-21 18:00 | 30.2 | 61.5 | 100825 | 100 | 3000 | 22.5845 | 72.7354 | 67.7737 | 0 | 7.2692 | FALSE | FALSE
2025-10-21 19:00 | 29.7 | 63.5 | 100900 | 100 | 3000 | 22.3934 | 73.7583 | 67.4919 | 0 | 7.2692 | FALSE | FALSE
2025-10-21 20:00 | 28.8 | 67.5 | 100955 | 100 | 3000 | 22.0465 | 75.8043 | 67.1579 | 0 | 7.2692 | FALSE | FALSE
2025-10-21 21:00 | 28 | 70.5 | 100980 | 100 | 3000 | 21.7376 | 77.1775 | 66.1655 | 0 | 7.2692 | FALSE | FALSE
2025-10-21 22:00 | 27.45 | 71.5 | 100980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-21 23:00 | 26.9 | 73.5 | 100960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-22 | 26.25 | 77 | 100950 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-22 01:00 | 25.65 | 80 | 100960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-22 02:00 | 25.15 | 81.5 | 100965 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-22 03:00 | 24.6 | 84.5 | 100980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-22 04:00 | 24.25 | 86.5 | 101000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-22 05:00 | 23.95 | 85.5 | 101040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-22 06:00 | 23.7 | 82 | 101110 | 100 | 3000 | 20.041 | 81.0203 | 55.2553 | 0 | 7.2692 | FALSE | FALSE
2025-10-22 07:00 | 25.05 | 71.5 | 101190 | 100 | 3000 | 20.5926 | 75.7728 | 53.6879 | 0 | 7.2692 | FALSE | FALSE
2025-10-22 08:00 | 28 | 58 | 101245 | 100 | 3000 | 21.7676 | 68.9826 | 55.2142 | 0 | 7.2692 | FALSE | FALSE
2025-10-22 09:00 | 30.85 | 50 | 101265 | 100 | 3000 | 22.8643 | 64.9465 | 59.1446 | 0 | 7.2692 | FALSE | FALSE
2025-10-22 10:00 | 33.1 | 42.5 | 101240 | 100 | 3000 | 23.7167 | 60.44 | 59.7448 | 0 | 7.2692 | FALSE | FALSE
2025-10-22 11:00 | 34.85 | 32.5 | 101175 | 100 | 3000 | 24.3968 | 53.1738 | 54.0207 | 0 | 7.2692 | FALSE | FALSE
2025-10-22 12:00 | 35.7 | 29.5 | 101095 | 100 | 3000 | 24.7172 | 50.9277 | 52.941 | 0 | 7.2692 | FALSE | FALSE
2025-10-22 13:00 | 35.2 | 37.5 | 101030 | 100 | 3000 | 24.4905 | 57.3811 | 61.4183 | 0 | 7.2692 | FALSE | FALSE
2025-10-22 14:00 | 34.35 | 44.5 | 100995 | 100 | 3000 | 24.151 | 62.6387 | 66.7807 | 0 | 7.2692 | FALSE | FALSE
2025-10-22 15:00 | 34.25 | 40 | 100980 | 100 | 3000 | 24.1407 | 59.006 | 61.0242 | 0 | 7.2692 | FALSE | FALSE
2025-10-22 16:00 | 33.85 | 36 | 100980 | 100 | 3000 | 24.0193 | 55.693 | 54.8485 | 0 | 7.2692 | FALSE | FALSE
2025-10-22 17:00 | 32.2 | 43.5 | 100970 | 100 | 3000 | 23.3857 | 60.8377 | 57.4385 | 0 | 7.2692 | FALSE | FALSE
2025-10-22 18:00 | 30.8 | 51 | 100970 | 100 | 3000 | 22.8421 | 65.6638 | 59.9008 | 0 | 7.2692 | FALSE | FALSE
2025-10-22 19:00 | 30.2 | 53 | 101020 | 100 | 3000 | 22.6128 | 66.7619 | 59.4932 | 0 | 7.2692 | FALSE | FALSE
2025-10-22 20:00 | 29.4 | 55 | 101075 | 100 | 3000 | 22.3072 | 67.7198 | 58.1803 | 0 | 7.2692 | FALSE | FALSE
2025-10-22 21:00 | 28.3 | 56 | 101095 | 100 | 3000 | 21.8873 | 67.832 | 54.6304 | 0 | 7.2692 | FALSE | FALSE
2025-10-22 22:00 | 27.45 | 57 | 101090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-22 23:00 | 26.85 | 60 | 101070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-23 | 26.5 | 65 | 101050 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-23 01:00 | 26.3 | 70 | 101035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-23 02:00 | 26 | 73 | 101015 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-23 03:00 | 25.6 | 71.5 | 101005 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-23 04:00 | 25.4 | 70 | 101005 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-23 05:00 | 25.15 | 72.5 | 101030 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-23 06:00 | 24.65 | 75 | 101085 | 100 | 3000 | 20.429 | 77.6075 | 54.5267 | 0 | 7.2692 | FALSE | FALSE
2025-10-23 07:00 | 25.45 | 72 | 101130 | 100 | 3000 | 20.7499 | 76.324 | 55.8422 | 0 | 7.2692 | FALSE | FALSE
2025-10-23 08:00 | 27.95 | 64 | 101165 | 100 | 3000 | 21.7342 | 72.8828 | 60.2782 | 0 | 7.2692 | FALSE | FALSE
2025-10-23 09:00 | 30.7 | 55 | 101180 | 100 | 3000 | 22.7911 | 68.4412 | 63.5664 | 0 | 7.2692 | FALSE | FALSE
2025-10-23 10:00 | 32.55 | 47 | 101150 | 100 | 3000 | 23.4974 | 63.6121 | 62.6445 | 0 | 7.2692 | FALSE | FALSE
2025-10-23 11:00 | 33.65 | 43 | 101075 | 100 | 3000 | 23.9113 | 61.0919 | 62.3466 | 0 | 7.2692 | FALSE | FALSE
2025-10-23 12:00 | 34.15 | 42.5 | 100985 | 100 | 3000 | 24.0915 | 60.9459 | 63.6308 | 0 | 7.2692 | FALSE | FALSE
2025-10-23 13:00 | 33.95 | 42.5 | 100925 | 100 | 3000 | 24.0206 | 60.8552 | 62.8607 | 0 | 7.2692 | FALSE | FALSE
2025-10-23 14:00 | 33.35 | 43 | 100885 | 100 | 3000 | 23.804 | 60.9688 | 61.17 | 0 | 7.2692 | FALSE | FALSE
2025-10-23 15:00 | 32.5 | 49 | 100845 | 100 | 3000 | 23.4703 | 65.1207 | 64.5726 | 0 | 7.2692 | FALSE | FALSE
2025-10-23 16:00 | 31.55 | 54.5 | 100830 | 100 | 3000 | 23.1036 | 68.6365 | 66.5422 | 0 | 7.2692 | FALSE | FALSE
2025-10-23 17:00 | 30.6 | 55.5 | 100840 | 100 | 3000 | 22.7523 | 68.7683 | 63.5813 | 0 | 7.2692 | FALSE | FALSE
2025-10-23 18:00 | 29.95 | 56.5 | 100860 | 100 | 3000 | 22.5083 | 69.0814 | 61.8497 | 0 | 7.2692 | FALSE | FALSE
2025-10-23 19:00 | 29.55 | 57 | 100890 | 100 | 3000 | 22.3575 | 69.1908 | 60.6631 | 0 | 7.2692 | FALSE | FALSE
2025-10-23 20:00 | 28.75 | 60 | 100930 | 100 | 3000 | 22.048 | 70.7521 | 60.0969 | 0 | 7.2692 | FALSE | FALSE
2025-10-23 21:00 | 27.65 | 63 | 100985 | 100 | 3000 | 21.6218 | 72.0678 | 58.0792 | 0 | 7.2692 | FALSE | FALSE
2025-10-23 22:00 | 26.8 | 65.5 | 101010 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-23 23:00 | 26.45 | 68 | 100985 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-24 | 26.35 | 67.5 | 100960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-24 01:00 | 26.2 | 66.5 | 100930 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-24 02:00 | 25.95 | 66 | 100910 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-24 03:00 | 25.45 | 68.5 | 100910 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-24 04:00 | 24.85 | 72 | 100920 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-24 05:00 | 24.25 | 74.5 | 100955 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-24 06:00 | 23.95 | 75.5 | 100995 | 100 | 3000 | 20.1486 | 77.4764 | 51.7391 | 0 | 7.2692 | FALSE | FALSE
2025-10-24 07:00 | 25.1 | 70 | 101030 | 100 | 3000 | 20.6146 | 74.9249 | 52.742 | 0 | 7.2692 | FALSE | FALSE
2025-10-24 08:00 | 27.85 | 58 | 101070 | 100 | 3000 | 21.71 | 68.9237 | 54.5684 | 0 | 7.2692 | FALSE | FALSE
2025-10-24 09:00 | 30.45 | 46 | 101095 | 100 | 3000 | 22.7295 | 61.9388 | 53.531 | 0 | 7.2692 | FALSE | FALSE
2025-10-24 10:00 | 32.15 | 37.5 | 101085 | 100 | 3000 | 23.393 | 56.3295 | 50.7384 | 0 | 7.2692 | FALSE | FALSE
2025-10-24 11:00 | 33.45 | 31 | 101035 | 100 | 3000 | 23.8997 | 51.6798 | 47.6624 | 0 | 7.2692 | FALSE | FALSE
2025-10-24 12:00 | 34.05 | 28.5 | 100965 | 100 | 3000 | 24.1312 | 49.8208 | 46.5387 | 0 | 7.2692 | FALSE | FALSE
2025-10-24 13:00 | 33.95 | 30 | 100895 | 100 | 3000 | 24.087 | 50.997 | 48.0161 | 0 | 7.2692 | FALSE | FALSE
2025-10-24 14:00 | 33.4 | 32.5 | 100825 | 100 | 3000 | 23.8741 | 52.8533 | 49.2047 | 0 | 7.2692 | FALSE | FALSE
2025-10-24 15:00 | 32.7 | 36 | 100775 | 100 | 3000 | 23.6017 | 55.377 | 50.8817 | 0 | 7.2692 | FALSE | FALSE
2025-10-24 16:00 | 31.9 | 39 | 100755 | 100 | 3000 | 23.2945 | 57.4023 | 51.4314 | 0 | 7.2692 | FALSE | FALSE
2025-10-24 17:00 | 31 | 40 | 100760 | 100 | 3000 | 22.9563 | 57.8702 | 49.3438 | 0 | 7.2692 | FALSE | FALSE
2025-10-24 18:00 | 30.3 | 41 | 100780 | 100 | 3000 | 22.6899 | 58.3868 | 47.913 | 0 | 7.2692 | FALSE | FALSE
2025-10-24 19:00 | 29.65 | 43 | 100815 | 100 | 3000 | 22.4375 | 59.598 | 47.5897 | 0 | 7.2692 | FALSE | FALSE
2025-10-24 20:00 | 28.95 | 46 | 100860 | 100 | 3000 | 22.162 | 61.4333 | 47.924 | 0 | 7.2692 | FALSE | FALSE
2025-10-24 21:00 | 28.25 | 50 | 100880 | 100 | 3000 | 21.883 | 63.8669 | 48.9916 | 0 | 7.2692 | FALSE | FALSE
2025-10-24 22:00 | 27.75 | 53 | 100875 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-24 23:00 | 27.35 | 54.5 | 100850 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-25 | 26.7 | 56.5 | 100810 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-25 01:00 | 25.6 | 60.5 | 100785 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-25 02:00 | 24.35 | 64 | 100775 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-25 03:00 | 23.5 | 64.5 | 100780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-25 04:00 | 23.3 | 63.5 | 100780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-25 05:00 | 23.2 | 64 | 100785 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-25 06:00 | 23.05 | 65 | 100815 | 100 | 3000 | 19.7945 | 71.1093 | 40.4552 | 0 | 7.2692 | FALSE | FALSE
2025-10-25 07:00 | 24.6 | 59.5 | 100850 | 100 | 3000 | 20.4293 | 68.4914 | 42.6721 | 0 | 7.2692 | FALSE | FALSE
2025-10-25 08:00 | 27.75 | 49.5 | 100890 | 100 | 3000 | 21.691 | 63.3659 | 46.66 | 0 | 7.2692 | FALSE | FALSE
2025-10-25 09:00 | 30.15 | 45.5 | 100900 | 100 | 3000 | 22.6186 | 61.492 | 51.8757 | 0 | 7.2692 | FALSE | FALSE
2025-10-25 10:00 | 31.5 | 43.5 | 100855 | 100 | 3000 | 23.1287 | 60.5681 | 54.8178 | 0 | 7.2692 | FALSE | FALSE
2025-10-25 11:00 | 32.7 | 38 | 100770 | 100 | 3000 | 23.5926 | 56.8961 | 53.1247 | 0 | 7.2692 | FALSE | FALSE
2025-10-25 12:00 | 33.75 | 33.5 | 100680 | 100 | 3000 | 23.9962 | 53.7271 | 51.4865 | 0 | 7.2692 | FALSE | FALSE
2025-10-25 13:00 | 34.2 | 33 | 100605 | 100 | 3000 | 24.1613 | 53.4526 | 52.3536 | 0 | 7.2692 | FALSE | FALSE
2025-10-25 14:00 | 33.35 | 40.5 | 100555 | 100 | 3000 | 23.8164 | 59.0629 | 58.226 | 0 | 7.2692 | FALSE | FALSE
2025-10-25 15:00 | 31.9 | 47.5 | 100530 | 100 | 3000 | 23.2593 | 63.7145 | 60.5113 | 0 | 7.2692 | FALSE | FALSE
2025-10-25 16:00 | 31.2 | 47.5 | 100525 | 100 | 3000 | 23.0026 | 63.3823 | 57.7971 | 0 | 7.2692 | FALSE | FALSE
2025-10-25 17:00 | 30.45 | 49.5 | 100545 | 100 | 3000 | 22.7175 | 64.4658 | 56.9256 | 0 | 7.2692 | FALSE | FALSE
2025-10-25 18:00 | 29.8 | 54 | 100590 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-25 19:00 | 29.45 | 58 | 100650 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-25 20:00 | 28.7 | 61.5 | 100700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-25 21:00 | 27.95 | 63 | 100725 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-25 22:00 | 27.25 | 64 | 100720 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-25 23:00 | 26.5 | 66.5 | 100710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 | 25.8 | 69 | 100705 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 01:00 | 25.1 | 72 | 100700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 02:00 | 24.35 | 75.5 | 100695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 03:00 | 23.7 | 78.5 | 100680 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 04:00 | 23.1 | 81 | 100675 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 05:00 | 22.55 | 83 | 100680 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 06:00 | 22.4 | 83 | 100715 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 07:00 | 24 | 75 | 100770 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 08:00 | 26.9 | 63.5 | 100815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 09:00 | 28.9 | 57 | 100845 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 10:00 | 30.05 | 52.5 | 100835 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 11:00 | 31.15 | 47.5 | 100780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 12:00 | 31.9 | 44.5 | 100710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 13:00 | 31.85 | 44.5 | 100650 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 14:00 | 31.35 | 45.5 | 100595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 15:00 | 31.25 | 46 | 100570 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 16:00 | 30.75 | 48 | 100580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 17:00 | 29.7 | 52 | 100600 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 18:00 | 29 | 55.5 | 100635 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 19:00 | 28.35 | 59 | 100690 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 20:00 | 27.75 | 62 | 100740 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 21:00 | 27.15 | 64 | 100750 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 22:00 | 26.4 | 66.5 | 100740 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-26 23:00 | 25.65 | 69 | 100725 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-27 | 24.9 | 72 | 100710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-27 01:00 | 24.1 | 75 | 100700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-27 02:00 | 23.3 | 77.5 | 100680 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-27 03:00 | 22.55 | 80.5 | 100675 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-27 04:00 | 21.8 | 83.5 | 100695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-27 05:00 | 21.1 | 86.5 | 100730 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-27 06:00 | 20.9 | 87.5 | 100790 | 100 | 3000 | 18.8913 | 82.2442 | 45.8786 | 0 | 7.2692 | FALSE | FALSE
2025-10-27 07:00 | 22.35 | 80.5 | 100865 | 100 | 3000 | 19.4947 | 79.3511 | 48.0064 | 0 | 7.2692 | FALSE | FALSE
2025-10-27 08:00 | 25.35 | 66.5 | 100920 | 100 | 3000 | 20.7188 | 72.9761 | 51.1093 | 0 | 7.2692 | FALSE | FALSE
2025-10-27 09:00 | 28.25 | 54 | 100950 | 100 | 3000 | 21.8731 | 66.5018 | 52.6069 | 0 | 7.2692 | FALSE | FALSE
2025-10-27 10:00 | 30.25 | 46 | 100930 | 100 | 3000 | 22.6545 | 61.8774 | 52.7498 | 0 | 7.2692 | FALSE | FALSE
2025-10-27 11:00 | 31.55 | 41.5 | 100855 | 100 | 3000 | 23.1551 | 59.1226 | 52.8858 | 0 | 7.2692 | FALSE | FALSE
2025-10-27 12:00 | 32.4 | 39.5 | 100780 | 100 | 3000 | 23.4762 | 57.9317 | 53.7413 | 0 | 7.2692 | FALSE | FALSE
2025-10-27 13:00 | 32.5 | 41.5 | 100725 | 100 | 3000 | 23.5039 | 59.4787 | 56.2974 | 0 | 7.2692 | FALSE | FALSE
2025-10-27 14:00 | 31.95 | 46 | 100690 | 100 | 3000 | 23.2838 | 62.6132 | 59.1335 | 0 | 7.2692 | FALSE | FALSE
2025-10-27 15:00 | 31.35 | 49.5 | 100685 | 100 | 3000 | 23.0502 | 64.8911 | 60.4911 | 0 | 7.2692 | FALSE | FALSE
2025-10-27 16:00 | 30.8 | 52.5 | 100690 | 100 | 3000 | 22.8367 | 66.7616 | 61.3622 | 0 | 7.2692 | FALSE | FALSE
2025-10-27 17:00 | 29.85 | 57.5 | 100710 | 100 | 3000 | 22.4678 | 69.7302 | 62.3671 | 0 | 7.2692 | FALSE | FALSE
2025-10-27 18:00 | 29.05 | 61.5 | 100760 | 100 | 3000 | 22.1568 | 71.9631 | 62.7329 | 0 | 7.2692 | FALSE | FALSE
2025-10-27 19:00 | 28.65 | 64 | 100825 | 100 | 3000 | 21.9995 | 73.3717 | 63.2864 | 0 | 7.2692 | FALSE | FALSE
2025-10-27 20:00 | 28.1 | 68 | 100880 | 100 | 3000 | 21.7815 | 75.6272 | 64.4128 | 0 | 7.2692 | FALSE | FALSE
2025-10-27 21:00 | 27.6 | 69.5 | 100890 | 100 | 3000 | 21.5879 | 76.2413 | 63.4523 | 0 | 7.2692 | FALSE | FALSE
2025-10-27 22:00 | 27.15 | 69.5 | 100870 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-27 23:00 | 26.7 | 70.5 | 100845 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-28 | 26.1 | 72.5 | 100830 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-28 01:00 | 25.35 | 75.5 | 100810 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-28 02:00 | 24.55 | 79.5 | 100785 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-28 03:00 | 23.85 | 83 | 100785 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-28 04:00 | 23.5 | 84.5 | 100795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-28 05:00 | 23.25 | 85.5 | 100820 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-28 06:00 | 23.25 | 85 | 100865 | 100 | 3000 | 19.8567 | 82.4239 | 55.2148 | 0 | 7.2692 | FALSE | FALSE
2025-10-28 07:00 | 24.7 | 78 | 100905 | 100 | 3000 | 20.4448 | 79.4226 | 56.9696 | 0 | 7.2692 | FALSE | FALSE
2025-10-28 08:00 | 27.45 | 66.5 | 100935 | 100 | 3000 | 21.5373 | 74.204 | 60.215 | 0 | 7.2692 | FALSE | FALSE
2025-10-28 09:00 | 29.95 | 57.5 | 100960 | 100 | 3000 | 22.5051 | 69.7671 | 62.8368 | 0 | 7.2692 | FALSE | FALSE
2025-10-28 10:00 | 31.9 | 49.5 | 100945 | 100 | 3000 | 23.2511 | 65.1557 | 62.7333 | 0 | 7.2692 | FALSE | FALSE
2025-10-28 11:00 | 33.2 | 44 | 100875 | 100 | 3000 | 23.7453 | 61.6716 | 61.7403 | 0 | 7.2692 | FALSE | FALSE
2025-10-28 12:00 | 33.6 | 44 | 100790 | 100 | 3000 | 23.8883 | 61.8732 | 63.2475 | 0 | 7.2692 | FALSE | FALSE
2025-10-28 13:00 | 33.15 | 48 | 100730 | 100 | 3000 | 23.7079 | 64.736 | 66.0381 | 0 | 7.2692 | FALSE | FALSE
2025-10-28 14:00 | 32.5 | 49.5 | 100695 | 100 | 3000 | 23.468 | 65.5109 | 65.0863 | 0 | 7.2692 | FALSE | FALSE
2025-10-28 15:00 | 32.2 | 49.5 | 100670 | 100 | 3000 | 23.3598 | 65.3447 | 63.8748 | 0 | 7.2692 | FALSE | FALSE
2025-10-28 16:00 | 31.35 | 53.5 | 100660 | 100 | 3000 | 23.0346 | 67.8004 | 64.634 | 0 | 7.2692 | FALSE | FALSE
2025-10-28 17:00 | 30.4 | 57.5 | 100680 | 100 | 3000 | 22.6716 | 70.074 | 64.6911 | 0 | 7.2692 | FALSE | FALSE
2025-10-28 18:00 | 29.9 | 60.5 | 100730 | 100 | 3000 | 22.4769 | 71.8403 | 65.4728 | 0 | 7.2692 | FALSE | FALSE
2025-10-28 19:00 | 29.3 | 63.5 | 100790 | 100 | 3000 | 22.2447 | 73.4841 | 65.6922 | 0 | 7.2692 | FALSE | FALSE
2025-10-28 20:00 | 28.6 | 66.5 | 100840 | 100 | 3000 | 21.9741 | 75.0008 | 65.3261 | 0 | 7.2692 | FALSE | FALSE
2025-10-28 21:00 | 27.95 | 68.5 | 100875 | 100 | 3000 | 21.7234 | 75.8464 | 64.1714 | 0 | 7.2692 | FALSE | FALSE
2025-10-28 22:00 | 27.45 | 70 | 100880 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-28 23:00 | 27 | 72 | 100860 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-29 | 26.55 | 74 | 100845 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-29 01:00 | 26.05 | 76 | 100820 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-29 02:00 | 25.4 | 78.5 | 100790 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-29 03:00 | 24.6 | 80.5 | 100780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-29 04:00 | 24.15 | 81.5 | 100790 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-29 05:00 | 23.85 | 83 | 100815 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-29 06:00 | 23.5 | 84.5 | 100855 | 100 | 3000 | 19.9579 | 82.3239 | 56.0487 | 0 | 7.2692 | FALSE | FALSE
2025-10-29 07:00 | 24.6 | 79.5 | 100905 | 100 | 3000 | 20.4031 | 80.2327 | 57.6205 | 0 | 7.2692 | FALSE | FALSE
2025-10-29 08:00 | 27.25 | 68.5 | 100950 | 100 | 3000 | 21.4562 | 75.3498 | 61.0305 | 0 | 7.2692 | FALSE | FALSE
2025-10-29 09:00 | 29.75 | 60.5 | 100975 | 100 | 3000 | 22.4213 | 71.7167 | 64.8674 | 0 | 7.2692 | FALSE | FALSE
2025-10-29 10:00 | 31.55 | 55 | 100950 | 100 | 3000 | 23.1016 | 68.9908 | 67.0883 | 0 | 7.2692 | FALSE | FALSE
2025-10-29 11:00 | 32.75 | 50.5 | 100870 | 100 | 3000 | 23.5532 | 66.3979 | 67.2396 | 0 | 7.2692 | FALSE | FALSE
2025-10-29 12:00 | 33.2 | 47.5 | 100785 | 100 | 3000 | 23.7281 | 64.3746 | 65.6857 | 0 | 7.2692 | FALSE | FALSE
2025-10-29 13:00 | 32.95 | 46 | 100725 | 100 | 3000 | 23.6459 | 63.096 | 63.0007 | 0 | 7.2692 | FALSE | FALSE
2025-10-29 14:00 | 32.45 | 47.5 | 100670 | 100 | 3000 | 23.4589 | 63.9804 | 62.6943 | 0 | 7.2692 | FALSE | FALSE
2025-10-29 15:00 | 32 | 49 | 100635 | 100 | 3000 | 23.2894 | 64.8672 | 62.5313 | 0 | 7.2692 | FALSE | FALSE
2025-10-29 16:00 | 31.5 | 50 | 100615 | 100 | 3000 | 23.1031 | 65.3398 | 61.5941 | 0 | 7.2692 | FALSE | FALSE
2025-10-29 17:00 | 30.65 | 52 | 100620 | 100 | 3000 | 22.783 | 66.331 | 60.2377 | 0 | 7.2692 | FALSE | FALSE
2025-10-29 18:00 | 29.95 | 54.5 | 100665 | 100 | 3000 | 22.5146 | 67.7089 | 59.873 | 0 | 7.2692 | FALSE | FALSE
2025-10-29 19:00 | 29.5 | 58.5 | 100720 | 100 | 3000 | 22.3342 | 70.2066 | 61.8448 | 0 | 7.2692 | FALSE | FALSE
2025-10-29 20:00 | 28.85 | 63.5 | 100755 | 100 | 3000 | 22.0761 | 73.1785 | 63.699 | 0 | 7.2692 | FALSE | FALSE
2025-10-29 21:00 | 28.1 | 67.5 | 100775 | 100 | 3000 | 21.7827 | 75.3101 | 63.955 | 0 | 7.2692 | FALSE | FALSE
2025-10-29 22:00 | 27.55 | 70 | 100775 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-29 23:00 | 27.1 | 72 | 100740 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-30 | 26.6 | 74 | 100705 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-30 01:00 | 26.25 | 76 | 100675 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-30 02:00 | 25.95 | 78 | 100660 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-30 03:00 | 25.5 | 77.5 | 100670 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-30 04:00 | 25.05 | 77 | 100675 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-30 05:00 | 24.55 | 79 | 100695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-30 06:00 | 24.15 | 80.5 | 100760 | 100 | 3000 | 20.2228 | 80.5119 | 56.2396 | 0 | 7.2692 | FALSE | FALSE
2025-10-30 07:00 | 25.2 | 76 | 100815 | 100 | 3000 | 20.6453 | 78.592 | 57.75 | 0 | 7.2692 | FALSE | FALSE
2025-10-30 08:00 | 27.6 | 67.5 | 100850 | 100 | 3000 | 21.5924 | 74.9556 | 61.7257 | 0 | 7.2692 | FALSE | FALSE
2025-10-30 09:00 | 29.9 | 60 | 100895 | 100 | 3000 | 22.4786 | 71.4777 | 65.0231 | 0 | 7.2692 | FALSE | FALSE
2025-10-30 10:00 | 31.65 | 51 | 100895 | 100 | 3000 | 23.154 | 66.1276 | 63.3046 | 0 | 7.2692 | FALSE | FALSE
2025-10-30 11:00 | 32.7 | 44.5 | 100830 | 100 | 3000 | 23.5629 | 61.8229 | 60.3895 | 0 | 7.2692 | FALSE | FALSE
2025-10-30 12:00 | 33 | 42 | 100770 | 100 | 3000 | 23.6829 | 60.0555 | 58.7009 | 0 | 7.2692 | FALSE | FALSE
2025-10-30 13:00 | 32.85 | 41 | 100735 | 100 | 3000 | 23.6334 | 59.234 | 57.0167 | 0 | 7.2692 | FALSE | FALSE
2025-10-30 14:00 | 32.45 | 42.5 | 100715 | 100 | 3000 | 23.4812 | 60.2134 | 57.2152 | 0 | 7.2692 | FALSE | FALSE
2025-10-30 15:00 | 32 | 45.5 | 100695 | 100 | 3000 | 23.3042 | 62.2648 | 58.7885 | 0 | 7.2692 | FALSE | FALSE
2025-10-30 16:00 | 31.3 | 50 | 100685 | 100 | 3000 | 23.0299 | 65.2286 | 60.8118 | 0 | 7.2692 | FALSE | FALSE
2025-10-30 17:00 | 30.3 | 55.5 | 100710 | 100 | 3000 | 22.6415 | 68.6021 | 62.3041 | 0 | 7.2692 | FALSE | FALSE
2025-10-30 18:00 | 29.65 | 59 | 100760 | 100 | 3000 | 22.3887 | 70.6386 | 62.965 | 0 | 7.2692 | FALSE | FALSE
2025-10-30 19:00 | 29.15 | 61.5 | 100815 | 100 | 3000 | 22.1944 | 72.0224 | 63.1762 | 0 | 7.2692 | FALSE | FALSE
2025-10-30 20:00 | 28.4 | 64.5 | 100870 | 100 | 3000 | 21.9038 | 73.5321 | 62.6433 | 0 | 7.2692 | FALSE | FALSE
2025-10-30 21:00 | 27.75 | 66.5 | 100905 | 100 | 3000 | 21.652 | 74.4046 | 61.5379 | 0 | 7.2692 | FALSE | FALSE
2025-10-30 22:00 | 27.2 | 68 | 100915 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-30 23:00 | 26.55 | 70 | 100910 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-31 | 25.8 | 72.5 | 100890 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-31 01:00 | 25.15 | 75 | 100885 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-31 02:00 | 24.6 | 77.5 | 100880 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-31 03:00 | 23.9 | 79.5 | 100870 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-31 04:00 | 23.5 | 80 | 100875 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-31 05:00 | 23.35 | 80.5 | 100900 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-31 06:00 | 23.3 | 80.5 | 100955 | 100 | 3000 | 19.8813 | 79.9205 | 52.3332 | 0 | 7.2692 | FALSE | FALSE
2025-10-31 07:00 | 24.7 | 74.5 | 101015 | 100 | 3000 | 20.4495 | 77.3524 | 54.37 | 0 | 7.2692 | FALSE | FALSE
2025-10-31 08:00 | 27.4 | 65 | 101060 | 100 | 3000 | 21.5214 | 73.1972 | 58.7324 | 0 | 7.2692 | FALSE | FALSE
2025-10-31 09:00 | 29.8 | 58 | 101105 | 100 | 3000 | 22.4478 | 70.0083 | 62.7113 | 0 | 7.2692 | FALSE | FALSE
2025-10-31 10:00 | 31.5 | 51.5 | 101100 | 100 | 3000 | 23.0974 | 66.3904 | 63.263 | 0 | 7.2692 | FALSE | FALSE
2025-10-31 11:00 | 32.75 | 44.5 | 101025 | 100 | 3000 | 23.581 | 61.8287 | 60.6234 | 0 | 7.2692 | FALSE | FALSE
2025-10-31 12:00 | 33.45 | 40 | 100945 | 100 | 3000 | 23.8549 | 58.6805 | 58.1031 | 0 | 7.2692 | FALSE | FALSE
2025-10-31 13:00 | 33.35 | 39 | 100885 | 100 | 3000 | 23.8238 | 57.8725 | 56.5767 | 0 | 7.2692 | FALSE | FALSE
2025-10-31 14:00 | 32.8 | 40 | 100850 | 100 | 3000 | 23.6199 | 58.4432 | 55.739 | 0 | 7.2692 | FALSE | FALSE
2025-10-31 15:00 | 32.25 | 42.5 | 100845 | 100 | 3000 | 23.4083 | 60.1216 | 56.5066 | 0 | 7.2692 | FALSE | FALSE
2025-10-31 16:00 | 31.45 | 45.5 | 100850 | 100 | 3000 | 23.1025 | 62.0092 | 56.7341 | 0 | 7.2692 | FALSE | FALSE
2025-10-31 17:00 | 30.5 | 49 | 100865 | 100 | 3000 | 22.7379 | 64.105 | 56.6832 | 0 | 7.2692 | FALSE | FALSE
2025-10-31 18:00 | 29.8 | 52 | 100900 | 100 | 3000 | 22.4665 | 65.8739 | 56.8898 | 0 | 7.2692 | FALSE | FALSE
2025-10-31 19:00 | 29.2 | 53.5 | 100970 | 100 | 3000 | 22.2361 | 66.6059 | 55.9376 | 0 | 7.2692 | FALSE | FALSE
2025-10-31 20:00 | 28.55 | 55.5 | 101030 | 100 | 3000 | 21.984 | 67.6289 | 55.1798 | 0 | 7.2692 | FALSE | FALSE
2025-10-31 21:00 | 27.95 | 58 | 101050 | 100 | 3000 | 21.7484 | 68.9762 | 54.976 | 0 | 7.2692 | FALSE | FALSE
2025-10-31 22:00 | 27.5 | 60 | 101050 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-10-31 23:00 | 27.05 | 62 | 101020 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-01 | 26.65 | 63.5 | 100985 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-01 01:00 | 26.25 | 65 | 100960 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-01 02:00 | 25.75 | 67.5 | 100950 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-01 03:00 | 24.55 | 71 | 100950 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-01 04:00 | 23.35 | 74.5 | 100955 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-01 05:00 | 22.9 | 77 | 100980 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-01 06:00 | 22.85 | 78 | 101030 | 100 | 3000 | 19.7011 | 78.2431 | 48.581 | 0 | 7.2692 | FALSE | FALSE
2025-11-01 07:00 | 24.2 | 73 | 101095 | 100 | 3000 | 20.2518 | 76.1687 | 51.0453 | 0 | 7.2692 | FALSE | FALSE
2025-11-01 08:00 | 27 | 63 | 101155 | 100 | 3000 | 21.3713 | 71.6785 | 55.3309 | 0 | 7.2692 | FALSE | FALSE
2025-11-01 09:00 | 29.75 | 54 | 101195 | 100 | 3000 | 22.4416 | 67.2049 | 58.6741 | 0 | 7.2692 | FALSE | FALSE
2025-11-01 10:00 | 31.8 | 45.5 | 101185 | 100 | 3000 | 23.2311 | 62.1308 | 58.132 | 0 | 7.2692 | FALSE | FALSE
2025-11-01 11:00 | 33.1 | 38.5 | 101115 | 100 | 3000 | 23.7358 | 57.3783 | 55.1699 | 0 | 7.2692 | FALSE | FALSE
2025-11-01 12:00 | 33.5 | 35.5 | 101035 | 100 | 3000 | 23.8955 | 55.1916 | 53.0795 | 0 | 7.2692 | FALSE | FALSE
2025-11-01 13:00 | 33.4 | 34.5 | 100980 | 100 | 3000 | 23.8642 | 54.3919 | 51.5668 | 0 | 7.2692 | FALSE | FALSE
2025-11-01 14:00 | 33.1 | 35 | 100945 | 100 | 3000 | 23.7526 | 54.7031 | 51.1322 | 0 | 7.2692 | FALSE | FALSE
2025-11-01 15:00 | 32.5 | 38 | 100930 | 100 | 3000 | 23.5194 | 56.8203 | 52.4647 | 0 | 7.2692 | FALSE | FALSE
2025-11-01 16:00 | 31.55 | 43 | 100940 | 100 | 3000 | 23.1492 | 60.2135 | 54.4915 | 0 | 7.2692 | FALSE | FALSE
2025-11-01 17:00 | 30.5 | 48.5 | 100965 | 100 | 3000 | 22.7396 | 63.7416 | 56.202 | 0 | 7.2692 | FALSE | FALSE
2025-11-01 18:00 | 29.7 | 52.5 | 101005 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-01 19:00 | 29.2 | 54 | 101040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-01 20:00 | 28.65 | 56 | 101080 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-01 21:00 | 27.7 | 58.5 | 101105 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-01 22:00 | 26.95 | 59.5 | 101080 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-01 23:00 | 26.6 | 61.5 | 101045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 | 26.2 | 65.5 | 101025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 01:00 | 25.8 | 69.5 | 101010 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 02:00 | 25.45 | 72.5 | 101000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 03:00 | 25.15 | 71 | 101010 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 04:00 | 25.05 | 69 | 101025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 05:00 | 25.05 | 71 | 101045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 06:00 | 25.1 | 72 | 101090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 07:00 | 26.2 | 68.5 | 101150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 08:00 | 28.25 | 60.5 | 101200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 09:00 | 30.05 | 50 | 101250 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 10:00 | 31.35 | 40 | 101255 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 11:00 | 32.05 | 35 | 101195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 12:00 | 32.1 | 35.5 | 101120 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 13:00 | 31.85 | 39 | 101060 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 14:00 | 31.5 | 42 | 101015 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 15:00 | 31.05 | 44 | 100990 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 16:00 | 30.3 | 46.5 | 100995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 17:00 | 29.3 | 50 | 101000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 18:00 | 28.35 | 54 | 101020 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 19:00 | 27.55 | 57 | 101065 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 20:00 | 26.95 | 59 | 101110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 21:00 | 26.5 | 58.5 | 101140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 22:00 | 26.15 | 57 | 101135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-02 23:00 | 25.65 | 58.5 | 101105 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-03 | 24.95 | 61 | 101070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-03 01:00 | 24.35 | 62.5 | 101035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-03 02:00 | 23.75 | 65.5 | 101015 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-03 03:00 | 23.35 | 67.5 | 101005 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-03 04:00 | 23.1 | 66.5 | 101000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-03 05:00 | 22.55 | 66.5 | 101010 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-03 06:00 | 22.4 | 66.5 | 101050 | 100 | 3000 | 19.5262 | 71.6892 | 38.874 | 0 | 7.2692 | FALSE | FALSE
2025-11-03 07:00 | 23.85 | 61.5 | 101110 | 100 | 3000 | 20.124 | 69.3695 | 41.2085 | 0 | 7.2692 | FALSE | FALSE
2025-11-03 08:00 | 26.55 | 52.5 | 101155 | 100 | 3000 | 21.216 | 64.8648 | 44.7373 | 0 | 7.2692 | FALSE | FALSE
2025-11-03 09:00 | 28.95 | 47 | 101195 | 100 | 3000 | 22.1593 | 62.077 | 48.9195 | 0 | 7.2692 | FALSE | FALSE
2025-11-03 10:00 | 30.55 | 44 | 101190 | 100 | 3000 | 22.7737 | 60.5493 | 51.9081 | 0 | 7.2692 | FALSE | FALSE
2025-11-03 11:00 | 31.5 | 41 | 101110 | 100 | 3000 | 23.1385 | 58.7168 | 52.2307 | 0 | 7.2692 | FALSE | FALSE
2025-11-03 12:00 | 31.9 | 40 | 101020 | 100 | 3000 | 23.2904 | 58.1191 | 52.5673 | 0 | 7.2692 | FALSE | FALSE
2025-11-03 13:00 | 31.95 | 40.5 | 100950 | 100 | 3000 | 23.3067 | 58.5125 | 53.2698 | 0 | 7.2692 | FALSE | FALSE
2025-11-03 14:00 | 31.7 | 42 | 100905 | 100 | 3000 | 23.2085 | 59.5376 | 53.9698 | 0 | 7.2692 | FALSE | FALSE
2025-11-03 15:00 | 31.4 | 43.5 | 100875 | 100 | 3000 | 23.0918 | 60.5282 | 54.4533 | 0 | 7.2692 | FALSE | FALSE
2025-11-03 16:00 | 30.95 | 45 | 100870 | 100 | 3000 | 22.9194 | 61.4412 | 54.3415 | 0 | 7.2692 | FALSE | FALSE
2025-11-03 17:00 | 30.25 | 47.5 | 100890 | 100 | 3000 | 22.6496 | 62.9359 | 54.2314 | 0 | 7.2692 | FALSE | FALSE
2025-11-03 18:00 | 29.7 | 51 | 100925 | 100 | 3000 | 22.432 | 65.1327 | 55.5337 | 0 | 7.2692 | FALSE | FALSE
2025-11-03 19:00 | 29.05 | 55.5 | 100985 | 100 | 3000 | 22.1737 | 67.8855 | 57.2044 | 0 | 7.2692 | FALSE | FALSE
2025-11-03 20:00 | 28.3 | 59 | 101050 | 100 | 3000 | 21.8798 | 69.8182 | 57.3166 | 0 | 7.2692 | FALSE | FALSE
2025-11-03 21:00 | 27.85 | 60 | 101075 | 100 | 3000 | 21.7054 | 70.2257 | 56.3257 | 0 | 7.2692 | FALSE | FALSE
2025-11-03 22:00 | 27.5 | 60.5 | 101065 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-03 23:00 | 27 | 61.5 | 101055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-04 | 26.4 | 63 | 101030 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-04 01:00 | 25.7 | 65.5 | 101000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-04 02:00 | 24.7 | 70 | 100995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-04 03:00 | 23.6 | 73 | 101000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-04 04:00 | 22.9 | 73.5 | 101005 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-04 05:00 | 22.45 | 75.5 | 101045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-04 06:00 | 22.15 | 77.5 | 101115 | 100 | 3000 | 19.4149 | 77.5807 | 45.1521 | 0 | 7.2692 | FALSE | FALSE
2025-11-04 07:00 | 23.45 | 72 | 101185 | 100 | 3000 | 19.9506 | 75.1841 | 47.0678 | 0 | 7.2692 | FALSE | FALSE
2025-11-04 08:00 | 26.45 | 59.5 | 101250 | 100 | 3000 | 21.1638 | 69.1917 | 50.1458 | 0 | 7.2692 | FALSE | FALSE
2025-11-04 09:00 | 28.95 | 50.5 | 101305 | 100 | 3000 | 22.1497 | 64.4299 | 52.2067 | 0 | 7.2692 | FALSE | FALSE
2025-11-04 10:00 | 30.55 | 43.5 | 101300 | 100 | 3000 | 22.7754 | 60.1841 | 51.4248 | 0 | 7.2692 | FALSE | FALSE
2025-11-04 11:00 | 32.1 | 35.5 | 101215 | 100 | 3000 | 23.3829 | 54.8132 | 48.409 | 0 | 7.2692 | FALSE | FALSE
2025-11-04 12:00 | 33.35 | 31 | 101120 | 100 | 3000 | 23.8632 | 51.6547 | 47.3664 | 0 | 7.2692 | FALSE | FALSE
2025-11-04 13:00 | 34.45 | 26.5 | 101030 | 100 | 3000 | 24.2874 | 48.272 | 45.3175 | 0 | 7.2692 | FALSE | FALSE
2025-11-04 14:00 | 34.65 | 24 | 100975 | 100 | 3000 | 24.3741 | 46.2822 | 42.784 | 0 | 7.2692 | FALSE | FALSE
2025-11-04 15:00 | 33 | 35.5 | 100960 | 100 | 3000 | 23.7137 | 55.0593 | 51.3707 | 0 | 7.2692 | FALSE | FALSE
2025-11-04 16:00 | 31.1 | 50 | 100950 | 100 | 3000 | 22.9564 | 65.1013 | 60.0715 | 0 | 7.2692 | FALSE | FALSE
2025-11-04 17:00 | 29.8 | 55 | 100975 | 100 | 3000 | 22.4571 | 67.9444 | 59.8003 | 0 | 7.2692 | FALSE | FALSE
2025-11-04 18:00 | 28.85 | 54.5 | 101025 | 100 | 3000 | 22.1007 | 67.1068 | 55.4734 | 0 | 7.2692 | FALSE | FALSE
2025-11-04 19:00 | 28.1 | 51 | 101075 | 100 | 3000 | 21.8228 | 64.4518 | 49.3511 | 0 | 7.2692 | FALSE | FALSE
2025-11-04 20:00 | 27.1 | 45 | 101120 | 100 | 3000 | 21.4469 | 60.2705 | 40.4114 | 0 | 7.2692 | FALSE | FALSE
2025-11-04 21:00 | 26.15 | 38.5 | 101150 | 100 | 3000 | 21.0824 | 56.0622 | 31.7292 | 0 | 7.2692 | FALSE | FALSE
2025-11-04 22:00 | 25.5 | 36.5 | 101145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-04 23:00 | 24.8 | 38.5 | 101120 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-05 | 24.15 | 39 | 101095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-05 01:00 | 23.55 | 37.5 | 101050 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-05 02:00 | 22.95 | 37 | 101015 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-05 03:00 | 22.75 | 36 | 101025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-05 04:00 | 22.8 | 36 | 101035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-05 05:00 | 22.35 | 40 | 101060 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-05 06:00 | 21.9 | 44 | 101120 | 100 | 3000 | 19.3347 | 59.3268 | 22.9116 | 0 | 7.2692 | FALSE | FALSE
2025-11-05 07:00 | 23.15 | 42 | 101175 | 100 | 3000 | 19.857 | 58.1423 | 24.7058 | 0 | 7.2692 | FALSE | FALSE
2025-11-05 08:00 | 25.95 | 35.5 | 101215 | 100 | 3000 | 21.0072 | 54.1982 | 28.6376 | 0 | 7.2692 | FALSE | FALSE
2025-11-05 09:00 | 28.85 | 29.5 | 101255 | 100 | 3000 | 22.1678 | 50.2313 | 32.4375 | 0 | 7.2692 | FALSE | FALSE
2025-11-05 10:00 | 31.35 | 24.5 | 101255 | 100 | 3000 | 23.1454 | 46.6258 | 35.6107 | 0 | 7.2692 | FALSE | FALSE
2025-11-05 11:00 | 33.3 | 19 | 101185 | 100 | 3000 | 23.9028 | 42.3472 | 38.0285 | 0 | 7.2692 | FALSE | FALSE
2025-11-05 12:00 | 34.45 | 15.5 | 101090 | 100 | 3000 | 24.3482 | 39.4434 | 39.4223 | 0 | 7.2692 | FALSE | FALSE
2025-11-05 13:00 | 34.7 | 16.5 | 100995 | 100 | 3000 | 24.435 | 40.2213 | 39.6415 | 0 | 7.2692 | FALSE | FALSE
2025-11-05 14:00 | 34 | 20.5 | 100930 | 100 | 3000 | 24.1552 | 43.4879 | 38.7009 | 0 | 7.2692 | FALSE | FALSE
2025-11-05 15:00 | 32.65 | 28 | 100910 | 100 | 3000 | 23.6193 | 49.2826 | 41.727 | 0 | 7.2692 | FALSE | FALSE
2025-11-05 16:00 | 30.95 | 40 | 100915 | 100 | 3000 | 22.9375 | 57.842 | 49.2005 | 0 | 7.2692 | FALSE | FALSE
2025-11-05 17:00 | 29.1 | 51 | 100925 | 100 | 3000 | 22.2053 | 64.8672 | 53.1878 | 0 | 7.2692 | FALSE | FALSE
2025-11-05 18:00 | 27.8 | 59 | 100945 | 100 | 3000 | 21.6885 | 69.5613 | 55.2194 | 0 | 7.2692 | FALSE | FALSE
2025-11-05 19:00 | 26.95 | 65 | 100990 | 100 | 3000 | 21.3478 | 72.9328 | 56.7702 | 0 | 7.2692 | FALSE | FALSE
2025-11-05 20:00 | 25.9 | 66.5 | 101045 | 100 | 3000 | 20.9357 | 73.2593 | 53.479 | 0 | 7.2692 | FALSE | FALSE
2025-11-05 21:00 | 24.85 | 64.5 | 101090 | 100 | 3000 | 20.5228 | 71.5203 | 47.4943 | 0 | 7.2692 | FALSE | FALSE
2025-11-05 22:00 | 24.2 | 63.5 | 101100 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-05 23:00 | 23.55 | 65.5 | 101070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-06 | 22.65 | 66 | 101045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-06 01:00 | 21.8 | 61.5 | 101020 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-06 02:00 | 21.05 | 56 | 100985 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-06 03:00 | 20.75 | 58.5 | 100975 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-06 04:00 | 20.95 | 65 | 100975 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-06 05:00 | 20.8 | 68.5 | 100995 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-06 06:00 | 20.45 | 68.5 | 101055 | 100 | 3000 | 18.7113 | 72.1722 | 32.3191 | 0 | 7.2692 | FALSE | FALSE
2025-11-06 07:00 | 21.75 | 59.5 | 101120 | 100 | 3000 | 19.2616 | 67.7045 | 31.6909 | 0 | 7.2692 | FALSE | FALSE
2025-11-06 08:00 | 24.8 | 46.5 | 101175 | 100 | 3000 | 20.5272 | 60.814 | 33.5697 | 0 | 7.2692 | FALSE | FALSE
2025-11-06 09:00 | 27.85 | 40.5 | 101225 | 100 | 3000 | 21.7505 | 57.4865 | 39.0777 | 0 | 7.2692 | FALSE | FALSE
2025-11-06 10:00 | 30.35 | 31.5 | 101215 | 100 | 3000 | 22.7402 | 51.6469 | 38.5839 | 0 | 7.2692 | FALSE | FALSE
2025-11-06 11:00 | 32.25 | 19.5 | 101135 | 100 | 3000 | 23.5063 | 42.8565 | 36.7586 | 0 | 7.2692 | FALSE | FALSE
2025-11-06 12:00 | 33.4 | 15 | 101035 | 100 | 3000 | 23.9597 | 39.2392 | 38.1957 | 0 | 7.2692 | FALSE | FALSE
2025-11-06 13:00 | 33.7 | 17 | 100955 | 100 | 3000 | 24.062 | 40.7569 | 38.4624 | 0 | 7.2692 | FALSE | FALSE
2025-11-06 14:00 | 32.85 | 27 | 100910 | 100 | 3000 | 23.6981 | 48.5355 | 41.1785 | 0 | 7.2692 | FALSE | FALSE
2025-11-06 15:00 | 31.35 | 34 | 100895 | 100 | 3000 | 23.1096 | 53.588 | 44.2639 | 0 | 7.2692 | FALSE | FALSE
2025-11-06 16:00 | 29.9 | 40 | 100910 | 100 | 3000 | 22.5417 | 57.5729 | 45.553 | 0 | 7.2692 | FALSE | FALSE
2025-11-06 17:00 | 28.5 | 50 | 100935 | 100 | 3000 | 21.9791 | 63.9538 | 49.9526 | 0 | 7.2692 | FALSE | FALSE
2025-11-06 18:00 | 27.45 | 55 | 100980 | 100 | 3000 | 21.5624 | 66.8049 | 50.3244 | 0 | 7.2692 | FALSE | FALSE
2025-11-06 19:00 | 26.6 | 57 | 101045 | 100 | 3000 | 21.2272 | 67.7144 | 48.6543 | 0 | 7.2692 | FALSE | FALSE
2025-11-06 20:00 | 25.65 | 58.5 | 101095 | 100 | 3000 | 20.8501 | 68.2544 | 46.0944 | 0 | 7.2692 | FALSE | FALSE
2025-11-06 21:00 | 24.65 | 58.5 | 101120 | 100 | 3000 | 20.4507 | 67.8909 | 42.1477 | 0 | 7.2692 | FALSE | FALSE
2025-11-06 22:00 | 23.85 | 54.5 | 101120 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-06 23:00 | 23.1 | 52.5 | 101105 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-07 | 22.2 | 55.5 | 101090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-07 01:00 | 21.55 | 57 | 101075 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-07 02:00 | 21.05 | 57 | 101060 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-07 03:00 | 20.35 | 57.5 | 101060 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-07 04:00 | 19.85 | 59 | 101070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-07 05:00 | 19.45 | 61 | 101095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-07 06:00 | 18.95 | 61 | 101160 | 100 | 3000 | 18.0736 | 68.1551 | 22.1759 | 0 | 7.2692 | FALSE | FALSE
2025-11-07 07:00 | 20.15 | 53 | 101235 | 100 | 3000 | 18.5901 | 64.1388 | 21.7945 | 0 | 7.2692 | FALSE | FALSE
2025-11-07 08:00 | 23.25 | 40 | 101300 | 100 | 3000 | 19.9003 | 56.9908 | 24.8896 | 0 | 7.2692 | FALSE | FALSE
2025-11-07 09:00 | 26.35 | 33.5 | 101365 | 100 | 3000 | 21.1711 | 52.9237 | 29.1865 | 0 | 7.2692 | FALSE | FALSE
2025-11-07 10:00 | 28.55 | 27.5 | 101380 | 100 | 3000 | 22.0556 | 48.8911 | 32.127 | 0 | 7.2692 | FALSE | FALSE
2025-11-07 11:00 | 30.15 | 20 | 101315 | 100 | 3000 | 22.7005 | 43.532 | 34.248 | 0 | 7.2692 | FALSE | FALSE
2025-11-07 12:00 | 31.4 | 17 | 101230 | 100 | 3000 | 23.1926 | 41.139 | 35.8214 | 0 | 7.2692 | FALSE | FALSE
2025-11-07 13:00 | 32.2 | 15 | 101170 | 100 | 3000 | 23.5061 | 39.4855 | 36.8159 | 0 | 7.2692 | FALSE | FALSE
2025-11-07 14:00 | 32.5 | 13.5 | 101125 | 100 | 3000 | 23.6266 | 38.2857 | 37.1964 | 0 | 7.2692 | FALSE | FALSE
2025-11-07 15:00 | 32.25 | 16.5 | 101090 | 100 | 3000 | 23.5189 | 40.6075 | 36.8126 | 0 | 7.2692 | FALSE | FALSE
2025-11-07 16:00 | 31.1 | 25 | 101085 | 100 | 3000 | 23.0486 | 47.0156 | 35.2399 | 0 | 7.2692 | FALSE | FALSE
2025-11-07 17:00 | 29.1 | 36 | 101115 | 100 | 3000 | 22.2472 | 54.6618 | 39.0431 | 0 | 7.2692 | FALSE | FALSE
2025-11-07 18:00 | 27.6 | 45 | 101180 | 100 | 3000 | 21.6427 | 60.3733 | 42.194 | 0 | 7.2692 | FALSE | FALSE
2025-11-07 19:00 | 26.75 | 51.5 | 101255 | 100 | 3000 | 21.2965 | 64.2901 | 44.6749 | 0 | 7.2692 | FALSE | FALSE
2025-11-07 20:00 | 25.9 | 56 | 101300 | 100 | 3000 | 20.9533 | 66.7991 | 45.1132 | 0 | 7.2692 | FALSE | FALSE
2025-11-07 21:00 | 25 | 56.5 | 101310 | 100 | 3000 | 20.594 | 66.7982 | 42.0096 | 0 | 7.2692 | FALSE | FALSE
2025-11-07 22:00 | 24.15 | 52 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-07 23:00 | 23.15 | 47 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-08 | 22.1 | 47 | 101305 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-08 01:00 | 21.35 | 49.5 | 101290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-08 02:00 | 20.75 | 51 | 101275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-08 03:00 | 19.9 | 50.5 | 101285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-08 04:00 | 19.25 | 48 | 101305 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-08 05:00 | 19 | 45 | 101325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-08 06:00 | 18.85 | 42.5 | 101375 | 100 | 3000 | 18.0338 | 59.0103 | 18.4621 | 0 | 7.2692 | FALSE | FALSE
2025-11-08 07:00 | 20.15 | 37 | 101445 | 100 | 3000 | 18.5959 | 55.888 | 20.452 | 0 | 7.2692 | FALSE | FALSE
2025-11-08 08:00 | 23.3 | 28.5 | 101505 | 100 | 3000 | 19.9319 | 50.4235 | 25.0881 | 0 | 7.2692 | FALSE | FALSE
2025-11-08 09:00 | 26.45 | 24 | 101560 | 100 | 3000 | 21.2281 | 46.9343 | 29.4814 | 0 | 7.2692 | FALSE | FALSE
2025-11-08 10:00 | 28.7 | 22 | 101570 | 100 | 3000 | 22.1284 | 45.158 | 32.4617 | 0 | 7.2692 | FALSE | FALSE
2025-11-08 11:00 | 30.4 | 18.5 | 101515 | 100 | 3000 | 22.802 | 42.4044 | 34.6544 | 0 | 7.2692 | FALSE | FALSE
2025-11-08 12:00 | 31.6 | 16.5 | 101440 | 100 | 3000 | 23.2709 | 40.7113 | 36.1496 | 0 | 7.2692 | FALSE | FALSE
2025-11-08 13:00 | 32.25 | 15.5 | 101370 | 100 | 3000 | 23.5228 | 39.8326 | 36.936 | 0 | 7.2692 | FALSE | FALSE
2025-11-08 14:00 | 32.15 | 17 | 101315 | 100 | 3000 | 23.4786 | 40.9825 | 36.7611 | 0 | 7.2692 | FALSE | FALSE
2025-11-08 15:00 | 31.2 | 23 | 101300 | 100 | 3000 | 23.0938 | 45.5389 | 35.4764 | 0 | 7.2692 | FALSE | FALSE
2025-11-08 16:00 | 29.65 | 33 | 101300 | 100 | 3000 | 22.4675 | 52.638 | 37.9268 | 0 | 7.2692 | FALSE | FALSE
2025-11-08 17:00 | 28.1 | 46.5 | 101305 | 100 | 3000 | 21.8336 | 61.4693 | 45.3509 | 0 | 7.2692 | FALSE | FALSE
2025-11-08 18:00 | 27.1 | 53 | 101335 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-08 19:00 | 26.4 | 52.5 | 101380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-08 20:00 | 25.4 | 53 | 101420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-08 21:00 | 24.25 | 54 | 101425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-08 22:00 | 23.3 | 56.5 | 101410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-08 23:00 | 22.55 | 58.5 | 101390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 | 21.65 | 60.5 | 101365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 01:00 | 20.75 | 61.5 | 101340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 02:00 | 20.05 | 61 | 101325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 03:00 | 19.65 | 59 | 101335 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 04:00 | 19.45 | 57.5 | 101350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 05:00 | 19.25 | 59 | 101370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 06:00 | 19.2 | 59.5 | 101420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 07:00 | 20.45 | 55 | 101465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 08:00 | 23.65 | 46.5 | 101500 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 09:00 | 26.95 | 42.5 | 101540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 10:00 | 29.1 | 42 | 101525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 11:00 | 30.5 | 38 | 101435 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 12:00 | 31.2 | 34.5 | 101340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 13:00 | 31.2 | 33.5 | 101270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 14:00 | 30.85 | 33.5 | 101220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 15:00 | 30.4 | 35 | 101185 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 16:00 | 29.75 | 37 | 101170 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 17:00 | 28.7 | 39.5 | 101185 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 18:00 | 27.7 | 42.5 | 101215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 19:00 | 26.95 | 46.5 | 101250 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 20:00 | 26.3 | 51 | 101295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 21:00 | 25.55 | 54.5 | 101315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 22:00 | 25.05 | 56.5 | 101300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-09 23:00 | 24.8 | 58 | 101270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-10 | 24.4 | 59 | 101240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-10 01:00 | 24.05 | 59.5 | 101230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-10 02:00 | 23.75 | 60 | 101210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-10 03:00 | 23.25 | 59.5 | 101185 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-10 04:00 | 22.35 | 61 | 101185 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-10 05:00 | 21.15 | 65 | 101220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-10 06:00 | 20 | 69.5 | 101280 | 100 | 3000 | 18.5204 | 72.5473 | 31.1405 | 0 | 7.2692 | FALSE | FALSE
2025-11-10 07:00 | 20.75 | 66.5 | 101325 | 100 | 3000 | 18.8386 | 71.1783 | 32.2985 | 0 | 7.2692 | FALSE | FALSE
2025-11-10 08:00 | 24.1 | 54.5 | 101350 | 100 | 3000 | 20.2334 | 65.3718 | 37.0821 | 0 | 7.2692 | FALSE | FALSE
2025-11-10 09:00 | 27.35 | 44 | 101385 | 100 | 3000 | 21.5471 | 59.654 | 40.4685 | 0 | 7.2692 | FALSE | FALSE
2025-11-10 10:00 | 29.1 | 38 | 101380 | 100 | 3000 | 22.2415 | 55.9971 | 40.9945 | 0 | 7.2692 | FALSE | FALSE
2025-11-10 11:00 | 30.1 | 34 | 101295 | 100 | 3000 | 22.6367 | 53.3776 | 40.3357 | 0 | 7.2692 | FALSE | FALSE
2025-11-10 12:00 | 30.8 | 31 | 101195 | 100 | 3000 | 22.9131 | 51.3256 | 39.4494 | 0 | 7.2692 | FALSE | FALSE
2025-11-10 13:00 | 31.15 | 30.5 | 101115 | 100 | 3000 | 23.0474 | 50.9996 | 39.9815 | 0 | 7.2692 | FALSE | FALSE
2025-11-10 14:00 | 30.75 | 33 | 101065 | 100 | 3000 | 22.8872 | 52.7654 | 41.3364 | 0 | 7.2692 | FALSE | FALSE
2025-11-10 15:00 | 29.65 | 39 | 101045 | 100 | 3000 | 22.4496 | 56.8121 | 43.7438 | 0 | 7.2692 | FALSE | FALSE
2025-11-10 16:00 | 28.8 | 44.5 | 101030 | 100 | 3000 | 22.1086 | 60.3613 | 46.0088 | 0 | 7.2692 | FALSE | FALSE
2025-11-10 17:00 | 28.2 | 47.5 | 101035 | 100 | 3000 | 21.8699 | 62.1842 | 46.5736 | 0 | 7.2692 | FALSE | FALSE
2025-11-10 18:00 | 27.5 | 49 | 101075 | 100 | 3000 | 21.595 | 62.9449 | 45.3178 | 0 | 7.2692 | FALSE | FALSE
2025-11-10 19:00 | 26.7 | 50.5 | 101130 | 100 | 3000 | 21.2788 | 63.6572 | 43.6287 | 0 | 7.2692 | FALSE | FALSE
2025-11-10 20:00 | 25.85 | 54 | 101175 | 100 | 3000 | 20.9367 | 65.5686 | 43.2957 | 0 | 7.2692 | FALSE | FALSE
2025-11-10 21:00 | 25.2 | 58 | 101195 | 100 | 3000 | 20.6718 | 67.7746 | 43.9343 | 0 | 7.2692 | FALSE | FALSE
2025-11-10 22:00 | 24.5 | 62 | 101195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-10 23:00 | 23.7 | 66.5 | 101175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-11 | 22.85 | 71.5 | 101155 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-11 01:00 | 21.85 | 77 | 101160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-11 02:00 | 20.6 | 83.5 | 101165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-11 03:00 | 19.75 | 86 | 101170 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-11 04:00 | 19.7 | 84 | 101180 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-11 05:00 | 19.75 | 82 | 101210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-11 06:00 | 19.75 | 79.5 | 101275 | 100 | 3000 | 18.4111 | 77.5305 | 36.0054 | 0 | 7.2692 | FALSE | FALSE
2025-11-11 07:00 | 21 | 71.5 | 101330 | 100 | 3000 | 18.9412 | 73.8647 | 36.4194 | 0 | 7.2692 | FALSE | FALSE
2025-11-11 08:00 | 24.05 | 58 | 101375 | 100 | 3000 | 20.2091 | 67.3851 | 39.4699 | 0 | 7.2692 | FALSE | FALSE
2025-11-11 09:00 | 27.25 | 47.5 | 101410 | 100 | 3000 | 21.5005 | 61.8762 | 43.1486 | 0 | 7.2692 | FALSE | FALSE
2025-11-11 10:00 | 29.3 | 38 | 101390 | 100 | 3000 | 22.3184 | 56.0282 | 41.663 | 0 | 7.2692 | FALSE | FALSE
2025-11-11 11:00 | 30.5 | 29.5 | 101300 | 100 | 3000 | 22.8041 | 50.2288 | 37.0165 | 0 | 7.2692 | FALSE | FALSE
2025-11-11 12:00 | 31.3 | 26 | 101195 | 100 | 3000 | 23.1208 | 47.7267 | 35.6662 | 0 | 7.2692 | FALSE | FALSE
2025-11-11 13:00 | 31.7 | 26 | 101120 | 100 | 3000 | 23.2721 | 47.7303 | 36.7877 | 0 | 7.2692 | FALSE | FALSE
2025-11-11 14:00 | 31.25 | 32.5 | 101070 | 100 | 3000 | 23.0777 | 52.4658 | 42.3938 | 0 | 7.2692 | FALSE | FALSE
2025-11-11 15:00 | 30.1 | 41 | 101055 | 100 | 3000 | 22.6143 | 58.3077 | 47.2647 | 0 | 7.2692 | FALSE | FALSE
2025-11-11 16:00 | 29.1 | 46 | 101065 | 100 | 3000 | 22.2193 | 61.4616 | 48.5115 | 0 | 7.2692 | FALSE | FALSE
2025-11-11 17:00 | 28.35 | 48 | 101090 | 100 | 3000 | 21.9265 | 62.5573 | 47.592 | 0 | 7.2692 | FALSE | FALSE
2025-11-11 18:00 | 27.6 | 49.5 | 101150 | 100 | 3000 | 21.6328 | 63.2921 | 46.1401 | 0 | 7.2692 | FALSE | FALSE
2025-11-11 19:00 | 26.8 | 53 | 101215 | 100 | 3000 | 21.3132 | 65.2571 | 46.1202 | 0 | 7.2692 | FALSE | FALSE
2025-11-11 20:00 | 25.85 | 57 | 101255 | 100 | 3000 | 20.9318 | 67.3985 | 45.7133 | 0 | 7.2692 | FALSE | FALSE
2025-11-11 21:00 | 24.9 | 61.5 | 101280 | 100 | 3000 | 20.547 | 69.7419 | 45.4404 | 0 | 7.2692 | FALSE | FALSE
2025-11-11 22:00 | 24.1 | 65.5 | 101280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-11 23:00 | 23.1 | 69 | 101260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-12 | 21.75 | 72.5 | 101245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-12 01:00 | 20.55 | 73.5 | 101245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-12 02:00 | 19.8 | 73 | 101255 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-12 03:00 | 19.35 | 69.5 | 101270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-12 04:00 | 18.9 | 67.5 | 101290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-12 05:00 | 18.45 | 70 | 101330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-12 06:00 | 18.35 | 71 | 101390 | 100 | 3000 | 17.8131 | 72.9469 | 25.466 | 0 | 7.2692 | FALSE | FALSE
2025-11-12 07:00 | 19.7 | 65.5 | 101450 | 100 | 3000 | 18.3941 | 70.4412 | 27.6081 | 0 | 7.2692 | FALSE | FALSE
2025-11-12 08:00 | 22.85 | 53.5 | 101505 | 100 | 3000 | 19.7226 | 64.5523 | 31.7669 | 0 | 7.2692 | FALSE | FALSE
2025-11-12 09:00 | 26.3 | 42 | 101550 | 100 | 3000 | 21.136 | 58.2102 | 35.1787 | 0 | 7.2692 | FALSE | FALSE
2025-11-12 10:00 | 28.9 | 32 | 101545 | 100 | 3000 | 22.1804 | 51.8945 | 34.6911 | 0 | 7.2692 | FALSE | FALSE
2025-11-12 11:00 | 30.5 | 24.5 | 101485 | 100 | 3000 | 22.8207 | 46.6568 | 34.6544 | 0 | 7.2692 | FALSE | FALSE
2025-11-12 12:00 | 31.55 | 20 | 101415 | 100 | 3000 | 23.2384 | 43.2972 | 36.0043 | 0 | 7.2692 | FALSE | FALSE
2025-11-12 13:00 | 32.15 | 18 | 101355 | 100 | 3000 | 23.4745 | 41.7278 | 36.7522 | 0 | 7.2692 | FALSE | FALSE
2025-11-12 14:00 | 31.6 | 24 | 101315 | 100 | 3000 | 23.242 | 46.2424 | 35.943 | 0 | 7.2692 | FALSE | FALSE
2025-11-12 15:00 | 30.15 | 34 | 101290 | 100 | 3000 | 22.6558 | 53.3838 | 40.4941 | 0 | 7.2692 | FALSE | FALSE
2025-11-12 16:00 | 29.05 | 43 | 101290 | 100 | 3000 | 22.2085 | 59.3903 | 45.5419 | 0 | 7.2692 | FALSE | FALSE
2025-11-12 17:00 | 28.2 | 47 | 101325 | 100 | 3000 | 21.8711 | 61.8261 | 46.1711 | 0 | 7.2692 | FALSE | FALSE
2025-11-12 18:00 | 27.3 | 52 | 101380 | 100 | 3000 | 21.5106 | 64.7796 | 47.2126 | 0 | 7.2692 | FALSE | FALSE
2025-11-12 19:00 | 26.55 | 61.5 | 101435 | 100 | 3000 | 21.1992 | 70.4695 | 52.2319 | 0 | 7.2692 | FALSE | FALSE
2025-11-12 20:00 | 25.75 | 67 | 101470 | 100 | 3000 | 20.876 | 73.4377 | 53.2887 | 0 | 7.2692 | FALSE | FALSE
2025-11-12 21:00 | 25 | 68.5 | 101480 | 100 | 3000 | 20.5771 | 73.9291 | 51.2205 | 0 | 7.2692 | FALSE | FALSE
2025-11-12 22:00 | 24.4 | 69 | 101470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-12 23:00 | 23.85 | 71 | 101460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-13 | 22.9 | 74 | 101465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-13 01:00 | 21.65 | 74.5 | 101465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-13 02:00 | 20.85 | 71 | 101470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-13 03:00 | 20.5 | 67 | 101480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-13 04:00 | 20.1 | 66 | 101490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-13 05:00 | 19.3 | 68.5 | 101525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-13 06:00 | 18.7 | 70 | 101590 | 100 | 3000 | 17.9643 | 72.4944 | 26.2973 | 0 | 7.2692 | FALSE | FALSE
2025-11-13 07:00 | 20 | 63.5 | 101650 | 100 | 3000 | 18.5225 | 69.4501 | 27.5849 | 0 | 7.2692 | FALSE | FALSE
2025-11-13 08:00 | 23.45 | 50.5 | 101695 | 100 | 3000 | 19.9723 | 62.921 | 31.8356 | 0 | 7.2692 | FALSE | FALSE
2025-11-13 09:00 | 26.75 | 44.5 | 101740 | 100 | 3000 | 21.3099 | 59.8247 | 38.8489 | 0 | 7.2692 | FALSE | FALSE
2025-11-13 10:00 | 28.75 | 44 | 101725 | 100 | 3000 | 22.0906 | 59.9454 | 45.4869 | 0 | 7.2692 | FALSE | FALSE
2025-11-13 11:00 | 30.05 | 39.5 | 101630 | 100 | 3000 | 22.6001 | 57.1918 | 45.7134 | 0 | 7.2692 | FALSE | FALSE
2025-11-13 12:00 | 30.9 | 35 | 101530 | 100 | 3000 | 22.9366 | 54.1795 | 43.9814 | 0 | 7.2692 | FALSE | FALSE
2025-11-13 13:00 | 31.1 | 36.5 | 101450 | 100 | 3000 | 23.0064 | 55.3061 | 46.1871 | 0 | 7.2692 | FALSE | FALSE
2025-11-13 14:00 | 30.6 | 40 | 101400 | 100 | 3000 | 22.8062 | 57.7021 | 48.0757 | 0 | 7.2692 | FALSE | FALSE
2025-11-13 15:00 | 29.9 | 40 | 101370 | 100 | 3000 | 22.5416 | 57.5302 | 45.6406 | 0 | 7.2692 | FALSE | FALSE
2025-11-13 16:00 | 29.2 | 41.5 | 101365 | 100 | 3000 | 22.2702 | 58.4004 | 44.6617 | 0 | 7.2692 | FALSE | FALSE
2025-11-13 17:00 | 28.2 | 44.5 | 101385 | 100 | 3000 | 21.8771 | 60.1697 | 43.9204 | 0 | 7.2692 | FALSE | FALSE
2025-11-13 18:00 | 27.15 | 46.5 | 101410 | 100 | 3000 | 21.4634 | 61.2112 | 41.9245 | 0 | 7.2692 | FALSE | FALSE
2025-11-13 19:00 | 26.15 | 50.5 | 101455 | 100 | 3000 | 21.0616 | 63.4714 | 41.6295 | 0 | 7.2692 | FALSE | FALSE
2025-11-13 20:00 | 25.05 | 56.5 | 101490 | 100 | 3000 | 20.614 | 66.7955 | 42.2262 | 0 | 7.2692 | FALSE | FALSE
2025-11-13 21:00 | 24 | 62.5 | 101490 | 100 | 3000 | 20.1836 | 69.9586 | 42.5789 | 0 | 7.2692 | FALSE | FALSE
2025-11-13 22:00 | 23.3 | 67 | 101470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-13 23:00 | 22.9 | 70 | 101450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-14 | 22.45 | 72.5 | 101435 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-14 01:00 | 21.7 | 77 | 101425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-14 02:00 | 20.7 | 81.5 | 101415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-14 03:00 | 19.85 | 81.5 | 101415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-14 04:00 | 19.4 | 79 | 101415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-14 05:00 | 19.1 | 77 | 101425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-14 06:00 | 18.75 | 75 | 101470 | 100 | 3000 | 17.985 | 74.9607 | 29.2754 | 0 | 7.2692 | FALSE | FALSE
2025-11-14 07:00 | 19.85 | 67.5 | 101520 | 100 | 3000 | 18.4573 | 71.4711 | 29.3741 | 0 | 7.2692 | FALSE | FALSE
2025-11-14 08:00 | 23.1 | 54 | 101565 | 100 | 3000 | 19.8252 | 64.865 | 33.0367 | 0 | 7.2692 | FALSE | FALSE
2025-11-14 09:00 | 26.45 | 45 | 101615 | 100 | 3000 | 21.1902 | 60.0983 | 38.1979 | 0 | 7.2692 | FALSE | FALSE
2025-11-14 10:00 | 28.7 | 38.5 | 101605 | 100 | 3000 | 22.0857 | 56.2526 | 40.1723 | 0 | 7.2692 | FALSE | FALSE
2025-11-14 11:00 | 30.25 | 30 | 101525 | 100 | 3000 | 22.7068 | 50.5541 | 36.8209 | 0 | 7.2692 | FALSE | FALSE
2025-11-14 12:00 | 31.1 | 26 | 101440 | 100 | 3000 | 23.0447 | 47.7085 | 35.3414 | 0 | 7.2692 | FALSE | FALSE
2025-11-14 13:00 | 31.2 | 27.5 | 101370 | 100 | 3000 | 23.0772 | 48.8024 | 37.0112 | 0 | 7.2692 | FALSE | FALSE
2025-11-14 14:00 | 30.7 | 30.5 | 101330 | 100 | 3000 | 22.8768 | 50.9485 | 38.6539 | 0 | 7.2692 | FALSE | FALSE
2025-11-14 15:00 | 29.8 | 35 | 101305 | 100 | 3000 | 22.519 | 54.0395 | 40.3695 | 0 | 7.2692 | FALSE | FALSE
2025-11-14 16:00 | 29.1 | 38.5 | 101290 | 100 | 3000 | 22.2402 | 56.3454 | 41.4534 | 0 | 7.2692 | FALSE | FALSE
2025-11-14 17:00 | 28.25 | 40 | 101290 | 100 | 3000 | 21.9075 | 57.2133 | 39.9895 | 0 | 7.2692 | FALSE | FALSE
2025-11-14 18:00 | 27.05 | 42.5 | 101310 | 100 | 3000 | 21.4323 | 58.6478 | 38.1188 | 0 | 7.2692 | FALSE | FALSE
2025-11-14 19:00 | 26.1 | 45 | 101360 | 100 | 3000 | 21.0512 | 60.0658 | 36.9364 | 0 | 7.2692 | FALSE | FALSE
2025-11-14 20:00 | 25.25 | 47.5 | 101410 | 100 | 3000 | 20.7072 | 61.4518 | 35.9575 | 0 | 7.2692 | FALSE | FALSE
2025-11-14 21:00 | 24.2 | 50.5 | 101425 | 100 | 3000 | 20.2787 | 63.0572 | 34.4961 | 0 | 7.2692 | FALSE | FALSE
2025-11-14 22:00 | 23.1 | 55 | 101415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-14 23:00 | 22.1 | 60.5 | 101385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-15 | 21.2 | 65 | 101350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-15 01:00 | 20.5 | 68 | 101330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-15 02:00 | 19.9 | 70 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-15 03:00 | 19.45 | 69.5 | 101315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-15 04:00 | 19.05 | 68.5 | 101330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-15 05:00 | 18.55 | 69.5 | 101355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-15 06:00 | 18.3 | 69.5 | 101410 | 100 | 3000 | 17.7916 | 72.2135 | 24.4526 | 0 | 7.2692 | FALSE | FALSE
2025-11-15 07:00 | 19.65 | 63.5 | 101480 | 100 | 3000 | 18.3733 | 69.4222 | 26.2447 | 0 | 7.2692 | FALSE | FALSE
2025-11-15 08:00 | 22.95 | 52 | 101550 | 100 | 3000 | 19.7652 | 63.7218 | 31.0893 | 0 | 7.2692 | FALSE | FALSE
2025-11-15 09:00 | 26.4 | 44 | 101600 | 100 | 3000 | 21.1722 | 59.4664 | 37.189 | 0 | 7.2692 | FALSE | FALSE
2025-11-15 10:00 | 28.7 | 38 | 101585 | 100 | 3000 | 22.087 | 55.9187 | 39.7024 | 0 | 7.2692 | FALSE | FALSE
2025-11-15 11:00 | 29.95 | 31.5 | 101505 | 100 | 3000 | 22.5871 | 51.5955 | 37.4119 | 0 | 7.2692 | FALSE | FALSE
2025-11-15 12:00 | 30.65 | 28.5 | 101410 | 100 | 3000 | 22.8646 | 49.5102 | 36.4551 | 0 | 7.2692 | FALSE | FALSE
2025-11-15 13:00 | 30.8 | 28.5 | 101320 | 100 | 3000 | 22.9218 | 49.5212 | 36.8789 | 0 | 7.2692 | FALSE | FALSE
2025-11-15 14:00 | 30.35 | 30 | 101275 | 100 | 3000 | 22.7451 | 50.5803 | 37.0722 | 0 | 7.2692 | FALSE | FALSE
2025-11-15 15:00 | 29.6 | 33.5 | 101255 | 100 | 3000 | 22.4468 | 52.9841 | 38.2512 | 0 | 7.2692 | FALSE | FALSE
2025-11-15 16:00 | 28.85 | 39.5 | 101265 | 100 | 3000 | 22.1411 | 56.9821 | 41.5514 | 0 | 7.2692 | FALSE | FALSE
2025-11-15 17:00 | 27.9 | 43 | 101305 | 100 | 3000 | 21.7642 | 59.1233 | 41.4981 | 0 | 7.2692 | FALSE | FALSE
2025-11-15 18:00 | 26.95 | 43 | 101335 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-15 19:00 | 26.1 | 44 | 101380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-15 20:00 | 25.2 | 46.5 | 101435 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-15 21:00 | 24.1 | 50.5 | 101480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-15 22:00 | 22.95 | 55 | 101510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-15 23:00 | 22.1 | 58.5 | 101500 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 | 21.4 | 61 | 101470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 01:00 | 20.7 | 64 | 101450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 02:00 | 19.95 | 67 | 101445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 03:00 | 19.55 | 66 | 101450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 04:00 | 19.4 | 64.5 | 101460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 05:00 | 19.25 | 66.5 | 101490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 06:00 | 19.35 | 69.5 | 101550 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 07:00 | 20.7 | 67 | 101625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 08:00 | 23.65 | 57 | 101695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 09:00 | 26.95 | 44 | 101755 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 10:00 | 29.25 | 33 | 101750 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 11:00 | 30.45 | 27 | 101675 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 12:00 | 31.2 | 24 | 101580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 13:00 | 31.65 | 22.5 | 101510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 14:00 | 31.45 | 24.5 | 101475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 15:00 | 30.3 | 33 | 101470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 16:00 | 28.85 | 41.5 | 101500 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 17:00 | 27.7 | 45.5 | 101535 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 18:00 | 26.9 | 47.5 | 101580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 19:00 | 26 | 50.5 | 101635 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 20:00 | 25.1 | 54 | 101675 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 21:00 | 24.35 | 58 | 101700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 22:00 | 23.75 | 61 | 101705 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-16 23:00 | 23.25 | 62 | 101675 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-17 | 22.35 | 65 | 101640 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-17 01:00 | 21.2 | 69.5 | 101625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-17 02:00 | 20.15 | 74 | 101615 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-17 03:00 | 19.3 | 77.5 | 101600 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-17 04:00 | 19.05 | 79 | 101595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-17 05:00 | 18.9 | 82 | 101625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-17 06:00 | 18.55 | 86 | 101680 | 100 | 3000 | 17.8974 | 80.2191 | 34.513 | 0 | 7.2692 | FALSE | FALSE
2025-11-17 07:00 | 19.75 | 81 | 101740 | 100 | 3000 | 18.4106 | 78.2314 | 36.9069 | 0 | 7.2692 | FALSE | FALSE
2025-11-17 08:00 | 22.7 | 67 | 101780 | 100 | 3000 | 19.6493 | 71.9919 | 40.5039 | 0 | 7.2692 | FALSE | FALSE
2025-11-17 09:00 | 26 | 54 | 101810 | 100 | 3000 | 20.9962 | 65.5522 | 43.9593 | 0 | 7.2692 | FALSE | FALSE
2025-11-17 10:00 | 28.35 | 44.5 | 101810 | 100 | 3000 | 21.9351 | 60.1667 | 44.5293 | 0 | 7.2692 | FALSE | FALSE
2025-11-17 11:00 | 29.65 | 36.5 | 101740 | 100 | 3000 | 22.4569 | 55.0189 | 41.4353 | 0 | 7.2692 | FALSE | FALSE
2025-11-17 12:00 | 30.5 | 32 | 101635 | 100 | 3000 | 22.7955 | 51.975 | 39.6402 | 0 | 7.2692 | FALSE | FALSE
2025-11-17 13:00 | 30.6 | 33.5 | 101550 | 100 | 3000 | 22.8284 | 53.0604 | 41.4721 | 0 | 7.2692 | FALSE | FALSE
2025-11-17 14:00 | 29.85 | 37 | 101505 | 100 | 3000 | 22.5319 | 55.4192 | 42.5419 | 0 | 7.2692 | FALSE | FALSE
2025-11-17 15:00 | 28.9 | 40 | 101490 | 100 | 3000 | 22.159 | 57.3075 | 42.2309 | 0 | 7.2692 | FALSE | FALSE
2025-11-17 16:00 | 28 | 46 | 101495 | 100 | 3000 | 21.796 | 61.0947 | 44.5702 | 0 | 7.2692 | FALSE | FALSE
2025-11-17 17:00 | 26.95 | 51.5 | 101520 | 100 | 3000 | 21.3749 | 64.3279 | 45.4723 | 0 | 7.2692 | FALSE | FALSE
2025-11-17 18:00 | 26.05 | 54.5 | 101550 | 100 | 3000 | 21.0151 | 65.9031 | 44.52 | 0 | 7.2692 | FALSE | FALSE
2025-11-17 19:00 | 25.35 | 58 | 101585 | 100 | 3000 | 20.7316 | 67.7884 | 44.5769 | 0 | 7.2692 | FALSE | FALSE
2025-11-17 20:00 | 24.6 | 61.5 | 101605 | 100 | 3000 | 20.4267 | 69.5898 | 44.269 | 0 | 7.2692 | FALSE | FALSE
2025-11-17 21:00 | 23.8 | 64 | 101600 | 100 | 3000 | 20.101 | 70.7351 | 42.8706 | 0 | 7.2692 | FALSE | FALSE
2025-11-17 22:00 | 23.15 | 65.5 | 101585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-17 23:00 | 22.35 | 67.5 | 101545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-18 | 21.25 | 70 | 101505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-18 01:00 | 20.1 | 73.5 | 101475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-18 02:00 | 19.1 | 78 | 101445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-18 03:00 | 18.65 | 79.5 | 101425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-18 04:00 | 18.6 | 79 | 101410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-18 05:00 | 18.4 | 80.5 | 101410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-18 06:00 | 18.2 | 82.5 | 101445 | 100 | 3000 | 17.7471 | 78.4349 | 31.0947 | 0 | 7.2692 | FALSE | FALSE
2025-11-18 07:00 | 19.25 | 78.5 | 101500 | 100 | 3000 | 18.1986 | 76.8248 | 33.3188 | 0 | 7.2692 | FALSE | FALSE
2025-11-18 08:00 | 22.15 | 67 | 101555 | 100 | 3000 | 19.4226 | 71.8224 | 38.2403 | 0 | 7.2692 | FALSE | FALSE
2025-11-18 09:00 | 25.3 | 57.5 | 101600 | 100 | 3000 | 20.7124 | 67.4677 | 43.9915 | 0 | 7.2692 | FALSE | FALSE
2025-11-18 10:00 | 27.3 | 53 | 101575 | 100 | 3000 | 21.5085 | 65.4016 | 48.1047 | 0 | 7.2692 | FALSE | FALSE
2025-11-18 11:00 | 28.75 | 46.5 | 101485 | 100 | 3000 | 22.084 | 61.6473 | 47.7654 | 0 | 7.2692 | FALSE | FALSE
2025-11-18 12:00 | 30.05 | 39.5 | 101380 | 100 | 3000 | 22.6001 | 57.215 | 45.6653 | 0 | 7.2692 | FALSE | FALSE
2025-11-18 13:00 | 30.5 | 39.5 | 101270 | 100 | 3000 | 22.7703 | 57.333 | 47.1953 | 0 | 7.2692 | FALSE | FALSE
2025-11-18 14:00 | 29.95 | 43 | 101200 | 100 | 3000 | 22.5512 | 59.6498 | 48.7366 | 0 | 7.2692 | FALSE | FALSE
2025-11-18 15:00 | 29.1 | 45.5 | 101175 | 100 | 3000 | 22.2207 | 61.1117 | 48.0599 | 0 | 7.2692 | FALSE | FALSE
2025-11-18 16:00 | 28.05 | 54.5 | 101175 | 100 | 3000 | 21.7952 | 66.7202 | 52.2977 | 0 | 7.2692 | FALSE | FALSE
2025-11-18 17:00 | 26.8 | 67 | 101195 | 100 | 3000 | 21.2858 | 74.0831 | 57.8162 | 0 | 7.2692 | FALSE | FALSE
2025-11-18 18:00 | 25.8 | 73.5 | 101225 | 100 | 3000 | 20.8849 | 77.4526 | 58.607 | 0 | 7.2692 | FALSE | FALSE
2025-11-18 19:00 | 25.05 | 76.5 | 101255 | 100 | 3000 | 20.5854 | 78.7407 | 57.4985 | 0 | 7.2692 | FALSE | FALSE
2025-11-18 20:00 | 24.45 | 79 | 101280 | 100 | 3000 | 20.3443 | 79.7953 | 56.5991 | 0 | 7.2692 | FALSE | FALSE
2025-11-18 21:00 | 23.7 | 81 | 101280 | 100 | 3000 | 20.0421 | 80.4327 | 54.5649 | 0 | 7.2692 | FALSE | FALSE
2025-11-18 22:00 | 22.7 | 84 | 101260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-18 23:00 | 21.65 | 88 | 101235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-19 | 20.55 | 91.5 | 101215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-19 01:00 | 19.7 | 94 | 101210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-19 02:00 | 19.2 | 95 | 101200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-19 03:00 | 18.85 | 94.5 | 101195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-19 04:00 | 18.45 | 94.5 | 101200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-19 05:00 | 18 | 95 | 101220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-19 06:00 | 17.75 | 94.5 | 101275 | 100 | 3000 | 17.5518 | 83.9775 | 35.4883 | 0 | 7.2692 | FALSE | FALSE
2025-11-19 07:00 | 18.75 | 90.5 | 101345 | 100 | 3000 | 17.9825 | 82.5316 | 37.864 | 0 | 7.2692 | FALSE | FALSE
2025-11-19 08:00 | 21.65 | 80.5 | 101400 | 100 | 3000 | 19.2066 | 78.9039 | 44.9166 | 0 | 7.2692 | FALSE | FALSE
2025-11-19 09:00 | 25 | 70.5 | 101425 | 100 | 3000 | 20.5742 | 75.1241 | 52.7364 | 0 | 7.2692 | FALSE | FALSE
2025-11-19 10:00 | 27.55 | 60.5 | 101395 | 100 | 3000 | 21.589 | 70.3562 | 55.5566 | 0 | 7.2692 | FALSE | FALSE
2025-11-19 11:00 | 29.6 | 47 | 101325 | 100 | 3000 | 22.4065 | 62.2937 | 51.3695 | 0 | 7.2692 | FALSE | FALSE
2025-11-19 12:00 | 31.3 | 35 | 101240 | 100 | 3000 | 23.087 | 54.2766 | 45.2309 | 0 | 7.2692 | FALSE | FALSE
2025-11-19 13:00 | 32.05 | 31 | 101155 | 100 | 3000 | 23.3831 | 51.4557 | 43.3016 | 0 | 7.2692 | FALSE | FALSE
2025-11-19 14:00 | 31.25 | 43 | 101095 | 100 | 3000 | 23.0382 | 60.0891 | 53.4251 | 0 | 7.2692 | FALSE | FALSE
2025-11-19 15:00 | 29.65 | 53.5 | 101070 | 100 | 3000 | 22.4056 | 66.8199 | 57.7652 | 0 | 7.2692 | FALSE | FALSE
2025-11-19 16:00 | 28.35 | 59.5 | 101080 | 100 | 3000 | 21.8976 | 70.1735 | 57.9798 | 0 | 7.2692 | FALSE | FALSE
2025-11-19 17:00 | 27.25 | 69 | 101115 | 100 | 3000 | 21.4552 | 75.6522 | 61.4796 | 0 | 7.2692 | FALSE | FALSE
2025-11-19 18:00 | 26.35 | 72 | 101180 | 100 | 3000 | 21.1018 | 76.9126 | 59.9037 | 0 | 7.2692 | FALSE | FALSE
2025-11-19 19:00 | 25.45 | 74 | 101240 | 100 | 3000 | 20.7468 | 77.5176 | 57.408 | 0 | 7.2692 | FALSE | FALSE
2025-11-19 20:00 | 24.5 | 78 | 101275 | 100 | 3000 | 20.3654 | 79.2464 | 56.0922 | 0 | 7.2692 | FALSE | FALSE
2025-11-19 21:00 | 23.6 | 83 | 101300 | 100 | 3000 | 19.9997 | 81.498 | 55.5142 | 0 | 7.2692 | FALSE | FALSE
2025-11-19 22:00 | 22.8 | 87.5 | 101320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-19 23:00 | 22 | 91 | 101315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-20 | 21 | 95 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-20 01:00 | 20.2 | 98.5 | 101320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-20 02:00 | 19.6 | 100 | 101320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-20 03:00 | 19.55 | 100 | 101325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-20 04:00 | 19.4 | 100 | 101340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-20 05:00 | 18.5 | 99 | 101375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-20 06:00 | 17.5 | 93.5 | 101425 | 100 | 3000 | 17.4434 | 83.3766 | 33.8431 | 0 | 7.2692 | FALSE | FALSE
2025-11-20 07:00 | 18.05 | 79.5 | 101485 | 100 | 3000 | 17.6825 | 76.9512 | 28.8543 | 0 | 7.2692 | FALSE | FALSE
2025-11-20 08:00 | 21.05 | 64 | 101535 | 100 | 3000 | 18.966 | 69.9138 | 31.9276 | 0 | 7.2692 | FALSE | FALSE
2025-11-20 09:00 | 24.35 | 62 | 101575 | 100 | 3000 | 20.3255 | 69.7903 | 43.631 | 0 | 7.2692 | FALSE | FALSE
2025-11-20 10:00 | 26.75 | 64.5 | 101565 | 100 | 3000 | 21.2714 | 72.4438 | 55.5793 | 0 | 7.2692 | FALSE | FALSE
2025-11-20 11:00 | 28.95 | 56 | 101485 | 100 | 3000 | 22.1346 | 68.1229 | 57.3491 | 0 | 7.2692 | FALSE | FALSE
2025-11-20 12:00 | 30.75 | 45 | 101400 | 100 | 3000 | 22.845 | 61.3152 | 53.7028 | 0 | 7.2692 | FALSE | FALSE
2025-11-20 13:00 | 31.15 | 45.5 | 101330 | 100 | 3000 | 22.9918 | 61.8396 | 55.7009 | 0 | 7.2692 | FALSE | FALSE
2025-11-20 14:00 | 30.2 | 54.5 | 101280 | 100 | 3000 | 22.6079 | 67.789 | 61.0175 | 0 | 7.2692 | FALSE | FALSE
2025-11-20 15:00 | 29.2 | 61 | 101260 | 100 | 3000 | 22.2147 | 71.6726 | 63.0082 | 0 | 7.2692 | FALSE | FALSE
2025-11-20 16:00 | 28.45 | 65.5 | 101270 | 100 | 3000 | 21.9203 | 74.1889 | 63.8297 | 0 | 7.2692 | FALSE | FALSE
2025-11-20 17:00 | 27.35 | 72.5 | 101305 | 100 | 3000 | 21.486 | 77.9403 | 64.9296 | 0 | 7.2692 | FALSE | FALSE
2025-11-20 18:00 | 26.2 | 80 | 101355 | 100 | 3000 | 21.0293 | 81.7221 | 65.6562 | 0 | 7.2692 | FALSE | FALSE
2025-11-20 19:00 | 25.2 | 85.5 | 101405 | 100 | 3000 | 20.6313 | 84.199 | 65.0613 | 0 | 7.2692 | FALSE | FALSE
2025-11-20 20:00 | 24.35 | 88.5 | 101450 | 100 | 3000 | 20.2926 | 85.2245 | 63.0913 | 0 | 7.2692 | FALSE | FALSE
2025-11-20 21:00 | 23.7 | 88.5 | 101470 | 100 | 3000 | 20.034 | 84.679 | 59.8911 | 0 | 7.2692 | FALSE | FALSE
2025-11-20 22:00 | 23.3 | 87.5 | 101470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-20 23:00 | 23.05 | 87 | 101445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-21 | 22.75 | 87.5 | 101425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-21 01:00 | 22.3 | 89 | 101420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-21 02:00 | 21.45 | 91.5 | 101405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-21 03:00 | 20.95 | 94 | 101410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-21 04:00 | 20.4 | 97.5 | 101420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-21 05:00 | 19.5 | 100 | 101440 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-21 06:00 | 18.7 | 100 | 101500 | 100 | 3000 | 17.9595 | 87.0983 | 42.8644 | 0 | 7.2692 | FALSE | FALSE
2025-11-21 07:00 | 18.45 | 99.5 | 101565 | 100 | 3000 | 17.8527 | 86.696 | 41.4051 | 0 | 7.2692 | FALSE | FALSE
2025-11-21 08:00 | 19.5 | 98.5 | 101625 | 100 | 3000 | 18.2997 | 86.864 | 45.8653 | 0 | 7.2692 | FALSE | FALSE
2025-11-21 09:00 | 21.8 | 94.5 | 101665 | 100 | 3000 | 19.2592 | 86.4555 | 54.6271 | 0 | 7.2692 | FALSE | FALSE
2025-11-21 10:00 | 25.05 | 80.5 | 101660 | 100 | 3000 | 20.5798 | 81.0754 | 60.581 | 0 | 7.2692 | FALSE | FALSE
2025-11-21 11:00 | 27.75 | 63 | 101610 | 100 | 3000 | 21.6603 | 72.0654 | 58.6107 | 0 | 7.2692 | FALSE | FALSE
2025-11-21 12:00 | 29.35 | 51.5 | 101515 | 100 | 3000 | 22.2986 | 65.261 | 54.7449 | 0 | 7.2692 | FALSE | FALSE
2025-11-21 13:00 | 30.2 | 47 | 101425 | 100 | 3000 | 22.6325 | 62.5144 | 53.6498 | 0 | 7.2692 | FALSE | FALSE
2025-11-21 14:00 | 30 | 49.5 | 101370 | 100 | 3000 | 22.5494 | 64.1847 | 55.3333 | 0 | 7.2692 | FALSE | FALSE
2025-11-21 15:00 | 29.25 | 53.5 | 101365 | 100 | 3000 | 22.2551 | 66.5925 | 56.2098 | 0 | 7.2692 | FALSE | FALSE
2025-11-21 16:00 | 28.4 | 60 | 101380 | 100 | 3000 | 21.9154 | 70.5035 | 58.6914 | 0 | 7.2692 | FALSE | FALSE
2025-11-21 17:00 | 27.4 | 65.5 | 101410 | 100 | 3000 | 21.5204 | 73.483 | 59.2155 | 0 | 7.2692 | FALSE | FALSE
2025-11-21 18:00 | 26.35 | 69 | 101475 | 100 | 3000 | 21.1074 | 75.0226 | 57.5149 | 0 | 7.2692 | FALSE | FALSE
2025-11-21 19:00 | 25.4 | 73.5 | 101515 | 100 | 3000 | 20.7279 | 77.155 | 56.8308 | 0 | 7.2692 | FALSE | FALSE
2025-11-21 20:00 | 24.55 | 77 | 101530 | 100 | 3000 | 20.3867 | 78.6683 | 55.613 | 0 | 7.2692 | FALSE | FALSE
2025-11-21 21:00 | 23.65 | 80 | 101540 | 100 | 3000 | 20.0231 | 79.8023 | 53.6533 | 0 | 7.2692 | FALSE | FALSE
2025-11-21 22:00 | 22.95 | 81.5 | 101555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-21 23:00 | 22.3 | 83 | 101550 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-22 | 21.5 | 85 | 101525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-22 01:00 | 20.85 | 86 | 101505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-22 02:00 | 20.3 | 86.5 | 101485 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-22 03:00 | 19.6 | 88.5 | 101480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-22 04:00 | 18.7 | 90.5 | 101480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-22 05:00 | 17.85 | 90.5 | 101495 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-22 06:00 | 17.35 | 91.5 | 101535 | 100 | 3000 | 17.3782 | 82.3678 | 32.146 | 0 | 7.2692 | FALSE | FALSE
2025-11-22 07:00 | 18.1 | 92 | 101590 | 100 | 3000 | 17.7031 | 82.9175 | 35.7571 | 0 | 7.2692 | FALSE | FALSE
2025-11-22 08:00 | 20.7 | 83.5 | 101645 | 100 | 3000 | 18.8097 | 79.9579 | 42.5742 | 0 | 7.2692 | FALSE | FALSE
2025-11-22 09:00 | 24.05 | 67 | 101690 | 100 | 3000 | 20.1987 | 72.5571 | 46.0893 | 0 | 7.2692 | FALSE | FALSE
2025-11-22 10:00 | 26.95 | 49.5 | 101675 | 100 | 3000 | 21.3789 | 63.0433 | 43.7984 | 0 | 7.2692 | FALSE | FALSE
2025-11-22 11:00 | 29.15 | 35 | 101585 | 100 | 3000 | 22.2691 | 53.9424 | 38.3352 | 0 | 7.2692 | FALSE | FALSE
2025-11-22 12:00 | 30.85 | 26 | 101480 | 100 | 3000 | 22.9495 | 47.7114 | 35.0517 | 0 | 7.2692 | FALSE | FALSE
2025-11-22 13:00 | 32.1 | 21.5 | 101380 | 100 | 3000 | 23.4411 | 44.3495 | 36.6205 | 0 | 7.2692 | FALSE | FALSE
2025-11-22 14:00 | 31.95 | 26 | 101305 | 100 | 3000 | 23.3661 | 47.7152 | 37.5407 | 0 | 7.2692 | FALSE | FALSE
2025-11-22 15:00 | 30.15 | 33.5 | 101300 | 100 | 3000 | 22.6574 | 53.0316 | 39.9945 | 0 | 7.2692 | FALSE | FALSE
2025-11-22 16:00 | 28.5 | 42.5 | 101330 | 100 | 3000 | 21.9982 | 58.9183 | 43.1458 | 0 | 7.2692 | FALSE | FALSE
2025-11-22 17:00 | 27.35 | 55.5 | 101355 | 100 | 3000 | 21.5226 | 67.0469 | 50.4188 | 0 | 7.2692 | FALSE | FALSE
2025-11-22 18:00 | 26.25 | 64.5 | 101400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-22 19:00 | 25.45 | 68.5 | 101450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-22 20:00 | 24.45 | 70 | 101480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-22 21:00 | 23.35 | 71.5 | 101475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-22 22:00 | 22.1 | 69.5 | 101465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-22 23:00 | 20.7 | 62.5 | 101450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 | 19.65 | 57 | 101420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 01:00 | 18.75 | 57 | 101405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 02:00 | 17.8 | 60.5 | 101400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 03:00 | 16.9 | 61 | 101415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 04:00 | 16.15 | 59 | 101440 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 05:00 | 15.55 | 58 | 101470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 06:00 | 15.2 | 59.5 | 101515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 07:00 | 16.2 | 61 | 101575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 08:00 | 19.5 | 55 | 101630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 09:00 | 23.85 | 46.5 | 101670 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 10:00 | 27 | 40 | 101650 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 11:00 | 28.6 | 34.5 | 101555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 12:00 | 29.75 | 29 | 101445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 13:00 | 30.65 | 24 | 101350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 14:00 | 30.85 | 24.5 | 101300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 15:00 | 30.05 | 30 | 101290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 16:00 | 28.85 | 35.5 | 101295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 17:00 | 27.55 | 42.5 | 101325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 18:00 | 26.25 | 49.5 | 101375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 19:00 | 25.25 | 55 | 101415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 20:00 | 24.3 | 60.5 | 101445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 21:00 | 23.85 | 63 | 101450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 22:00 | 23.6 | 64 | 101425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-23 23:00 | 22.95 | 68 | 101405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-24 | 22.3 | 73 | 101395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-24 01:00 | 21.65 | 76 | 101390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-24 02:00 | 21.2 | 77 | 101380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-24 03:00 | 20.45 | 74 | 101375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-24 04:00 | 19.35 | 73 | 101375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-24 05:00 | 18.7 | 76.5 | 101395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-24 06:00 | 18.45 | 78 | 101445 | 100 | 3000 | 17.8554 | 76.3436 | 29.6986 | 0 | 7.2692 | FALSE | FALSE
2025-11-24 07:00 | 19.45 | 71.5 | 101500 | 100 | 3000 | 18.2857 | 73.398 | 30.1232 | 0 | 7.2692 | FALSE | FALSE
2025-11-24 08:00 | 22.2 | 56 | 101555 | 100 | 3000 | 19.4514 | 65.8323 | 31.0923 | 0 | 7.2692 | FALSE | FALSE
2025-11-24 09:00 | 25.5 | 45.5 | 101590 | 100 | 3000 | 20.8105 | 60.2609 | 35.2805 | 0 | 7.2692 | FALSE | FALSE
2025-11-24 10:00 | 27.9 | 42 | 101565 | 100 | 3000 | 21.7665 | 58.4436 | 40.6467 | 0 | 7.2692 | FALSE | FALSE
2025-11-24 11:00 | 29.35 | 35 | 101490 | 100 | 3000 | 22.3462 | 53.9713 | 38.9583 | 0 | 7.2692 | FALSE | FALSE
2025-11-24 12:00 | 30.5 | 25.5 | 101405 | 100 | 3000 | 22.8174 | 47.3753 | 34.6083 | 0 | 7.2692 | FALSE | FALSE
2025-11-24 13:00 | 31.05 | 20.5 | 101325 | 100 | 3000 | 23.0456 | 43.7404 | 35.3536 | 0 | 7.2692 | FALSE | FALSE
2025-11-24 14:00 | 30.95 | 20 | 101285 | 100 | 3000 | 23.0091 | 43.3976 | 35.2276 | 0 | 7.2692 | FALSE | FALSE
2025-11-24 15:00 | 30.1 | 23.5 | 101275 | 100 | 3000 | 22.6701 | 46.0058 | 34.1086 | 0 | 7.2692 | FALSE | FALSE
2025-11-24 16:00 | 28.7 | 30 | 101280 | 100 | 3000 | 22.1079 | 50.5704 | 32.2482 | 0 | 7.2692 | FALSE | FALSE
2025-11-24 17:00 | 27.05 | 40 | 101315 | 100 | 3000 | 21.4373 | 57.0525 | 35.9694 | 0 | 7.2692 | FALSE | FALSE
2025-11-24 18:00 | 25.5 | 50.5 | 101370 | 100 | 3000 | 20.8029 | 63.3189 | 39.219 | 0 | 7.2692 | FALSE | FALSE
2025-11-24 19:00 | 24.25 | 56.5 | 101425 | 100 | 3000 | 20.2919 | 66.5649 | 39.1382 | 0 | 7.2692 | FALSE | FALSE
2025-11-24 20:00 | 23.1 | 61.5 | 101480 | 100 | 3000 | 19.8182 | 69.0904 | 38.2823 | 0 | 7.2692 | FALSE | FALSE
2025-11-24 21:00 | 22.05 | 65.5 | 101505 | 100 | 3000 | 19.3823 | 70.9803 | 36.8385 | 0 | 7.2692 | FALSE | FALSE
2025-11-24 22:00 | 21 | 66.5 | 101490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-24 23:00 | 19.9 | 64.5 | 101470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-25 | 18.85 | 62 | 101455 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-25 01:00 | 18 | 61.5 | 101455 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-25 02:00 | 17.1 | 63.5 | 101445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-25 03:00 | 16.5 | 71 | 101420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-25 04:00 | 16.3 | 76.5 | 101420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-25 05:00 | 16 | 75.5 | 101465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-25 06:00 | 15.65 | 74 | 101535 | 100 | 3000 | 16.6281 | 74.0697 | 16.491 | 0 | 7.2692 | FALSE | FALSE
2025-11-25 07:00 | 16.65 | 67.5 | 101605 | 100 | 3000 | 17.0705 | 71.1435 | 17.1244 | 0 | 7.2692 | FALSE | FALSE
2025-11-25 08:00 | 19.75 | 55 | 101660 | 100 | 3000 | 18.4186 | 65.1133 | 21.6113 | 0 | 7.2692 | FALSE | FALSE
2025-11-25 09:00 | 23.65 | 45 | 101695 | 100 | 3000 | 20.0601 | 59.794 | 28.5636 | 0 | 7.2692 | FALSE | FALSE
2025-11-25 10:00 | 26.8 | 39 | 101675 | 100 | 3000 | 21.3402 | 56.3592 | 34.3424 | 0 | 7.2692 | FALSE | FALSE
2025-11-25 11:00 | 28.8 | 28 | 101585 | 100 | 3000 | 22.152 | 49.1899 | 32.5019 | 0 | 7.2692 | FALSE | FALSE
2025-11-25 12:00 | 29.95 | 17.5 | 101470 | 100 | 3000 | 22.6305 | 41.8049 | 34.0936 | 0 | 7.2692 | FALSE | FALSE
2025-11-25 13:00 | 30.4 | 14.5 | 101370 | 100 | 3000 | 22.8152 | 39.5765 | 34.6809 | 0 | 7.2692 | FALSE | FALSE
2025-11-25 14:00 | 30.4 | 14 | 101315 | 100 | 3000 | 22.8169 | 39.2261 | 34.6718 | 0 | 7.2692 | FALSE | FALSE
2025-11-25 15:00 | 29.6 | 19 | 101290 | 100 | 3000 | 22.4896 | 42.9477 | 33.5668 | 0 | 7.2692 | FALSE | FALSE
2025-11-25 16:00 | 28.05 | 31.5 | 101285 | 100 | 3000 | 21.8497 | 51.5845 | 31.6064 | 0 | 7.2692 | FALSE | FALSE
2025-11-25 17:00 | 26.3 | 45 | 101305 | 100 | 3000 | 21.1308 | 60.1036 | 37.627 | 0 | 7.2692 | FALSE | FALSE
2025-11-25 18:00 | 24.9 | 52.5 | 101335 | 100 | 3000 | 20.5593 | 64.3843 | 38.5583 | 0 | 7.2692 | FALSE | FALSE
2025-11-25 19:00 | 23.95 | 55.5 | 101375 | 100 | 3000 | 20.1713 | 65.9129 | 37.2559 | 0 | 7.2692 | FALSE | FALSE
2025-11-25 20:00 | 22.95 | 58 | 101405 | 100 | 3000 | 19.7598 | 67.097 | 35.2549 | 0 | 7.2692 | FALSE | FALSE
2025-11-25 21:00 | 21.75 | 62 | 101420 | 100 | 3000 | 19.26 | 69.0176 | 33.3504 | 0 | 7.2692 | FALSE | FALSE
2025-11-25 22:00 | 20.5 | 66.5 | 101415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-25 23:00 | 19.6 | 68 | 101380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-26 | 18.9 | 67 | 101355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-26 01:00 | 18.15 | 65 | 101345 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-26 02:00 | 17.6 | 63.5 | 101330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-26 03:00 | 17.25 | 69 | 101330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-26 04:00 | 16.95 | 75.5 | 101335 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-26 05:00 | 16.5 | 76 | 101360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-26 06:00 | 16 | 76 | 101425 | 100 | 3000 | 16.7839 | 74.9909 | 18.8055 | 0 | 7.2692 | FALSE | FALSE
2025-11-26 07:00 | 17 | 69.5 | 101485 | 100 | 3000 | 17.2247 | 72.0867 | 19.4531 | 0 | 7.2692 | FALSE | FALSE
2025-11-26 08:00 | 20.35 | 55 | 101525 | 100 | 3000 | 18.6744 | 65.1366 | 23.7349 | 0 | 7.2692 | FALSE | FALSE
2025-11-26 09:00 | 24.2 | 46 | 101550 | 100 | 3000 | 20.284 | 60.4202 | 31.1598 | 0 | 7.2692 | FALSE | FALSE
2025-11-26 10:00 | 26.65 | 42.5 | 101525 | 100 | 3000 | 21.2741 | 58.5688 | 36.7823 | 0 | 7.2692 | FALSE | FALSE
2025-11-26 11:00 | 27.85 | 36.5 | 101460 | 100 | 3000 | 21.7596 | 54.8471 | 35.5335 | 0 | 7.2692 | FALSE | FALSE
2025-11-26 12:00 | 28.6 | 31 | 101390 | 100 | 3000 | 22.0663 | 51.2335 | 32.814 | 0 | 7.2692 | FALSE | FALSE
2025-11-26 13:00 | 29 | 28.5 | 101315 | 100 | 3000 | 22.2289 | 49.5425 | 32.6614 | 0 | 7.2692 | FALSE | FALSE
2025-11-26 14:00 | 28.9 | 29 | 101265 | 100 | 3000 | 22.1886 | 49.8904 | 32.5116 | 0 | 7.2692 | FALSE | FALSE
2025-11-26 15:00 | 28.45 | 30.5 | 101240 | 100 | 3000 | 22.009 | 50.9158 | 31.9114 | 0 | 7.2692 | FALSE | FALSE
2025-11-26 16:00 | 27.6 | 32 | 101240 | 100 | 3000 | 21.6713 | 51.9278 | 30.8022 | 0 | 7.2692 | FALSE | FALSE
2025-11-26 17:00 | 26.45 | 35 | 101275 | 100 | 3000 | 21.2085 | 53.8683 | 29.7822 | 0 | 7.2692 | FALSE | FALSE
2025-11-26 18:00 | 25.45 | 39.5 | 101325 | 100 | 3000 | 20.7996 | 56.6392 | 30.2991 | 0 | 7.2692 | FALSE | FALSE
2025-11-26 19:00 | 24.5 | 44 | 101370 | 100 | 3000 | 20.4087 | 59.2876 | 30.6571 | 0 | 7.2692 | FALSE | FALSE
2025-11-26 20:00 | 23.7 | 47.5 | 101400 | 100 | 3000 | 20.078 | 61.2629 | 30.5187 | 0 | 7.2692 | FALSE | FALSE
2025-11-26 21:00 | 23.15 | 48.5 | 101410 | 100 | 3000 | 19.8509 | 61.7883 | 29.3244 | 0 | 7.2692 | FALSE | FALSE
2025-11-26 22:00 | 22.55 | 49.5 | 101410 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-26 23:00 | 21.35 | 52 | 101400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-27 | 19.7 | 55 | 101380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-27 01:00 | 18.45 | 59.5 | 101365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-27 02:00 | 17.65 | 63.5 | 101355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-27 03:00 | 17.25 | 64 | 101355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-27 04:00 | 17.6 | 61 | 101365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-27 05:00 | 17.55 | 60.5 | 101390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-27 06:00 | 17 | 62.5 | 101450 | 100 | 3000 | 17.2244 | 68.8493 | 15.8826 | 0 | 7.2692 | FALSE | FALSE
2025-11-27 07:00 | 17.95 | 59 | 101515 | 100 | 3000 | 17.6405 | 67.1448 | 17.4643 | 0 | 7.2692 | FALSE | FALSE
2025-11-27 08:00 | 20.8 | 49.5 | 101560 | 100 | 3000 | 18.8678 | 62.2706 | 21.9036 | 0 | 7.2692 | FALSE | FALSE
2025-11-27 09:00 | 24.3 | 42 | 101600 | 100 | 3000 | 20.3296 | 58.0815 | 28.5073 | 0 | 7.2692 | FALSE | FALSE
2025-11-27 10:00 | 26.55 | 38 | 101590 | 100 | 3000 | 21.2428 | 55.7219 | 32.6689 | 0 | 7.2692 | FALSE | FALSE
2025-11-27 11:00 | 27.45 | 34 | 101515 | 100 | 3000 | 21.6076 | 53.2003 | 32.0558 | 0 | 7.2692 | FALSE | FALSE
2025-11-27 12:00 | 28.15 | 30 | 101430 | 100 | 3000 | 21.8925 | 50.5768 | 31.5947 | 0 | 7.2692 | FALSE | FALSE
2025-11-27 13:00 | 28.65 | 27 | 101355 | 100 | 3000 | 22.0961 | 48.5493 | 32.2541 | 0 | 7.2692 | FALSE | FALSE
2025-11-27 14:00 | 28.6 | 28.5 | 101310 | 100 | 3000 | 22.0727 | 49.5644 | 32.1537 | 0 | 7.2692 | FALSE | FALSE
2025-11-27 15:00 | 27.9 | 36 | 101300 | 100 | 3000 | 21.7804 | 54.5383 | 35.2176 | 0 | 7.2692 | FALSE | FALSE
2025-11-27 16:00 | 26.75 | 42.5 | 101315 | 100 | 3000 | 21.3138 | 58.6033 | 37.0923 | 0 | 7.2692 | FALSE | FALSE
2025-11-27 17:00 | 25.7 | 46 | 101355 | 100 | 3000 | 20.8899 | 60.6187 | 36.347 | 0 | 7.2692 | FALSE | FALSE
2025-11-27 18:00 | 24.85 | 51 | 101415 | 100 | 3000 | 20.5412 | 63.4725 | 37.2326 | 0 | 7.2692 | FALSE | FALSE
2025-11-27 19:00 | 24 | 55.5 | 101470 | 100 | 3000 | 20.1916 | 65.915 | 37.4555 | 0 | 7.2692 | FALSE | FALSE
2025-11-27 20:00 | 23.35 | 58 | 101505 | 100 | 3000 | 19.9239 | 67.182 | 36.7912 | 0 | 7.2692 | FALSE | FALSE
2025-11-27 21:00 | 22.45 | 59.5 | 101535 | 100 | 3000 | 19.5524 | 67.8021 | 34.3898 | 0 | 7.2692 | FALSE | FALSE
2025-11-27 22:00 | 21.35 | 60 | 101545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-27 23:00 | 20.55 | 61 | 101525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-28 | 19.85 | 62 | 101505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-28 01:00 | 19.15 | 62.5 | 101495 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-28 02:00 | 18.65 | 63 | 101490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-28 03:00 | 18.2 | 60.5 | 101495 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-28 04:00 | 17.7 | 57.5 | 101510 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-28 05:00 | 17.25 | 57.5 | 101545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-28 06:00 | 16.85 | 58.5 | 101605 | 100 | 3000 | 17.1581 | 66.993 | 15.3758 | 0 | 7.2692 | FALSE | FALSE
2025-11-28 07:00 | 17.65 | 55.5 | 101650 | 100 | 3000 | 17.5096 | 65.4876 | 16.6373 | 0 | 7.2692 | FALSE | FALSE
2025-11-28 08:00 | 20.35 | 47.5 | 101675 | 100 | 3000 | 18.6774 | 61.2448 | 20.7572 | 0 | 7.2692 | FALSE | FALSE
2025-11-28 09:00 | 23.55 | 41.5 | 101710 | 100 | 3000 | 20.0225 | 57.7867 | 25.6945 | 0 | 7.2692 | FALSE | FALSE
2025-11-28 10:00 | 25.65 | 41.5 | 101695 | 100 | 3000 | 20.8769 | 57.8292 | 32.6085 | 0 | 7.2692 | FALSE | FALSE
2025-11-28 11:00 | 26.75 | 41.5 | 101605 | 100 | 3000 | 21.3156 | 57.9428 | 36.289 | 0 | 7.2692 | FALSE | FALSE
2025-11-28 12:00 | 27.55 | 37.5 | 101500 | 100 | 3000 | 21.6395 | 55.4723 | 35.4616 | 0 | 7.2692 | FALSE | FALSE
2025-11-28 13:00 | 28 | 34.5 | 101425 | 100 | 3000 | 21.823 | 53.5463 | 34.2007 | 0 | 7.2692 | FALSE | FALSE
2025-11-28 14:00 | 27.85 | 36.5 | 101380 | 100 | 3000 | 21.7596 | 54.8548 | 35.5202 | 0 | 7.2692 | FALSE | FALSE
2025-11-28 15:00 | 27.3 | 42 | 101340 | 100 | 3000 | 21.5317 | 58.3634 | 38.548 | 0 | 7.2692 | FALSE | FALSE
2025-11-28 16:00 | 26.5 | 46 | 101340 | 100 | 3000 | 21.2083 | 60.761 | 39.1672 | 0 | 7.2692 | FALSE | FALSE
2025-11-28 17:00 | 25.7 | 47 | 101380 | 100 | 3000 | 20.8883 | 61.2273 | 37.1529 | 0 | 7.2692 | FALSE | FALSE
2025-11-28 18:00 | 25 | 50 | 101430 | 100 | 3000 | 20.603 | 62.9051 | 37.0106 | 0 | 7.2692 | FALSE | FALSE
2025-11-28 19:00 | 24.2 | 55 | 101475 | 100 | 3000 | 20.2734 | 65.673 | 37.842 | 0 | 7.2692 | FALSE | FALSE
2025-11-28 20:00 | 23.35 | 58.5 | 101505 | 100 | 3000 | 19.9234 | 67.4652 | 37.1457 | 0 | 7.2692 | FALSE | FALSE
2025-11-28 21:00 | 22.45 | 60 | 101515 | 100 | 3000 | 19.552 | 68.0796 | 34.7267 | 0 | 7.2692 | FALSE | FALSE
2025-11-28 22:00 | 21.55 | 61 | 101495 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-28 23:00 | 20.65 | 64 | 101465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-29 | 19.95 | 67.5 | 101445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-29 01:00 | 19.5 | 70.5 | 101430 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-29 02:00 | 19.1 | 72.5 | 101405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-29 03:00 | 18.6 | 74.5 | 101405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-29 04:00 | 18.25 | 75.5 | 101420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-29 05:00 | 17.95 | 75.5 | 101440 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-29 06:00 | 17.55 | 76 | 101485 | 100 | 3000 | 17.4654 | 75.1813 | 24.9596 | 0 | 7.2692 | FALSE | FALSE
2025-11-29 07:00 | 18.45 | 71 | 101540 | 100 | 3000 | 17.8563 | 72.9451 | 25.8649 | 0 | 7.2692 | FALSE | FALSE
2025-11-29 08:00 | 21.2 | 60 | 101590 | 100 | 3000 | 19.0311 | 67.8242 | 29.9746 | 0 | 7.2692 | FALSE | FALSE
2025-11-29 09:00 | 24.2 | 52 | 101635 | 100 | 3000 | 20.2769 | 63.9092 | 35.6354 | 0 | 7.2692 | FALSE | FALSE
2025-11-29 10:00 | 26.25 | 45.5 | 101615 | 100 | 3000 | 21.11 | 60.3752 | 37.9095 | 0 | 7.2692 | FALSE | FALSE
2025-11-29 11:00 | 27.45 | 37.5 | 101515 | 100 | 3000 | 21.6002 | 55.4633 | 35.1395 | 0 | 7.2692 | FALSE | FALSE
2025-11-29 12:00 | 28.25 | 31 | 101410 | 100 | 3000 | 21.9293 | 51.2375 | 31.7695 | 0 | 7.2692 | FALSE | FALSE
2025-11-29 13:00 | 28.7 | 28.5 | 101325 | 100 | 3000 | 22.1118 | 49.5571 | 32.2854 | 0 | 7.2692 | FALSE | FALSE
2025-11-29 14:00 | 28.6 | 30.5 | 101270 | 100 | 3000 | 22.0676 | 50.9095 | 32.3252 | 0 | 7.2692 | FALSE | FALSE
2025-11-29 15:00 | 27.85 | 31.5 | 101240 | 100 | 3000 | 21.771 | 51.594 | 31.1308 | 0 | 7.2692 | FALSE | FALSE
2025-11-29 16:00 | 26.9 | 33 | 101225 | 100 | 3000 | 21.3917 | 52.5967 | 29.8757 | 0 | 7.2692 | FALSE | FALSE
2025-11-29 17:00 | 25.9 | 38.5 | 101230 | 100 | 3000 | 20.9822 | 56.0471 | 30.9344 | 0 | 7.2692 | FALSE | FALSE
2025-11-29 18:00 | 24.95 | 42.5 | 101270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-29 19:00 | 24.05 | 44.5 | 101315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-29 20:00 | 23.05 | 47.5 | 101350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-29 21:00 | 22.05 | 52 | 101380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-29 22:00 | 21 | 58.5 | 101395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-29 23:00 | 20.05 | 65 | 101385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 | 19.35 | 69 | 101365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 01:00 | 18.85 | 71 | 101350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 02:00 | 18.3 | 73.5 | 101325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 03:00 | 17.8 | 77.5 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 04:00 | 17.35 | 81.5 | 101315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 05:00 | 16.85 | 84 | 101335 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 06:00 | 16.45 | 85 | 101390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 07:00 | 17.3 | 78.5 | 101465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 08:00 | 20.3 | 63 | 101520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 09:00 | 23.95 | 49 | 101560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 10:00 | 26.3 | 39 | 101540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 11:00 | 27.4 | 31 | 101460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 12:00 | 28.1 | 26.5 | 101360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 13:00 | 28.55 | 24.5 | 101270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 14:00 | 28.4 | 28.5 | 101225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 15:00 | 27.75 | 36.5 | 101195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 16:00 | 26.65 | 42 | 101195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 17:00 | 25.5 | 46 | 101230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 18:00 | 24.7 | 51 | 101275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 19:00 | 23.9 | 57 | 101315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 20:00 | 23.2 | 62.5 | 101350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 21:00 | 22.4 | 66 | 101380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 22:00 | 21.4 | 63.5 | 101390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-11-30 23:00 | 20.4 | 57 | 101375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-01 | 19.65 | 54 | 101335 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-01 01:00 | 19.25 | 54.5 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-01 02:00 | 18.85 | 56 | 101285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-01 03:00 | 18.65 | 57 | 101270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-01 04:00 | 18.8 | 56 | 101265 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-01 05:00 | 18.8 | 55 | 101270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-01 06:00 | 18.55 | 55.5 | 101330 | 100 | 3000 | 17.9017 | 65.4427 | 17.9664 | 0 | 7.2692 | FALSE | FALSE
2025-12-01 07:00 | 19.2 | 53 | 101410 | 100 | 3000 | 18.183 | 64.1575 | 18.9709 | 0 | 7.2692 | FALSE | FALSE
2025-12-01 08:00 | 21.5 | 46 | 101480 | 100 | 3000 | 19.1653 | 60.3921 | 22.4056 | 0 | 7.2692 | FALSE | FALSE
2025-12-01 09:00 | 24.25 | 40.5 | 101545 | 100 | 3000 | 20.311 | 57.2091 | 27.2103 | 0 | 7.2692 | FALSE | FALSE
2025-12-01 10:00 | 26.1 | 41.5 | 101545 | 100 | 3000 | 21.0572 | 57.8802 | 34.092 | 0 | 7.2692 | FALSE | FALSE
2025-12-01 11:00 | 27.1 | 42.5 | 101465 | 100 | 3000 | 21.4519 | 58.6403 | 38.3146 | 0 | 7.2692 | FALSE | FALSE
2025-12-01 12:00 | 27.85 | 38 | 101365 | 100 | 3000 | 21.7562 | 55.8378 | 36.863 | 0 | 7.2692 | FALSE | FALSE
2025-12-01 13:00 | 28.25 | 35 | 101280 | 100 | 3000 | 21.9197 | 53.902 | 35.4185 | 0 | 7.2692 | FALSE | FALSE
2025-12-01 14:00 | 27.95 | 36.5 | 101240 | 100 | 3000 | 21.7988 | 54.8755 | 35.8183 | 0 | 7.2692 | FALSE | FALSE
2025-12-01 15:00 | 27.3 | 37.5 | 101220 | 100 | 3000 | 21.5411 | 55.4813 | 34.6066 | 0 | 7.2692 | FALSE | FALSE
2025-12-01 16:00 | 26.45 | 39 | 101225 | 100 | 3000 | 21.2012 | 56.3804 | 33.1296 | 0 | 7.2692 | FALSE | FALSE
2025-12-01 17:00 | 25.3 | 45 | 101260 | 100 | 3000 | 20.731 | 59.9662 | 34.1472 | 0 | 7.2692 | FALSE | FALSE
2025-12-01 18:00 | 24.25 | 52 | 101310 | 100 | 3000 | 20.2973 | 63.9528 | 35.7801 | 0 | 7.2692 | FALSE | FALSE
2025-12-01 19:00 | 23.45 | 57 | 101365 | 100 | 3000 | 19.9658 | 66.6539 | 36.4463 | 0 | 7.2692 | FALSE | FALSE
2025-12-01 20:00 | 22.8 | 60 | 101400 | 100 | 3000 | 19.6964 | 68.1775 | 36.064 | 0 | 7.2692 | FALSE | FALSE
2025-12-01 21:00 | 22.15 | 61.5 | 101425 | 100 | 3000 | 19.4266 | 68.8399 | 34.5689 | 0 | 7.2692 | FALSE | FALSE
2025-12-01 22:00 | 21.2 | 64 | 101445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-01 23:00 | 19.95 | 67.5 | 101440 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-02 | 18.7 | 70 | 101425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-02 01:00 | 17.65 | 72.5 | 101425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-02 02:00 | 17.05 | 74 | 101400 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-02 03:00 | 16.95 | 73.5 | 101370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-02 04:00 | 16.95 | 73.5 | 101365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-02 05:00 | 16.8 | 75 | 101375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-02 06:00 | 16.75 | 76 | 101425 | 100 | 3000 | 17.1152 | 75.0659 | 21.7634 | 0 | 7.2692 | FALSE | FALSE
2025-12-02 07:00 | 17.7 | 71.5 | 101490 | 100 | 3000 | 17.5309 | 73.0818 | 23.1905 | 0 | 7.2692 | FALSE | FALSE
2025-12-02 08:00 | 20.4 | 60 | 101540 | 100 | 3000 | 18.6936 | 67.7197 | 26.9723 | 0 | 7.2692 | FALSE | FALSE
2025-12-02 09:00 | 23.7 | 50 | 101570 | 100 | 3000 | 20.0753 | 62.68 | 32.3533 | 0 | 7.2692 | FALSE | FALSE
2025-12-02 10:00 | 25.95 | 47 | 101530 | 100 | 3000 | 20.9881 | 61.2576 | 38.0625 | 0 | 7.2692 | FALSE | FALSE
2025-12-02 11:00 | 27.3 | 44.5 | 101430 | 100 | 3000 | 21.5264 | 59.961 | 40.7343 | 0 | 7.2692 | FALSE | FALSE
2025-12-02 12:00 | 28.25 | 40.5 | 101315 | 100 | 3000 | 21.9063 | 57.542 | 40.4495 | 0 | 7.2692 | FALSE | FALSE
2025-12-02 13:00 | 28.6 | 40.5 | 101210 | 100 | 3000 | 22.042 | 57.614 | 41.6241 | 0 | 7.2692 | FALSE | FALSE
2025-12-02 14:00 | 28.25 | 46.5 | 101155 | 100 | 3000 | 21.8916 | 61.527 | 45.8733 | 0 | 7.2692 | FALSE | FALSE
2025-12-02 15:00 | 27.4 | 52.5 | 101135 | 100 | 3000 | 21.5485 | 65.161 | 47.99 | 0 | 7.2692 | FALSE | FALSE
2025-12-02 16:00 | 26.2 | 56.5 | 101140 | 100 | 3000 | 21.0709 | 67.2342 | 46.672 | 0 | 7.2692 | FALSE | FALSE
2025-12-02 17:00 | 25 | 63 | 101175 | 100 | 3000 | 20.5848 | 70.687 | 46.9809 | 0 | 7.2692 | FALSE | FALSE
2025-12-02 18:00 | 24.25 | 68.5 | 101230 | 100 | 3000 | 20.2774 | 73.5693 | 47.9786 | 0 | 7.2692 | FALSE | FALSE
2025-12-02 19:00 | 23.75 | 71.5 | 101280 | 100 | 3000 | 20.0725 | 75.042 | 48.0178 | 0 | 7.2692 | FALSE | FALSE
2025-12-02 20:00 | 23.15 | 74.5 | 101315 | 100 | 3000 | 19.8264 | 76.4242 | 47.5272 | 0 | 7.2692 | FALSE | FALSE
2025-12-02 21:00 | 22.35 | 75.5 | 101325 | 100 | 3000 | 19.4986 | 76.5684 | 44.7185 | 0 | 7.2692 | FALSE | FALSE
2025-12-02 22:00 | 21.4 | 76.5 | 101315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-02 23:00 | 20.2 | 81 | 101285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-03 | 19.15 | 86 | 101245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-03 01:00 | 18.6 | 89.5 | 101220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-03 02:00 | 18.15 | 91.5 | 101205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-03 03:00 | 17.9 | 92.5 | 101205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-03 04:00 | 17.9 | 93 | 101220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-03 05:00 | 17.9 | 92.5 | 101260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-03 06:00 | 17.75 | 92 | 101325 | 100 | 3000 | 17.5519 | 82.7935 | 34.1798 | 0 | 7.2692 | FALSE | FALSE
2025-12-03 07:00 | 18.3 | 89 | 101380 | 100 | 3000 | 17.7895 | 81.5972 | 35.0335 | 0 | 7.2692 | FALSE | FALSE
2025-12-03 08:00 | 20.65 | 78.5 | 101435 | 100 | 3000 | 18.7911 | 77.3677 | 39.2812 | 0 | 7.2692 | FALSE | FALSE
2025-12-03 09:00 | 23.6 | 67 | 101495 | 100 | 3000 | 20.0166 | 72.3804 | 44.1893 | 0 | 7.2692 | FALSE | FALSE
2025-12-03 10:00 | 25.65 | 61 | 101495 | 100 | 3000 | 20.8461 | 69.7341 | 48.128 | 0 | 7.2692 | FALSE | FALSE
2025-12-03 11:00 | 27.1 | 53.5 | 101430 | 100 | 3000 | 21.4295 | 65.6608 | 47.7348 | 0 | 7.2692 | FALSE | FALSE
2025-12-03 12:00 | 28.25 | 45 | 101335 | 100 | 3000 | 21.8953 | 60.5177 | 44.5442 | 0 | 7.2692 | FALSE | FALSE
2025-12-03 13:00 | 28.7 | 43.5 | 101250 | 100 | 3000 | 22.0727 | 59.6421 | 44.7607 | 0 | 7.2692 | FALSE | FALSE
2025-12-03 14:00 | 28.35 | 48 | 101220 | 100 | 3000 | 21.9265 | 62.5448 | 47.6142 | 0 | 7.2692 | FALSE | FALSE
2025-12-03 15:00 | 27.55 | 52 | 101215 | 100 | 3000 | 21.6078 | 64.886 | 48.146 | 0 | 7.2692 | FALSE | FALSE
2025-12-03 16:00 | 26.6 | 58.5 | 101215 | 100 | 3000 | 21.2244 | 68.6374 | 49.9238 | 0 | 7.2692 | FALSE | FALSE
2025-12-03 17:00 | 25.55 | 67.5 | 101240 | 100 | 3000 | 20.7963 | 73.654 | 52.7883 | 0 | 7.2692 | FALSE | FALSE
2025-12-03 18:00 | 24.65 | 71.5 | 101290 | 100 | 3000 | 20.4336 | 75.529 | 51.9385 | 0 | 7.2692 | FALSE | FALSE
2025-12-03 19:00 | 24 | 73 | 101335 | 100 | 3000 | 20.1716 | 76.0306 | 50.1932 | 0 | 7.2692 | FALSE | FALSE
2025-12-03 20:00 | 23.4 | 74.5 | 101365 | 100 | 3000 | 19.9278 | 76.5528 | 48.6293 | 0 | 7.2692 | FALSE | FALSE
2025-12-03 21:00 | 22.6 | 77 | 101385 | 100 | 3000 | 19.5999 | 77.5135 | 46.8261 | 0 | 7.2692 | FALSE | FALSE
2025-12-03 22:00 | 21.65 | 82 | 101385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-03 23:00 | 20.7 | 87.5 | 101370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-04 | 19.85 | 91.5 | 101355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-04 01:00 | 19.3 | 93 | 101360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-04 02:00 | 18.85 | 93 | 101365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-04 03:00 | 18.7 | 91.5 | 101375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-04 04:00 | 18.8 | 89.5 | 101380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-04 05:00 | 18.7 | 88 | 101395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-04 06:00 | 18.6 | 86.5 | 101455 | 100 | 3000 | 17.9188 | 80.5086 | 34.998 | 0 | 7.2692 | FALSE | FALSE
2025-12-04 07:00 | 19.3 | 82 | 101520 | 100 | 3000 | 18.219 | 78.5763 | 35.5289 | 0 | 7.2692 | FALSE | FALSE
2025-12-04 08:00 | 21.55 | 71 | 101585 | 100 | 3000 | 19.171 | 73.7651 | 38.3954 | 0 | 7.2692 | FALSE | FALSE
2025-12-04 09:00 | 24.3 | 59 | 101640 | 100 | 3000 | 20.309 | 68.0151 | 41.2126 | 0 | 7.2692 | FALSE | FALSE
2025-12-04 10:00 | 26.25 | 47.5 | 101630 | 100 | 3000 | 21.1065 | 61.6169 | 39.5595 | 0 | 7.2692 | FALSE | FALSE
2025-12-04 11:00 | 27.65 | 37.5 | 101550 | 100 | 3000 | 21.6788 | 55.4755 | 35.7946 | 0 | 7.2692 | FALSE | FALSE
2025-12-04 12:00 | 28.65 | 33 | 101445 | 100 | 3000 | 22.0806 | 52.5707 | 34.8465 | 0 | 7.2692 | FALSE | FALSE
2025-12-04 13:00 | 29.2 | 31 | 101360 | 100 | 3000 | 22.2996 | 51.2377 | 34.6137 | 0 | 7.2692 | FALSE | FALSE
2025-12-04 14:00 | 29.3 | 31.5 | 101320 | 100 | 3000 | 22.337 | 51.5855 | 35.3914 | 0 | 7.2692 | FALSE | FALSE
2025-12-04 15:00 | 28.65 | 37 | 101300 | 100 | 3000 | 22.0703 | 55.2682 | 38.5553 | 0 | 7.2692 | FALSE | FALSE
2025-12-04 16:00 | 27.25 | 45 | 101300 | 100 | 3000 | 21.5058 | 60.2842 | 40.9703 | 0 | 7.2692 | FALSE | FALSE
2025-12-04 17:00 | 26 | 51 | 101340 | 100 | 3000 | 21.0013 | 63.7519 | 41.4632 | 0 | 7.2692 | FALSE | FALSE
2025-12-04 18:00 | 25.15 | 56.5 | 101405 | 100 | 3000 | 20.654 | 66.8364 | 42.6029 | 0 | 7.2692 | FALSE | FALSE
2025-12-04 19:00 | 24.35 | 62 | 101465 | 100 | 3000 | 20.3255 | 69.8019 | 43.618 | 0 | 7.2692 | FALSE | FALSE
2025-12-04 20:00 | 23.7 | 66 | 101485 | 100 | 3000 | 20.0583 | 71.8528 | 43.8872 | 0 | 7.2692 | FALSE | FALSE
2025-12-04 21:00 | 23.2 | 68 | 101495 | 100 | 3000 | 19.853 | 72.778 | 43.2315 | 0 | 7.2692 | FALSE | FALSE
2025-12-04 22:00 | 22.8 | 69 | 101490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-04 23:00 | 22.15 | 71 | 101445 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-05 | 21.65 | 71.5 | 101420 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-05 01:00 | 21.5 | 71.5 | 101415 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-05 02:00 | 21.15 | 72.5 | 101395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-05 03:00 | 20.95 | 71.5 | 101375 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-05 04:00 | 20.95 | 70 | 101380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-05 05:00 | 20.55 | 71.5 | 101425 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-05 06:00 | 20.15 | 73 | 101490 | 100 | 3000 | 18.5827 | 74.3482 | 33.8498 | 0 | 7.2692 | FALSE | FALSE
2025-12-05 07:00 | 20.4 | 71.5 | 101550 | 100 | 3000 | 18.6889 | 73.6482 | 33.9736 | 0 | 7.2692 | FALSE | FALSE
2025-12-05 08:00 | 21.5 | 67 | 101595 | 100 | 3000 | 19.1526 | 71.6127 | 35.62 | 0 | 7.2692 | FALSE | FALSE
2025-12-05 09:00 | 23.35 | 62.5 | 101645 | 100 | 3000 | 19.9195 | 69.7149 | 39.9921 | 0 | 7.2692 | FALSE | FALSE
2025-12-05 10:00 | 25.25 | 57.5 | 101655 | 100 | 3000 | 20.6925 | 67.4446 | 43.8023 | 0 | 7.2692 | FALSE | FALSE
2025-12-05 11:00 | 27 | 49.5 | 101585 | 100 | 3000 | 21.3985 | 63.0667 | 43.9703 | 0 | 7.2692 | FALSE | FALSE
2025-12-05 12:00 | 28.1 | 42 | 101495 | 100 | 3000 | 21.8443 | 58.4881 | 41.3263 | 0 | 7.2692 | FALSE | FALSE
2025-12-05 13:00 | 28.25 | 38.5 | 101430 | 100 | 3000 | 21.9111 | 56.2067 | 38.645 | 0 | 7.2692 | FALSE | FALSE
2025-12-05 14:00 | 27.9 | 42.5 | 101390 | 100 | 3000 | 21.7653 | 58.7878 | 41.0651 | 0 | 7.2692 | FALSE | FALSE
2025-12-05 15:00 | 27.2 | 51 | 101405 | 100 | 3000 | 21.4737 | 64.1027 | 45.9754 | 0 | 7.2692 | FALSE | FALSE
2025-12-05 16:00 | 26.45 | 54.5 | 101445 | 100 | 3000 | 21.1729 | 66.0525 | 46.0531 | 0 | 7.2692 | FALSE | FALSE
2025-12-05 17:00 | 25.55 | 58.5 | 101470 | 100 | 3000 | 20.8104 | 68.1773 | 45.7471 | 0 | 7.2692 | FALSE | FALSE
2025-12-05 18:00 | 24.25 | 69.5 | 101510 | 100 | 3000 | 20.2762 | 74.1208 | 48.7464 | 0 | 7.2692 | FALSE | FALSE
2025-12-05 19:00 | 23.1 | 76 | 101550 | 100 | 3000 | 19.8047 | 77.212 | 48.3704 | 0 | 7.2692 | FALSE | FALSE
2025-12-05 20:00 | 22.15 | 78 | 101575 | 100 | 3000 | 19.4145 | 77.8013 | 45.5224 | 0 | 7.2692 | FALSE | FALSE
2025-12-05 21:00 | 21.55 | 78.5 | 101580 | 100 | 3000 | 19.1664 | 77.7656 | 43.2067 | 0 | 7.2692 | FALSE | FALSE
2025-12-05 22:00 | 21.65 | 75 | 101575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-05 23:00 | 21.6 | 73.5 | 101550 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-06 | 20.95 | 76.5 | 101530 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-06 01:00 | 19.9 | 82 | 101520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-06 02:00 | 18.85 | 87.5 | 101490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-06 03:00 | 18.55 | 85.5 | 101480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-06 04:00 | 18.55 | 82 | 101490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-06 05:00 | 18.05 | 86 | 101505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-06 06:00 | 17.55 | 90.5 | 101550 | 100 | 3000 | 17.4652 | 81.9782 | 32.5141 | 0 | 7.2692 | FALSE | FALSE
2025-12-06 07:00 | 17.95 | 89.5 | 101600 | 100 | 3000 | 17.6385 | 81.6621 | 33.7581 | 0 | 7.2692 | FALSE | FALSE
2025-12-06 08:00 | 20.1 | 79.5 | 101645 | 100 | 3000 | 18.5592 | 77.6264 | 37.5276 | 0 | 7.2692 | FALSE | FALSE
2025-12-06 09:00 | 23.25 | 66 | 101690 | 100 | 3000 | 19.8753 | 71.651 | 42.0575 | 0 | 7.2692 | FALSE | FALSE
2025-12-06 10:00 | 25.65 | 56.5 | 101680 | 100 | 3000 | 20.8533 | 66.9774 | 44.5876 | 0 | 7.2692 | FALSE | FALSE
2025-12-06 11:00 | 27.1 | 50 | 101615 | 100 | 3000 | 21.4367 | 63.4117 | 44.7747 | 0 | 7.2692 | FALSE | FALSE
2025-12-06 12:00 | 28.1 | 44 | 101530 | 100 | 3000 | 21.8396 | 59.8019 | 43.1373 | 0 | 7.2692 | FALSE | FALSE
2025-12-06 13:00 | 28.55 | 41.5 | 101455 | 100 | 3000 | 22.02 | 58.2496 | 42.4198 | 0 | 7.2692 | FALSE | FALSE
2025-12-06 14:00 | 28 | 46.5 | 101415 | 100 | 3000 | 21.7949 | 61.4305 | 45.0046 | 0 | 7.2692 | FALSE | FALSE
2025-12-06 15:00 | 27.15 | 52.5 | 101390 | 100 | 3000 | 21.4511 | 65.0453 | 47.0677 | 0 | 7.2692 | FALSE | FALSE
2025-12-06 16:00 | 26.6 | 55.5 | 101385 | 100 | 3000 | 21.23 | 66.7399 | 47.4588 | 0 | 7.2692 | FALSE | FALSE
2025-12-06 17:00 | 25.75 | 60.5 | 101405 | 100 | 3000 | 20.8865 | 69.4823 | 48.1267 | 0 | 7.2692 | FALSE | FALSE
2025-12-06 18:00 | 24.95 | 65.5 | 101450 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-06 19:00 | 24.4 | 69.5 | 101495 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-06 20:00 | 23.85 | 74.5 | 101540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-06 21:00 | 23.1 | 78 | 101580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-06 22:00 | 22.45 | 79.5 | 101580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-06 23:00 | 22.05 | 81.5 | 101560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 | 21.4 | 84 | 101545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 01:00 | 20.65 | 86 | 101540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 02:00 | 20.05 | 87 | 101545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 03:00 | 19.55 | 85.5 | 101550 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 04:00 | 19.25 | 83.5 | 101550 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 05:00 | 19.15 | 83.5 | 101575 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 06:00 | 19 | 84.5 | 101625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 07:00 | 19.65 | 81.5 | 101680 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 08:00 | 21.8 | 72 | 101735 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 09:00 | 24.7 | 59.5 | 101785 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 10:00 | 27.05 | 48 | 101775 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 11:00 | 28.5 | 39.5 | 101690 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 12:00 | 29.55 | 34.5 | 101585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 13:00 | 30.3 | 32 | 101505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 14:00 | 30.35 | 32 | 101455 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 15:00 | 29.4 | 38 | 101405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 16:00 | 28.15 | 45.5 | 101380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 17:00 | 26.95 | 52 | 101405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 18:00 | 25.95 | 55.5 | 101475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 19:00 | 25.1 | 51 | 101545 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 20:00 | 23.95 | 48.5 | 101590 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 21:00 | 22.5 | 51.5 | 101615 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 22:00 | 21.4 | 56.5 | 101610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-07 23:00 | 20.6 | 64 | 101590 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-08 | 19.65 | 71 | 101585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-08 01:00 | 18.75 | 76.5 | 101595 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-08 02:00 | 18.05 | 80.5 | 101600 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-08 03:00 | 17.85 | 80 | 101590 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-08 04:00 | 17.85 | 78.5 | 101585 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-08 05:00 | 17.6 | 81 | 101610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-08 06:00 | 17.2 | 84 | 101660 | 100 | 3000 | 17.3128 | 78.8165 | 27.6571 | 0 | 7.2692 | FALSE | FALSE
2025-12-08 07:00 | 17.75 | 81 | 101720 | 100 | 3000 | 17.5523 | 77.5543 | 28.4086 | 0 | 7.2692 | FALSE | FALSE
2025-12-08 08:00 | 20.35 | 68 | 101785 | 100 | 3000 | 18.6692 | 71.8063 | 31.6641 | 0 | 7.2692 | FALSE | FALSE
2025-12-08 09:00 | 24 | 51.5 | 101840 | 100 | 3000 | 20.1961 | 63.5611 | 34.5597 | 0 | 7.2692 | FALSE | FALSE
2025-12-08 10:00 | 27.05 | 36.5 | 101825 | 100 | 3000 | 21.4441 | 54.7687 | 33.0307 | 0 | 7.2692 | FALSE | FALSE
2025-12-08 11:00 | 29 | 24 | 101755 | 100 | 3000 | 22.2407 | 46.4448 | 32.8729 | 0 | 7.2692 | FALSE | FALSE
2025-12-08 12:00 | 30.15 | 18 | 101665 | 100 | 3000 | 22.7066 | 42.0918 | 34.4008 | 0 | 7.2692 | FALSE | FALSE
2025-12-08 13:00 | 30.85 | 17 | 101570 | 100 | 3000 | 22.9809 | 41.2295 | 35.2615 | 0 | 7.2692 | FALSE | FALSE
2025-12-08 14:00 | 31.25 | 17 | 101515 | 100 | 3000 | 23.1348 | 41.1462 | 35.7364 | 0 | 7.2692 | FALSE | FALSE
2025-12-08 15:00 | 31.3 | 17.5 | 101475 | 100 | 3000 | 23.1522 | 41.5038 | 35.7735 | 0 | 7.2692 | FALSE | FALSE
2025-12-08 16:00 | 30.1 | 23.5 | 101460 | 100 | 3000 | 22.67 | 45.9891 | 34.17 | 0 | 7.2692 | FALSE | FALSE
2025-12-08 17:00 | 27.7 | 41 | 101485 | 100 | 3000 | 21.6906 | 57.7647 | 39.0572 | 0 | 7.2692 | FALSE | FALSE
2025-12-08 18:00 | 25.95 | 53.5 | 101525 | 100 | 3000 | 20.9772 | 65.2575 | 43.3238 | 0 | 7.2692 | FALSE | FALSE
2025-12-08 19:00 | 25.2 | 44.5 | 101560 | 100 | 3000 | 20.6914 | 59.6231 | 33.4497 | 0 | 7.2692 | FALSE | FALSE
2025-12-08 20:00 | 24.45 | 35.5 | 101560 | 100 | 3000 | 20.3988 | 54.2602 | 26.6549 | 0 | 7.2692 | FALSE | FALSE
2025-12-08 21:00 | 23.45 | 38 | 101550 | 100 | 3000 | 19.9849 | 55.8091 | 25.2447 | 0 | 7.2692 | FALSE | FALSE
2025-12-08 22:00 | 22.55 | 41.5 | 101540 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-08 23:00 | 21.8 | 42 | 101525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-09 | 21 | 39.5 | 101515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-09 01:00 | 20.3 | 38 | 101495 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-09 02:00 | 19.55 | 38.5 | 101470 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-09 03:00 | 18.75 | 41.5 | 101465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-09 04:00 | 18.05 | 44.5 | 101465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-09 05:00 | 17.3 | 46 | 101485 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-09 06:00 | 16.65 | 48.5 | 101540 | 100 | 3000 | 17.069 | 62.4337 | 15.061 | 0 | 7.2692 | FALSE | FALSE
2025-12-09 07:00 | 17.2 | 49 | 101590 | 100 | 3000 | 17.312 | 62.5153 | 15.9351 | 0 | 7.2692 | FALSE | FALSE
2025-12-09 08:00 | 19.75 | 43.5 | 101630 | 100 | 3000 | 18.4221 | 59.2838 | 19.8677 | 0 | 7.2692 | FALSE | FALSE
2025-12-09 09:00 | 23.55 | 35 | 101665 | 100 | 3000 | 20.0292 | 54.0685 | 25.4345 | 0 | 7.2692 | FALSE | FALSE
2025-12-09 10:00 | 26.75 | 29.5 | 101660 | 100 | 3000 | 21.3384 | 50.3438 | 29.8464 | 0 | 7.2692 | FALSE | FALSE
2025-12-09 11:00 | 28.55 | 27 | 101600 | 100 | 3000 | 22.0568 | 48.5356 | 32.2033 | 0 | 7.2692 | FALSE | FALSE
2025-12-09 12:00 | 29.55 | 26 | 101515 | 100 | 3000 | 22.4495 | 47.7779 | 33.4578 | 0 | 7.2692 | FALSE | FALSE
2025-12-09 13:00 | 29.8 | 27.5 | 101445 | 100 | 3000 | 22.5418 | 48.8103 | 33.7208 | 0 | 7.2692 | FALSE | FALSE
2025-12-09 14:00 | 29.3 | 31.5 | 101410 | 100 | 3000 | 22.3369 | 51.5771 | 35.4081 | 0 | 7.2692 | FALSE | FALSE
2025-12-09 15:00 | 28.3 | 38 | 101375 | 100 | 3000 | 21.9318 | 55.8867 | 38.3437 | 0 | 7.2692 | FALSE | FALSE
2025-12-09 16:00 | 26.95 | 47 | 101350 | 100 | 3000 | 21.3839 | 61.4882 | 41.622 | 0 | 7.2692 | FALSE | FALSE
2025-12-09 17:00 | 25.35 | 59.5 | 101365 | 100 | 3000 | 20.7294 | 68.7151 | 45.7194 | 0 | 7.2692 | FALSE | FALSE
2025-12-09 18:00 | 24.05 | 69 | 101400 | 100 | 3000 | 20.1963 | 73.743 | 47.5131 | 0 | 7.2692 | FALSE | FALSE
2025-12-09 19:00 | 23.2 | 69.5 | 101455 | 100 | 3000 | 19.8515 | 73.6259 | 44.2754 | 0 | 7.2692 | FALSE | FALSE
2025-12-09 20:00 | 22.4 | 64.5 | 101485 | 100 | 3000 | 19.5278 | 70.5436 | 37.5677 | 0 | 7.2692 | FALSE | FALSE
2025-12-09 21:00 | 21.8 | 61 | 101490 | 100 | 3000 | 19.2815 | 68.482 | 32.8946 | 0 | 7.2692 | FALSE | FALSE
2025-12-09 22:00 | 21.15 | 61 | 101480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-09 23:00 | 20.2 | 60.5 | 101435 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-10 | 19.2 | 60.5 | 101390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-10 01:00 | 18.35 | 64.5 | 101365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-10 02:00 | 17.8 | 71 | 101340 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-10 03:00 | 17.45 | 73.5 | 101320 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-10 04:00 | 17.2 | 71.5 | 101330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-10 05:00 | 16.85 | 68.5 | 101360 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-10 06:00 | 15.9 | 64 | 101410 | 100 | 3000 | 16.7377 | 69.6246 | 13.8383 | 0 | 7.2692 | FALSE | FALSE
2025-12-10 07:00 | 16.05 | 58.5 | 101485 | 100 | 3000 | 16.8037 | 67.1263 | 14.0912 | 0 | 7.2692 | FALSE | FALSE
2025-12-10 08:00 | 18.95 | 52 | 101555 | 100 | 3000 | 18.0753 | 63.665 | 18.6225 | 0 | 7.2692 | FALSE | FALSE
2025-12-10 09:00 | 22.85 | 45.5 | 101600 | 100 | 3000 | 19.7295 | 60.0707 | 26.21 | 0 | 7.2692 | FALSE | FALSE
2025-12-10 10:00 | 25.85 | 40 | 101615 | 100 | 3000 | 20.9596 | 56.9299 | 32.0471 | 0 | 7.2692 | FALSE | FALSE
2025-12-10 11:00 | 27.75 | 35 | 101570 | 100 | 3000 | 21.7236 | 53.8508 | 33.8896 | 0 | 7.2692 | FALSE | FALSE
2025-12-10 12:00 | 29 | 30.5 | 101480 | 100 | 3000 | 22.2234 | 50.8851 | 33.556 | 0 | 7.2692 | FALSE | FALSE
2025-12-10 13:00 | 29.8 | 26 | 101395 | 100 | 3000 | 22.5464 | 47.7707 | 33.7308 | 0 | 7.2692 | FALSE | FALSE
2025-12-10 14:00 | 30.1 | 23.5 | 101350 | 100 | 3000 | 22.6701 | 45.999 | 34.1335 | 0 | 7.2692 | FALSE | FALSE
2025-12-10 15:00 | 29.1 | 31.5 | 101330 | 100 | 3000 | 22.2595 | 51.5796 | 34.7853 | 0 | 7.2692 | FALSE | FALSE
2025-12-10 16:00 | 27.1 | 43.5 | 101335 | 100 | 3000 | 21.4499 | 59.2917 | 39.1551 | 0 | 7.2692 | FALSE | FALSE
2025-12-10 17:00 | 25.35 | 52.5 | 101375 | 100 | 3000 | 20.7399 | 64.492 | 40.2409 | 0 | 7.2692 | FALSE | FALSE
2025-12-10 18:00 | 24.15 | 59.5 | 101415 | 100 | 3000 | 20.2478 | 68.2813 | 40.9673 | 0 | 7.2692 | FALSE | FALSE
2025-12-10 19:00 | 23.1 | 63.5 | 101445 | 100 | 3000 | 19.8164 | 70.2172 | 39.6753 | 0 | 7.2692 | FALSE | FALSE
2025-12-10 20:00 | 22.05 | 67.5 | 101465 | 100 | 3000 | 19.3809 | 72.0704 | 38.1574 | 0 | 7.2692 | FALSE | FALSE
2025-12-10 21:00 | 21.2 | 69 | 101480 | 100 | 3000 | 19.0262 | 72.5965 | 35.6758 | 0 | 7.2692 | FALSE | FALSE
2025-12-10 22:00 | 20.45 | 69 | 101480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-10 23:00 | 19.7 | 69 | 101430 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-11 | 19.1 | 69.5 | 101365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-11 01:00 | 18.55 | 75 | 101330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-11 02:00 | 17.9 | 84 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-11 03:00 | 17.45 | 88 | 101290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-11 04:00 | 17.1 | 88.5 | 101290 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-11 05:00 | 16.55 | 90 | 101315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-11 06:00 | 15.9 | 92 | 101365 | 100 | 3000 | 16.742 | 82.1162 | 26.0513 | 0 | 7.2692 | FALSE | FALSE
2025-12-11 07:00 | 16.35 | 88.5 | 101420 | 100 | 3000 | 16.9402 | 80.6704 | 26.2971 | 0 | 7.2692 | FALSE | FALSE
2025-12-11 08:00 | 18.9 | 74 | 101465 | 100 | 3000 | 18.0497 | 74.5083 | 29.3258 | 0 | 7.2692 | FALSE | FALSE
2025-12-11 09:00 | 22.75 | 57 | 101490 | 100 | 3000 | 19.6783 | 66.4872 | 33.8152 | 0 | 7.2692 | FALSE | FALSE
2025-12-11 10:00 | 26.05 | 42 | 101450 | 100 | 3000 | 21.0364 | 58.1944 | 34.3206 | 0 | 7.2692 | FALSE | FALSE
2025-12-11 11:00 | 28.15 | 30 | 101365 | 100 | 3000 | 21.8925 | 50.583 | 31.5747 | 0 | 7.2692 | FALSE | FALSE
2025-12-11 12:00 | 29.3 | 24 | 101275 | 100 | 3000 | 22.3582 | 46.4488 | 33.0995 | 0 | 7.2692 | FALSE | FALSE
2025-12-11 13:00 | 29.7 | 21.5 | 101200 | 100 | 3000 | 22.5213 | 44.6707 | 33.6204 | 0 | 7.2692 | FALSE | FALSE
2025-12-11 14:00 | 29.8 | 21 | 101155 | 100 | 3000 | 22.5617 | 44.3098 | 33.7397 | 0 | 7.2692 | FALSE | FALSE
2025-12-11 15:00 | 28.8 | 31.5 | 101140 | 100 | 3000 | 22.1431 | 51.593 | 33.8417 | 0 | 7.2692 | FALSE | FALSE
2025-12-11 16:00 | 26.85 | 45.5 | 101150 | 100 | 3000 | 21.3475 | 60.5345 | 39.9586 | 0 | 7.2692 | FALSE | FALSE
2025-12-11 17:00 | 25.4 | 54.5 | 101165 | 100 | 3000 | 20.7569 | 65.7355 | 41.9727 | 0 | 7.2692 | FALSE | FALSE
2025-12-11 18:00 | 24.55 | 60.5 | 101195 | 100 | 3000 | 20.4079 | 69.0259 | 43.2675 | 0 | 7.2692 | FALSE | FALSE
2025-12-11 19:00 | 23.7 | 62 | 101230 | 100 | 3000 | 20.0626 | 69.5923 | 40.9858 | 0 | 7.2692 | FALSE | FALSE
2025-12-11 20:00 | 22.65 | 64 | 101260 | 100 | 3000 | 19.6312 | 70.3704 | 38.2047 | 0 | 7.2692 | FALSE | FALSE
2025-12-11 21:00 | 21.45 | 65.5 | 101285 | 100 | 3000 | 19.1327 | 70.8334 | 34.4321 | 0 | 7.2692 | FALSE | FALSE
2025-12-11 22:00 | 20.4 | 67.5 | 101285 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-11 23:00 | 19.55 | 71.5 | 101270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-12 | 18.9 | 74.5 | 101245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-12 01:00 | 18.4 | 75.5 | 101205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-12 02:00 | 17.8 | 75.5 | 101175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-12 03:00 | 17.3 | 79 | 101170 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-12 04:00 | 17.05 | 86.5 | 101170 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-12 05:00 | 17 | 90.5 | 101180 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-12 06:00 | 16.8 | 90 | 101210 | 100 | 3000 | 17.138 | 81.5156 | 28.9719 | 0 | 7.2692 | FALSE | FALSE
2025-12-12 07:00 | 17.2 | 76.5 | 101250 | 100 | 3000 | 17.3126 | 75.3837 | 23.8088 | 0 | 7.2692 | FALSE | FALSE
2025-12-12 08:00 | 19.4 | 50 | 101305 | 100 | 3000 | 18.2698 | 62.6532 | 19.2604 | 0 | 7.2692 | FALSE | FALSE
2025-12-12 09:00 | 22.9 | 32 | 101350 | 100 | 3000 | 19.7621 | 52.5209 | 24.4604 | 0 | 7.2692 | FALSE | FALSE
2025-12-12 10:00 | 26.25 | 27.5 | 101345 | 100 | 3000 | 21.1415 | 49.1881 | 29.1139 | 0 | 7.2692 | FALSE | FALSE
2025-12-12 11:00 | 28.35 | 25.5 | 101285 | 100 | 3000 | 21.9821 | 47.5855 | 31.8713 | 0 | 7.2692 | FALSE | FALSE
2025-12-12 12:00 | 29.25 | 24 | 101190 | 100 | 3000 | 22.3388 | 46.4631 | 33.0091 | 0 | 7.2692 | FALSE | FALSE
2025-12-12 13:00 | 29.65 | 24.5 | 101110 | 100 | 3000 | 22.493 | 46.7676 | 33.4766 | 0 | 7.2692 | FALSE | FALSE
2025-12-12 14:00 | 29.8 | 25 | 101050 | 100 | 3000 | 22.5496 | 47.1057 | 33.6351 | 0 | 7.2692 | FALSE | FALSE
2025-12-12 15:00 | 29.4 | 28 | 101015 | 100 | 3000 | 22.3858 | 49.2111 | 33.0745 | 0 | 7.2692 | FALSE | FALSE
2025-12-12 16:00 | 28.1 | 35 | 101015 | 100 | 3000 | 21.8611 | 53.9191 | 34.8996 | 0 | 7.2692 | FALSE | FALSE
2025-12-12 17:00 | 26.3 | 41 | 101040 | 100 | 3000 | 21.1379 | 57.6377 | 34.2747 | 0 | 7.2692 | FALSE | FALSE
2025-12-12 18:00 | 25.05 | 45 | 101080 | 100 | 3000 | 20.6303 | 59.9568 | 33.2627 | 0 | 7.2692 | FALSE | FALSE
2025-12-12 19:00 | 24.35 | 48.5 | 101125 | 100 | 3000 | 20.3422 | 61.9421 | 33.5024 | 0 | 7.2692 | FALSE | FALSE
2025-12-12 20:00 | 23.55 | 52 | 101155 | 100 | 3000 | 20.0119 | 63.8475 | 33.2135 | 0 | 7.2692 | FALSE | FALSE
2025-12-12 21:00 | 22.7 | 55 | 101155 | 100 | 3000 | 19.6594 | 65.4027 | 32.2196 | 0 | 7.2692 | FALSE | FALSE
2025-12-12 22:00 | 21.85 | 57 | 101140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-12 23:00 | 20.95 | 59 | 101095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-13 | 20.1 | 60 | 101045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-13 01:00 | 19.35 | 60 | 101030 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-13 02:00 | 18.7 | 60.5 | 101020 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-13 03:00 | 18.5 | 61.5 | 101000 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-13 04:00 | 18.6 | 63.5 | 100990 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-13 05:00 | 18.35 | 65.5 | 101035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-13 06:00 | 17.85 | 66.5 | 101125 | 100 | 3000 | 17.5965 | 70.7683 | 21.1035 | 0 | 7.2692 | FALSE | FALSE
2025-12-13 07:00 | 18.3 | 65 | 101195 | 100 | 3000 | 17.7921 | 70.0683 | 21.9889 | 0 | 7.2692 | FALSE | FALSE
2025-12-13 08:00 | 20.4 | 58 | 101245 | 100 | 3000 | 18.6945 | 66.7204 | 25.7308 | 0 | 7.2692 | FALSE | FALSE
2025-12-13 09:00 | 23.35 | 47.5 | 101285 | 100 | 3000 | 19.9343 | 61.2492 | 29.2942 | 0 | 7.2692 | FALSE | FALSE
2025-12-13 10:00 | 26.15 | 38 | 101275 | 100 | 3000 | 21.0832 | 55.7394 | 31.3344 | 0 | 7.2692 | FALSE | FALSE
2025-12-13 11:00 | 28.2 | 32.5 | 101205 | 100 | 3000 | 21.9062 | 52.2515 | 32.9601 | 0 | 7.2692 | FALSE | FALSE
2025-12-13 12:00 | 29.25 | 30.5 | 101115 | 100 | 3000 | 22.3205 | 50.9191 | 34.2371 | 0 | 7.2692 | FALSE | FALSE
2025-12-13 13:00 | 29.2 | 32.5 | 101045 | 100 | 3000 | 22.2956 | 52.2911 | 35.9979 | 0 | 7.2692 | FALSE | FALSE
2025-12-13 14:00 | 28.65 | 36 | 101000 | 100 | 3000 | 22.073 | 54.6257 | 37.5703 | 0 | 7.2692 | FALSE | FALSE
2025-12-13 15:00 | 28.15 | 37.5 | 100955 | 100 | 3000 | 21.8747 | 55.579 | 37.3239 | 0 | 7.2692 | FALSE | FALSE
2025-12-13 16:00 | 27.1 | 43 | 100945 | 100 | 3000 | 21.451 | 59.0107 | 38.6641 | 0 | 7.2692 | FALSE | FALSE
2025-12-13 17:00 | 25.65 | 53.5 | 100975 | 100 | 3000 | 20.8581 | 65.2225 | 42.1071 | 0 | 7.2692 | FALSE | FALSE
2025-12-13 18:00 | 24.7 | 62 | 101020 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-13 19:00 | 24.15 | 66.5 | 101070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-13 20:00 | 23.75 | 69.5 | 101095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-13 21:00 | 23.45 | 70 | 101110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-13 22:00 | 22.6 | 69 | 101115 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-13 23:00 | 21.45 | 68.5 | 101090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 | 20.9 | 65.5 | 101045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 01:00 | 20.35 | 62.5 | 101015 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 02:00 | 19.5 | 62.5 | 101010 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 03:00 | 19.2 | 60 | 100990 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 04:00 | 19.4 | 60.5 | 101025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 05:00 | 19.6 | 75.5 | 101125 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 06:00 | 20.1 | 85.5 | 101195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 07:00 | 21.05 | 81.5 | 101260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 08:00 | 22.6 | 72.5 | 101330 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 09:00 | 24.15 | 61.5 | 101390 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 10:00 | 25.05 | 55 | 101405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 11:00 | 24.85 | 55.5 | 101365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 12:00 | 24.05 | 60 | 101300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 13:00 | 23.7 | 60.5 | 101240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 14:00 | 24.25 | 53 | 101195 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 15:00 | 24.7 | 52 | 101165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 16:00 | 24.2 | 58 | 101175 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 17:00 | 23.45 | 62.5 | 101205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 18:00 | 22.6 | 69 | 101250 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 19:00 | 22 | 72.5 | 101305 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 20:00 | 21.6 | 74 | 101350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 21:00 | 21.25 | 74 | 101380 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 22:00 | 20.8 | 74 | 101385 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-14 23:00 | 20.1 | 76.5 | 101350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-15 | 19.25 | 79.5 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-15 01:00 | 18.2 | 85 | 101295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-15 02:00 | 17.25 | 91 | 101280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-15 03:00 | 16.95 | 89.5 | 101275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-15 04:00 | 17 | 86 | 101265 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-15 05:00 | 16.95 | 86 | 101260 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-15 06:00 | 16.75 | 87 | 101285 | 100 | 3000 | 17.1159 | 80.1188 | 27.2607 | 0 | 7.2692 | FALSE | FALSE
2025-12-15 07:00 | 17.35 | 84.5 | 101315 | 100 | 3000 | 17.3782 | 79.1342 | 28.5412 | 0 | 7.2692 | FALSE | FALSE
2025-12-15 08:00 | 19.75 | 73.5 | 101365 | 100 | 3000 | 18.4129 | 74.4969 | 32.4976 | 0 | 7.2692 | FALSE | FALSE
2025-12-15 09:00 | 22.9 | 60.5 | 101405 | 100 | 3000 | 19.7371 | 68.4819 | 36.7973 | 0 | 7.2692 | FALSE | FALSE
2025-12-15 10:00 | 25.3 | 50.5 | 101375 | 100 | 3000 | 20.7228 | 63.2733 | 38.4863 | 0 | 7.2692 | FALSE | FALSE
2025-12-15 11:00 | 26.9 | 44 | 101270 | 100 | 3000 | 21.3701 | 59.5812 | 38.8772 | 0 | 7.2692 | FALSE | FALSE
2025-12-15 12:00 | 28.35 | 40 | 101115 | 100 | 3000 | 21.9464 | 57.2462 | 40.2976 | 0 | 7.2692 | FALSE | FALSE
2025-12-15 13:00 | 29.65 | 35.5 | 100995 | 100 | 3000 | 22.4601 | 54.3962 | 40.3177 | 0 | 7.2692 | FALSE | FALSE
2025-12-15 14:00 | 30.45 | 31.5 | 100940 | 100 | 3000 | 22.7785 | 51.679 | 38.8372 | 0 | 7.2692 | FALSE | FALSE
2025-12-15 15:00 | 29.85 | 35.5 | 100915 | 100 | 3000 | 22.5367 | 54.4297 | 40.95 | 0 | 7.2692 | FALSE | FALSE
2025-12-15 16:00 | 27.75 | 50.5 | 100910 | 100 | 3000 | 21.6887 | 64.0146 | 47.5451 | 0 | 7.2692 | FALSE | FALSE
2025-12-15 17:00 | 26 | 61 | 100930 | 100 | 3000 | 20.9843 | 69.9481 | 49.4811 | 0 | 7.2692 | FALSE | FALSE
2025-12-15 18:00 | 25.3 | 61 | 100980 | 100 | 3000 | 20.7072 | 69.6378 | 46.6362 | 0 | 7.2692 | FALSE | FALSE
2025-12-15 19:00 | 24.5 | 64 | 101025 | 100 | 3000 | 20.3834 | 71.0786 | 45.6649 | 0 | 7.2692 | FALSE | FALSE
2025-12-15 20:00 | 23.6 | 70.5 | 101050 | 100 | 3000 | 20.0129 | 74.4212 | 46.6345 | 0 | 7.2692 | FALSE | FALSE
2025-12-15 21:00 | 23.05 | 74.5 | 101075 | 100 | 3000 | 19.7857 | 76.3978 | 47.0657 | 0 | 7.2692 | FALSE | FALSE
2025-12-15 22:00 | 22.75 | 75.5 | 101080 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-15 23:00 | 22.5 | 74.5 | 101040 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-16 | 22.3 | 73 | 100985 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-16 01:00 | 22.2 | 70.5 | 100950 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-16 02:00 | 21.9 | 68.5 | 100900 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-16 03:00 | 21.95 | 66 | 100855 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-16 04:00 | 22.3 | 61 | 100840 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-16 05:00 | 22.05 | 56.5 | 100855 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-16 06:00 | 21.5 | 57 | 100900 | 100 | 3000 | 19.1587 | 66.348 | 29.1136 | 0 | 7.2692 | FALSE | FALSE
2025-12-16 07:00 | 21.4 | 59.5 | 100960 | 100 | 3000 | 19.1153 | 67.6615 | 30.3588 | 0 | 7.2692 | FALSE | FALSE
2025-12-16 08:00 | 22.1 | 57.5 | 101040 | 100 | 3000 | 19.4088 | 66.6915 | 31.6778 | 0 | 7.2692 | FALSE | FALSE
2025-12-16 09:00 | 23.4 | 52.5 | 101105 | 100 | 3000 | 19.9499 | 64.1143 | 33.0223 | 0 | 7.2692 | FALSE | FALSE
2025-12-16 10:00 | 24.5 | 48.5 | 101125 | 100 | 3000 | 20.4031 | 61.9628 | 34.0333 | 0 | 7.2692 | FALSE | FALSE
2025-12-16 11:00 | 25.3 | 46 | 101075 | 100 | 3000 | 20.7295 | 60.5888 | 34.9102 | 0 | 7.2692 | FALSE | FALSE
2025-12-16 12:00 | 25.95 | 43.5 | 100970 | 100 | 3000 | 20.994 | 59.1577 | 35.1381 | 0 | 7.2692 | FALSE | FALSE
2025-12-16 13:00 | 26.5 | 41 | 100900 | 100 | 3000 | 21.2176 | 57.6702 | 34.9216 | 0 | 7.2692 | FALSE | FALSE
2025-12-16 14:00 | 26.65 | 40.5 | 100870 | 100 | 3000 | 21.2781 | 57.3733 | 34.9966 | 0 | 7.2692 | FALSE | FALSE
2025-12-16 15:00 | 26.2 | 42 | 100840 | 100 | 3000 | 21.0964 | 58.2703 | 34.7381 | 0 | 7.2692 | FALSE | FALSE
2025-12-16 16:00 | 25.6 | 44 | 100810 | 100 | 3000 | 20.8531 | 59.4396 | 34.3229 | 0 | 7.2692 | FALSE | FALSE
2025-12-16 17:00 | 24.7 | 49 | 100800 | 100 | 3000 | 20.4835 | 62.3218 | 35.0838 | 0 | 7.2692 | FALSE | FALSE
2025-12-16 18:00 | 23.6 | 57.5 | 100830 | 100 | 3000 | 20.0266 | 67.0328 | 37.3173 | 0 | 7.2692 | FALSE | FALSE
2025-12-16 19:00 | 22.55 | 68 | 100865 | 100 | 3000 | 19.5868 | 72.5884 | 40.4811 | 0 | 7.2692 | FALSE | FALSE
2025-12-16 20:00 | 21.4 | 77 | 100880 | 100 | 3000 | 19.105 | 76.9758 | 41.5418 | 0 | 7.2692 | FALSE | FALSE
2025-12-16 21:00 | 20.6 | 79.5 | 100875 | 100 | 3000 | 18.7696 | 77.9275 | 39.6386 | 0 | 7.2692 | FALSE | FALSE
2025-12-16 22:00 | 20.55 | 77 | 100850 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-16 23:00 | 20.45 | 76.5 | 100820 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-17 | 20.1 | 78.5 | 100795 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-17 01:00 | 20.55 | 74 | 100770 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-17 02:00 | 21.3 | 64 | 100750 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-17 03:00 | 22.15 | 56.5 | 100700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-17 04:00 | 22.75 | 54.5 | 100645 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-17 05:00 | 22.7 | 55.5 | 100690 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-17 06:00 | 22.75 | 57.5 | 100805 | 100 | 3000 | 19.678 | 66.8395 | 34.0927 | 0 | 7.2692 | FALSE | FALSE
2025-12-17 07:00 | 22.9 | 60.5 | 100915 | 100 | 3000 | 19.7371 | 68.5348 | 36.7486 | 0 | 7.2692 | FALSE | FALSE
2025-12-17 08:00 | 23.1 | 63.5 | 101020 | 100 | 3000 | 19.8164 | 70.263 | 39.632 | 0 | 7.2692 | FALSE | FALSE
2025-12-17 09:00 | 23.45 | 63.5 | 101120 | 100 | 3000 | 19.9593 | 70.3721 | 41.0452 | 0 | 7.2692 | FALSE | FALSE
2025-12-17 10:00 | 25 | 56.5 | 101150 | 100 | 3000 | 20.594 | 66.8148 | 41.9892 | 0 | 7.2692 | FALSE | FALSE
2025-12-17 11:00 | 26.85 | 48.5 | 101095 | 100 | 3000 | 21.3416 | 62.4395 | 42.4929 | 0 | 7.2692 | FALSE | FALSE
2025-12-17 12:00 | 27.85 | 44 | 101015 | 100 | 3000 | 21.7425 | 59.7947 | 42.1673 | 0 | 7.2692 | FALSE | FALSE
2025-12-17 13:00 | 28.45 | 40.5 | 100945 | 100 | 3000 | 21.984 | 57.612 | 41.0665 | 0 | 7.2692 | FALSE | FALSE
2025-12-17 14:00 | 28.4 | 38.5 | 100915 | 100 | 3000 | 21.9696 | 56.2755 | 39.054 | 0 | 7.2692 | FALSE | FALSE
2025-12-17 15:00 | 27.7 | 42.5 | 100935 | 100 | 3000 | 21.6874 | 58.794 | 40.2974 | 0 | 7.2692 | FALSE | FALSE
2025-12-17 16:00 | 27.15 | 46 | 100970 | 100 | 3000 | 21.4645 | 60.9349 | 41.4256 | 0 | 7.2692 | FALSE | FALSE
2025-12-17 17:00 | 26.5 | 47.5 | 101020 | 100 | 3000 | 21.2056 | 61.7324 | 40.3705 | 0 | 7.2692 | FALSE | FALSE
2025-12-17 18:00 | 25.2 | 55.5 | 101090 | 100 | 3000 | 20.6755 | 66.2848 | 41.9787 | 0 | 7.2692 | FALSE | FALSE
2025-12-17 19:00 | 24.05 | 66 | 101140 | 100 | 3000 | 20.1998 | 72.0376 | 45.2971 | 0 | 7.2692 | FALSE | FALSE
2025-12-17 20:00 | 23.25 | 72.5 | 101180 | 100 | 3000 | 19.869 | 75.3667 | 46.5554 | 0 | 7.2692 | FALSE | FALSE
2025-12-17 21:00 | 22.5 | 75.5 | 101210 | 100 | 3000 | 19.5602 | 76.6557 | 45.3609 | 0 | 7.2692 | FALSE | FALSE
2025-12-17 22:00 | 21.6 | 78.5 | 101230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-17 23:00 | 21.3 | 77 | 101230 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-18 | 21.45 | 74.5 | 101225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-18 01:00 | 21.3 | 77 | 101225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-18 02:00 | 21.25 | 80 | 101220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-18 03:00 | 21.2 | 78.5 | 101190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-18 04:00 | 20.9 | 77.5 | 101170 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-18 05:00 | 20.65 | 78.5 | 101210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-18 06:00 | 20.15 | 79 | 101280 | 100 | 3000 | 18.5805 | 77.4342 | 37.4228 | 0 | 7.2692 | FALSE | FALSE
2025-12-18 07:00 | 20.05 | 79.5 | 101335 | 100 | 3000 | 18.5381 | 77.6419 | 37.2943 | 0 | 7.2692 | FALSE | FALSE
2025-12-18 08:00 | 20.9 | 79 | 101405 | 100 | 3000 | 18.8955 | 77.7417 | 40.6697 | 0 | 7.2692 | FALSE | FALSE
2025-12-18 09:00 | 23.05 | 69.5 | 101450 | 100 | 3000 | 19.7904 | 73.5605 | 43.6436 | 0 | 7.2692 | FALSE | FALSE
2025-12-18 10:00 | 24.45 | 62.5 | 101420 | 100 | 3000 | 20.3652 | 70.1377 | 44.3889 | 0 | 7.2692 | FALSE | FALSE
2025-12-18 11:00 | 23.95 | 65.5 | 101350 | 100 | 3000 | 20.16 | 71.6842 | 44.5432 | 0 | 7.2692 | FALSE | FALSE
2025-12-18 12:00 | 22.8 | 71.5 | 101270 | 100 | 3000 | 19.6864 | 74.5838 | 43.9463 | 0 | 7.2692 | FALSE | FALSE
2025-12-18 13:00 | 21.8 | 77.5 | 101190 | 100 | 3000 | 19.2706 | 77.3968 | 43.6249 | 0 | 7.2692 | FALSE | FALSE
2025-12-18 14:00 | 22.4 | 76.5 | 101095 | 100 | 3000 | 19.5184 | 77.1659 | 45.5834 | 0 | 7.2692 | FALSE | FALSE
2025-12-18 15:00 | 22.95 | 74.5 | 101030 | 100 | 3000 | 19.745 | 76.3509 | 46.625 | 0 | 7.2692 | FALSE | FALSE
2025-12-18 16:00 | 22.65 | 75.5 | 100970 | 100 | 3000 | 19.6216 | 76.758 | 45.9927 | 0 | 7.2692 | FALSE | FALSE
2025-12-18 17:00 | 22.55 | 76.5 | 100895 | 100 | 3000 | 19.5798 | 77.2655 | 46.2228 | 0 | 7.2692 | FALSE | FALSE
2025-12-18 18:00 | 22.55 | 76.5 | 100835 | 100 | 3000 | 19.5798 | 77.2721 | 46.2172 | 0 | 7.2692 | FALSE | FALSE
2025-12-18 19:00 | 22.25 | 78 | 100805 | 100 | 3000 | 19.4556 | 77.939 | 45.8956 | 0 | 7.2692 | FALSE | FALSE
2025-12-18 20:00 | 21.95 | 80 | 100805 | 100 | 3000 | 19.3307 | 78.8627 | 45.8799 | 0 | 7.2692 | FALSE | FALSE
2025-12-18 21:00 | 22.1 | 78.5 | 100770 | 100 | 3000 | 19.3936 | 78.1355 | 45.5601 | 0 | 7.2692 | FALSE | FALSE
2025-12-18 22:00 | 23.15 | 67.5 | 100780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-18 23:00 | 22.35 | 72.5 | 100870 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-19 | 20.2 | 88 | 100915 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-19 01:00 | 20 | 89 | 100930 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-19 02:00 | 20 | 89.5 | 100940 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-19 03:00 | 19.7 | 92.5 | 100950 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-19 04:00 | 19.85 | 93.5 | 100945 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-19 05:00 | 20 | 92.5 | 100970 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-19 06:00 | 20.05 | 90 | 101035 | 100 | 3000 | 18.5343 | 83.0062 | 43.4892 | 0 | 7.2692 | FALSE | FALSE
2025-12-19 07:00 | 19.95 | 87.5 | 101095 | 100 | 3000 | 18.493 | 81.6788 | 41.5641 | 0 | 7.2692 | FALSE | FALSE
2025-12-19 08:00 | 20 | 85 | 101165 | 100 | 3000 | 18.515 | 80.4305 | 40.3203 | 0 | 7.2692 | FALSE | FALSE
2025-12-19 09:00 | 20.1 | 83 | 101245 | 100 | 3000 | 18.5579 | 79.4535 | 39.584 | 0 | 7.2692 | FALSE | FALSE
2025-12-19 10:00 | 20.05 | 79 | 101285 | 100 | 3000 | 18.5382 | 77.3936 | 36.9946 | 0 | 7.2692 | FALSE | FALSE
2025-12-19 11:00 | 20.15 | 71 | 101240 | 100 | 3000 | 18.5834 | 73.3554 | 32.6367 | 0 | 7.2692 | FALSE | FALSE
2025-12-19 12:00 | 20.25 | 65.5 | 101170 | 100 | 3000 | 18.6279 | 70.5704 | 29.7191 | 0 | 7.2692 | FALSE | FALSE
2025-12-19 13:00 | 20.15 | 65 | 101130 | 100 | 3000 | 18.5857 | 70.3002 | 29.0281 | 0 | 7.2692 | FALSE | FALSE
2025-12-19 14:00 | 19.75 | 65 | 101110 | 100 | 3000 | 18.4155 | 70.2361 | 27.4875 | 0 | 7.2692 | FALSE | FALSE
2025-12-19 15:00 | 19.55 | 62.5 | 101100 | 100 | 3000 | 18.3309 | 68.952 | 25.2622 | 0 | 7.2692 | FALSE | FALSE
2025-12-19 16:00 | 19.15 | 64 | 101120 | 100 | 3000 | 18.1591 | 69.6579 | 24.6254 | 0 | 7.2692 | FALSE | FALSE
2025-12-19 17:00 | 18.15 | 68.5 | 101155 | 100 | 3000 | 17.7267 | 71.7451 | 23.3212 | 0 | 7.2692 | FALSE | FALSE
2025-12-19 18:00 | 17.1 | 73 | 101200 | 100 | 3000 | 17.2687 | 73.7511 | 21.62 | 0 | 7.2692 | FALSE | FALSE
2025-12-19 19:00 | 16.25 | 76 | 101245 | 100 | 3000 | 16.8946 | 75.0343 | 19.7869 | 0 | 7.2692 | FALSE | FALSE
2025-12-19 20:00 | 15.5 | 77.5 | 101270 | 100 | 3000 | 16.5619 | 75.6431 | 17.557 | 0 | 7.2692 | FALSE | FALSE
2025-12-19 21:00 | 15.1 | 79 | 101290 | 100 | 3000 | 16.3835 | 76.2743 | 16.679 | 0 | 7.2692 | FALSE | FALSE
2025-12-19 22:00 | 15.05 | 78.5 | 101305 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-19 23:00 | 14.65 | 78.5 | 101280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-20 | 13.85 | 80.5 | 101235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-20 01:00 | 13.45 | 82.5 | 101220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-20 02:00 | 13.35 | 84 | 101220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-20 03:00 | 13.2 | 83 | 101215 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-20 04:00 | 13.05 | 81 | 101210 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-20 05:00 | 12.85 | 81.5 | 101245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-20 06:00 | 12.8 | 82.5 | 101310 | 100 | 3000 | 15.3431 | 77.755 | 9.1926 | 0 | 7.2692 | FALSE | FALSE
2025-12-20 07:00 | 13.05 | 82 | 101370 | 100 | 3000 | 15.4573 | 77.5284 | 9.9573 | 0 | 7.2692 | FALSE | FALSE
2025-12-20 08:00 | 13.95 | 80 | 101435 | 100 | 3000 | 15.8661 | 76.661 | 12.6163 | 0 | 7.2692 | FALSE | FALSE
2025-12-20 09:00 | 15.4 | 76 | 101500 | 100 | 3000 | 16.517 | 74.9492 | 16.4635 | 0 | 7.2692 | FALSE | FALSE
2025-12-20 10:00 | 17 | 71.5 | 101510 | 100 | 3000 | 17.2248 | 73.0088 | 20.4714 | 0 | 7.2692 | FALSE | FALSE
2025-12-20 11:00 | 18.5 | 69 | 101455 | 100 | 3000 | 17.8782 | 71.9933 | 24.9571 | 0 | 7.2692 | FALSE | FALSE
2025-12-20 12:00 | 19.85 | 59.5 | 101365 | 100 | 3000 | 18.4599 | 67.4325 | 24.6243 | 0 | 7.2692 | FALSE | FALSE
2025-12-20 13:00 | 20.4 | 51 | 101290 | 100 | 3000 | 18.6973 | 63.0959 | 21.4451 | 0 | 7.2692 | FALSE | FALSE
2025-12-20 14:00 | 20.15 | 51 | 101260 | 100 | 3000 | 18.5908 | 63.1093 | 20.5847 | 0 | 7.2692 | FALSE | FALSE
2025-12-20 15:00 | 19.8 | 52.5 | 101260 | 100 | 3000 | 18.4408 | 63.8906 | 20.2798 | 0 | 7.2692 | FALSE | FALSE
2025-12-20 16:00 | 18.85 | 58 | 101270 | 100 | 3000 | 18.0311 | 66.6628 | 20.1219 | 0 | 7.2692 | FALSE | FALSE
2025-12-20 17:00 | 17.25 | 66 | 101300 | 100 | 3000 | 17.3343 | 70.4904 | 18.5963 | 0 | 7.2692 | FALSE | FALSE
2025-12-20 18:00 | 16 | 72.5 | 101365 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-20 19:00 | 15.25 | 77 | 101405 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-20 20:00 | 14.45 | 79 | 101430 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-20 21:00 | 14.1 | 77 | 101460 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-20 22:00 | 14.2 | 74.5 | 101475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-20 23:00 | 13.9 | 75 | 101480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 | 13.25 | 77.5 | 101480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 01:00 | 12.6 | 80.5 | 101480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 02:00 | 12.1 | 82 | 101475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 03:00 | 11.8 | 80.5 | 101475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 04:00 | 11.6 | 80 | 101485 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 05:00 | 11.3 | 82 | 101515 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 06:00 | 10.95 | 83.5 | 101560 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 07:00 | 11.2 | 83 | 101625 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 08:00 | 12.75 | 79.5 | 101705 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 09:00 | 15.25 | 72.5 | 101770 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 10:00 | 17.5 | 64.5 | 101780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 11:00 | 19 | 57.5 | 101735 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 12:00 | 19.95 | 51.5 | 101680 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 13:00 | 20.55 | 48 | 101610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 14:00 | 20.9 | 48 | 101555 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 15:00 | 21.1 | 52.5 | 101520 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 16:00 | 20.4 | 63 | 101525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 17:00 | 18.9 | 72.5 | 101580 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 18:00 | 17.9 | 77 | 101630 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 19:00 | 17.1 | 80.5 | 101665 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 20:00 | 16.25 | 83.5 | 101690 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 21:00 | 15.9 | 81.5 | 101700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 22:00 | 15.9 | 77.5 | 101690 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-21 23:00 | 15.45 | 79 | 101675 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-22 | 14.75 | 81.5 | 101680 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-22 01:00 | 14.2 | 82.5 | 101690 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-22 02:00 | 13.65 | 83.5 | 101700 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-22 03:00 | 13.4 | 83.5 | 101715 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-22 04:00 | 13.4 | 82.5 | 101710 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-22 05:00 | 13.15 | 82.5 | 101715 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-22 06:00 | 12.75 | 83.5 | 101750 | 100 | 3000 | 15.3207 | 78.1003 | 9.3785 | 0 | 7.2692 | FALSE | FALSE
2025-12-22 07:00 | 13.3 | 81.5 | 101795 | 100 | 3000 | 15.5713 | 77.2534 | 10.7051 | 0 | 7.2692 | FALSE | FALSE
2025-12-22 08:00 | 15.35 | 74.5 | 101850 | 100 | 3000 | 16.4944 | 74.2447 | 15.5682 | 0 | 7.2692 | FALSE | FALSE
2025-12-22 09:00 | 18.05 | 67.5 | 101905 | 100 | 3000 | 17.6834 | 71.1655 | 22.4215 | 0 | 7.2692 | FALSE | FALSE
2025-12-22 10:00 | 20.4 | 56 | 101895 | 100 | 3000 | 18.6952 | 65.6129 | 24.5498 | 0 | 7.2692 | FALSE | FALSE
2025-12-22 11:00 | 21.7 | 44.5 | 101815 | 100 | 3000 | 19.2502 | 59.5354 | 22.7761 | 0 | 7.2692 | FALSE | FALSE
2025-12-22 12:00 | 22.2 | 42 | 101725 | 100 | 3000 | 19.4616 | 58.1452 | 23.4893 | 0 | 7.2692 | FALSE | FALSE
2025-12-22 13:00 | 22.5 | 42.5 | 101640 | 100 | 3000 | 19.5865 | 58.4071 | 23.8955 | 0 | 7.2692 | FALSE | FALSE
2025-12-22 14:00 | 22.55 | 43.5 | 101590 | 100 | 3000 | 19.6066 | 58.9639 | 23.949 | 0 | 7.2692 | FALSE | FALSE
2025-12-22 15:00 | 22.25 | 47.5 | 101565 | 100 | 3000 | 19.4785 | 61.1787 | 25.5476 | 0 | 7.2692 | FALSE | FALSE
2025-12-22 16:00 | 20.95 | 55.5 | 101555 | 100 | 3000 | 18.9283 | 65.4244 | 26.2008 | 0 | 7.2692 | FALSE | FALSE
2025-12-22 17:00 | 19 | 63 | 101585 | 100 | 3000 | 18.0948 | 69.0949 | 23.514 | 0 | 7.2692 | FALSE | FALSE
2025-12-22 18:00 | 17.7 | 67.5 | 101635 | 100 | 3000 | 17.5311 | 71.1716 | 21.0807 | 0 | 7.2692 | FALSE | FALSE
2025-12-22 19:00 | 16.95 | 71 | 101680 | 100 | 3000 | 17.2028 | 72.753 | 20.027 | 0 | 7.2692 | FALSE | FALSE
2025-12-22 20:00 | 16.15 | 74.5 | 101720 | 100 | 3000 | 16.8502 | 74.2907 | 18.6666 | 0 | 7.2692 | FALSE | FALSE
2025-12-22 21:00 | 15.4 | 77 | 101745 | 100 | 3000 | 16.5172 | 75.3566 | 16.9273 | 0 | 7.2692 | FALSE | FALSE
2025-12-22 22:00 | 14.8 | 79 | 101730 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-22 23:00 | 14.25 | 80 | 101695 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-23 | 13.75 | 80 | 101680 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-23 01:00 | 13.25 | 80.5 | 101680 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-23 02:00 | 12.75 | 81.5 | 101665 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-23 03:00 | 12.35 | 82.5 | 101635 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-23 04:00 | 12.15 | 84.5 | 101610 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-23 05:00 | 12 | 86 | 101605 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-23 06:00 | 11.8 | 86.5 | 101630 | 100 | 3000 | 14.8845 | 79.3788 | 7.0912 | 0 | 7.2692 | FALSE | FALSE
2025-12-23 07:00 | 12.15 | 86.5 | 101680 | 100 | 3000 | 15.0461 | 79.3435 | 8.2156 | 0 | 7.2692 | FALSE | FALSE
2025-12-23 08:00 | 14.05 | 83 | 101740 | 100 | 3000 | 15.9123 | 77.8788 | 14.2939 | 0 | 7.2692 | FALSE | FALSE
2025-12-23 09:00 | 17.25 | 74 | 101790 | 100 | 3000 | 17.3344 | 74.1608 | 22.7326 | 0 | 7.2692 | FALSE | FALSE
2025-12-23 10:00 | 19.9 | 61.5 | 101780 | 100 | 3000 | 18.4806 | 68.4047 | 26.0225 | 0 | 7.2692 | FALSE | FALSE
2025-12-23 11:00 | 21.3 | 50.5 | 101710 | 100 | 3000 | 19.0784 | 62.7757 | 24.2704 | 0 | 7.2692 | FALSE | FALSE
2025-12-23 12:00 | 22.1 | 44.5 | 101630 | 100 | 3000 | 19.418 | 59.5316 | 23.3105 | 0 | 7.2692 | FALSE | FALSE
2025-12-23 13:00 | 22.55 | 42 | 101555 | 100 | 3000 | 19.6078 | 58.1357 | 23.9498 | 0 | 7.2692 | FALSE | FALSE
2025-12-23 14:00 | 22.65 | 41 | 101500 | 100 | 3000 | 19.6503 | 57.5783 | 24.085 | 0 | 7.2692 | FALSE | FALSE
2025-12-23 15:00 | 22.25 | 47 | 101475 | 100 | 3000 | 19.4789 | 60.914 | 25.2013 | 0 | 7.2692 | FALSE | FALSE
2025-12-23 16:00 | 21 | 59 | 101475 | 100 | 3000 | 18.9476 | 67.2798 | 28.5831 | 0 | 7.2692 | FALSE | FALSE
2025-12-23 17:00 | 19.2 | 67 | 101485 | 100 | 3000 | 18.1798 | 71.1097 | 26.5489 | 0 | 7.2692 | FALSE | FALSE
2025-12-23 18:00 | 17.8 | 71.5 | 101515 | 100 | 3000 | 17.5745 | 73.0914 | 23.5821 | 0 | 7.2692 | FALSE | FALSE
2025-12-23 19:00 | 16.95 | 74.5 | 101560 | 100 | 3000 | 17.203 | 74.3836 | 21.8002 | 0 | 7.2692 | FALSE | FALSE
2025-12-23 20:00 | 16.3 | 76 | 101605 | 100 | 3000 | 16.9168 | 74.9934 | 19.9852 | 0 | 7.2692 | FALSE | FALSE
2025-12-23 21:00 | 15.85 | 77 | 101615 | 100 | 3000 | 16.7175 | 75.4016 | 18.6951 | 0 | 7.2692 | FALSE | FALSE
2025-12-23 22:00 | 15.45 | 78.5 | 101570 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-23 23:00 | 14.9 | 81 | 101525 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-24 | 14.35 | 82.5 | 101505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-24 01:00 | 13.85 | 83.5 | 101495 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-24 02:00 | 13.3 | 84.5 | 101490 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-24 03:00 | 12.8 | 86.5 | 101480 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-24 04:00 | 12.6 | 88 | 101465 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-24 05:00 | 12.45 | 88 | 101475 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-24 06:00 | 12.2 | 87.5 | 101510 | 100 | 3000 | 15.0695 | 79.7594 | 8.8123 | 0 | 7.2692 | FALSE | FALSE
2025-12-24 07:00 | 12.8 | 85 | 101550 | 100 | 3000 | 15.3441 | 78.7299 | 10.1888 | 0 | 7.2692 | FALSE | FALSE
2025-12-24 08:00 | 15.05 | 79 | 101595 | 100 | 3000 | 16.3612 | 76.2319 | 16.4776 | 0 | 7.2692 | FALSE | FALSE
2025-12-24 09:00 | 18.1 | 72 | 101645 | 100 | 3000 | 17.7047 | 73.3573 | 25.0322 | 0 | 7.2692 | FALSE | FALSE
2025-12-24 10:00 | 20.6 | 62.5 | 101640 | 100 | 3000 | 18.7772 | 69.0309 | 29.2667 | 0 | 7.2692 | FALSE | FALSE
2025-12-24 11:00 | 22 | 53.5 | 101550 | 100 | 3000 | 19.3699 | 64.4447 | 28.6929 | 0 | 7.2692 | FALSE | FALSE
2025-12-24 12:00 | 22.7 | 50 | 101445 | 100 | 3000 | 19.6636 | 62.5918 | 28.8016 | 0 | 7.2692 | FALSE | FALSE
2025-12-24 13:00 | 23.15 | 48.5 | 101380 | 100 | 3000 | 19.8509 | 61.7915 | 29.3212 | 0 | 7.2692 | FALSE | FALSE
2025-12-24 14:00 | 23.05 | 49.5 | 101345 | 100 | 3000 | 19.8087 | 62.3508 | 29.6728 | 0 | 7.2692 | FALSE | FALSE
2025-12-24 15:00 | 22.45 | 52.5 | 101330 | 100 | 3000 | 19.5579 | 63.9666 | 29.6169 | 0 | 7.2692 | FALSE | FALSE
2025-12-24 16:00 | 21.35 | 59 | 101335 | 100 | 3000 | 19.0946 | 67.3455 | 29.8798 | 0 | 7.2692 | FALSE | FALSE
2025-12-24 17:00 | 19.8 | 67 | 101345 | 100 | 3000 | 18.4362 | 71.2285 | 28.8732 | 0 | 7.2692 | FALSE | FALSE
2025-12-24 18:00 | 19 | 69.5 | 101365 | 100 | 3000 | 18.0935 | 72.3276 | 27.1856 | 0 | 7.2692 | FALSE | FALSE
2025-12-24 19:00 | 19.05 | 68.5 | 101395 | 100 | 3000 | 18.1151 | 71.8392 | 26.8164 | 0 | 7.2692 | FALSE | FALSE
2025-12-24 20:00 | 18.4 | 71 | 101415 | 100 | 3000 | 17.8347 | 72.9519 | 25.6635 | 0 | 7.2692 | FALSE | FALSE
2025-12-24 21:00 | 17.55 | 74.5 | 101415 | 100 | 3000 | 17.4655 | 74.4845 | 24.1737 | 0 | 7.2692 | FALSE | FALSE
2025-12-24 22:00 | 17 | 77.5 | 101395 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-24 23:00 | 15.9 | 84 | 101355 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-25 | 14.9 | 89 | 101325 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-25 01:00 | 14.45 | 90.5 | 101315 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-25 02:00 | 14.15 | 91.5 | 101300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-25 03:00 | 13.9 | 92.5 | 101295 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-25 04:00 | 14 | 92.5 | 101300 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-25 05:00 | 14.05 | 92.5 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-25 06:00 | 13.85 | 92.5 | 101340 | 100 | 3000 | 15.8247 | 81.8866 | 17.5677 | 0 | 7.2692 | FALSE | FALSE
2025-12-25 07:00 | 14.5 | 90 | 101395 | 100 | 3000 | 16.1171 | 80.9257 | 19.1938 | 0 | 7.2692 | FALSE | FALSE
2025-12-25 08:00 | 16.45 | 84.5 | 101450 | 100 | 3000 | 16.9838 | 78.8833 | 24.7605 | 0 | 7.2692 | FALSE | FALSE
2025-12-25 09:00 | 19.1 | 77.5 | 101495 | 100 | 3000 | 18.1347 | 76.2825 | 32.1221 | 0 | 7.2692 | FALSE | FALSE
2025-12-25 10:00 | 21 | 71 | 101495 | 100 | 3000 | 18.9414 | 73.5837 | 36.1186 | 0 | 7.2692 | FALSE | FALSE
2025-12-25 11:00 | 22.05 | 65 | 101430 | 100 | 3000 | 19.3826 | 70.7171 | 36.5011 | 0 | 7.2692 | FALSE | FALSE
2025-12-25 12:00 | 23.1 | 60 | 101335 | 100 | 3000 | 19.8196 | 68.2633 | 37.2188 | 0 | 7.2692 | FALSE | FALSE
2025-12-25 13:00 | 23.85 | 57 | 101260 | 100 | 3000 | 20.129 | 66.7649 | 37.9577 | 0 | 7.2692 | FALSE | FALSE
2025-12-25 14:00 | 24.1 | 55.5 | 101220 | 100 | 3000 | 20.2323 | 65.9658 | 37.8044 | 0 | 7.2692 | FALSE | FALSE
2025-12-25 15:00 | 23.5 | 59.5 | 101200 | 100 | 3000 | 19.9837 | 68.1064 | 38.4042 | 0 | 7.2692 | FALSE | FALSE
2025-12-25 16:00 | 22.55 | 66 | 101200 | 100 | 3000 | 19.5884 | 71.449 | 39.1576 | 0 | 7.2692 | FALSE | FALSE
2025-12-25 17:00 | 21.4 | 72 | 101215 | 100 | 3000 | 19.108 | 74.2837 | 38.3834 | 0 | 7.2692 | FALSE | FALSE
2025-12-25 18:00 | 20.35 | 76.5 | 101255 | 100 | 3000 | 18.6658 | 76.2359 | 36.7728 | 0 | 7.2692 | FALSE | FALSE
2025-12-25 19:00 | 20.05 | 76.5 | 101290 | 100 | 3000 | 18.5391 | 76.1218 | 35.5098 | 0 | 7.2692 | FALSE | FALSE
2025-12-25 20:00 | 19.65 | 78 | 101315 | 100 | 3000 | 18.3691 | 76.7348 | 34.7079 | 0 | 7.2692 | FALSE | FALSE
2025-12-25 21:00 | 19.35 | 79.5 | 101330 | 100 | 3000 | 18.241 | 77.3759 | 34.3048 | 0 | 7.2692 | FALSE | FALSE
2025-12-25 22:00 | 19.25 | 79.5 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-25 23:00 | 18.9 | 81 | 101275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-26 | 18.5 | 82 | 101270 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-26 01:00 | 18 | 83 | 101265 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-26 02:00 | 17.35 | 85.5 | 101245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-26 03:00 | 16.8 | 89.5 | 101220 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-26 04:00 | 16.5 | 92.5 | 101205 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-26 05:00 | 16.2 | 93 | 101225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-26 06:00 | 15.9 | 93 | 101270 | 100 | 3000 | 16.7421 | 82.5728 | 26.5273 | 0 | 7.2692 | FALSE | FALSE
2025-12-26 07:00 | 16.15 | 91.5 | 101320 | 100 | 3000 | 16.8524 | 81.9737 | 26.8928 | 0 | 7.2692 | FALSE | FALSE
2025-12-26 08:00 | 17.5 | 87 | 101385 | 100 | 3000 | 17.4435 | 80.341 | 30.4762 | 0 | 7.2692 | FALSE | FALSE
2025-12-26 09:00 | 19.35 | 80.5 | 101435 | 100 | 3000 | 18.2407 | 77.8606 | 34.8824 | 0 | 7.2692 | FALSE | FALSE
2025-12-26 10:00 | 21.2 | 73 | 101405 | 100 | 3000 | 19.024 | 74.717 | 38.1978 | 0 | 7.2692 | FALSE | FALSE
2025-12-26 11:00 | 22.8 | 66.5 | 101320 | 100 | 3000 | 19.6907 | 71.8014 | 40.5262 | 0 | 7.2692 | FALSE | FALSE
2025-12-26 12:00 | 23.7 | 61.5 | 101235 | 100 | 3000 | 20.0631 | 69.3057 | 40.6266 | 0 | 7.2692 | FALSE | FALSE
2025-12-26 13:00 | 24.15 | 57.5 | 101165 | 100 | 3000 | 20.2502 | 67.1461 | 39.4637 | 0 | 7.2692 | FALSE | FALSE
2025-12-26 14:00 | 24.2 | 55 | 101105 | 100 | 3000 | 20.2734 | 65.7118 | 37.7986 | 0 | 7.2692 | FALSE | FALSE
2025-12-26 15:00 | 24 | 53.5 | 101065 | 100 | 3000 | 20.194 | 64.8004 | 35.9409 | 0 | 7.2692 | FALSE | FALSE
2025-12-26 16:00 | 23.1 | 56 | 101060 | 100 | 3000 | 19.8234 | 66.0443 | 34.3887 | 0 | 7.2692 | FALSE | FALSE
2025-12-26 17:00 | 21.4 | 63 | 101085 | 100 | 3000 | 19.1133 | 69.5119 | 32.6162 | 0 | 7.2692 | FALSE | FALSE
2025-12-26 18:00 | 20.2 | 68 | 101125 | 100 | 3000 | 18.6058 | 71.8467 | 31.028 | 0 | 7.2692 | FALSE | FALSE
2025-12-26 19:00 | 19.65 | 69.5 | 101175 | 100 | 3000 | 18.3716 | 72.4789 | 29.742 | 0 | 7.2692 | FALSE | FALSE
2025-12-26 20:00 | 19 | 71.5 | 101220 | 100 | 3000 | 18.0931 | 73.3304 | 28.3095 | 0 | 7.2692 | FALSE | FALSE
2025-12-26 21:00 | 18.15 | 77.5 | 101230 | 100 | 3000 | 17.7259 | 76.0515 | 28.1845 | 0 | 7.2692 | FALSE | FALSE
2025-12-26 22:00 | 17.25 | 85 | 101200 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-26 23:00 | 16.5 | 89 | 101165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-27 | 16.4 | 89.5 | 101145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-27 01:00 | 16.35 | 89.5 | 101150 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-27 02:00 | 16 | 90 | 101160 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-27 03:00 | 15.85 | 88.5 | 101135 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-27 04:00 | 15.7 | 87 | 101110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-27 05:00 | 15.25 | 87.5 | 101130 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-27 06:00 | 14.8 | 88 | 101180 | 100 | 3000 | 16.2512 | 80.1463 | 19.5531 | 0 | 7.2692 | FALSE | FALSE
2025-12-27 07:00 | 15.4 | 85.5 | 101235 | 100 | 3000 | 16.5188 | 79.1502 | 20.8869 | 0 | 7.2692 | FALSE | FALSE
2025-12-27 08:00 | 17.5 | 78 | 101295 | 100 | 3000 | 17.4436 | 76.1342 | 25.7966 | 0 | 7.2692 | FALSE | FALSE
2025-12-27 09:00 | 20.35 | 65.5 | 101340 | 100 | 3000 | 18.6702 | 70.5706 | 30.1186 | 0 | 7.2692 | FALSE | FALSE
2025-12-27 10:00 | 22.65 | 54.5 | 101335 | 100 | 3000 | 19.6391 | 65.0979 | 31.7097 | 0 | 7.2692 | FALSE | FALSE
2025-12-27 11:00 | 23.85 | 51.5 | 101265 | 100 | 3000 | 20.1351 | 63.5966 | 33.9499 | 0 | 7.2692 | FALSE | FALSE
2025-12-27 12:00 | 24.5 | 51 | 101155 | 100 | 3000 | 20.3999 | 63.4306 | 35.9243 | 0 | 7.2692 | FALSE | FALSE
2025-12-27 13:00 | 25 | 49 | 101075 | 100 | 3000 | 20.6045 | 62.344 | 36.1914 | 0 | 7.2692 | FALSE | FALSE
2025-12-27 14:00 | 25.2 | 47.5 | 101030 | 100 | 3000 | 20.6871 | 61.4826 | 35.7305 | 0 | 7.2692 | FALSE | FALSE
2025-12-27 15:00 | 25.05 | 47 | 101005 | 100 | 3000 | 20.6275 | 61.1625 | 34.8086 | 0 | 7.2692 | FALSE | FALSE
2025-12-27 16:00 | 24.25 | 52 | 101010 | 100 | 3000 | 20.2973 | 63.9841 | 35.7447 | 0 | 7.2692 | FALSE | FALSE
2025-12-27 17:00 | 22.55 | 62.5 | 101025 | 100 | 3000 | 19.5913 | 69.5371 | 36.7653 | 0 | 7.2692 | FALSE | FALSE
2025-12-27 18:00 | 21.05 | 71.5 | 101070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-27 19:00 | 20.35 | 75.5 | 101130 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-27 20:00 | 19.9 | 76 | 101165 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-27 21:00 | 19.55 | 74 | 101170 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-27 22:00 | 19.2 | 72.5 | 101145 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-27 23:00 | 18.45 | 74.5 | 101110 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 | 17.65 | 76 | 101085 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 01:00 | 17.1 | 77 | 101070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 02:00 | 16.65 | 79.5 | 101055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 03:00 | 16.45 | 83.5 | 101045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 04:00 | 16.35 | 88 | 101025 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 05:00 | 16.05 | 90.5 | 101035 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 06:00 | 15.6 | 92 | 101090 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 07:00 | 16.05 | 88.5 | 101140 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 08:00 | 18.2 | 74 | 101190 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 09:00 | 21.5 | 54.5 | 101240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 10:00 | 24.4 | 42 | 101225 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 11:00 | 26.05 | 37.5 | 101120 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 12:00 | 26.85 | 36 | 100990 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 13:00 | 27.3 | 34 | 100890 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 14:00 | 27.5 | 32.5 | 100820 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 15:00 | 27.35 | 35 | 100770 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 16:00 | 26.7 | 39 | 100755 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 17:00 | 24.95 | 46.5 | 100780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 18:00 | 23.2 | 54 | 100830 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 19:00 | 22.3 | 59 | 100890 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 20:00 | 21.4 | 63.5 | 100935 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 21:00 | 21 | 64 | 100945 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 22:00 | 20.85 | 63.5 | 100925 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-28 23:00 | 20.25 | 64.5 | 100890 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-29 | 20.05 | 63 | 100870 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-29 01:00 | 20.15 | 60.5 | 100845 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-29 02:00 | 20 | 61 | 100805 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-29 03:00 | 20.35 | 62 | 100785 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-29 04:00 | 20.6 | 63 | 100775 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-29 05:00 | 20.6 | 63.5 | 100780 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-29 06:00 | 20.7 | 64 | 100820 | 100 | 3000 | 18.8188 | 69.9223 | 30.5207 | 0 | 7.2692 | FALSE | FALSE
2025-12-29 07:00 | 20.85 | 68 | 100905 | 100 | 3000 | 18.88 | 72.0344 | 33.5973 | 0 | 7.2692 | FALSE | FALSE
2025-12-29 08:00 | 21.85 | 70.5 | 101005 | 100 | 3000 | 19.2959 | 73.6726 | 39.2674 | 0 | 7.2692 | FALSE | FALSE
2025-12-29 09:00 | 23.45 | 66.5 | 101080 | 100 | 3000 | 19.9562 | 72.0784 | 43.1683 | 0 | 7.2692 | FALSE | FALSE
2025-12-29 10:00 | 25.05 | 61 | 101090 | 100 | 3000 | 20.6076 | 69.5242 | 45.6396 | 0 | 7.2692 | FALSE | FALSE
2025-12-29 11:00 | 26.5 | 55.5 | 101015 | 100 | 3000 | 21.1908 | 66.7388 | 47.0117 | 0 | 7.2692 | FALSE | FALSE
2025-12-29 12:00 | 27.5 | 49.5 | 100915 | 100 | 3000 | 21.5939 | 63.2834 | 45.7283 | 0 | 7.2692 | FALSE | FALSE
2025-12-29 13:00 | 27.6 | 46.5 | 100845 | 100 | 3000 | 21.6395 | 61.3782 | 43.4587 | 0 | 7.2692 | FALSE | FALSE
2025-12-29 14:00 | 27 | 49 | 100815 | 100 | 3000 | 21.3996 | 62.8249 | 43.4259 | 0 | 7.2692 | FALSE | FALSE
2025-12-29 15:00 | 26.15 | 53.5 | 100795 | 100 | 3000 | 21.0564 | 65.3946 | 43.9837 | 0 | 7.2692 | FALSE | FALSE
2025-12-29 16:00 | 24.85 | 62.5 | 100800 | 100 | 3000 | 20.5256 | 70.3649 | 45.9386 | 0 | 7.2692 | FALSE | FALSE
2025-12-29 17:00 | 23.55 | 71.5 | 100845 | 100 | 3000 | 19.9916 | 74.9872 | 47.1084 | 0 | 7.2692 | FALSE | FALSE
2025-12-29 18:00 | 23 | 67.5 | 100910 | 100 | 3000 | 19.7718 | 72.4795 | 41.9955 | 0 | 7.2692 | FALSE | FALSE
2025-12-29 19:00 | 22.6 | 63 | 100985 | 100 | 3000 | 19.6115 | 69.832 | 37.2985 | 0 | 7.2692 | FALSE | FALSE
2025-12-29 20:00 | 22 | 67 | 101045 | 100 | 3000 | 19.3605 | 71.8291 | 37.5882 | 0 | 7.2692 | FALSE | FALSE
2025-12-29 21:00 | 21.8 | 67 | 101075 | 100 | 3000 | 19.2775 | 71.7619 | 36.7839 | 0 | 7.2692 | FALSE | FALSE
2025-12-29 22:00 | 21.8 | 64 | 101085 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-29 23:00 | 21.6 | 61 | 101070 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-30 | 21.35 | 59 | 101045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-30 01:00 | 20.95 | 61.5 | 101050 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-30 02:00 | 20.75 | 61.5 | 101055 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-30 03:00 | 21 | 57.5 | 101045 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-30 04:00 | 21.15 | 53 | 101050 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-30 05:00 | 21.05 | 50 | 101095 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-30 06:00 | 20.9 | 47.5 | 101180 | 100 | 3000 | 18.9111 | 61.2581 | 21.4632 | 0 | 7.2692 | FALSE | FALSE
2025-12-30 07:00 | 21 | 44.5 | 101270 | 100 | 3000 | 18.955 | 59.658 | 21.6409 | 0 | 7.2692 | FALSE | FALSE
2025-12-30 08:00 | 21.8 | 40.5 | 101335 | 100 | 3000 | 19.2949 | 57.414 | 22.8342 | 0 | 7.2692 | FALSE | FALSE
2025-12-30 09:00 | 22.9 | 35 | 101380 | 100 | 3000 | 19.7595 | 54.2036 | 24.4485 | 0 | 7.2692 | FALSE | FALSE
2025-12-30 10:00 | 23.75 | 31.5 | 101385 | 100 | 3000 | 20.1156 | 52.0496 | 25.6705 | 0 | 7.2692 | FALSE | FALSE
2025-12-30 11:00 | 23.8 | 32.5 | 101340 | 100 | 3000 | 20.1352 | 52.6224 | 25.7216 | 0 | 7.2692 | FALSE | FALSE
2025-12-30 12:00 | 23.55 | 35 | 101285 | 100 | 3000 | 20.0293 | 54.1083 | 25.3405 | 0 | 7.2692 | FALSE | FALSE
2025-12-30 13:00 | 23.8 | 34.5 | 101240 | 100 | 3000 | 20.1331 | 53.7886 | 25.6817 | 0 | 7.2692 | FALSE | FALSE
2025-12-30 14:00 | 23.85 | 33.5 | 101210 | 100 | 3000 | 20.1548 | 53.2058 | 25.7512 | 0 | 7.2692 | FALSE | FALSE
2025-12-30 15:00 | 23.6 | 35 | 101195 | 100 | 3000 | 20.05 | 54.1104 | 25.3881 | 0 | 7.2692 | FALSE | FALSE
2025-12-30 16:00 | 23.35 | 36.5 | 101195 | 100 | 3000 | 19.9451 | 55.0025 | 25.028 | 0 | 7.2692 | FALSE | FALSE
2025-12-30 17:00 | 22.5 | 43 | 101230 | 100 | 3000 | 19.5862 | 58.7282 | 23.7971 | 0 | 7.2692 | FALSE | FALSE
2025-12-30 18:00 | 21.85 | 47.5 | 101285 | 100 | 3000 | 19.3113 | 61.2102 | 24.1632 | 0 | 7.2692 | FALSE | FALSE
2025-12-30 19:00 | 21.9 | 47 | 101315 | 100 | 3000 | 19.3326 | 60.9348 | 24.0031 | 0 | 7.2692 | FALSE | FALSE
2025-12-30 20:00 | 21.7 | 49.5 | 101330 | 100 | 3000 | 19.2471 | 62.2865 | 24.9733 | 0 | 7.2692 | FALSE | FALSE
2025-12-30 21:00 | 21.45 | 51 | 101355 | 100 | 3000 | 19.1413 | 63.0845 | 25.0865 | 0 | 7.2692 | FALSE | FALSE
2025-12-30 22:00 | 21.35 | 50 | 101370 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-30 23:00 | 21.25 | 48.5 | 101350 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-31 | 21.3 | 48.5 | 101310 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-31 01:00 | 21.35 | 49.5 | 101275 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-31 02:00 | 21.35 | 50 | 101245 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-31 03:00 | 21.35 | 52 | 101235 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-31 04:00 | 20.95 | 55.5 | 101240 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-31 05:00 | 20.25 | 56.5 | 101280 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-31 06:00 | 19.75 | 57.5 | 101355 | 100 | 3000 | 18.4178 | 66.4144 | 23.0738 | 0 | 7.2692 | FALSE | FALSE
2025-12-31 07:00 | 19.7 | 56.5 | 101425 | 100 | 3000 | 18.3967 | 65.8992 | 22.307 | 0 | 7.2692 | FALSE | FALSE
2025-12-31 08:00 | 20.25 | 52 | 101490 | 100 | 3000 | 18.6331 | 63.5936 | 21.5515 | 0 | 7.2692 | FALSE | FALSE
2025-12-31 09:00 | 21.1 | 47 | 101540 | 100 | 3000 | 18.996 | 60.9415 | 21.8331 | 0 | 7.2692 | FALSE | FALSE
2025-12-31 10:00 | 21.75 | 43 | 101550 | 100 | 3000 | 19.2723 | 58.7499 | 22.7971 | 0 | 7.2692 | FALSE | FALSE
2025-12-31 11:00 | 22.2 | 42.5 | 101505 | 100 | 3000 | 19.4613 | 58.4434 | 23.4362 | 0 | 7.2692 | FALSE | FALSE
2025-12-31 12:00 | 22.3 | 43 | 101430 | 100 | 3000 | 19.5027 | 58.7189 | 23.559 | 0 | 7.2692 | FALSE | FALSE
2025-12-31 13:00 | 22.3 | 43 | 101365 | 100 | 3000 | 19.5027 | 58.726 | 23.5441 | 0 | 7.2692 | FALSE | FALSE
2025-12-31 14:00 | 22.25 | 42.5 | 101325 | 100 | 3000 | 19.4822 | 58.459 | 23.4665 | 0 | 7.2692 | FALSE | FALSE
2025-12-31 15:00 | 22 | 43 | 101310 | 100 | 3000 | 19.3772 | 58.7542 | 23.1029 | 0 | 7.2692 | FALSE | FALSE
2025-12-31 16:00 | 21.55 | 45 | 101310 | 100 | 3000 | 19.1869 | 59.8709 | 22.4455 | 0 | 7.2692 | FALSE | FALSE
2025-12-31 17:00 | 20.9 | 48.5 | 101330 | 100 | 3000 | 18.9106 | 61.7673 | 21.5977 | 0 | 7.2692 | FALSE | FALSE
2025-12-31 18:00 | 20.1 | 53.5 | 101385 | 100 | 3000 | 18.5686 | 64.3786 | 21.9312 | 0 | 7.2692 | FALSE | FALSE
2025-12-31 19:00 | 19.1 | 58 | 101440 | 100 | 3000 | 18.1388 | 66.642 | 21.0266 | 0 | 7.2692 | FALSE | FALSE
2025-12-31 20:00 | 18.15 | 61.5 | 101470 | 100 | 3000 | 17.7273 | 68.3442 | 19.5362 | 0 | 7.2692 | FALSE | FALSE
2025-12-31 21:00 | 17.5 | 64 | 101495 | 100 | 3000 | 17.4438 | 69.5303 | 18.4861 | 0 | 7.2692 | FALSE | FALSE
2025-12-31 22:00 | 17.05 | 66.5 | 101505 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE
2025-12-31 23:00 | 16.8 | 68 | 101500 | 0 | 0 |  |  | 0 | 0 | 0 | FALSE | FALSE