IPC Fixture Unit Calculation

IPC 2021 — WSFU → Peak Design Flow (Hunter's Curve)

| Project Information |  |
| --- | --- |
| Project Name | Test Tower |
| Project No. | MCT-2026-MEP-001 |
| Revision | P2 |
| Client | Test Dev |
| Prepared by | Hussein Ragab |
| Checked by | Principal MEP Review |
| Date | 2026-09-02 |

Values in this report are displayed in SI (metric) units.

# 1.  Methodology & Standards

| Reference | Application |
| --- | --- |
| IPC 2021 App. E, Table E103.3(2) | Water-Supply Fixture Units (WSFU) per fixture type. |
| IPC 2021 App. E, Table E103.3(3) | Hunter's Curve — WSFU → Peak Design Flow; separate flush-tank and flush-valve columns (the flush-valve column begins at 5 WSFU = 15 gpm). |
| Interpolation | Piecewise-linear between tabulated points; proportional scaling below the smallest WSFU. |

# 2.  Design Inputs

| Parameter | Value |
| --- | --- |
| System | Cold + Hot + Combined |
| Hunter's Curve | Flush Tank |
| Building | Test Tower — 248 apartments + podium amenities |
| Location / stage | Dubai Marina, Dubai, UAE · RIBA Stage 3 |
| Cold — WSFU / design flow | 1910.2 · 19.8698 L/s |
| Hot — WSFU / design flow | 1590.2 · 17.6087 L/s |
| Combined — WSFU / design flow | 2887.2 · 26.5637 L/s |

# 3.  Design Assumptions

IPC 2021 Table E103.3(2) water-supply fixture units. Residential WCs are flush-tank. Bathroom groups are the packaged private flush-tank row (combined / cold / hot as printed in the library). WC + lavatory + shower are not added on top of a bathroom group.

Hunter's curve is the flush-tank column of IPC 2021 Table E103.3(3). Piecewise-linear interpolation between tabulated points.

Typical-floor count: 88 x 1BR (1 bathroom group), 112 x 2BR (2 bathroom groups), 48 x 3BR (3 bathroom groups). Each apartment also has one private kitchen sink, one residential dishwasher and one 8 lb washing machine.

Podium fixtures (public WCs, urinals, lavatories, commercial kitchen sinks, gym showers, hose bibbs, mop sinks) are added at the building riser total. Diversity is the Hunter curve, not a second factor.

Design flow reported here is the combined (cold + hot) Hunter flow used to size the main. Cold-only and hot-only flows are printed as reference rows.

# 4.  Step-by-Step Calculation

Step 1: Sum water-supply fixture units

Formula: WSFU_total = Sigma (WSFU_unit x quantity)

Substitution: Library row x apartment / podium count, combined column

Result: Combined WSFU = 2887.20

Note: Cold 1910.20 · Hot 1590.20

Step 2: Hunter flush-tank interpolation (IPC Table E103.3(3))

Formula: Q = interpolate(WSFU, flush-tank column)

Substitution: WSFU_combined = 2887.20

Result: Q_combined = 26.5637 L/s (421.04 GPM)

Note: Cold 19.8698 L/s · Hot 17.6087 L/s

# 5.  Results

| Parameter | Value |
| --- | --- |
| Total WSFU | 2887.20 |
| Design flow | 26.5637 L/s |
| (equivalent) | 421.04 GPM |

# 6.  Hunter's Curve

IPC 2021 Table E103.3(3) flush-tank Hunter curve with the cold, hot and combined operating points for Test Tower.

# 7.  Fixture Schedule

| # | Fixture | WSFU / unit | Qty | WSFU total |
| --- | --- | --- | --- | --- |
| 1 | Bathroom Group — Flush Tank (Private) | 3.600 | 456 | 1641.600 |
| 2 | Kitchen Sink (Private/Residential) | 1.400 | 248 | 347.200 |
| 3 | Dishwasher (Residential) | 1.400 | 248 | 347.200 |
| 4 | Washing Machine 8 lb (Private) | 1.400 | 248 | 347.200 |
| 5 | WC — Flush Tank (Public) | 5.000 | 12 | 60.000 |
| 6 | Urinal — Flush Valve ¾" | 5.000 | 8 | 40.000 |
| 7 | Lavatory (Public) | 2.000 | 16 | 32.000 |
| 8 | Kitchen Sink (Commercial) | 4.000 | 4 | 16.000 |
| 9 | Shower (Public / Locker Room) | 4.000 | 6 | 24.000 |
| 10 | Hose Bibb (each) | 2.500 | 8 | 20.000 |
| 11 | Service / Mop Sink | 3.000 | 4 | 12.000 |

# R.  Reference Standards

IPC 2021 Appendix E, Table E103.3(2) — Water-Supply Fixture Units (WSFU) per fixture type (private / public variants, cold / hot / combined).

IPC 2021 Appendix E, Table E103.3(3) — Hunter's Curve, WSFU → Peak Design Flow (GPM); separate flush-tank and flush-valve columns (the flush-valve column begins at 5 WSFU = 15 gpm).

Interpolation between tabulated points is piecewise-linear; below the smallest tabulated WSFU, a proportional scaling from the first point is used.

Library values (fixture WSFU assignments and curve points) may have been user-edited via the in-tool Library editor.  Verify each plugged-in value against the governing edition before issuing for construction.

Library: user-edited overrides are active (file: C:\Users\enghu\AppData\Roaming\MEP Suite\16a\custom_ipc_tables.json).

Engineer of record: Hussein Ragab

IPC Fixture Calculator  ·  IPC 2021 Table E103.3  ·  Water Supply Calculations Suite