## Fixture Schedule
IPC Fixture Unit Demand Schedule
IPC 2021 — WSFU → Peak Design Flow (Hunter's Curve)
Project: |  | Test Tower
Project No.: |  | MCT-2026-MEP-001
Client: |  | Test Dev
Date: |  | 2026-09-02
Prepared by: |  | Hussein Ragab
Checked by: |  | Principal MEP Review
Revision: |  | P2
Hunter's Curve: Flush Tank ¦ Fixture units are IPC WSFU (standards-native — summed, never converted).
# | Fixture | Cold WSFU / unit | Hot WSFU / unit | Combined WSFU / unit | Qty | Σ Cold WSFU | Σ Hot WSFU | Σ Combined WSFU
1 | Bathroom Group — Flush Tank (Private) | 2.7 | 1.5 | 3.6 | 456 | 1231.2 | 684 | 1641.6
2 | Kitchen Sink (Private/Residential) | 1 | 1 | 1.4 | 248 | 248 | 248 | 347.2
3 | Dishwasher (Residential) | 0 | 1.4 | 1.4 | 248 | 0 | 347.2 | 347.2
4 | Washing Machine 8 lb (Private) | 1 | 1 | 1.4 | 248 | 248 | 248 | 347.2
5 | WC — Flush Tank (Public) | 5 | 0 | 5 | 12 | 60 | 0 | 60
6 | Urinal — Flush Valve ¾" | 5 | 0 | 5 | 8 | 40 | 0 | 40
7 | Lavatory (Public) | 1.5 | 1.5 | 2 | 16 | 24 | 24 | 32
8 | Kitchen Sink (Commercial) | 3 | 3 | 4 | 4 | 12 | 12 | 16
9 | Shower (Public / Locker Room) | 3 | 3 | 4 | 6 | 18 | 18 | 24
10 | Hose Bibb (each) | 2.5 | 0 | 2.5 | 8 | 20 | 0 | 20
11 | Service / Mop Sink | 2.25 | 2.25 | 3 | 4 | 9 | 9 | 12
— | TOTAL | — | — | — | — | 1910.2 | 1590.2 | 2887.2
Reference standards
• IPC 2021 Appendix E, Table E103.3(2) — Water-Supply Fixture Units (WSFU) per fixture type (private / public variants, cold / hot / combined).
• IPC 2021 Appendix E, Table E103.3(3) — Hunter's Curve, WSFU → Peak Design Flow (GPM); separate flush-tank and flush-valve columns (the flush-valve column begins at 5 WSFU = 15 gpm).
• Interpolation between tabulated points is piecewise-linear; below the smallest tabulated WSFU, a proportional scaling from the first point is used.
• Library values (fixture WSFU assignments and curve points) may have been user-edited via the in-tool Library editor. Verify each plugged-in value against the governing edition before issuing for construction.

## Design Flow
IPC Fixture Units — Design Flow
Hunter's Curve: Flush Tank
Project: | Test Tower
Project No.: | MCT-2026-MEP-001
Client: | Test Dev
Date: | 2026-09-02
Prepared by: | Hussein Ragab
Checked by: | Principal MEP Review
Revision: | P2
System | Total WSFU | Design flow (L/s) | Design flow (GPM)
Cold | 1910.2 | 19.8698 | 314.94
Hot | 1590.2 | 17.6087 | 279.1
Combined | 2887.2 | 26.5637 | 421.04
Method and citations
• Design flow from the IPC 2021 Table E103.3(3) Hunter's Curve; piecewise-linear interpolation between tabulated points.