Water Treatment Calculation

Hospital water treatment — equipment & pump schedules

Per-application treatment train sizing · catalogue selection where model tables exist, engineered sizing elsewhere

| Project Information |  |
| --- | --- |
| Project Name | Marina Commercial Tower |
| Project No. | MCT-2026-MEP-001 |
| Revision | P2 |
| Client | — |
| Prepared by | Hussein Ragab |
| Checked by | — |
| Date | 2026-10-20 |

Values in this report are displayed in SI (metric) units.  Catalogue and standards-native quantities (motor kW, bar, ppm, grains/ft3, gpm/ft3, lb/ft3, DN, um) are printed as their source publishes them and are not converted.

# 1.  Methodology & Standards

Each application is sized LINE BY LINE on the duty flow of that line — circulation on the storage tank, tank-to-tank transfer, and the boosted outgoing distribution. Where a reverse-osmosis stage is present the pre-treatment is sized on the RO FEED flow (permeate divided by recovery), not on the permeate — sizing pre-treatment on the product flow is a systematic under-size. Equipment is selected from the manufacturers' printed model tables where those exist (multimedia and activated-carbon vessels, cartridge housings, copper-silver flow cells); the remaining items are engineered from the cited design rules. Pump duties are built from the EXTERNAL HEAD stated for that line by the engineer — static lift plus pipe, fittings and valves — plus the summed pressure drop of the treatment stages installed on that same line at their dirty / design values, plus a safety margin, then converted to shaft power and a standard motor frame.

| Reference | Application |
| --- | --- |
| ASPE PEDH Vol 4 (2016) Ch.10 'Water Treatment' | Softener capacity, service rate, bed depth and pressure differential; filter backwash rate, bed expansion and backwash trigger |
| ASPE PEDH Vol 2 Ch.11 'Water Treatment, Conditioning, and Purification' and Ch.12 'Special Waste Drainage Systems' | Reverse-osmosis recovery definition and practical minimum; chlorine residual range; UV germicidal band; copper-silver optimum concentration (Ch.6 p121); acid-waste neutralisation to pH 5 or higher before discharge, a pH between 7.5 and 5 before any public sewer, and the dilution / limestone-basin / chemical-feed methods (Ch.12 p267, p271, p272). AAMI/ANSI dialysis water quality (Table 11-13) is listed for reference only -- its limits are NOT checked by this tool |
| BS EN 60034-1:2010 | Motor rated output (rated shaft power) |
| ASHRAE Fundamentals 2021 SI, Ch.33 Table 2 | Water density at 20 degC (998.20 kg/m3) for pump power |
| Media filters -- typical market data (catalogue-derived envelope) | Multimedia / activated-carbon size ladder; service 20 m/h, backwash 30 m/h. Generic sizes reflecting real market availability -- no vendor selection is implied |
| Project design narrative (Water Treatment Presentation) | Treatment train process order and per-application RO duty |

# 2.  Design Inputs

| Raw water analysis | Value |
| --- | --- |
| Total hardness (as CaCO3) | 150.0 mg/L |
| Feed TDS | 300 ppm |
| UV transmittance | 95 % |

Applications

| Application | Duty · stages per line |
| --- | --- |
| WT01 Domestic water | 2.60 L/s product · 150.00 m³/day · loop: Chlorine · transfer: MMF -> Softener -> Carbon |

Line hydraulics

| Application / line | Duty flow · head |
| --- | --- |
| WT01 Domestic water — Loop | 3.47 L/s (tank turnover) · external head 8.00 m (user input, excludes tool-selected equipment) · stage pressure drop 0.00 bar |
| WT01 Domestic water — Transfer | 2.60 L/s (tank fill time) · external head 8.00 m (user input, excludes tool-selected equipment) · stage pressure drop 2.42 bar |

# 3.  Design Assumptions

Each application's peak flow is coincident with itself; NO diversity is applied between applications — the scheme total is a straight sum.

Pre-treatment upstream of any RO passes the RO feed flow, not the permeate.

The 0.2 um sterilising cartridge and any loop UV are on the PRODUCT side, downstream of the membranes; the pre-RO cartridge is a membrane guard.

Backwash is performed on one vessel at a time — the largest vessel governs the backwash pump.

Duty and standby are provided for every pump and every dosing pump.

Dosing pumps are selected at the top of the printed dose range so they can deliver the whole band; chemical consumption and tank volumes use the design dose.

Reverse-osmosis second-pass reject is sent to drain unless stated otherwise (the conservative case — recycling it would reduce the feed requirement).

AHJ basis

AHJ basis: Chlorine at terminal outlets, minimum 0.2 mg/L (default)

AHJ basis: Chlorine at terminal outlets, maximum 0.5 mg/L (default)

AHJ basis: Water pH maximum for chlorine efficacy 7.6 (default)

Default values - verify against the local AHJ requirement.

# 4.  Step-by-Step Calculation

Step 1: WT01 Domestic water -- circulation loop flow (tank turnover)

Formula: Q_loop = V_tank / t_turnover / 3.6

Substitution: 75.00 m3 / 6.00 h / 3.6 = 3.472 L/s

Result: 3.472 L/s

Note: Loop basis per ruling R1: the loop stages and the circulation pump are sized on the tank-turnover flow, not on any other line's flow.

Step 2: WT01 Domestic water -- transfer line flow (tank fill time)

Formula: Q_transfer = V_tank / t_fill / 3.6

Substitution: 75.00 m3 / 8.00 h / 3.6 = 2.604 L/s

Result: 2.604 L/s

Note: Transfer basis per round-3 ruling R5/R7: the destination tank fills in the stated time; the transfer line's stages, its pressure-drop advisory and the opted-in transfer pump are sized on this flow.

Step 3: Multimedia filter -- model selection

Formula: select smallest model with Q_printed >= Q_unit

Substitution: Generic multimedia FRP 975 mm: 3.60 L/s >= 2.60 L/s

Result: Generic multimedia FRP 975 mm

Note: Service basis 20 m/h; printed catalogue duty. SOURCE: Media filters -- typical market data (catalogue-derived envelope): service 20 m/h, backwash 30 m/h; cross-checked against ASPE PEDH Vol 4 (2016) Ch.10 # 10 backwash 10-20 gpm/ft2, bed expansion >= 50 %

Step 4: Multimedia filter -- filtration area

Formula: A = pi/4 * D^2

Substitution: pi/4 * (0.975 m)^2 = 0.747 m2

Result: 0.747 m2

Step 5: Multimedia filter -- backwash duty

Formula: Q_bw = Q_bw_printed (one vessel at a time)

Substitution: 5.50 L/s per vessel = 5.50 L/s

Result: 5.5 L/s

Note: Backwash 26.5 m/h from the printed duty on D975 mm (10.8 gpm/ft2); envelope basis 30 m/h. ASPE PEDH Vol 4 # 10 prints 10-20 gpm/ft2 with bed expansion >= 50 %. Vessels are backwashed one at a time; the others stay in service.

Step 6: Multimedia filter -- design pressure drop allowance

Formula: dP_design = dP_clean + dP_dirty_rise

Substitution: 0.35 + 0.34 = 0.69 bar

Result: 0.695 bar

Note: Dirty rise = ASPE's printed 5 psi backwash trigger (ASPE PEDH Vol 4 # 10). Clean dP is provisional (X-12).

Step 7: Softener -- raw water hardness

Formula: H_gpg = H_mgl / 17.118

Substitution: 150.0 mg/L as CaCO3 = 8.76 gpg

Result: 8.763 gpg

Note: 1 grain per US gallon = 17.118 mg/L as CaCO3. ASPE PEDH Vol 4 # 10 works in gpg -- kept code-native, never flipped.

Step 8: Softener -- resin volume, hydraulic

Formula: V_hyd = Q / r_service

Substitution: 41.3 gpm / 3 gpm/ft3 = 13.76 ft3

Result: 13.759 ft3

Note: ASPE PEDH Vol 4 # 10 prints service flow 1-5 gpm/ft3 with bed depth 30 in or more.

Step 9: Softener -- working capacity

Formula: C = f(salt dose) [printed ladder, p205]

Substitution: 10 lb salt/ft3 -> 25,000 grains/ft3 (57.2 g CaCO3/L resin)

Result: 25,000 grains/ft3

Note: ASPE PEDH Vol 4 # 10 printed p205: 6 / 10 / 15 lb salt per ft3 -> 20,000 / 25,000 / 30,000 grains/ft3 (linear between rungs). The default 10 lb/ft3 rung is the engineer's choice (X-01).

Step 10: Softener -- hardness load per cycle

Formula: L = V_cycle * H_gpg

Substitution: 39,626 gal * 8.76 gpg = 347,228 grains

Result: 347,228.063 grains

Note: Cycle = 1 day(s) of throughput.

Step 11: Softener -- resin volume, capacity

Formula: V_cap = L / C

Substitution: 347,228 / 25,000 = 13.89 ft3

Result: 13.889 ft3

Step 12: Softener -- governing resin volume

Formula: V_resin = max(V_hyd, V_cap)

Substitution: max(13.76, 13.89) = 13.89 ft3 -- capacity (hardness load) governs

Result: 13.889 ft3

Note: Taking the larger satisfies BOTH of ASPE's constraints (service rate AND exchange capacity) at once.

Step 13: Softener -- vessel diameter

Formula: A = V_resin / d_bed ; D = sqrt(4A / pi)

Substitution: A = 0.393 m3 / 0.762 m = 0.516 m2 -> D = 811 mm

Result: 810.658 mm

Note: Bed depth 30 in (ASPE prints 30-36 in).

Step 14: Softener -- vessel height

Formula: H = d_bed * (1 + freeboard)

Substitution: 0.762 * (1 + 0.50) = 1.14 m

Result: 1.143 m

Note: Freeboard is the space ASPE requires above the mineral for proper expansion during backwashing. Percentage is provisional.

Step 15: Softener -- salt per regeneration

Formula: M_salt = dose * V_resin

Substitution: 10 lb/ft3 * 13.89 ft3 = 138.9 lb = 63.0 kg

Result: 63 kg

Note: Salt dose per ft3 as printed (Vol 4 p205); the default rung is the engineer's choice (X-01). 1 lb = 0.45359237 kg.

Step 16: Softener -- salt storage

Formula: M_store = M_salt * regens/day * storage days

Substitution: 63.00 kg * 1.00/day * 30 days = 1,890 kg

Result: 1,890 kg

Note: 30-day salt storage (provisional, X-03).

Step 17: Softener -- saturated brine per regeneration

Formula: V_brine = M_salt / C_brine

Substitution: 63.0 kg * 1000 g/kg / 312 g/L = 202 L

Result: 201.923 L

Note: Saturated NaCl 26 % w/w (provisional, X-03).

Step 18: Softener -- throughput between regenerations

Formula: V_run = C_total / H_gpg

Substitution: 347,228 grains / 8.76 gpg = 39,626 gal (150.0 m3)

Result: 150 m3

Note: ASPE PEDH Vol 4 # 10 printed method (p203).

Step 19: Activated carbon filter -- model selection

Formula: select smallest model with Q_printed >= Q_unit

Substitution: Generic carbon FRP 975 mm: 3.60 L/s >= 2.60 L/s

Result: Generic carbon FRP 975 mm

Note: Service basis 20 m/h; printed catalogue duty. SOURCE: Media filters -- typical market data (catalogue-derived envelope): service 20 m/h, backwash 30 m/h; cross-checked against ASPE PEDH Vol 4 (2016) Ch.10 # 10 backwash 10-20 gpm/ft2, bed expansion >= 50 %

Step 20: Activated carbon filter -- filtration area

Formula: A = pi/4 * D^2

Substitution: pi/4 * (0.975 m)^2 = 0.747 m2

Result: 0.747 m2

Step 21: Activated carbon filter -- backwash duty

Formula: Q_bw = Q_bw_printed (one vessel at a time)

Substitution: 5.50 L/s per vessel = 5.50 L/s

Result: 5.5 L/s

Note: Backwash 26.5 m/h from the printed duty on D975 mm (10.8 gpm/ft2); envelope basis 30 m/h. ASPE PEDH Vol 4 # 10 prints 10-20 gpm/ft2 with bed expansion >= 50 %. Vessels are backwashed one at a time; the others stay in service.

Step 22: Activated carbon filter -- design pressure drop allowance

Formula: dP_design = dP_clean + dP_dirty_rise

Substitution: 0.35 + 0.34 = 0.69 bar

Result: 0.695 bar

Note: Dirty rise = ASPE's printed 5 psi backwash trigger (ASPE PEDH Vol 4 # 10). Clean dP is provisional (X-12).

Step 23: Chlorine dosing -- design dosing rate

Formula: q_dose = Q * dose / C_stock

Substitution: 12.50 m3/h * 1 g/m3 / 125 g/L = 0.100 L/h

Result: 0.1 L/h

Note: Sodium hypochlorite. ASPE PEDH Vol 2 # 11 prints a residual range of 0.5-1 ppm as generally accepted for typical waters. Chlorine at the terminal outlets (AHJ, default): 0.2-0.5 mg/L; water pH at or below 7.6 for chlorine efficacy (AHJ, default) -- verify against the local AHJ requirement and confirm by sampling at commissioning.

Step 24: Chlorine dosing -- pump selection duty

Formula: q_pump = Q * dose_max / C_stock

Substitution: 12.50 * 2 / 125 = 0.200 L/h

Result: 0.2 L/h

Note: The pump is sized at the printed range MAXIMUM so it can deliver the whole band; consumption and tank use the design dose.

Step 25: Chlorine dosing -- chemical consumption

Formula: V_day = q_dose * t_run

Substitution: 0.100 L/h * 12.0 h/day = 1.20 L/day

Result: 1.2 L/day

Step 26: Chlorine dosing -- stock tank

Formula: V_tank = V_day * storage days -> next standard size

Substitution: 1.20 * 30 = 36.0 L -> 50 L tank

Result: 50 L

Note: 30-day stock (provisional, X-11).

Step 27: WT01 Domestic water -- circulation line external head (user input)

Formula: H_ext = static lift + pipe + fittings + valves

Substitution: 8.00 m entered by the engineer

Result: 8 m

Note: R-2: ONE external-head figure per pumped line. It EXCLUDES every treatment stage the tool selects on the line -- those dirty pressure drops are added next, then the 10 % head margin. A closed circulation circuit carries no net static lift.

Step 28: WT01 Domestic water -- transfer line external head (user input)

Formula: H_ext = static lift + pipe + fittings + valves

Substitution: 8.00 m entered by the engineer

Result: 8 m

Note: R-2: ONE external-head figure per pumped line. It EXCLUDES every treatment stage the tool selects on the line -- those dirty pressure drops are added next, then the 10 % head margin.

Step 29: WT01 Domestic water -- governing backwash duty

Formula: Q_bw = max(backwash flow of each media vessel)

Substitution: Multimedia filter Generic multimedia FRP 975 mm: 5.50 L/s

Result: 5.5 L/s

Note: Backwash is one vessel at a time; the largest vessel governs the pump. Dedicated backwash pump on the per-application opt-in (treated-storage wash). Head basis: the Transfer — tank to tank line's external head 8.00 m plus the media clean pressure drop -- confirm the backwash circuit with the vendor.

Step 30: WT01 Domestic water -- circulation pump -- total head

Formula: H = (H_static + H_pipe + H_equip) * (1 + margin)

Substitution: (0.00 + 8.00 + 0.00) * (1 + 0.10) = 8.80 m

Result: 8.8 m

Note: Head margin 10 % is PROVISIONAL (X-09).

Step 31: WT01 Domestic water -- circulation pump -- hydraulic power

Formula: P_hyd = rho * g * Q * H / 3.6e6

Substitution: 998.20 * 9.80665 * 12.50 * 8.80 / 3.6e6 = 0.299 kW

Result: 0.299 kW

Note: Q in m3/h and H in m; 3.6e6 converts to kW.

Step 32: WT01 Domestic water -- circulation pump -- shaft power

Formula: P_shaft = P_hyd / eta_p

Substitution: 0.299 / 0.65 = 0.460 kW

Result: 0.46 kW

Note: Pump efficiency 0.65 is PROVISIONAL (X-09).

Step 33: WT01 Domestic water -- circulation pump -- electrical input power

Formula: P_elec = P_shaft / eta_m

Substitution: 0.460 / 0.90 = 0.511 kW

Result: 0.511 kW

Note: Electrical input at the duty point -- for energy / tariff estimates only. NOT the motor nameplate, and NOT a cable or breaker basis: those are sized on the motor's rated current.

Step 34: WT01 Domestic water -- circulation pump -- motor frame selection

Formula: frame = next standard kW >= P_shaft * SF

Substitution: 0.460 * 1.15 = 0.529 kW -> 0.55 kW frame

Result: 0.55 kW

Note: Motor frame kW steps per IEC 60072 / EN 50347 typical range (X-13 -- the library holds PREVIEW-only copies of both; ladder reused from the Water Supply tool). Motor rated output = rated shaft power per BS EN 60034-1:2010.

Step 35: WT01 Domestic water -- transfer / feed pump -- equipment pressure drop as head

Formula: H_equip = dP * 1e5 / (rho * g)

Substitution: 2.424 bar * 1e5 / (998.20 * 9.80665) = 24.76 m

Result: 24.765 m

Note: rho 998.2 kg/m3 @ 20 degC per ASHRAE Fundamentals 2021 SI Ch.33 Table 2.

Step 36: WT01 Domestic water -- transfer / feed pump -- total head

Formula: H = (H_static + H_pipe + H_equip) * (1 + margin)

Substitution: (0.00 + 8.00 + 24.76) * (1 + 0.10) = 36.04 m

Result: 36.041 m

Note: Head margin 10 % is PROVISIONAL (X-09).

Step 37: WT01 Domestic water -- transfer / feed pump -- hydraulic power

Formula: P_hyd = rho * g * Q * H / 3.6e6

Substitution: 998.20 * 9.80665 * 9.38 * 36.04 / 3.6e6 = 0.919 kW

Result: 0.919 kW

Note: Q in m3/h and H in m; 3.6e6 converts to kW.

Step 38: WT01 Domestic water -- transfer / feed pump -- shaft power

Formula: P_shaft = P_hyd / eta_p

Substitution: 0.919 / 0.65 = 1.413 kW

Result: 1.413 kW

Note: Pump efficiency 0.65 is PROVISIONAL (X-09).

Step 39: WT01 Domestic water -- transfer / feed pump -- electrical input power

Formula: P_elec = P_shaft / eta_m

Substitution: 1.413 / 0.90 = 1.571 kW

Result: 1.571 kW

Note: Electrical input at the duty point -- for energy / tariff estimates only. NOT the motor nameplate, and NOT a cable or breaker basis: those are sized on the motor's rated current.

Step 40: WT01 Domestic water -- transfer / feed pump -- motor frame selection

Formula: frame = next standard kW >= P_shaft * SF

Substitution: 1.413 * 1.15 = 1.626 kW -> 2.2 kW frame

Result: 2.2 kW

Note: Motor frame kW steps per IEC 60072 / EN 50347 typical range (X-13 -- the library holds PREVIEW-only copies of both; ladder reused from the Water Supply tool). Motor rated output = rated shaft power per BS EN 60034-1:2010.

Step 41: WT01 Domestic water -- backwash pump -- equipment pressure drop as head

Formula: H_equip = dP * 1e5 / (rho * g)

Substitution: 0.350 bar * 1e5 / (998.20 * 9.80665) = 3.58 m

Result: 3.575 m

Note: rho 998.2 kg/m3 @ 20 degC per ASHRAE Fundamentals 2021 SI Ch.33 Table 2.

Step 42: WT01 Domestic water -- backwash pump -- total head

Formula: H = (H_static + H_pipe + H_equip) * (1 + margin)

Substitution: (0.00 + 8.00 + 3.58) * (1 + 0.10) = 12.73 m

Result: 12.733 m

Note: Head margin 10 % is PROVISIONAL (X-09).

Step 43: WT01 Domestic water -- backwash pump -- hydraulic power

Formula: P_hyd = rho * g * Q * H / 3.6e6

Substitution: 998.20 * 9.80665 * 19.80 * 12.73 / 3.6e6 = 0.686 kW

Result: 0.686 kW

Note: Q in m3/h and H in m; 3.6e6 converts to kW.

Step 44: WT01 Domestic water -- backwash pump -- shaft power

Formula: P_shaft = P_hyd / eta_p

Substitution: 0.686 / 0.65 = 1.055 kW

Result: 1.055 kW

Note: Pump efficiency 0.65 is PROVISIONAL (X-09).

Step 45: WT01 Domestic water -- backwash pump -- electrical input power

Formula: P_elec = P_shaft / eta_m

Substitution: 1.055 / 0.90 = 1.172 kW

Result: 1.172 kW

Note: Electrical input at the duty point -- for energy / tariff estimates only. NOT the motor nameplate, and NOT a cable or breaker basis: those are sized on the motor's rated current.

Step 46: WT01 Domestic water -- backwash pump -- motor frame selection

Formula: frame = next standard kW >= P_shaft * SF

Substitution: 1.055 * 1.15 = 1.213 kW -> 1.5 kW frame

Result: 1.5 kW

Note: Motor frame kW steps per IEC 60072 / EN 50347 typical range (X-13 -- the library holds PREVIEW-only copies of both; ladder reused from the Water Supply tool). Motor rated output = rated shaft power per BS EN 60034-1:2010.

Step 47: Scheme -- total product flow

Formula: Q_total = sum(application product flows)

Substitution: 2.60 = 2.60 L/s

Result: 2.604 L/s

Note: Simple sum -- NO diversity applied between applications. Apply a diversity factor on the input side if the peaks do not coincide. The product flow is the treated-water demand on an RO application and the delivering line's flow otherwise; a drain-only application contributes nothing.

# 5.  Results

| Scheme summary | Value |
| --- | --- |
| Applications | 1 |
| Total product flow | 2.60 L/s |
| Total pre-treatment flow | 2.60 L/s |
| Total daily volume | 150.00 m³ |
| Equipment items | 4 |
| Pumps (duty) | 3 |
| Installed motor power (duty) | 4.25 kW |

WT01 Domestic water

| Duty | Value |
| --- | --- |
| Product flow | 2.60 L/s |
| Pre-treatment flow | 2.60 L/s |
| Daily volume | 150.00 m³ |
| Transfer-line pressure drop | 2.42 bar |

# 7.  Equipment Schedule

| Application / stage (line) | Selection & details (SI) |
| --- | --- |
| WT01 Domestic water — Multimedia / sand filter [Transfer] | Generic multimedia FRP 975 mm · FRP, D975 x H2150 mm, DN50, backwash 5.5 L/s, 1 off |
| WT01 Domestic water — Softener [Transfer] | Engineered · resin 13.9 ft3, vessel D811 mm x H1.14 m, salt 63 kg/regen |
| WT01 Domestic water — Activated carbon filter [Transfer] | Generic carbon FRP 975 mm · FRP, D975 x H2150 mm, DN50, backwash 5.5 L/s, 1 off |
| WT01 Domestic water — Chlorine dosing [Loop] | Engineered · 0.20 L/h pump, 50 L tank, dose 1 ppm, Duty + standby |

Pump Schedule

| Application / duty | Selection |
| --- | --- |
| WT01 Domestic water — circulation pump | 3.47 L/s @ 8.80 m · shaft 0.460 kW · motor 0.55 kW · 2-pole 3000 rpm · Duty + standby |
| WT01 Domestic water — transfer / feed pump | 2.60 L/s @ 36.04 m · shaft 1.413 kW · motor 2.2 kW · 2-pole 3000 rpm · Duty + standby |
| WT01 Domestic water — backwash pump | 5.50 L/s @ 12.73 m · shaft 1.055 kW · motor 1.5 kW · 2-pole 3000 rpm · Duty + standby |

Provisional values applied

The values below have NO primary source in the reference library. They are documented engineering defaults, signed off for use on this project and disclosed here. Supplying the governing document for any of them closes it.

| Ref. | Provisional value |
| --- | --- |
| X-01 | Softener salt-dose DEFAULT rung (10 lb/ft3 -> 25,000 gr/ft3): engineer choice; the 6/10/15 lb/ft3 pairing itself is printed (ASPE PEDH Vol 4 p205) |
| X-03 | Brine saturation and salt storage days |
| X-09 | Pump efficiency, motor efficiency, service factor, head margin |
| X-11 | Chemical stock concentrations and tank storage days |
| X-12 | Filter clean pressure drop |
| X-13 | Standard motor kW ladder (library holds PREVIEW-only IEC 60072-1 / EN 50347) |

# R.  Reference Standards

ASPE PEDH Vol 4 (2016) Ch.10 'Water Treatment' — Softener capacity, service rate, bed depth and pressure differential; filter backwash rate, bed expansion and backwash trigger

ASPE PEDH Vol 2 Ch.11 'Water Treatment, Conditioning, and Purification' and Ch.12 'Special Waste Drainage Systems' — Reverse-osmosis recovery definition and practical minimum; chlorine residual range; UV germicidal band; copper-silver optimum concentration (Ch.6 p121); acid-waste neutralisation to pH 5 or higher before discharge, a pH between 7.5 and 5 before any public sewer, and the dilution / limestone-basin / chemical-feed methods (Ch.12 p267, p271, p272). AAMI/ANSI dialysis water quality (Table 11-13) is listed for reference only -- its limits are NOT checked by this tool

BS EN 60034-1:2010 — Motor rated output (rated shaft power)

ASHRAE Fundamentals 2021 SI, Ch.33 Table 2 — Water density at 20 degC (998.20 kg/m3) for pump power

Media filters -- typical market data (catalogue-derived envelope) — Multimedia / activated-carbon size ladder; service 20 m/h, backwash 30 m/h. Generic sizes reflecting real market availability -- no vendor selection is implied

Project design narrative (Water Treatment Presentation) — Treatment train process order and per-application RO duty

Engineer of record: Hussein Ragab