## Equipment Schedule
Water Treatment — Schedules
Main equipment — catalogue selection where model tables exist, engineered sizing elsewhere
Project: |  | Marina Commercial Tower
Project No.: |  | MCT-2026-MEP-001
Client: |  | -
Date: |  | 2026-10-20
Prepared by: |  | Hussein Ragab
Checked by: |  | -
Revision: |  | P2
Application | Stage | Model / selection | Flow (L/s) | Line | Details (SI)
WT01 Domestic water | Multimedia / sand filter | Generic multimedia FRP 975 mm | 2.6042 | Transfer | FRP, D975 x H2150 mm, DN50, backwash 5.5 L/s, 1 off
WT01 Domestic water | Softener | Engineered | 2.6042 | Transfer | resin 13.9 ft3, vessel D811 mm x H1.14 m, salt 63 kg/regen
WT01 Domestic water | Activated carbon filter | Generic carbon FRP 975 mm | 2.6042 | Transfer | FRP, D975 x H2150 mm, DN50, backwash 5.5 L/s, 1 off
WT01 Domestic water | Chlorine dosing | Engineered | 3.4722 | Loop | 0.20 L/h pump, 50 L tank, dose 1 ppm, Duty + standby

## Pump Schedule
Water Treatment — Schedules
Circulation / backwash / RO feed & high-pressure pumps — duty and standby
Project: |  | Marina Commercial Tower
Project No.: |  | MCT-2026-MEP-001
Client: |  | -
Date: |  | 2026-10-20
Prepared by: |  | Hussein Ragab
Checked by: |  | -
Revision: |  | P2
Application | Duty | Flow (L/s) | Head (m) | Shaft power (kW) | Motor (kW) | Poles | Speed (rpm) | Arrangement
WT01 Domestic water | circulation pump | 3.4722 | 8.8 | 0.46017 | 0.55 | 2 | 3000 | Duty + standby
WT01 Domestic water | transfer / feed pump | 2.6042 | 36.0411 | 1.4135 | 2.2 | 2 | 3000 | Duty + standby
WT01 Domestic water | backwash pump | 5.5 | 12.733 | 1.0547 | 1.5 | 2 | 3000 | Duty + standby
TOTAL — 3 duty pumps |  |  |  |  | 4.25 |  |  | Duty only; add standby for the installed total

## Design Basis
Water Treatment — Schedules
Reference standards engaged and provisional values applied on this calculation
Project: | Marina Commercial Tower
Project No.: | MCT-2026-MEP-001
Client: | -
Date: | 2026-10-20
Prepared by: | Hussein Ragab
Checked by: | -
Revision: | P2
REFERENCE STANDARDS ENGAGED
Reference | Application
ASPE PEDH Vol 4 (2016) Ch.10 'Water Treatment' | Softener capacity, service rate, bed depth and pressure differential; filter backwash rate, bed expansion and backwash trigger
ASPE PEDH Vol 2 Ch.11 'Water Treatment, Conditioning, and Purification' and Ch.12 'Special Waste Drainage Systems' | Reverse-osmosis recovery definition and practical minimum; chlorine residual range; UV germicidal band; copper-silver optimum concentration (Ch.6 p121); acid-waste neutralisation to pH 5 or higher before discharge, a pH between 7.5 and 5 before any public sewer, and the dilution / limestone-basin / chemical-feed methods (Ch.12 p267, p271, p272). AAMI/ANSI dialysis water quality (Table 11-13) is listed for reference only -- its limits are NOT checked by this tool
BS EN 60034-1:2010 | Motor rated output (rated shaft power)
ASHRAE Fundamentals 2021 SI, Ch.33 Table 2 | Water density at 20 degC (998.20 kg/m3) for pump power
Media filters -- typical market data (catalogue-derived envelope) | Multimedia / activated-carbon size ladder; service 20 m/h, backwash 30 m/h. Generic sizes reflecting real market availability -- no vendor selection is implied
Project design narrative (Water Treatment Presentation) | Treatment train process order and per-application RO duty
PROVISIONAL VALUES APPLIED
No primary source in the reference library; documented engineering defaults, signed off and disclosed.
Value | Basis / disclosure
X-01 | Softener salt-dose DEFAULT rung (10 lb/ft3 -> 25,000 gr/ft3): engineer choice; the 6/10/15 lb/ft3 pairing itself is printed (ASPE PEDH Vol 4 p205)
X-03 | Brine saturation and salt storage days
X-09 | Pump efficiency, motor efficiency, service factor, head margin
X-11 | Chemical stock concentrations and tank storage days
X-12 | Filter clean pressure drop
X-13 | Standard motor kW ladder (library holds PREVIEW-only IEC 60072-1 / EN 50347)
AHJ BASIS
AHJ basis: Chlorine at terminal outlets, minimum 0.2 mg/L (default)
AHJ basis: Chlorine at terminal outlets, maximum 0.5 mg/L (default)
AHJ basis: Water pH maximum for chlorine efficacy 7.6 (default)
Default values - verify against the local AHJ requirement.